## hl1986to2001Fields
Hazardous Liquid Pipeline Accident Reports for 1986 - 2001 (PHMSA Form 7000-1 Rev.04-85) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | Date | Data as of date | Not on the form
SIGNIFICANT | Varchar2 | Identify if record meets the significant criteria or not: If there was fatality, injury, fire, explosion, total property damage $50K or more in 1984 dollars, non-HVL loss >= 50bbls, HVL loss >= 5bbls, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | VARCHAR2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury then SERIOUS = ‘YES’ else SERIOUS = ’NO’. | Not on the form
RPTID | Number | PHMSA DOT assigned unique identifier for report | Top of first page
DOR | Varchar2 | Date the report was received at DOT | Top of first page
OPID | Number | Operator's OPS-issued Operator Identification number | Part A - Operator information
NAME | Varchar2 | Operator Name | Part A - Operator information
INTER | Varchar2 | Is pipeline interstate (Yes/No/Null) | Part A - Operator information
IDATE | Date | Date accident occurred | Part B - Time and Location of accident
DTHH | Number | Time accident occurred (24 hour clock) | Part B - Time and Location of accident
ACSTATE | Varchar2 | Location of accident - State | Part B - Time and Location of accident
ACCOUNTY | Varchar2 | Location of accident - County | Part B - Time and Location of accident
ACCITY | Varchar2 | Location of accident - City | Part B - Time and Location of accident
OFFSHORE | Varchar2 | Offshore accident (Yes/No) | Part B - Time and Location of accident
COOR | Varchar2 | Offshore coordinates | Part B - Time and Location of accident
IFED | Varchar2 | Accident occurred on Federal land (Y/N) | Part B - Time and Location of accident
SPLOC | Varchar2 | Description of the Specific location were accident occurred | Part B - Time and Location of accident
TELRN | Varchar2 | Report number of matching NRC telephonic report | Not on the form
CSYS | Varchar2 | Part of system involved; Line Pipe, Tank Farm, Pump Station | Part C - Origin of release of liquid or vapor
ORGLK | Varchar2 | Item involved; Pipe, Valve, Scraper Trap, Pump, Welding Fitting, Girth, Tank, Bolted Fitting, Longitudinal Weld, Other | Part C - Origin of release of liquid or vapor
ORGLO | Varchar2 | Text describing Other for the ORGLK field | Part C - Origin of release of liquid or vapor
ITMYR | Number | Year item installed | Part C - Origin of release of liquid or vapor
CAUSE | Varchar2 | Apparent Cause of accident | Part D - Cause of accident
CAUSO | Varchar2 | Text describing Other for the CAUSO field | Part D - Cause of accident
MAP_CAUSE | Varchar2 | Cause by PHMSA for 20 year accident trending | Not on the form
MAP_SUBCAUSE | Varchar2 | SubCause by PHMSA for 20 year accident trending | Not on the form
TFAT | Number | Total number of fatalities | Part E - Death and injury
EFAT | Number | Number of operator employee fatalities | Part E - Death and injury
NFAT | Number | Number of non-employee fatalities | Part E - Death and injury
TINJ | Number | Total number of injuries | Part E - Death and injury
EINJ | Number | Number of operator employees injured | Part E - Death and injury
NINJ | Number | Number of non-employees injured | Part E - Death and injury
TOTAL_COST | Number | Total Property Damage | Part F - Estimated total property damage
TOTAL_COST_IN84 | Number | Converted Property Damage to 1984 dollars | Not on the form
TOTAL_COST_CURRENT | Number | Converted Property Damage to Current Year dollars | Not on the form
COMM | Varchar2 | Name of commodity spilled | Part G - Commodity spilled
CLASS | Varchar2 | Classification of commodity spilled; Petroleum/Petroleum product (1), HVL (2), Non-HVL (3) | Part G - Commodity spilled
LOSS | Number | Estimated amount of barrels spilled | Part G - Commodity spilled
RECOV | Number | Estimated number of barrels recovered | Part G - Commodity spilled
FIRE | Varchar2 | Was there a Fire | Part G - Commodity spilled
EXP | Varchar2 | Was there an explosion | Part G - Commodity spilled
NMDIA | Number | Nominal Diameter (inches) | Part H - Occurred in line pipe
THK | Number | Wall thickness (inches) | Part H - Occurred in line pipe
SMYS | Number | Maximum yield strength of systems (psi) | Part H - Occurred in line pipe
JNT | Varchar2 | Type of joint; Welded, Flanged, Threaded, Coupled, Other | Part H - Occurred in line pipe
GRND | Varchar2 | Level of pipe; Below ground, Above ground | Part H - Occurred in line pipe
DSPRS | Number | Maximum operating pressure (psig) | Part H - Occurred in line pipe
ACPRS | Number | Pressure at time and location of accident (psig) | Part H - Occurred in line pipe
PRTST | Varchar2 | Had there been a pressure test on the system | Part H - Occurred in line pipe
DUR | Number | Duration of test (hrs) | Part H - Occurred in line pipe
MXPRS | Number | Maximum test pressure (psig) | Part H - Occurred in line pipe
TSTMM | Number | Month of latest test | Part H - Occurred in line pipe
TSTYY | Number | Year of latest test | Part H - Occurred in line pipe
CORLC | Varchar2 | Location of corrosion; Internal, External | Part I - Caused by corrosion
FACTD | Varchar2 | Was the facility coated | Part I - Caused by corrosion
FACAT | Varchar2 | Was the facility under cathodic protection | Part I - Caused by corrosion
CORR | Varchar2 | Type of corrosion; Galvanic, Other | Part I - Caused by corrosion
CORRO | Varchar2 | Text describing Other for the CORR field | Part I - Caused by corrosion
CAULK | Varchar2 | Cause of outside force damage | Part J - Caused by outside force
CAULO | Varchar2 | Text describing Other for the CAULK field | Part J - Caused by outside force
PREVT | Varchar2 | Was a damage prevention program in effect | Part J - Caused by outside force
ONECL | Varchar2 | Was the program "one-call" | Part J - Caused by outside force
ONEOT | Varchar2 | Text describing Other for the ONECL field | Part J - Caused by outside force
EXCAL | Varchar2 | Did excavator call | Part J - Caused by outside force
TMPMK | Varchar2 | Was pipeline location temporarily marked for the excavator | Part J - Caused by outside force
PNAME | Varchar2 | accident Report Prepared by | Name and title of operator official filing report
PHONE | Varchar2 | Preparer's telephone number | Name and title of operator official filing report
NARRATIVE | Varchar2 | Narrative description of factors contributing to the accident | Part K

## hl1986to2001
DATAFILE_AS_OF | SIGNIFICANT | SERIOUS | RPTID | DOR | OPID | NAME | INTER | IDATE | DTHH | ACSTATE | ACCOUNTY | ACCITY | OFFSHORE | COOR | IFED | SPLOC | TELRN | CSYS | ORGLK | ORGLO | ITMYR | CAUSE | CAUSO | MAP_CAUSE | MAP_SUBCAUSE | TFAT | EFAT | NFAT | TINJ | EINJ | NINJ | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | COMM | CLASS | LOSS | RECOV | FIRE | EXP | NMDIA | THK | SMYS | JNT | GRND | DSPRS | ACPRS | PRTST | DUR | MXPRS | TSTMM | TSTYY | CORLC | FACTD | FACAT | CORR | CORRO | CAULK | CAULO | PREVT | ONECL | ONEOT | EXCAL | TMPMK | PNAME | PHONE | NARRATIVE
2017-09-29 08:50 | YES | NO | 19860003 |  | 22907 | WYCO PIPE LINE CO | YES | 1986-01-06 | 1600 | CO | EL PASO |  | NO |  | NO | EAST OF COLORADO SPRINGS APPROX 8 MI SEC 9 T 15-S R65W NW1/4 |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 57000 | 53939.2692 | 108817.2928 | GASOLINE | 3 | 1175 | 4 | NO | NO | 6 | 0.19 | 2383 | WELDED |  | 1440 | 800 | YES | 24 | 1910 | 9 | 66 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | CALL FOR LOCATE | NO | YES | H C OLIVER - AREA MGR DUPONT OPER | 3038304778
2017-09-29 08:50 | YES | NO | 19860005 |  | 18194 | SEMINOLE PIPELINE CO | YES | 1986-01-13 | 1022 | TX | CONCHO |  | NO |  | YES | RIVERSIDE RANCH CORP 144-TX-CO-12 MAP # 9008-AL-45 STATION 11482+85 |  | PUMPING STATION | NO DATA |  | 1982 | OTHER | PUMP SEAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1419.4545 | 2863.613 | NATURAL GAS LIQUID | 2 | 50 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S F ISAACS - PRES | 9185811800
2017-09-29 08:50 | YES | NO | 19860027 |  | 12628 | MOBIL PIPELINE CO | Null | 1986-01-30 | 600 | TX | CALDWELL | LULING | NO |  | NO | MOBIL PIPE LINE COMPANY TANK FARM ON HWY 90 AT EAST CITY LIMITS OF LULING, TX. |  | TANK FARM | TANK |  | 1963 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 400 | 350 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT OPERATIONS | 2146582226 | CRUDE OIL WAS DISCOVERED LEAKING FROM THE BOTTOM OF TANK NO. 2852 AT 0600 ON JANUARY 30, 1986. THE TANK WAS IMMEDIATELY TAKEN OUT OF SERVICE AND PUMPED DOWN, WHICH STOPPED THE LEAK. THE ESCAPED CRUDE OIL, WHICH WAS CONTAINED IN THE FIRE WALL, WAS PICKED UP AND RETURNED TO THE PIPELINE SYSTEM. THE BOTTOM OF THIS TANK WAS EPOXY COATED AT THE TIME IT WAS CONSTRUCTED IN 1963. TANKNO. 2652 WILL BE CLEANED, GAS FREED AND TAKEN OUT OF SERVICE.
2017-09-29 08:50 | YES | NO | 19860028 |  | 12628 | MOBIL PIPELINE CO | NO | 1986-01-15 | 1543 | TX | JASPER |  | NO |  | NO | FORM VIDOR, TEXAS, TAKE 105 NORTH APPROXIMATELY 8-10 MILES, TURN RIGHT ON GIST ROAD TO MOBIL PIPE LINE RIGTHS-OF-WAY, ACCIDENT WAS APPROXIMATELY 200 YARDS NORTH |  | LINE PIPE | PIPE |  | 1926 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 164 | 87 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AERIAL SURVEILLANCE, PIPE | NO | NO | D.L. DENNARD, VICE PRESIDENT OPERATIONS | 2146582226 | A CONTRACTOR WAS GRADING A LOGGING ROAD FOR THE KIRBY LUMBER COMPANY WITH A DOZER WHEN HE STRUCK AND RUPTURED THE 8" PRODUCTS PIPELINE. THERUPTURE WAS 8 INCHES LONG AND 4 INCHES WIDE. MOBIL PIPE LINE HAD NOT BEEN NOTIFIED THAT THE DOZER WOULD BE WORKING NEAR OUR PIPELINE. THE PIPELINE WAS MARKED AT GIST ROAD, 200 YARDS FROM THE ACCIDENT SITE. THE RIGHT-OF-WAY WAS CLEARED IN THE AREA WHERE THE DOZER STRUCK THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19860029 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-02-07 | 1400 | TX |  |  | NO |  | NO | SE 1/4, SW 1/4, SECTION 890, BLOCK D, JOHN H. GIBSON SURVEY ONE MILE EAST OF DENVER CITY ON FARM ROAD P-15 WASSON HOBBS 6-INCH. |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 200 | 150 | NO | NO | 7 | 0.28 | 25000 | WELDED |  | 0 | 400 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.J. EICHLER, MANAGER REGULATIONS & MAINT. STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19860030 |  | 18273 | SHELL PIPE LINE CORP | NO | 1986-01-30 | 1930 | TX | FORT BEND | KATY | NO |  | NO | 3700 FEET SOUTH SOUTHWEST OF M.P. 409 CINCO RANCH VENTURE AREA HOPE-HOUSTON 10-INCH PIPELINE, W.M. WHELESS SURVEY |  | LINE PIPE | PIPE |  | 1955 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 3000 | 2999 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 700 | 111 | YES | 12 | 800 | 0 | 55 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.J. EICHLER, MGR., REGULATIONS & MAINT STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19860031 |  | 18718 | SUN PIPELINE CO | YES | 1986-01-31 | 1500 | NJ | MERCER | WEST WINDSOR | NO |  | NO | 4,484 FEET SOUTH OF ALEXANDER ROAD, WEST WINDSOR TOWNSHIP, MERCER SOUNTY, NEW JERSEY. PARALLEL AND ADJACENT TO THE DELAWARE AND RAITAN CANAL. |  | LINE PIPE | PIPE |  | 1956 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 3589 | 0 | YES | YES | 14 | 0.25 | 52000 | WELDED |  | 1200 | 1163 | YES | 51 | 1520 | 0 | 56 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AERIAL PATROL | NO | YES | CLARENCE J. YABLONSKI, MGR. | 2159642523 | IT APPEARS PIPE WAS DAMAGED BY THIRD PARTY. UNDER INVESTIGATION. UNLEADED REGULAR GASOLINE. MR. RON LINDSEY, SUN PIPE LINE COMPANY FOREMAN,WAS NOTIFIED AT 1526 ON JANUARY 31, 1986, BY J. EDWARDS OF CANAL POINTE ASSOCIATION, PRINCETOWN, NJ, THAT THERE WAS A LEAK IN THE PIPE LINE SOUTH OF ALEXANDER ROAD IN THE AREA OF WEST CARNEGIE BOULEVARD. UPON ARRIVING AT THE SITE, MR. LINDSEY OBSERVED AN APPROXIMATELY 3-FOOT GASH ON TOP OF THE PIPE LINE. GASOLINE HAD ENTERED THE DELAWARE AND RARITAN CANAL AND SUBSEQUENTLY WAS CONTAINED BY SPILL BOOMS. AT APPROXIMATELY 2001, 1/31/86, A FIRE AND EXPLOSION OCCURRED DOWNSTREAM IN THE VICINITY OF THE ELIZABETHTOWN WATER COMPANY PUMPING STATION. THE FIRE ON THE CANAL ICE WAS ALLOWED TO BURN ITSELF OUT DURING THE NIGHT. FIREMEN FROM VARIOUS LOCAL FIRE COMPANIES WERE AT THE SCENE DURING THE TIME OF THE LEAK, FIRE AND REPAIR OF THE PIPE LINE.
2017-09-29 08:50 | YES | NO | 19860032 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1986-02-07 | 600 | TX | HUTCHINSON |  | NO |  | NO | LINE BP - BEAVER - BORGER, MP 48-03+31, SEC.22, BLK. M-25, T&CRR SURVEY |  | LINE PIPE | PIPE |  | 1930 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1300 | 212 | NO | NO | 8 | 0.28 | 30000 | WELDED |  | 1200 | 1245 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, VICE PRESIDENT | 9186614721 | LINE WAS ACCIDENTLY BLOCKED IN AND LINE FAILED WHEN THE PRESSURE REACHED 1220 PSIG AT BEAVER STATION.
2017-09-29 08:50 | YES | NO | 19860033 |  | 9175 | JAYHAWK PIPELINE CORP | YES | 1986-01-30 | 1045 | KS | HASKELL |  | NO |  | NO | NE/4 SECTION 25, T29S, R33W APPROXIMATELY 2 1/2 MILES NW OF SUBLETTE, KS - WHEAT FIELD. |  | LINE PIPE | NO DATA |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 970 | 820 | NO | NO | 7 | 0.19 | 35000 | WELDED |  | 800 | 300 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | WARNING SIGNS | NO | NO | DENNIS E. SMITH, PRESIDENT | 3162679669 | APPROXIMATELY 1045 JANUARY 30, 1986 A CONTRACT DOZER DIGGING A PIT FOR A NEW OIL WELL LOCATION SEVERED JAYHAWK'S 6" PIPELINE 2 1/2 MILES NORTHWEST OF SUBLETTE, KS. AN EMPLOYEE WITH THE DRILLING COMPANY HAD ANOTHER PARTYNOTIFY JAYHAWK OF THE ACCIDENT AT 1100. A JAYHAWK EMPLOYEE AT UPSTREAM PUMP STATION HAD NOTICED THE PRESSURE DROP AND WAS SHUTTING DOWN THE LINE WHEN NOTIFIED OF THE ACCIDENT. THE OIL SPILL AND DRAINAGE FROM THE PIPE LINE WAS CONTAINED IN THE PIT THAT WAS BEING DUG AT THE TIME OF THE ACCIDENT. 820 BARRELS WERE RECOVERED WITH AN ESTIMATED 150 BARRELS SOAKED INTO THE LOOSE SOIL IN THE PIT AREA. DAMAGED PIPE WAS REMOVED AND A REPLACEMENT SECTION ON 6 58" O.D., .188, 5L GR. B, 50' 1/2" PRE-TESTED PIPE WAS INSTALLED ON JANUARY 31, 1986. THE LINE WAS BACK IN OPERATION AT 1250. JAYHAWK PIPE LINE MARKERS WERE ON EACH SIDE OF COUNTY ROAD SOME 1,100 FEET NORTH OF ACCIDENT.WARNING -ROAD CROSSING SIGNS-PASS OUT LITERATURE.
2017-09-29 08:50 | YES | NO | 19860034 |  | 22855 | WOOD RIVER PIPELINE CO | YES | 1986-02-10 | 1430 | MN | DAKOTA | INVER GROVE HEIGHTS | NO |  | NO | MAP ENCLOSED |  | LINE PIPE | GIRTH |  | 1986 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2838.9089 | 5727.2259 | CRUDE OIL | 2 | 300 | 200 | NO | NO | 18 | 0.25 | 0 | WELDED |  | 1440 | 250 | YES | 8 | 1581 | 0 | 77 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.H. KLEIS, MANAGER | 6124592424 | INSTALLED CROSSOVER VALVES FROM 18" TO 16" LINES WEEK OF JANUARY 10, 1986. ALL WELDS WERE RADIOGRAPHICALLY INSPECTED AND FOUND SATISFACTORY. WELD W-49 LET LOOSE.
2017-09-29 08:50 | YES | NO | 19860035 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1986-02-10 | 1550 | CA | KERN |  | NO |  | NO | SKETCH ATTACHED |  | LINE PIPE | PIPE |  | 1924 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 47315.1484 | 95453.7657 | CRUDE OIL | 1 | 500 | 110 | NO | NO | 10 | 0.37 | 2044 | WELDED |  | 540 | 260 | YES | 8 | 680 | 7 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | R.B. KUPREWICZ, VICE PRESIDENT OPERATIONS | 2134289000 | FARM EQUIPMENT OPERATOR RIPPING FIELD HIT PIPELINE PUNCTURING LINE. EQUIPMENT OPERATOR WAS MADE AWARE OF PIPELINE BY HIS FOREMAN. THE AREA OVER THE PIPELINE HAD BEEN MARKED BY THE FOREMAN NOT TO BE PLOWED. EQUIPMENT OPERATOR DID NOT FOLLOW INSTRUCTIONS.
2017-09-29 08:50 | YES | NO | 19860036 |  | 13131 | CONOCO INC | NO | 1986-02-03 | 1045 | LA |  |  | YES | SHIP SHOAL BLOCK 113 1400 | NO | PIPELINE SEGMENT NO.580 6 5/8" OIL AND GAS LINE 74,975' IN LENGTH RUNNING FROM SS-94A PLATFORM TO SS-145B PLATFORM. THE LOCATION OF THE SPILL WASN IN THE NWEST. |  | NO DATA | NO DATA | PIPELINE WAS TORN IN HALF | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45453 | 43012.3088 | 86773.2002 | CRUDE OIL | 1 | 119 | 0 | NO | NO | 7 | 0.28 | 0 | WELDED |  | 1000 | 300 | YES | 2 | 1000 | 11 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | CAUSE UNKNOWN | Null | NO DATA |  | Null | Null | D.L. BYERS, COORDINATOR | 3182365078 | ON JAN 20, 1986 PURGING OPERATIONS BEGAN ON THE 6 5/8" OIL AND GAS LINE RUNNING FROM SS-94A TO SS-145B, IN PREPARATION TO REMOVE PRODUCTIONEQUIPMENT AND ABANDON THE PLATFORM. APPROX. 2470 BBL. OF WATER WERRE PUMPED FROM SS-94A WITHOUT RETURNS AT SS-158A (PUMPED TO SS-158A BECAUSE SS-145B COULD NOTHANDLE THE FLUID). THE LINE WAS BEING FLOWN DAILY LOOKING FOR EVIDENCE OF A LEAK BUT NONE WAS FOUND. ON FEB 2, 1986, GAS INJECTION WAS INITIATED INTO THE LINE AT SS-145B PLATFORM, EXPECTING TO FIND THE LEAK WITH GAS BUBBLES. ON FEB. 3, 1986, AT 10:45 A.M., OUR LAFAYETTE OFFICE RECEIVED TELEPHONE NOTIFICATION FROM THE MMS OF AN OIL SIGHTING IN THE SS-113 BLOCK. OFFSHORE PERSONNEL WERE NOTIFIED ANDINSTRUCTED TO INVESTIGATE THE SPILL SIGHTING AND TO DETERMINE IF IT WAS ORIGINATING FROM OUR PIPELINE. AFTER RECEIVING THE REPORT THAT THE SPILL DID ORIGINATEFROM OUR 6 5/8" OIL AND GAS LINE RUNNING FROM SS-94A TO SS-145B; THE SENIOR FOREMAN FOR THAT AREA ORDERED THE PRESSURING UP OPERATIONS AT THE SS-145B PLATFORM TO STOP. A FAXED SPILL REPORT WAS RECEIVED IN THE LAFAYETTE OFFICE AT 11:30 A.M.WHICH INCLUDED THE DETAILS KNOWN AT THAT TIME. THE REPORT INDICATED A SPILL 14OO' FNL AND 3640' FWL OF SS BLOCK 113; THE SLICK BEING 6 MILES WIDE BY 1 MILE LONG, LIGHT TO DARK BROWN COLOR. FORM THIS INFO AN ESTIMATION OF A DISCHARGE OF UP TO 5000 GALS. WAS MADE.
2017-09-29 08:50 | YES | NO | 19860037 |  | 443 | AMOCO PIPELINE CO | YES | 1986-02-17 | 0 | IL | WILL |  | NO |  | NO | WITHIN DIKED MANIFOLD AREA BETWEEN TANKS SOUTH OF WILMINGTON, IL ON ILLINOIS HWY 102 ON WEST SIDE OF ROAD. |  | TANK FARM | PIPE |  | 1936 | INCORRECT OPERATION BY OPERATOR PERSONNEL | CRAKED PUMP CASE | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3785.2119 | 7636.3013 | CRUDE OIL | 1 | 2220 | 2220 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN CARICO, AREA MANAGER OPERATIONS | 8154784007 | A PROGRAMMABLE LOGIC CONTROLLER (PLC), WITH A DEFECTIVE POWER SUPPLY AND CAR, INTERPRETED A VOLTAGE SPIKE TO BE A COMMAND TO OPEN A MOTOR OPERATED VALVE OFF THE MAIN LINE FEEDING A CONNECTED, BUT INACTIVE, TANK FARM. AT THE TIME OF THE MALFUNCTION THE LINE WAS NOT OPERATING. LATER THAN NIGHT WHENTHE LINE WAS BROUGHT UP, LINE PRESSURE FOUND A CRACKED FIELD BOOSTER PUMP CASE,BELIEVED TO HAVE RESULTED FROM FREEZING AT SOME EARLIER TIME, AT THE INACTIVE TANK FARM. OIL LEFT THE PUMP BUT WAS CONTAINED BY AREA DIKES. CLEAN UP OPERATIONS AND CORRECTIVE MEASURES TO PREVENT REOCCURRENCE WERE INITIATED ON 2/18/86.
2017-09-29 08:50 | YES | NO | 19860038 |  | 737 | ASHLAND PIPELINE CO | NO | 1986-02-27 | 1400 | IN | SPENCER |  | NO |  | NO | NW 1/4 OF SE 1/4 OF SECTION 32 - TOWNSHIP 6 SOUTH - RANGE 7 WEST |  | LINE PIPE | VALVE |  | 1923 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1419.4545 | 2863.613 | CRUDE OIL | 1 | 400 | 65 | NO | NO | 6 | 0.28 | 30000 | THREADED |  | 950 | 880 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | ONE CALL |  | Null | Null | JESSE BROTHERS, DIVISION SUPT. | 6182624106 | A SCRAPER PIG HUNG DURING NORMAL PIGGING OPERATIONS AND FAILED TO REACH THE RECEIVING TRAP. A "POLY-PIG" WAS INSERTED TO PUSH THE ORIGINALSCRAPER OUT OF THE PIPELINE, BUT THE "POLY-PIG" WEDGED INTO THE ORIGINAL SCRAPER AND SEALED OFF ALL THE BYPASS FLOW. THE RESULTING PRESSURE SURGE CAUSED A RUPTURE IN THE DOWNSTREAM END OF THE PIPELINE BEFORE IT REACHED PUMPING STATION TO TRIP THE HIGH DISCHARGE PRESSURE KILL. THE PRESSURE KILL DID TRIP, HOWEVER, REDUCING THE LOSS AND DAMAGE.
2017-09-29 08:50 | YES | NO | 19860039 |  | 737 | ASHLAND PIPELINE CO | NO | 1986-03-04 | 1500 | IN | SPENCER |  | NO |  | NO | NE 1/4 OF SW 1/4 OF SECTION 15 - TOWNSHIP 7 SOUTH - RANGE 7 WEST |  | LINE PIPE | PIPE |  | 1923 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 473.1515 | 954.5377 | CRUDE OIL | 2 | 130 | 50 | NO | NO | 6 | 0.28 | 30000 | THREADED |  | 950 | 980 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | ONE CALL |  | Null | Null | JESSE BROTHERS, DIVISION SUPT. | 6182624106 | THE LINE WAS BEING PRESSURED IN AN EFFORT TO LOCATE A SCRAPER THAT HAD BECOME LODGED AND SEALED THE PIPELINE. AS PRESSURE WAS APPLIED AT THE PUMPING STATION, PRESSURE GAUGES WERE CHECKED IN THE SUSPECT AREA TO DETERMINE IF THE GAUGE LOCATON WAS OPEN TO THE PRESSURE APPLIED AT THE PUMPING STATION.THE STATION OPERATOR SAW A RISE IN PRESSURE TO THE DESIRED LEVEL AND SWITCHED FROM "MANUAL" TO WHAT HE THOUGH WAS "OFF" AND RETURNED TO TEH RADIO IN THE OFFICEBUILDING TO NOTIGY THE WORK CREWS. SEVERAL MINUTES LATER HE REALIZED THE PUMPSHAD RESTARTED (OBVIOUSLY DUE TO THE SWITCH BEING PLACED IN "AUTOMATIC" WHEN HE THOUGH IT WAS OFF) AND THJE DOWNSTREAM PIPELINE RUPTURED DUE TO THE HIGH PRESSURE AGAINST THE SEALED SCRAPER. THIS RUPTURE WAS IN A SECTION OF PIPE DAMAGED BY CORROSION PRIOR TO THE APPLICATION OF CATHODIC PROTECTION.
2017-09-29 08:50 | YES | NO | 19860040 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1986-03-10 | 1145 | TX | GAINES |  | NO |  | YES | PUBLIC SCHOOL LAND BLOCK A9 |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 3 | 1250 | 0 | NO | NO | 6 | 0.16 | 1 | WELDED |  | 0 | 0 | YES | 24 | 1777 | 3 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PIPELINE SAFETY PROGRAM | NO | NO | S.F. ISAACS, PRESIDENT | 9185811800 | THIRD PARTY RUPTURED LINE HWILE PLOWING.
2017-09-29 08:50 | YES | NO | 19860041 |  | 809 | ARCO PIPE LINE CO | YES | 1986-02-23 | 700 | IL | LIVINGSTON |  | NO |  | NO | TANK FARM LOCATED AT COMPANY'S FLANAGAN STATION, LIVINGSTON COUNTY, NEAR PONTIAC, IL |  | TANK FARM | TANK |  | 1980 | OTHER | MALFUNCTION OF SWIVEL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 327 |  | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | NORMAN BENNETT, REGION MANAGER | 3163311300 | ROOF DRAIN ON #1403 TANK DEVELOPED A LEAK CAUSING OIL TO SPILL IN TANK DIKE.
2017-09-29 08:50 | YES | NO | 19860042 |  | 12127 | MARATHON PIPE LINE CO | YES | 1986-03-03 | 2030 | IN | BOONE | ZIONSVILLE | NO |  | NO | NEAR A HOUSING SUBDIVISION OF ZIONSVILLE, INDIANA, 1089 STANLEY ST., SECTION 26 TOWNSHIP 18 NORTH RANGE 2 EAST. |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9463.0297 | 19090.7531 | GASOLINE | 3 | 75 | 50 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1000 | 575 | YES | 24 | 1260 | 10 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H. E. MILLER, VICE PRESIDENT | 4194222121 | AT 2030 HOURS CST, MARATHON PIPE LINE CO., RECEIVED A CALL FROM A LANDOWNER ALONG THE RIGHT-0F-WAY ON MARATHON'S #2-10" PRODUCTS LINE. THELANDOWNER STATED HE SMELLED GASOLINE IN THE AREA. MPL PERSONNEL IMMEDIATELY PROCEEDED TO THE SITE WHERE THEY VERIFIED THAT THE SMELL WAS DUE TO A PIPELINE LEAK. AT 2047 HOURS, MARATHON'S CONTROL CENTER WAS NOTIFIED AND THE LINE WAS SHUT IN. ADDITIONAL PERSONNEL WERE DISPATCHED FROM MARTINSVILLE AND INDIANAPOLIS TO SECURE THE AREA THE EVENING OF MARCH 3.ON MARCH 4, MARATHON PERSONNEL EXCAVATED THE LINE, DISCOVERED A PINHOLE CORROSION LEAK, CLAMPED THE LEAK AND BEGAN RECOVERY OPERATIONS. THE LINE WAS REPAIRED ON MARCH 5 WITH A FULL ENCIRCLEMENT SLEEVE AND THE RECOVERY OPERATION WAS COMPLETED.
2017-09-29 08:50 | YES | NO | 19860043 |  | 1845 | BUCKEYE PIPELINE CO LP | YES | 1986-02-13 | 2155 | OH | HURON |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 574221 | 543387.0365 | 1096231.1354 | DIESEL FUEL | 1 | 10107 | 4609 | NO | NO | 16 | 0.28 | 1830 | WELDED |  | 1375 | 1010 | YES | 24 | 1761 | 8 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JAMES KELLY, MANAGER | 2158208300 | IT APPEARS THAT THE 16" LINE WAS HIT BY TILING CONTRACTOR APPROXIMATELY 9-27-84, THEREBY CAUSING DAMAGE TO PIPELINE RESULTING IN 2-13-86 RUPTURE.
2017-09-29 08:50 | YES | NO | 19860044 |  | 2731 | CHEVRON PIPELINE CO | YES | 1986-02-14 | 900 | UT | DUCHESNE | MYTON | NO |  | NO | CHEVRON PIPE LINE PUMP STATION AT MYTON, UT |  | LINE PIPE | PIPE |  | 0 | FAILED PIPE | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 350 | 350 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA | PUBLIC AWARENESS | Null | Null | R. V. SMITH, DIVISION MANAGER | 8015397251 | THE LEAK OCCURRED WITHIN A TANK CONTAINMENT DIKE AT OUR MYTON, UTAH PUMP STATION. AN OUT-OF-SERVICE 3/4" SAMPLE LINE WAS BROKEN OFF AN IN-SERVICE LINE AT THE THREADED CONNECTION. THE DAMAGE WAS EVIDENTLY DUE TO NATURAL FORCES. THE SPILL WAS ENTIRELY CONTAINED WITHIN THE TANK IMPOUND BASIN AND THE OUTDATED PIPING HAS BEEN REMOVED.
2017-09-29 08:50 | YES | NO | 19860045 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-03-10 | 1115 | TX | WINKLER |  | NO |  | NO | MP 60.68 KEYSTONE-GOLDSMITH #2-8 1 MILE EAST OF KEYSTONE STATION |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 236.5757 | 477.2688 | CRUDE OIL | 1 | 1550 | 1500 | NO | NO | 8 | 0.33 | 35000 | WELDED |  | 850 | 550 | YES | 0 | 730 | 5 | 73 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. L. DOWNIE, DIVISION MANAGER | 9156877551 | INTERNAL CORROSION ON SIDE OF PIPE.
2017-09-29 08:50 | YES | NO | 19860046 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1986-02-24 | 1545 | TX | HOCKLEY |  | NO |  | NO | LINE "80" MP 138+50+39 ONE MILE SOUTH OF PHILLIPS PIPE LINE'S PEP STATION |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 43000 | 40691.0276 | 82090.2385 | NATURAL GAS LIQUID | 1 | 3763 | 0 | NO | NO | 12 | 0.25 | 45000 | WELDED |  | 1180 | 450 | YES | 24 | 1510 | 4 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | LINE MARKERS ROAD CROSSIN | NO | NO | B. L. THORMAN, VICE PRESIDENT | 9186614721 | GRADER OPERATOR PUNCTURED LINE.
2017-09-29 08:50 | YES | NO | 19860047 |  | 12127 | MARATHON PIPE LINE CO | YES | 1986-02-22 | 1310 | MI | MUSKEGON | MUSKEGON | NO |  | NO | SECTION 35, TOWNSHIP 10 NORTH, RANGE 17 W - ON GRAND TRUNK RR RIGHT-OF-WAY NEAR INTERSECTION OF SHERMAN BOULEVARD. |  | LINE PIPE | GIRTH |  | 1947 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 229600 | 217271.1614 | 438323.6919 | GASOLINE | 3 | 977 | 150 | YES | NO | 8 | 0.31 | 42000 | WELDED |  | 1400 | 45 | YES | 41 | 1870 | 2 | 72 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. A. RYSENGA, PRESIDENT | 4194222121 | AT 1310 HOURS (CST), FEB. 22, 1986, MARATHON PIPE LINE CO.'S OPERATIONS CENTER WAS NOTIFIED OF A POTENTIAL LEAK ON OUR 8" LINE DELIVERING TO AMOCO'S MUSKEGON TERMINAL. THE LINE WAS SHUT DOWN AT 1312 HOURS AND MARATHON PERSONNEL WERE DISPATCHED TO THE SITE. TWO ABSORBENT BOOMS WERE INSTALLED ACROSS RUDIMAN CREEK BY THE COAST GUARD. MARATHON CALLED IN CONTRACTORS TO AFFECT PRODUCT RECOVERY, CLEANUP AND LINE REPAIR. THE GASOLINE LEAKED INTO THE MUSKEGON SANITARY SEWER SYSTEM AND FIVE MINOR BASEMENT FIRES WERE REPORTED THE EVENING OFFEB. 22.THE LINE WAS EXPOSED AND DRAINED UP ON FEB. 24. ON FEB. 25THE LINE WAS REPAIRED WITH A FACTORY BEND AND RETURNED TO SERVICE.A SIPHON DAM HAS BEEN INSTALLED DOWNSTREAM OF OUR LIEN CROSSING AND APPROXIMATELY ONE BARREL OF PRODUCT PER DAY IS BEING RECOVERED.THROUGHOUT THE ENTIRE LEAK RESPONSE, MARATHON RECEIVED EXCELLENT COOPERATION FROM THE MICHIGAN DEPARTMENT OF NATURAL RESOURCES AND THE MUSKEGON POLICE, FIRE AND PUBLIC WORKS DEPART.
2017-09-29 08:50 | YES | NO | 19860048 |  | 12127 | MARATHON PIPE LINE CO | YES | 1986-02-22 | 2300 | IL | MARION |  | NO |  | NO | SECTION 15, TOWNSHIP 4 NORTH RANGE 1 EAST - OCCURRED ON MARATHON PIPE LINE PROPERTY PATOKA TANK FARM |  | TANK FARM | BOLTED FITTING |  | 1953 | OTHER | 10" TANK VALVE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3900 | 3690.5816 | 7445.3937 | CRUDE OIL | 1 | 1300 | 1300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. A. RYSENGA, PRESIDENT | 4194222121 | ON FEB 22, 1986 A TEN INCH VALVE FLANGE FAILED. THE VALVE WAS ON THE TANK FILL LINE TO TANK 1285. APPROXIMATELY 1300 BARRELS OF CRUDE OILESCAPED INTO THE TANK DIKE. ALL THE CRUDE WAS PUMPED BACK INTO THE TANK, THE AREA CLEANED UP, THE VALVE REPAIRED AND THE TANK RETURNED TO SERVICE ON MARCH 7, 1986.
2017-09-29 08:50 | YES | NO | 19860049 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1986-02-23 | 727 | CA | SAN JOAQUIN | HOLT | NO |  | NO | COOK AND HOLT ROADS - TRAPPER SLOUGH, SAN JOAQUIN COUNTY, CALIFORNIA |  | LINE PIPE | PIPE |  | 1957 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 800000 | 757042.3743 | 1527260.2505 | DIESEL FUEL | 1 | 500 | 120 | NO | NO | 10 | 0.25 | 46000 | WELDED |  | 1440 | 305 | YES | 24 | 1820 | 12 | 57 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. B. MILLER, VICE PRESIDENT | 2136296251 | SLOUGH CONTAINS WATER MOST OF THE YEAR AND PRODUCT WAS DISCOVERED FLOATING ON SURFACE. BECAUSE OF DEPTH OF PIPELINE, RELOACTED APPROXIMATELY 650 FEET OF PIPELINE.
2017-09-29 08:50 | NO | NO | 19860050 |  | 25140 | UNOCAL CORP | NO | 1986-02-25 | 930 | AL |  |  | YES | SHORT CREEK | NO |  |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 12301.9386 | 24817.9791 | TOLUENE | 2 | 3 | 0 | NO | NO | 6 | 0.28 | 150 | WELDED |  | 225 | 150 | YES | 1 | 225 | 1 | 86 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BJ MORRIS, REGION OPERATIONS MANAGER | 4043204864 | AN APPARENT LINE OBSTRUCTION WAS NOTED WHILE UNLOADING A BARGE ON 2/11/86. A CONTRACTOR WAS CALLED IN ON 2/25/86 TO DETERMINE SOURCE OF THE OBSTRUCTION. TRIED TO FILL THE LINE WITH WATER AND WHILE PRESSURING LINE, RUPTURE OCCURRED SPILLING 1.2 - 2.5 BARRELS OF PRODUCT. ALL APPROPRIATE AGENCIES WERE CONTACTED. SPILL WAS CLEANED UP AND LINE WAS REPLACED WITH SCHEDULE 40 COATED PIPE.
2017-09-29 08:50 | YES | NO | 19860051 |  | 5075 | FARMERS UNION CENTRAL EXCHANGE INC - CENEX PIPELIN | YES | 1986-03-26 | 900 | ND | MCKENZIE |  | NO |  | NO | T15N, R96W, NE/4, SEC. 11 |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 18926.0594 | 38181.5063 | GASOLINE | 3 | 802 | 372 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1200 | 375 | YES | 8 | 1250 | 10 | 60 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER |  | NO | NO | BUDD BRATLIE, PIPELINE SUPERINTENDENT | 4062529280 | AT APPROXIMATELY 9:00 AM ON MAR 26, 1986, STATION OPERATORS AT GLENDIVE, MT, AND MINOT, ND, REPORTED LOW FLOW INTO TERMINALS AND LOSS OF PRESSURE ON PIPELINE.GLENDIVE PUMP STATION WAS IMMEDIATELY SHUT DOWN AND PEOPLE WERE SENT FROM GLENDIVE AND MINOT TO BEGIN CLOSING BLOCK VALVES. WE RECEIVED A REPORT 35 MINUTES LATER THAT NORTHWIND CONSTRUCTION CO., DOING WORK FOR WILLISTON GAS CO., HAD HIT OUR PIPELINE NEAR KEENE, N.D. THEY WERE INSTRUCTED ON THE LOCATION OF THE BLOCK VALVES FOR THIS AREA. ALSO VACUUM TRUCKS WERE DISPATCHED TO THE SITE TO RECOVERPRODUCT ISOLATED IN TEH TRENCH FOR THE 4" PIPELINE THEY WERE WORKING ON. THEY HAD NOT NOTIFIED US OF THEIR INTENTION TO LAY THIS LINE, ALTHOUGH THERE WAS AN AIR MARKER APPROXIMATELY ONE HALF MILE TO THE EAST OF THE SITE, AND LINE MARKER ATTHE HIGHWAY CROSSING APPROXIMATELY THREE FOURTHS OF A MILE WEST OF THE SITE. OUR MAINTENANCE CREW PROCEEDED TO THE SITE AND REPAIRED THE PUNCTURE BY INSTALLING 13" OF NEW PIPE.
2017-09-29 08:50 | YES | NO | 19860052 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1986-03-28 | 1000 | TX | WHARTON |  | NO |  | NO | 1 MILE WEST OF WHERE THE PIPELINE CROSSES HWY 71 AND 1/2 MILE NORTH OF COUNTY ROAD 403. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 28389.089 | 57272.2594 | L. P. G. | 2 | 1583 | 0 | NO | NO | 8 | 0.32 | 2612 | WELDED |  | 750 | 400 | YES | 24 | 1050 | 1 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PUBLIC EDUCATION | NO | NO | ROGER GUERRETTE, AREA SUPERVISOR | 5128972288 | PIPELINE STRUCK BY MAINTAINER (ROAD GRADER) CUTTING DRAINAGE IN CULTIVATED FIELD. BLADE PUNCTURED LINE AND MAINTAINER REMAINED IN POSITION WHEN REPAIR CREWS ARRIVED ON SITE.
2017-09-29 08:50 | YES | NO | 19860053 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-03-20 | 1030 | TX | HARDIN | SOUR LAKE | NO |  | NO |  |  | PUMPING STATION | SCRAPER TRAP |  | 0 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL |  | 200 | 195 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH, DIVISION MANAGER | 4098393088 | ON MARCH 20, 1986, CHEVRON PIPE LINE EMPLOYEES DISCOVERED A DITCH CONTAINING CRUDE OIL. INVESTIGATION REVEALED THAT AN ADJACENT CANAL AND SMALL LAKE WERE ALSOCONTAMINATED WITH OIL. CHEVRON EMERGENCY RESPONSE CREWS WERE NOTIFIED AND THE OIL WAS QUICKLY CONTAINED. APPROPRIATE FEDERAL AND STATE AGENCIES WERE NOTIFIED. CLEANUP OPERATIONS WERE INITIATED USING BOTH COMPANY AND CONTRACT PERSONNEL AND EQUIPMENT. OF THE ESTIMATED 200 BBLS SPILLED, APPROXIMATELY 98% HAD BEEN RECOVERED BY 7 PM ON MARCH THE 23. WHILE THE EXACT SOURCE OF THE SPILL HAS NOT YETBEEN DETERMINED, A 10" LINE FROM A NEARBY SUMP PIT HAS BEEN SEALED AS A PRECAUTIONARY MEASURE.
2017-09-29 08:50 | YES | NO | 19860054 |  | 7710 | HYDROCARBON TRANSPORTATION INC | YES | 1986-03-06 | 1956 | IA | CASS | MASSENA | NO |  | NO | FROM JUNCTION OF 92 AND 148 STATE HIGHWAYS (EAST OF MASSENA, IA) NORTH OF 148 TWO MILES, EAST ON GRAVEL COUNTY ROAD 3/4 MILE. STATION IS ON SOUTH OF ROAD. |  | PUMPING STATION | TANK | FUEL GAS SYSTEM ON TURBIN | 1969 | OTHER | RELEASE ETHANE FRM FUEL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 236575.742 | 477268.8283 | NATURAL GAS LIQUID | 2 | 1 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. C. SMITH, VICE PRESIDENT, OPERATIONS | 4026334208 | INVESTIGATION SUGGESTS A LEAK DEVELOPED IN THE FUEL GAS SYSTEM TO THE #1 UNIT ON 102 PIPELINE. THE ENSUING FIRE FROM AN UNKNOWN IGNITION SOURCE ACTIVATED THE EMERGENCY SHUTDOWN SYSTEM. DAMAGE WAS LIMITED TO ONE UNIT OF THE FOUR UNITS AT THE STATION.
2017-09-29 08:50 | YES | NO | 19860055 |  | 15774 | PORTAL PIPELINE CO | YES | 1986-03-20 | 1230 | MT | SHERIDAN |  | NO |  | NO | NW 1/4 SEC 16, TOWNSHIP 36 NORTH, RANGE 58 EAST, APPROXIMATELY 3 1/2 MILES WEST OF WESTBY, MT ON STATE HIGHWAY #5 AND THEN 1 1/4 MILES NORTH |  | LINE PIPE | PIPE |  | 1965 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 189.2606 | 381.8151 | CRUDE OIL | 1 | 10020 |  | NO | NO | 6 | 0.13 | 1585 | WELDED |  | 1140 | 0 | YES | 12 | 1268 | 1 | 65 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D. E. BELL, MANAGER | 7018521088 | LONGITUDINAL SEAM RIPPED OPEN 44".
2017-09-29 08:50 | YES | NO | 19860056 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-03-11 | 1030 | NM | LEA | JAL | NO |  | NO | NW 1/4, NW 1/4, SECTION 9, T-24-S, R-37-E, HOBBS-HENDRICK 10-INCH |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 1040.9333 | 2099.9828 | CRUDE OIL | 1 | 160 | 100 | NO | NO | 10 | 0.28 | 25000 | WELDED |  | 900 | 150 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. J. EITHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416000
2017-09-29 08:50 | YES | NO | 19860057 |  | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1986-03-16 | 1000 | CA | STANISLAUS |  | NO |  | NO | SECTION 8 T.8 R.S STANISLAUS CO |  | PUMPING STATION | BOLTED FITTING |  | 1968 | OTHER | FLANGE GASKET FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4731.5148 | 9545.3766 | CRUDE OIL | 1 | 200 | 100 | NO | NO | 20 | 0.25 | 52000 | FLANGED |  | 940 | 0 | YES | 8 | 1175 | 1 | 67 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | GARY HOHNSTEIN, PIPELINE SUPERINTENDENT | 8053270528 | A CATHODIC INSULATING GASKET FAILED IN A BOLTED FLANGE AT GUSTINE PUMP STATION.
2017-09-29 08:50 | YES | NO | 19860058 |  | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1986-03-11 | 1640 | CA | LOS ANGELES | LONG BEACH | NO |  | NO | 100 YARDS NORTHWEST OF THE INTERSECTION OF PICO AVENUE AND 7TH ST, LONG BEACH HARBOR AREA. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 13248.2416 | 26727.0544 | CRUDE OIL | 1 | 200 | 160 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1256 | 160 | YES | 8 | 720 | 9 | 82 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GARY HOHNSTEIN, PIPELINE SUPERINTENDENT | 8053270528 | A PINHOLE LEAK ON THE BOTTOM SIDE OF THE PIPE ALLOWED OIL TO ENTER AN ADJACENT STORM DRAIN THROUGH A BROKEN JOINT. THE ORIGINAL DAMAGE TO OUR COATING AND SUBSEQUENT CORROSION APPEARS TO HAVE BEEN CAUSED DURING THE INSTALLATION OF A SEWER LINE WHICH CROSSES UNDER OUR LINE. THERE WAS EVIDENCE THAT AN UNSUCCESSFUL ATTEMPT WAS MADE TO REPAIR OUR COATING.
2017-09-29 08:50 | YES | NO | 19860059 |  | 2745 | CONTINENTAL PIPELINE CO | YES | 1986-04-20 | 1926 | KS | COWLEY |  | NO |  | NO | R3E, T34S, SECTION 7 (NW 1/4) COWLEY CO, KS - 3 MILES NORTH OF ARKANSAS CITY, KS (EAST OF OLD HIGHWAY 77) |  | LINE PIPE | PIPE |  | 1923 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2838.9089 | 5727.2259 | GASOLINE | 3 | 500 | 350 | NO | NO | 6 | 0.28 | 1461 | COUPLED |  | 1050 | 1180 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | DWIGHT JACKSON, DIRECTOR OF ENVIRONMENTAL AFFAIRS | 7132932096 | INCORRECT PROCEDURES FOLLOWED BY SYSTEM OPERATOR CAUSED INCREASED LINE PRESSUREAND LINE BREAKAGE. SPILL WAS CONTAINED IN A 1/4 ACRE DRY WASH CREEK BED. CLEAN UP WAS BEGUN EVENING ON APRIL 20.
2017-09-29 08:50 | YES | NO | 19860060 |  | 19536 | TOTAL PIPELINE CORP | YES | 1986-01-13 | 1620 | OK | TILLMAN | DAVIDSON | NO |  | NO | T3S, R18W, SE 1/4, SECTION 18, FROM INTERSECTION OF HWY. 70 AND 183 AT DAVIDSON, OK - 3 1/2 MI. WEST, 3 MI. NORTH, 1/4 MI. EAST, AND 1/4 MI. |  | LINE PIPE | PIPE |  | 0 | OTHER | CORROSION, EXTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1800 | 1703.3453 | 3436.3356 | CRUDE OIL | 1 | 378 | 320 | NO | NO | 4 | 0.24 | 0 | WELDED |  | 480 | 0 | YES | 24 | 1000 | 1 | 42 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN BROWN, ASSISTANCE GENERAL MANAGER | 8175692283 | FARMER HIT 4" STEEL LINE WITH PLOW ABOUT 1620 HR. ON JAN 13, 1986. HE CALLED OUR AIR PATROL WHO CALLED TOTAL PIPELINE CORP. THE CREW WAS AT THE SITE ABOUT 1800 HRS. THE SYSTEM WAS SHUT DOWN ABOUT 1930 HRS. TWO TRANSPORTS WERE AT SITE TO PICK UP SPILL. JANUARY 15TH WE LOWERED THE PIPELINE AND TOOK OUT PLACES WHEREPLOW HIT LANE. CLEAN UP AND REPAIR ARE BEING DONE. REPORTED TO ENSIGN DIX ON JAN. 14, 1986.
2017-09-29 08:50 | YES | NO | 19860061 |  | 2745 | CONTINENTAL PIPELINE CO | YES | 1986-03-29 | 400 | MT | BASIN | JUDITH | NO |  | NO | SECTION 29, TOWNSHIP 19N, RANGE 7E, 75 MILES NORTH OF MILE POST #254 |  | LINE PIPE | GIRTH |  | 1961 | OTHER | PINHOLE LEAK IN A WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 23200 | 21954.2289 | 44290.5473 | CONDENSATE - WATER | 1 | 693 | 0 | NO | NO | 9 | 0.22 | 52000 | WELDED |  | 1850 | 1200 | YES | 0 | 0 | 1 | 61 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWIGHT JACKSON, DIRECTOR OF ENVIRONMENTAL AFFAIRS | 7132932096 | THE CONTINENTAL PIPE LINE GLACIER 8-INCH EXPERIENCED A LEAK AT APPROXIMATELY 0400 (MST) .75 MILES NORTH OF MILE POST 254, ABOUT 15 MILES NORTH OF FIFE PUMP STATION. A GIRTH WELD BETWEEN TWO SEGMENTS OF .219" WALL, X-52 PIPE FAILED ALLOWING 693 BARRELS OF CONDENSATE TO LEAK FROM THE LINE.DISTRICT PERSONNEL WERE NOTIFIED BY A LOCAL LANDOWNER. THEY LOCATED THE LEAK AND CLOSED THE ADJACENT BLOCK VALVES. SIX FEET OF PIPE CONTAINING THE PINHOLE LEAK WAS REMOVED AND REPLACED. CLEANUP WAS ACCOMPLISHED BY COMPANY PERSONNEL.
2017-09-29 08:50 | YES | NO | 19860062 |  | 19216 | TESORO NATURAL GAS CO | NO | 1986-01-12 | 1300 | TX | MAVERICK |  | NO |  | NO | 14 MILES EAST OF EAGLE PASS, TX, ON U.S.HWY. 277, PLUS 8 MILES NORTH ON CHITTUM RANCH PROPERTY. |  | LINE PIPE | PIPE |  | 1960 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 67000 | 63402.2989 | 127908.046 | CRUDE OIL | 1 | 4111 | 1735 | NO | NO | 8 | 0.2 | 2165 | WELDED |  | 1150 | 120 | YES | 8 | 1600 | 7 | 60 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BEN RUNNELS, MANAGER OPERATIONS, EASTERN DIVISION | 5123336192 | LEAK WAS DISCOVERED AT 1300 HOURS, JAN 12, 1986. PIPELINE HAD DEVELOPED A SMALL FATIQUE CRACK ABOUT 1" LONG ON THE BOTTOM SIDE OF LINE. LINE WAS FULLY COATEDAND WRAPPED WHERE LEAK OCCURRED. THERE WERE NO SIGNS OF CORRISION AROUND THE DAMAGED AREA.
2017-09-29 08:50 | YES | NO | 19860063 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1986-04-04 | 1100 | NM |  | LEA | NO |  | NO | LINE 80-3 - TEXACO EUNICE TO HOBBS - MP 14-37+34 SECTION 16, T2S, R37E, APPROX. 1.5 MILES NORTH OF EUNICE, NM SOUTH SIDE OF COUNTY RD C-34 |  | LINE PIPE | PIPE |  | 1943 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 4163.7331 | 8399.9314 | NATURAL GAS LIQUID | 2 | 446 | 0 | NO | NO | 4 | 0.19 | 42000 | WELDED |  | 1440 | 700 | YES | 8 | 1800 | 10 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS | NO | NO | B. L. THORMAN, VICE PRESIDENT | 9186615808 | COUNTY MAINTAINER PUNCTURED LINE WHILE MAINTAINING COUNTY ROAD.
2017-09-29 08:50 | YES | NO | 19860064 |  | 15490 | PHILLIPS PIPE LINE CO | Null | 1986-01-02 | 1323 | OK | KINGFISHER |  | NO |  | NO | LINE "O" - BUXTON-BORGER MP 209-02+89 4 MILES SOUTH OF STATE HWY. 33 AND 2 1/2 MI. WEST OF REDING ROAD. |  | LINE PIPE | NO DATA |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3900 | 3690.5816 | 7445.3937 | CRUDE OIL |  | 294 | 219 | NO | NO | 10 | 0.2 | 42000 | NO DATA |  | 1140 | 80 | YES | 24 | 1470 | 11 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B. L. THORMAN, VICE PRESIDENT | 9186615808 | CONTRACTOR RUPTURED LINE WHILE CUTTING NEW DITCHES IN EXISTING LEASE ROAD.
2017-09-29 08:50 | YES | NO | 19860065 |  | 18718 | SUN PIPELINE CO | YES | 1986-04-02 | 1300 | NJ | MERCER |  | NO |  | NO | 48 CARTER RD., PRINCETON, NJ 08540 |  | LINE PIPE | NO DATA |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 395 | 195 | NO | NO | 14 | 0.25 | 52000 | WELDED |  | 1200 | 700 | YES | 55 | 1500 | 11 | 56 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | CLARENCE YABLONSKI | 2159642368 | CONTRACTOR FOR DEVELOPER WAS DIGGING A SEPTIC SYSTEM TRENCH WHEN HE STRUCK THE PIPELINE WITH RIGHT-HAND TOOTH ON BUCKET OF TRAXCAVATOR.. TOOTH PUNCTURED LINE AT ABOUT 1500 ON PIPE. LEAK CLAMP (PLIDCO) SLEEVE WAS INSTALLED COMPLETELY AND TESTED AT 2100 HRS. LINE STARTED AT LIMITED RATE. PERMANENT REPAIRS MADE 4/10/86. A PRETESTED SECTIONN OF PIPE REPLACED THE DAMAGED PORTION OF PIPELINE. THEPIPELINE WAS DAMAGED BY M. P. HUNT CO OF EWING NJ.
2017-09-29 08:50 | YES | NO | 19860066 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-04-10 | 330 | TX | CRANE | MCCAMEY | NO |  | NO | SW 1/4, SECTION 22, BLOCK 35, SIX MILES NORTHWEST OF MCCAMEY HENDRICK-MCCAMEY 10 - INCH |  | LINE PIPE | PIPE |  | 1920 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2250 | 2129.1817 | 4295.4195 | CRUDE OIL | 1 | 150 | 0 | NO | NO | 10 | 0.28 | 25000 | WELDED |  | 900 | 400 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. J. EICHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416000
2017-09-29 08:50 | YES | YES | 19860067 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | NO | 1986-02-22 | 1100 | CA | PLACER | YUBA | NO |  | NO | NORTH END - RAILROAD TRESTLE AT BEAR CREEK |  | LINE PIPE | PIPE |  | 1961 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 1 | 0 | YES | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY NATURAL FORCES |  | Null |  |  | Null | Null | C. B. MILLER, VICE PRESIDENT, OPERATIONS | 2136296192 | WHILE REMOVING A PORTION OF THE ABANDONED PIPE FROM THE OLD RAILROAD TRESTLE APPROXIMATELY ONE BARREL OF GASOLINE SPILLED. THIS WAS INGITED BY THE RAILROAD CREWS WELDING TORCH RESULTING IN A FIRE WHICH CAUSED THREE WELDERS TO JUMP FROM BRIDGE INTO FLOODED CREEK.
2017-09-29 08:50 | YES | NO | 19860068 |  | 18214 | SHAMROCK PIPELINE CORP | YES | 1986-04-07 | 900 | TX | HANSFORD |  | NO |  | NO | SECTION 26, BLOCK 2, W.C. RR. SURVEY, HANSFORD COUNTY, TX 3 MILES EAST AND 5 1/4 MILES NORTH OF THE CITY OF SPEARMAN, TX |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3235 | 3061.2901 | 6175.8586 | CRUDE OIL | 1 | 60 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1264 | 370 | YES | 24 | 1580 | 6 | 57 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | W. C. TURNER, GENERAL MANAGER | 8063783936 | ON 7 APR 1986, A LOSS WAS EXPERIENCED IN THE SHAMROCK PIPE LINE CORP SUTTON 6" SYSTEM. THE LEAK WAS DISCOVERED AT 0900 HOURS. 96'5 OF 6 5/8" O.D., .188 WALL,X-42 COATED PIPE WAS REPLACED. THE CAUSE OF THE LEAK WAS A RESULT OF INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19860069 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1986-05-10 | 820 | TX | UPTON | MIDKIFF | NO |  | NO | LINE "80-1-6" - GOLDSMITH-BENEDUM - MP 67-08+33 EAST OF MIDKIFF, TX, ON F.M. ROAD 2401 APPROX. 2 MILES, THEN ONE-QUARTER MILE SOUTH. SEC 19, BLOCK 37, T5S, T&P |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4536 | 4292.4303 | 8659.5656 | NATURAL GAS LIQUID | 2 | 400 | 0 | NO | NO | 8 | 0.19 | 35000 | WELDED |  | 1100 | 560 | YES | 24 | 1395 | 9 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | B. L. THORMAN, VICE PRESIDENT | 9186614721 | LEAK CAUSED BY EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19860070 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1986-05-08 | 820 | TX | YOAKUM | PLAINS | NO |  | NO | LINE "80" - GAINES-BORGER - MP 93-09+00 APPROX. 3 MILES OUTHWEST OF PLAINS, TX, ON U.S. HWY. 82, THEN ONE-QUARTER MILE NORTH. SEC 445, BLOCK D, JOHN GIBSON |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7212 | 6824.737 | 13768.2512 | NATURAL GAS LIQUID | 2 | 636 | 0 | NO | NO | 8 | 0.19 | 35000 | WELDED |  | 1150 | 550 | YES | 24 | 1480 | 3 | 86 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | B. L. THORMAN, VICE PRESIDENT | 9186614721 | EXTERNAL CORROSION LEAK FOUND BY AN OFFICER OF THE YOAKUM COUNTY SHERIFF DEPARTMENT.
2017-09-29 08:50 | YES | NO | 19860071 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | NO | 1986-04-25 | 1545 | CA | KERN |  | NO |  | NO | APPROX 150 FEET NEAR HWY 99 SOUTHBOUND - AND APPROX 32 FEET FROM MAIN SOUTHERN PACIFIC RAILROAD TRACKS - 1/2 MILE SOUTH OF LERDO HWY. |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 141945.4452 | 286361.297 | GASOLINE | 1 | 1250 | 520 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1377 | 565 | YES | 24 | 1790 | 1 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | Null | BARRY PEARL, VICE PRESIDENT-OPERATIONS | 2136296759 | CONTRACTOR, OPERATING A HEAVY EQUIPMENT LOADER, STRUCK THE PIPELINE AND CAUSED A
2017-09-29 08:50 | YES | NO | 19860072 |  | 443 | AMOCO PIPELINE CO | NO | 1986-03-13 | 1200 | TX | MONTGOMERY | SPRING | NO |  | NO | DAMAGE VALVE IS LOCATED ABOUT 200 YARDS N. OF THE HARRIS, MONTGOMERY CO LINE, ABOUT 1/2 MILE WEST OF I-45, WITH ASHE LAKE 200 YARDS TO THE E.N.E. |  | LINE PIPE | VALVE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 354.8636 | 715.9032 | CRUDE OIL | 1 | 80 | 60 | NO | NO | 4 | 0.13 | 0 | THREADED |  | 50 | 40 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | DIRECT CALL TO AMOCO | YES | YES | MICHAEL CLANCY | 7133322476 | CONTRACTOR WAS CLEARING SEVERAL ACRES OF TREES FOR THE AREA AROUND OUR RIGHT OFWAY, THE USED OUR CLEARED RIGHT OF WAY AS A ROAD TO GET IN AND OUT OF THEIR WORK AREA. DURING THE USE OF THIS RIGHT OF WAY AS A ROAD ONE OF THE CONTRACTORS HEAVY PIECES OF EQIUPMENT RAN OVER THE VALVE WHICH RESULTED IN THE LEAK. THE CONTRACTOR HAD CALL US TO MARK THE LINE WHICH WE DID, BUT THE VALVE WAS STRUCK BY THE EQUIPMENT USED IN CLEARING. A PIT WAS DUG TO COLLECT THE OIL UNTIL REPAIRS COULD BE COMPLETED.
2017-09-29 08:50 | YES | NO | 19860073 |  | 19315 | TEXAS PIPELINE CO | NO | 1986-03-31 | 1210 | TX | BRAZORIA |  | NO |  | NO | TRACT 7B STEPHEN RICHARDSON A-122 SURVEY |  | LINE PIPE | VALVE |  | 1939 | OTHER | FLANGE GASKET ON 8" VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 473.1515 | 954.5377 | CRUDE OIL | 3 | 300 | 280 | NO | NO | 8 | 0.16 | 964 | WELDED |  | 600 | 360 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. S. MINER, DISTRICT MANAGER | 7134322765 | OIL REPORTED IN FARMERS FIELD AT 1210 HOURS ON 3/31/86 IN THE VICINITY OF THE WEST COLUMBIA TO TEXAS CITY 8 M/L. LINE IMMEDIATELY SHUTDOWN AND REPRESENTATIVE FROM TTPLCO SENT TO SITE. BY 1330 HOURS, HE CALLED IN AND SENT 2-130 BBL. VACUUM TRUCKS PLUS BACKHOE AND 3 MORE EMPLOYEES TO LEAK SITE. BY 1600 HOURS THE LEAKSOURCE (VALVE GASKET) WAS LOCATED AND NEW GASKET INSTALLED. BY 1800 HOURS WE HAD PICKED UP 280 BBLS. OF OIL. AT 1835 HOURS LINE WAS RESTARTED.
2017-09-29 08:50 | YES | YES | 19860074 |  | 12628 | MOBIL PIPELINE CO | NO | 1986-04-07 | 1930 | CA | LOS ANGELES | GRANADA HILLS | NO |  | NO | WOODLEY AVENUE, SOUTH OF BALBOA AVENUE |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 2 | 0 | 2 | 1000000 | 946302.9679 | 1909075.3131 | CRUDE OIL | 1 | 690 | 550 | NO | NO | 10 | 0.28 | 2180 | NO DATA |  | 1440 | 980 | YES | 4 | 1800 | 10 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null |  | 2133282550 | THE INCIDENT OCCURRED DURING NORMAL OPERATIONS. THE PIPE WALL HAD APPARENTLY BEEN WEAKENED BY EXTERNAL GALVANIC CORROSION IN THE AREA WHERE THE PIPE FAILED.
2017-09-29 08:50 | YES | NO | 19860075 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-04-29 | 700 | TX | HARDIN | SOUR LAKE | NO |  | NO | 1/2 MILE NORTH OF HWY 105 ON HWY 326 AT CHEVRON'S SOUR LAKE PUMP STATION |  | PUMPING STATION | NO DATA |  | 1970 | OTHER | FAILURE OF PACKING GLAND | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 555 | 551 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH, DIVISION MANAGER | 4098393100 | PACKING GLAND ON POSITIVE DISPLACEMENT PUMP FAILED ALLOWING CRUDE UNDER PRESSURE TO ESCAPE THROUGH SEALS.
2017-09-29 08:50 | YES | NO | 19860076 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-05-07 | 1115 | TX | HARDIN |  | NO |  | NO | APPROX 1/2 MILE SOUTH OF HWY. 943 AND 5 MILES NORTH OF HONEY ISLAND, TX IN HARDIN CO |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4731.5148 | 9545.3766 | GASOLINE | 1 | 400 | 175 | NO | NO | 12 | 0.38 | 60 | WELDED |  | 800 | 325 | YES | 24 | 1174 | 1 | 71 | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH, DIVISION MANAGER | 4098393103 | PIPELINE LEAK DUE TO EXTERNAL CORROSION. LEAK DISCOVERED BY ROUTINE AERIAL PATROL. LEAK OCCURRED IN AN SPARSLY POPULATED AND WOODED AREA. THE PIPELINE WAS REPAIRED USING PLIDCO SLEEVES.
2017-09-29 08:50 | YES | NO | 19860077 |  | 12127 | MARATHON PIPE LINE CO | YES | 1986-04-13 | 2223 | KS | OKETO |  | NO |  | NO | PUMP BUILDING AT PLATTE PIPE LINE COMPANY, MARYSVILLE STATION NE/4 SECT. 8, T. 1 S., R. 7 E. MARSHALL COUNTY, KANSAS |  | PUMPING STATION | PUMP |  | 1954 | OTHER | EQUIPMENT MALFUNCTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 42700 | 40407.1367 | 81517.5159 | CRUDE OIL | 1 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. A. RYSENGA, PRESIDENT | 4194222121 | AT 2022 (CST) ON APRIL 13, 1986, THE CONTROL CENTER NOTED THAT THE SUPERVISORY CONTROL EQUIPMENT AT MARYSVILLE STATION HAD GONE DOWN. BY 2039 (CST) A COMPANY TECHNICIAN WAS DISPATCHED FROM HIAWATHA, KS, ABOUT 70 MILES AWAY, TO INVESTIGATETHIS LOSS OF SUPERVISORY CONTROL. AT 2223 (CST) THE MARSHALL COUNTY SHERIFF CONTACTED THE CONTROL CENTER TO REPORT A FIRE IN THE PUMP BUILDING. THE TECHNICIAN ARRIVED AT THE STATION AT ABOUT THE SAME TIME. THE OKETO FIRE DEPARTMENT WAS ALREADY ON-SITE. TWO OF THE THREE PUMP UNITS THAT HAD BEEN RUNNING WERE OFF BUTTHE THIRD UNIT (UNIT #4) HAD FAILED TO SHUT DOWN AUTOMATICALLY. IT WAS STILL RUNNING AND OIL FROM THE SEALS WERE BURNING. APPARENTLY THE PUMP HAD BEEN RUNNING WITH BOTH THE DISCHARGE AND SUCTION VALVES CLOSED AND THE SEALS WERE BEGINNINGTO FAIL. THE TECHNICIAN SHUT OFF THE POWER TO THE PUMP UNIT AND THE FIRE WAS EXTINGUISHED. IT WAS LATER DETERMINED THAT LIGHTNING HAD DISABLED THE CONTROL SYSTEM. THE CAUSE OF THE FIRE IS NOT KNOWN. THERE WAS NO RESULTING OIL SPILL AS THE CRUDE WAS CONSUMED BY THE FIRE AS IT LEAKED FROM THE SEALS.
2017-09-29 08:50 | YES | NO | 19860078 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1986-05-09 | 630 | KS | BUTLER | EL DORADO | NO |  | YES |  |  | TANK FARM | VALVE |  | 1984 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 185 | 180 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S. F. ISAACS, PRESIDENT | 9185811800 | FIELD PERSONNEL INADVERTENTLY LEFT A VALVE PARTIALLY OPEN.
2017-09-29 08:50 | YES | NO | 19860079 |  | 443 | AMOCO PIPELINE CO | YES | 1986-04-24 | 1000 | OK | CREEK |  | NO |  | NO | SW 1/4 SECTION 33, T18N - R7E. 1 MI EAST, 1/4 NORTH OF DRUMRIGHT, OK. |  | TANK FARM | PIPE |  | 1976 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 94.6303 | 190.9075 | CRUDE OIL | 1 | 270 | 250 | NO | NO | 24 | 0.28 | 0 | WELDED |  | 0 | 10 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | SALT WATER | NO DATA |  | Null | NO DATA |  | Null | Null | J. W. WILHELM, AREA MANAGER - OPERATIONS | 9182257271 | THE LEAK WAS CAUSED BY INTERNAL CORROSION ADACENT TO GV #12468 IN THE 24" SUCTION LINE TO TANK #45. THE LINE HAS BEEN SITTING IDLE DUE TO REDUCED PUMPINGS NORTH, BUT WAS UNDER TANK HEAD PRESSURE. TANK #45 IS BEING OPERATED THRU AN ALTERNATE 16" LINE. THE 24" LINE WILL BE FLUSHED OUT AND DRAINED UP TO PREVENT FUTUREACCIDENTS.
2017-09-29 08:50 | YES | YES | 19860080 |  | 10250 | KIANTONE PIPELINE CORP | YES | 1986-04-30 | 1240 | NY | ERIE | SENECA | NO |  | NO | NYS ROUTE 240 (HARLEM ROAD) AT INDIAN CHURCH ROAD. |  | LINE PIPE | PIPE |  | 1971 | OTHER | SPARK IGNITED DRIP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | CRUDE OIL | 3 | 0 |  | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. V. BERTI, MANAGER | 8147231500 | KIANTONE PIPELINE CORPORATION CONTRACTED STROUSE BROTHERS PIPELINE TO RELOCATE 500 LINEAL FEET OF 12" STEEL PIPELINE AFFECTED BY NYS-DOT ROAD AND BRIDGE CONSTRUCTION. WHEN PERFORMING THE TIE-IN OF THE NEW SECTION OF PIPELINE A SPARK IGNITED A DRIP PAN THAT CONTAINED APPROX. 3-4 GALLONS OF CRUDE OIL. THE FIRE WAS IMMEDIATELY EXTINGUISHED. ONE EMPLOYEE OF STROUSE BROTHERS RECEIVED FIRST-DEGREE BURNS TO THE ARMS AND FACE. EMPLOYEE WAS TREATED AND RELEASED FROM THE LOCAL HOSPITAL. EMPLOYEE RETURNED TO WORK FOLLOWING RELEASE FROM HOSPITAL.
2017-09-29 08:50 | YES | NO | 19860081 |  | 2170 | CENEX PIPELINE | NO | 1986-04-29 | 0 | MT | GLACIER |  | NO |  | NO | T32N, R5W, S8 |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 148 | 0 | NO | NO | 4 | 0 | 0 | THREADED |  | 150 | 100 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | FRED J. MORGANTHALER, SUPT. OF CRUDE OIL | 4066284311 | OIL MOVEMENT REPORTS INDICATED UNACCOUNTABLE LINE LOSSES IN THE 4" MAINLINE IN OUR SOUTH CUT BANK FIELD. AERIAL AND GROUND SURVEYS, HOWEVER, INDICATED NO VISIBLE LEAKS. LINE WAS DUG OUT UNTIL LEAK WAS LOCATED. LEAK WAS A PINHOLE PIT THAT RELEASED OIL IN A DOWNWARD DIRECTION. LEAK AREA WAS REPAIRED WITH A 4" X 6" BAND CLAMP. A 20-FOOT SECTION OF PIPE WAS DUG OUT IN THE LEAK AREA TO DETERMINE IF ADDITIONAL CORROSION WAS PRESENT. NO ADDITIONAL PROBLEMS WERE FOUND.
2017-09-29 08:50 | YES | NO | 19860082 |  | 809 | ARCO PIPE LINE CO | YES | 1986-04-25 | 1530 | TX | ANDERSON |  | NO |  | NO | THREE MILES SOUTH OF TN COLONY - TROUP-TEAGUE 12" AT 2929 + 37 |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | CRUDE OIL | 1 | 75 | 74 | NO | NO | 12 | 0.38 | 30000 | WELDED |  | 450 | 520 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V. P. DRISKI, OPERATIONS - MANAGER | 3163311300 | HIGHER THAN NORMAL OPERATING PRESSURE DUE TO VALVE OPERATION.
2017-09-29 08:50 | YES | NO | 19860083 |  | 5522 | FOUR CORNERS PIPELINE CO | NO | 1986-04-23 | 730 | CA | BAKERSFIELD |  | NO |  | NO | INSIDE TEXACO BAKERSFIELD REFINERY |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 8516.7267 | 17181.6778 | CRUDE OIL | 1 | 100 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. B. KUPREWICZ, VICE PRESIDENT, OPERATIONS | 2134289017 | LEAK CAUSED BY INTERNAL CORROSION IN DEAD LEG OF PIPELINE.
2017-09-29 08:50 | YES | NO | 19860084 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-04-30 | 1700 | NM | LEA | HOBBS | NO |  | NO | NW1/4, SW1/4, SECTION 30, T-20-S, R-38-E10.5 MILES SOUTH OF HOBBS LEA STATION 8-INCH DISCHARGE LINE |  | LINE PIPE | NO DATA |  | 1935 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2840 | 2687.5004 | 5421.7739 | CRUDE OIL | 1 | 280 | 180 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 750 | 120 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | M. J. EICHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19860085 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-04-03 | 830 | IA | POLK | DES MOINES | NO |  | NO | SE SECTION OF DES MOINES |  | TANK FARM | NO DATA |  | 1931 | OTHER | ROOF LEG PUNCTURED TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | FUEL OIL | 1 | 280 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. K. MCCAW, VICE PRESIDENT | 9185883248 | ONE OF THE FLOATING ROOF SUPPORT LEGS WAS PINNED IN THE HIGH POSITION WITH AL OTHERS IN THE LOW POSITION. WHEN THE LEG TOUCHED THE TANK BOTTOM, THE ROOF WAS PLACED IN A SLANTED POSITION WHICH CAUSED THE LEG TO SLIDE OFF OF ITS SUPPORT PADAND PUCNTURE THE BOTTOM.
2017-09-29 08:50 | YES | NO | 19860086 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-04-12 | 1915 | NE | OTOE |  | NO |  | NO | NE 1/4, S28 T84 R13E |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 378.5212 | 763.6301 | L. P. G. | 2 | 20 | 0 | NO | NO | 6 | 0.22 | 35000 | WELDED |  | 1450 | 350 | YES | 8 | 1850 | 1 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | C. K. MCCAW, VICE PRESIDENT | 9185883248 | THE LANDOWNER STRUCK THE PIPELINE WITH A PLOW WHILE TILLING THE LAND.
2017-09-29 08:50 | YES | NO | 19860087 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1986-04-24 | 910 | IL | COOK | ELGIN | NO |  | NO | 737' SOUTH OF THE CENTERLINE OF BLUFF CITY BLVD., CITY LIMITS OF ELGIN, ON COMMONWEALTH EDISON PROPERTY. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 815000 | 771236.9189 | 1555896.3802 | CRUDE OIL | 1 | 12500 |  | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 600 | 250 | YES | 24 | 800 | 1 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | W. C. COCHRANE, PRESIDENT AND GENERAL MANAGER | 7153925631 | A FRONT-END LOADER APPARENTLY OWNED AND OPERATED BY CHICAGO GRAVEL COMPANY STRUCK THE 34" O.D. CRUDE LINE AT APPROXIMATELY 0910 MST CAUSING A 3-3/4" X 2-3/4" HOLE IN THE PIPELINE. LAKEHEAD HAD NOT BEEN ADVISED OF THE WORK OVER THE PIPELINE NOR HAD ANY ACTIVITY BEEN DETECTED BY LAKEHEAD LINEWALKERS ON THEIR APRIL 21 PATROL. THE LINE WAS SHUT DOWN AND REPAIRS MADE BY WELDING A PLIDCO REPAIR SLEEVE OVER THE HOLE. CLEAN-UP OF THE SITE, INCLUDING ADDITIONAL OIL RECOVERY, A LARGE AMOUNT OF OIL SOAKED SOIL HAS BEEN HAULED TO AN APPROVED LANDFILL.
2017-09-29 08:50 | YES | NO | 19860088 |  | 12434 | MID - CONTINENT PIPELINE CO | YES | 1986-02-21 | 800 | OK |  |  | NO |  | NO | 4 MILE S OF MILFAY OK |  | NO DATA | NO DATA |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 2 | 400 | 375 | Null | Null | 4 | 0.25 | 35000 | NO DATA |  | 300 | 200 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | OTHER | BARE FILE | NO DATA |  | Null | NO DATA |  | Null | Null | H. R. THOMPSON | 9183529442 | LEAK OCCURRED BECAUSE OF XETERVAL CORROSSION. OIL RAN DOWN BAR DITCH TO ONE POND CROSSED THE ROAD TO ANOTHER POND. LEAK IS CLEAN UP TO LANDOWNER'S WISHEN
2017-09-29 08:50 | YES | NO | 19860089 |  | 22430 | WEST SHORE PIPE LINE CO | YES | 1986-04-18 | 200 | WI | BROWN | GREEN BAY | NO |  | NO | 2119 NORTH QUINCY ST. |  | TANK FARM | TANK |  | 1961 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 5200 |  | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH ANDREEN, AREA MANAGER - OPERATIONS | 3122573740 | A MIXTURE OF PRODUCT BETWEEN A BATCH OF GASOLINE AND A BATCH OF OIL WAS BEING DELIVERED INTO OUR INTERFACE TANK. AT THE COMPLETION OF THE MIXTURE, THE INTERFACE VALVE WAS NOT CLOSED. THIS CAUSED THE TANK TO OVERFLOW. ALL PRODUCT WAS CONTAINED WITHIN EXISTING DIKED AREAS AND WAS CLEANED UP BY 2:00 PM ON APRIL 19.
2017-09-29 08:50 | YES | NO | 19860090 |  | 18273 | SHELL PIPE LINE CORP | NO | 1986-04-14 | 1000 | TX | CRANE | CRANE | NO |  | NO | NW1/2 NE1/4, SECTION 12, BLOCK 6, H&TCRR SURVEY 13 MILES NORTHWEST OF MCCAMEY, BARNSLEY-MCCAMEY 10-INCH. |  | LINE PIPE | PIPE |  | 1920 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4200 | 3974.4725 | 8018.1163 | CRUDE OIL | 1 | 300 | 0 | NO | NO | 10 | 0.28 | 25000 | WELDED |  | 900 | 75 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. J. EICHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19860091 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-04-16 | 130 | NM | LEA | JAL | NO |  | YES | SW1/4, NW1/4 SECTION 4, T-26-S, R-37-E, 3.5 MILES SOUTH OF JAL, HOBBS-HENDRICK 10-INCH. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 473.1515 | 954.5377 | CRUDE OIL | 1 | 65 | 45 | NO | NO | 10 | 0.28 | 25000 | WELDED |  | 900 | 390 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. J. EICHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19860092 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1986-05-01 | 1600 | TX | HARRIS | LAPORTE | NO |  | NO | 4" PROPYLENE LINE - MP 65-14+31 200 YARDS SOUTH OF FAIRMONT PARKWAY BETWEEN UNDERWOOD ROAD AND RED BLUFF ROAD |  | LINE PIPE | PIPE |  | 1957 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 2362 | 2235.1676 | 4509.2359 | NATURAL GAS LIQUID | 2 | 96 | 0 | NO | NO | 4 | 0.16 | 35000 | NO DATA |  | 1440 | 328 | YES | 24 | 2124 | 8 | 78 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B. L. THORMAN, VICE PRESIDENT | 9186614721 | AT APPROXIMATELY 3:30 PM ON MAY 1, 1986, DURING NORMAL OPERATIONS, A PIPELINE FAILURE WAS REPORTED BY THE PIPELINE OPERATORS. THE LEAK WAS LOCATED AT 4:12 P.M. AND VALVES CLOSED AND STOPPLIN GOPERATIONS BEGUN TO MINIMIZE PRODUCT LOSS.
2017-09-29 08:50 | YES | NO | 19860093 |  | 809 | ARCO PIPE LINE CO | YES | 1986-05-03 | 1930 | TX | RUSK |  | NO |  | NO | STATION 693 + 21, TWO MILES SE OF LAIRD HILL, TX |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 1230.1939 | 2481.7979 | CRUDE OIL | 1 | 100 | 98 | NO | NO | 12 | 0.38 | 24000 | WELDED |  | 425 | 70 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | V. P. DRISKI, OPERATIONS MANAGER, SOUTHERN AREA | 3163311300
2017-09-29 08:50 | YES | NO | 19860094 |  | 14295 | OLYMPIC PIPE LINE CO | YES | 1986-05-08 | 138 | WA | KING | TUKWILA | NO |  | NO | 17024 WEST VALLEY ROAD, TUKWILA, WA, IMMEDIATELY BEHIND STONEWAY CONCRETE BATCH PLANT. |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 220000 | 208186.6529 | 419996.5689 | DIESEL FUEL | 3 | 1974 | 1400 | NO | NO | 14 | 0.28 | 2087 | WELDED |  | 1440 | 1326 | YES | 24 | 1875 | 8 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JERRY C. DURBIN, PRESIDENT | 2146582400 | OLYMPIC'S 14" RENTON TO PORTLAND PIPELINE RUPTURED APPROXIMATELY 2 MILES DOWNSTREAM OF RENTON STATION WHEN THE PRESSURE WAS INCREASED, AT 0138, MAY 8, 1986. BOTH THE UPSTREAM AND DOWNSTREAM STATIONS WERE SHUT DOWN IMMEDIATELY AS A RESULT OF THE PRESSURE DROP. PERSONNEL WAS DISPATCHED TO LOCATE THE LEAK AND ISOLATE THEDAMAGE SECTION OF PIPELINE. INVESTIGATION REVEALED THE PIPELINE HAD BEEN SCRAPED AND GOUGED BY A THIRD PARTY, WEAKENING THE LINE WHICH THEN RUPTURED WHEN THE PRESSURE WAS INCREASED. THE SPLIT WAS 22" LONG AND 2" WIDE AT THE MAXIMUM POINT. CONTAINMENT AND REPAIR PROCEDURES WERE COMMENCED AS SOON AS THE LEAK WAS LOCATED.
2017-09-29 08:50 | YES | NO | 19860095 |  | 4906 | EXXON PIPELINE CO | NO | 1986-04-14 | 915 | TX | BRAZOS |  | NO |  | NO | LEAK OCCURRED AT STATION NO. 1573+52 SOME 3.5 MILES NORTH OF GATE PLANT "C" ON LINE #4 OF THE HEARNE-NAVASOTA 8-INCH CRUDE OIL LINE. |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7450 | 7049.9571 | 14222.6111 | CRUDE OIL | 1 | 350 | 330 | NO | NO | 9 | 0.32 | 25000 | THREADED |  | 741 | 220 | YES | 24 | 1130 | 11 | 58 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | A ROAD GRADER WORKING FOR THE LANDOWNER STRUCK OUR LINE, CAUSING AN OUTSIDE FORCE DAMAGE ON OUR HEARNE-NASASOTA 8" CRUDE OIL LINE ON 4/14/86. RON BORQUE, WITH BRAZOS COAL LIMITED, CALLED EPC DISPATCHER AT 9:15 A.M. TO REPORT THE LEAK. THE DISPATCHER IN TURN CALLED SAMMIE SCOTT, EPC GAUGING SUPERVISOR. THE LINE WAS SHUT DOWN BY THE DISPATCHER AT 9:30 A.M. THE CONTRACTOR BUILT A HOLE AT THE LEAK SITE TO CONFINE THE RELEASED OIL. EPC EMPLOYEES WORKING IN THE AREA WERE CALLED TOTHE LEAK SITE (BENNIE GARRETT, LARRY WHITEHEAD, DAVID HAMMES, HENRY TEER, AND TRAVIS STINSON). APPROX. 30 FEET OF 8" PIPE WAS REPLACED FOR PERMANENT REPAIRS THAT DAY AND THE LINE WAS PUT BACK IN SERVICE AT 10:00 PM THAT NIGHT. THREE TANK TRUCKS FROM PAUL'S TANK TRUCKS WERE USED TO PICK UP THE OIL. A BACKHOE AND TWO LABORERS WERE USED FROM A.D. RICHARDSON CONTRACTORS FOR THE CLEAN-UP OPERATIONS. CLEAN-UP OPERATIONS CONSISTED OF PICKING UP THE OIL WITH TANK TRUCKS AND USING A BACKHOE TO TURN THE SOIL. CLEAN-UP OPERATIONS WERE COMPLETED ON 4/17/86. AN ESTIMATED 1 ACRE OF LAND WAS AFFECTED BY THE SPILL. THE TEXAS RAILROAD COMMISSION INHOUSTON, DISTRICT #3, WAS NOTIFIED OF THE LEAK ON 4/14/86 AT 2:35 P.M., REPRESENTATIVE MARK GERDING, BY SALLY AVENT.
2017-09-29 08:50 | YES | NO | 19860096 |  | 4906 | EXXON PIPELINE CO | NO | 1986-05-08 | 1800 | LA | CLAIRBORNE |  | NO |  | NO | LOCATED AT EXXON PIPELINE COMPANY'S WELLER PUMP STATION, 10 MILES NORTH OF MINDEN, LA. AND 1/4 MILE WEST ON HWY 534. |  | PUMPING STATION | PUMP |  | 1984 | OTHER | ROD PULLED OUT PACKING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3075 | 2909.8816 | 5870.4066 | CRUDE OIL | 1 | 50 | 45 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | ON MAY 9, 1986 , MR. RICHARD LOUIS, WITH SCURLOCK OIL COMPANY, WAS ON HIS DAILYROUTINE AND WAS CHECKING OUT WELLER STATION. AT 7:00 A.M., MR. LOUIS NOTICED THAT OIL WAS SPILLING OUT OF EXXON'S UNIT #3 PUMP. MR. LOUIS PROCEEDED TO SHUT DOWN THE STATION BY PRESSING THE EMERGENCY SHUT DOWN SWITCH. MR LOUIS THEN CONTACTED HIS FOREMAN, MR. BILLY HENDRICKS WHO IN TURN CONTACTED MR. L.D. WILSON WITH EXXON PIPELINE COMPANY. WHEN MR. WILSON INSPECTED THE FACILITY, HE FOUND THAT THE PUMP ROD HAD PULLED THE PACKING OUT OF THE PUMP AND CAUSED THE LEAK. BY SHUTTINGDOWN THE STATION, THE OIL FLOW WAS STOPPED. MR. WILSON CONTACTED EXXON PIPELINE'S MAINTENANCE SUPERVISOR, MR. HOMER JENTES, WHO DISPATCHED A CREW TO THE LEAK SITE TO BEGIN CLEANUP OPERATIONS. A BACKHOE AND OPERATOR FROM MCMAHON CONSTRUCTION COMPANY, BEAUMONT TEXAS WAS DISPATCHED TO WELLER STATION AND CONSTRUCTED A DAMIN WHICH THE MAINTENANCE CREW INSTALLED A FLUME PIPE. THE DAM WAS CONSTRUCTED APPROXIMATELY 300 YARDS DOWNSTREAM FROM WELLER STATION. A VACUUM TRUCK FROM GARRETT OIL FIELD SERVICES, HAYNESVILLE, LA., WAS CALLED IN AND USED TO VACUUM UP 45 OF THE 50 BARRELS FROM THE CREEK. THE REMAINING BARRELS WERE BURNED. ANY REMAINING OIL AFTER THE BURNING WAS ABSORBED INTO HAY AND ABSORBANTS AND REMOVED FROM THE CREEK. THE CREEK BANKS HAD BEEN WASHED DOWN USING BELLHOLE PUMPS AND WASH HOSES.
2017-09-29 08:50 | YES | NO | 19860097 |  | 19212 | TESORO PIPELINE CO | NO | 1986-06-04 | 930 | TX | WHARTON |  | NO |  | NO | LOCATED IN WHARTON COUNTY, TX., APPROX. 4 MILES SOUTH OF FM 441 AND FM 3086, NEAREST CITY OF MIDFIELD, TX. |  | TANK FARM | TANK |  | 1965 | OTHER | PRODUCT IGNITED IN TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 165603.0194 | 334088.1798 | CRUDE OIL | 1 | 5037 |  | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BEN F. RUNNELS, MANAGER OPERATIONS | 5128288484 | CONTRACTOR WAS USING ACETYLENE TORCH TO REMOVE PART OF LADDER FROM STORAGE TANK. CONTRACTOR HEARD A ROAR FROM WITHIN TANK. HE LEFT THE AREA TO NOTIFY TESORO PERSONNEL. SHORTLY THEREAFTER, THE STORAGE TANK EXPLODED AND BURNED. SMALL AMOUNT OF CRUDE OIL SPILLED INTO CONTAINMENT AREA BUT BURNED SIMULTANEOUSLY WITH OIL INSIDE TANK.
2017-09-29 08:50 | YES | NO | 19860098 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1986-05-23 | 1356 | OH | BUTLER | ROSS | NO |  | NO | THE ACCIDENT OCCURRED ON A VACANT FIVE (5) ACRE BUILDING TRACT. THE POINT OF IMPACT TO PIPE WAS AT A POINT APPROX. 300 YDS. SOUTH OF ROSS-HANOVER ROAD IN ROSS. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 141945.4452 | 286361.297 | CRUDE OIL | 1 | 5918 |  | YES | NO | 20 | 0.32 | 52 | WELDED |  | 1215 | 490 | YES | 24 | 0 | 0 | 50 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PERIODIC CONTACT | NO | NO | C.R. MCCCORD, DISTRICT SUPERINTENDENT | 6063714469 | AT 1356 ON 5/23/86, A FRONT END LOADER OPERATED BY TIM PAYNE OF PAYNE EXCAVATING CO., HAMILTON, OH HIT THE 20" LINE ALLOWING OIL TO SPILL FROM A 3 DIAMETER HOLE IN THE SIDE OF THE PIPE. MR. PAYNE WAS EXCAVATING A POND (LAGOON) FOR THE SEPTIC SYSTEM FOR A NEW HOME TO BE BUILT BY THE GRANTOR. WHEN THE PUNCTURE OCCURRED,THE SCADA SYSTEM IN MVPL CO. CONTROL CENTER IN LONGVIEW, TX GAVE A HIGH FLOW ALAMR AT HEBRON STATION. THE OPERATOR IN THE CONTROL CENTER SHUTDOWN HEBRON STATION AND PYRMONT STATION SHUTDOWN AUTOMATICALLY ON LOW SUCTION. THE INCOMING STREAMAT HEBRON STATION WAS TAKEN INTO BREAKOUT TANKAGE. AT 1358 ON 5/23/86, THE CONTROL CENTER CALLED DISTRICT III OFFICE AND REPORTED THE PROBLEM. AT 1410 ON 5/23/86, A GRANTOR WHO LIVES NEAR THE INCIDENT LOCATION TELEPHONED THE DISTRICT III OFFICE AND REPORTED "A BULLDOZER HIT YOU LINE AT ROSS-HANOVER ROAD AND OIL WAS SQUIRTING OUT OF THE LINE". THE GRANTOR'S CALL GAVE AN EXACT LOCATION OF THE PROBLEM AND THE INFORMATION WAS RADIOED TO A MVPL CO. FOREMAN ALREADY ENROUTE TO PATROL THE LINE SEGMENT. THE MVPL CO. FOREMAN ARRIVED AT THE ACCIDENT SITE AT 1500 ON 5/23/86. THE FOREMAN INSTRUCTED THE EXCAVATING CONTRACTOR (PAYNE) TO BUILD TWOCONTAINMENT PONDS TO CONTAIN AND HOLD THE SPILLAGE. ONE POND WAS COMPLETED IN THIRTY MINUTES AND THE SPILLAGE WAS CONFINED TO THE ONE POND WITH THE SECOND PONDAS A BACKUP. TWO MVPL CO., EMPLOYEES WERE DISPATCHED AT 1430 ON 5/23/86 TO CLOSEMAIN LINE BLOCK VALVES AT MP 809, MP 836 & MP 840. THE MAIN LINE BLOCKVALVES WERE CLOSED AT 1510, 1537 AND 1505 ON 5/23/86 RESPECTIVELY THUSISOLATING A 31 MILE LINE SEGMENT.
2017-09-29 08:50 | YES | NO | 19860099 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-05-19 | 640 | MN | WASHINGTON |  | NO |  | NO |  |  | LINE PIPE | LONGITUDINAL WELD |  | 1957 | OTHER | WELD FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2838.9089 | 5727.2259 | FUEL OIL | 2 | 628 | 32 | NO | NO | 8 | 0.25 | 1753 | WELDED |  | 1600 | 1428 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.K. MCCAW, VICE PRESIDENT | 9185883248 | AT 0626 5/19/86, THE DISPATCHER NOTED PRESSURE DROP AND FLOW RATE INCREASE AT THE POINT OF ORIGIN, REVIEWED THE OPERATION WITH THE SHIFT CHIEF AND AT 0632 SHUTDOWN THE NEWPORT VILLAS STATION. A POSSIBLE LEAK WAS REPORTED AND THE MINN. MAINTENANCE CREW ALERTED. THE PRODUCT WENT INTO THE SANDY SOIL WITH VERY LITTLE SURFACING. THE LEAK WAS FINALLY LOCATED AT 1900 HOURS.
2017-09-29 08:50 | YES | NO | 19860100 |  | 18214 | SHAMROCK PIPELINE CORP | YES | 1986-05-16 | 1030 | TX | ROBERTS |  | NO |  | NO | SECTION 15, DL&C SURVEY, ROBERTS COUNTY, TX, 11 MILES SOUTH AND 5 1/2 MILES EAST OF THE CITY OF SPEARMAN. |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7070 | 6690.362 | 13497.1625 | CRUDE OIL | 1 | 360 | 200 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 1630 | 500 | YES | 24 | 2150 | 7 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | W.C. TURNER, GENERAL MANAGER | 8063783940 | ON MAY 16, 1986, AN EMPLOYEE OF SMITH & WHITE CONTRACTORS WAS DIGGING A MUD PITFOR AN IRRIGATION WELL DRILLING OPERATION WHEN HIS DOZER STRUCK AND RUPTURED OUR 8" STEWART BY-PASS LINE. THE DAMAGE ALLOWED APPROXIMATELY 360 BARRELS OF CRUDEOIL TO ESCAPE, OF WHICH, 200 BARRELS WAS SUBSEQUENTLY RECOVERED. THE PIPELINE WAS REPAIRED WITH 14 FEET OF 8 5/8" O.D., O.188 WALL, X-52 LINE PIPE AND RETURNEDTO SERVICE. THE PIPELINE WAS MARKED WITH PIPELINE WARNING SIGNS AT THE FENCE LINES WHERE IT ENTERED AND EXITED THE FARMERS WHEATFIELD.
2017-09-29 08:50 | YES | NO | 19860101 |  | 443 | AMOCO PIPELINE CO | YES | 1986-05-14 | 1345 | IL | DU PAGE | ELMHURST | NO |  | NO | 500 FEET NORTH OF THE INTERSECTION OF IL ROUTE 83 AND ST. CHARLES ROAD IN ELMHURST, IL. |  | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 37852.1187 | 76363.0125 | GASOLINE | 3 | 380 | 260 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1440 | 450 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | R.A. STAHL, AREA MANAGER-OPERATIONS | 2197382359 | ON THE EVENING OF MAY 13, 1986, A CAR BEING TOWED BY A TOW TRUCK CAME LOOSE ANDSTRUCK A TEMPORARY POWER POLE INSTALLED DURING HIGHWAY RECONSTRUCTION ON ILLINOIS ROUTE 83. THE POWER LINES BECAME TANGLED WITH A TRAFFIC SIGNAL CONTROLLER ANDTHE RESULTING ARC WAS GROUNDED THROUGH A GROUNDING ROD WHICH HAD BEEN DRIVEN TOTHE TOP OF THE PIPELINE. THE GROUNDING OF THE 4100 VOLT LINE RESULTED IN A HOLEBEING BURNED THROUGH THE PIPELINE. THE LEAK WAS DISCOVERED ON WEDNESDAY MAY 14,1986 BY ELMHURST SEWER TREATMENT PLANT EMPLOYEES WHEN GASOLINE STARTED SHOWING UP IN THE PLANT THROUGH COLLECTION SEWER LINES.
2017-09-29 08:50 | YES | NO | 19860102 |  | 26063 | MIAMI VALLEY CORP | YES | 1986-06-02 | 1257 | OH | MONTGOMERY | MAD RIVER | NO |  | NO | THE APPROXIMATE INTERSECTION OF SPRINGFIELD ROAD AND SMITHVILLE ROAD. |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4731.5148 | 9545.3766 | DIESEL FUEL | 3 | 523 | 510 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1230 | 1185 | YES | 24 | 1540 | 9 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | Null | D.L. AYERS, MANAGER ADMINISTRATION & OPERATIONS | 5138988101 | IN OCTOBER OF 1985, THE PIPELINE WAS STAKED SHOWING THE LOCATION AND THE APPROXIMATE DEPTH FOR THE MONTGOMERY COUNTY ENGINEERS. THEY WERE REDIRECTING THE LILY RUN CREEK AND LINING IT WITH CONCRETE AT THE TIME. THE MONTGOMERY COUNTY ENGINEERS STATED THEY WOULD NOT BE WORKING NEAR THE LINE AND THE ENGINEERS WERE WORKING. WHEN THE PIPE WAS EXPOSED, TWO GOUGES AND A DENT WERE FOUND ON THE PIPE. THE LINE WAS WELL MARKED WITH BOTH TEMPORARY AND PERMANENT PIPELINE IDENTIFICATION MARKER. ON JUNE 2, 1986, A CALL WAS RECEIVED FROM THE DAYTON FIRE DEPT. REPORTING THE LEAK AT APPROX. 12:57 P.M. THE PIPELINE CONTROL CENTER HAD ALSO NOTICED THE LEAK ON THE COMPUTERIZED SCADA SYSTEM AND HAD ALREADY TAKEN STEPS TO SHUT DOWN THE PIPELINE. THE NATIONAL RESPONSE CENTER (CHIEF PETTY OFFICER WALLACE) AND THE OHIO EPA WERE CALLED. THE AREA WAS CLEANED UP AND THE PIPELINE RETURNED TO SERVICE ON JUNE 3, 1986. THE DIESEL WAS REMOVED FROM THE SITE AND TAKEN TO COMPANY FACILITIES FOR RECOVERY/DISPOSAL.
2017-09-29 08:50 | YES | NO | 19860103 |  | 22359 | WESCO PIPELINE CO | YES | 1986-06-04 | 1145 | KS | COWLEY |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1918 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2365.7574 | 4772.6883 | CRUDE OIL | 1 | 660 | 410 | NO | NO | 8 | 0.32 | 1000 | THREADED |  | 600 | 760 | YES | 8 | 750 | 0 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | BOYD C. VRATIL, SUPERINTENDENT | 9182253469 | WE HAD A CONTRACTOR WORKING AT PONCA CITY STATION AND NEEDED THE STATION ISOLATED FROM THE MAINLINE. A WESCO EMPLOYEE WAS ISOLATING THE STATION AND IN THE PROCESS CLOSED THE WRONG VALVE SHUTTING OFF THE STREAM FROM EL DORADO, KS. OUR DISPATCHER AT CUSHING RECEIVED AN ALARM THAT BOYER STATION WENT DOWN ON HIGH DISCHARGE. WALNUT STATION WAS INJECTING INTO LINE AND WENT DOWN ON HIGH DISCHARGE. THE SURGE IN THE LINE CAUSED TO RUPTURE.
2017-09-29 08:50 | YES | NO | 19860104 |  | 18718 | SUN PIPELINE CO | YES | 1986-06-03 | 845 | OH | LUCAS | TOLEDO | NO |  | NO | BETWEEN SUMMIT ST. AND MANHATTEN @ B&P WRECKING, CONCRETE LANDFILL SITE, TOLEDO, OH |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 28389.089 | 57272.2594 | GASOLINE | 2 | 863 | 344 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1200 | 1100 | YES | 25 | 1650 | 7 | 53 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | LINE PATROL | NO | NO | ROBERT A. ARNETR, ENVIRONMENTAL & SAFETY COORD | 3132928850 | EQUIPMENT OPERATOR WAS MOVING TOP SOIL FROM SUN PIPELINE CO. ROW TO COVER CONCRETE AND SWARP AREA IN AN ADJACENT LANDFILL SITE. FRONT END LOADER PENETRATED 8" STEEL LINE CAUSING HOLE APPROXIMATELY 4"X6". NO LEAD GASOLINE WAS RELEASED FROM THE HOLE IN THE LINE AND ACCUMLATED IN A NEARBY DEPRESSION. A SMALL AMOUNT OF THE PRODUCT WAS BLOWN BY THE WIND INTO A NEARBY SWAMP AREA. EQUIPMENT OPERATOR TEMPORARILY PATCHED LINE WITH A WATER LINE CLAMP. SUN PIPE LINE CO. RESPONDED TO THE LEAK IMMEDIATELY. VISIBLE SPILLLED PRODUCT WAS RECOVERED TO THE SATISFACTION OF OHIO EPA REPRESENTATIVE ON SCENE. LINE REPAIRS WERE MADE IN APPROX. 2-1/2 DAYSAND LINE WAS RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19860105 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-06-11 | 1330 | TX | JOHNSON | GODLEY | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1957 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4731.5148 | 9545.3766 | DIESEL FUEL | 1 | 300 | 155 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 840 | 600 | YES | 24 | 1800 | 0 | 0 | NO DATA | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH, DIVISION MANAGER | 4098393100 | MINOR PRODUCT SHORTAGES INDICATED THE POSSIBILITY OF A LEAK AT APPROXIMATELY 6:00 A.M. ON JUNE 11, 1986. THIS COULD NOT BE IMMEDIATELY CONFIRMED BECAUSE AN ELECTRONIC PIG WAS BEING RUN IN THE LINE AND AT THE SAME TIME A CONTROL VALVE WAS OCCILATING. THE LINE WAS FLOWN SEVERAL TIMES BY AIR PATROL. NO LEAK WAS FOUND. ATAPPROX. 12 NOON A LANDOWNER PHONED IN REPORTING THE SMELL OF GASOLINE. THE LEAKWAS CONFIRMED AT 1:30 P.M. BY 7:45 P.M. CLEAN-UP OPERATIONS ARE ONGOING.
2017-09-29 08:50 | YES | NO | 19860106 |  | 5165 | FINA OIL & CHEMICAL CO | NO | 1986-05-28 | 930 | TX | ARCHER |  | NO |  | NO | 2.62 MILES NORTH OF ARCHER PUMP STATION 1.43 MILES SOUTH OF HWY 25 BETWEEN ARCHER CITY & HWY 277 |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1419.4545 | 2863.613 | DIESEL FUEL | 3 | 70 | 0 | NO | NO | 6 | 0.19 | 1716 | WELDED |  | 1200 | 575 | NO | 0 | 0 | 0 | 58 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | EXTERNAL CORROSION | Null | NO DATA |  | Null | Null | FRANK MASHBURN, PIPELINE SUPERVISOR | 9156734740 | SUSPECTED LEAK ON PIPELINE BECAUSE OF DIFFERENCES IN BARRELS BEING PUMPED AND RECEIVED. LINE SHUT DOWN UNTIL DAYLIGHT. PRESSURED LINE UP CHECK FOR LEAK. TOOK 30 BARRELS TO BRING LINE UP TO PRESSURE. BEFORE WE WERE ABLE TO DETERMINE SECTIONOF LINE WHERE LEAK WAS LOCATED. MR. GIL PETERS, A PUMPER IN THE AREA, CALLED THE WICHITA FALLS TERMINAL AND REPORTED THE LEAK SITE.
2017-09-29 08:50 | YES | NO | 19860107 |  | 443 | AMOCO PIPELINE CO | NO | 1986-05-10 | 1500 | TX | TRINITY |  | NO |  | NO | APPROX. 5 MILES NORTH OF HIGHWAY 94, TRINITY COUNTY, TX. |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 23025 | 21788.6258 | 43956.4591 | CRUDE OIL | 1 | 700 | 300 | YES | NO | 12 | 0.26 | 42000 | WELDED |  | 980 | 650 | YES | 8 | 1235 | 7 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LAND OWNER CONTACT | NO | NO | JOE NELSON, AREA MANAGER/OPERATIONS | 2147590005 | TEMPLE-EASTEX, INC. (LAND OWNER) WAS CLEARING TIMBER AREA WITH D-9 CATERPILLER WITH CLEARING BLADE AND STRUCK PIPELINE KNOCKING TWO (2) HOLES IN LINE. PUMPING EQUIPMENT WAS SHUT-DOWN IMMEDIATELY WHEN AMOCO OPERATOR NOTICED PRESSURE DROP AND INCREASED FLOW. MOST OF OIL LOSS RESULTED FROM HILL PRESSURE AFTER PUMPS WERE SHUT DOWN.
2017-09-29 08:50 | YES | NO | 19860108 |  | 2731 | CHEVRON PIPELINE CO | YES | 1986-06-16 | 925 | NM | VALENCIA |  | NO |  | NO | OFF HIGWAY 47, EAST OF EL CERRO LOOP ROAD SECT 6, TSP 6N R3E, VALENCIA COUNTY, NEW MEXICO |  | LINE PIPE | PIPE |  | 1954 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 37852.1187 | 76363.0125 | GASOLINE | 3 | 1140 | 0 | NO | NO | 7 | 0.25 | 42 | WELDED |  | 2080 | 1000 | YES | 24 | 2600 | 5 | 82 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | TV, NEWSPAPER, CONTACT | NO | NO | F. S.. GRANDA, MANAGER | 9156877551 | A VALENCIA COUNTY ROAD MAINTAINER (GRADER) WAS DEEPENING THE BAR DITCH ALONG SIDE A GRAVELED ROAD MAINTAINED BY THE COUNTY, (SEE AREA MAP AND SITE MAP ATTACHED). THE MAINTAINERS BLADE STRUCK CHEVRON PIPE LINE'S 6" PRODUCTS LINE, RESULTINGIN A RELEASE OF UNLEADED GASOLINE FROM THE LINE. THE MAINTAINER OPERATOR (ANDREW SAIR) IMMEDIATELY BACKED AWAY FROM THE SITE AND PROCEEDED TO A NEARBY HOUSE TO CALL THE SHERIFF'S DEPARTMENT. THE SHERIFF AND FIRE DEPT RESPONDED IMMEDIATELY TO THE SCENE AND DON PITTMAN (CHEVRON PIPE LINE SUPERVISOR) WAS CONTACTED AT 9:30 A.M. BY THE PUBLIC SERVICE COMMISSION OF NEW MEXICO. THE EL PASO PIPE LINE DISPATCHER WAS NOTIFIED AT 9:31 A.M. TO SHUT DOWN THE LINE. THE LINE WAS SHUT DOWN BY 9:35 A.M. THE VALENCIA COUNTY SHERRIFF'S AND FIRE DEPARTMENT HAD CLOSED OFF THE ROAD AND DIVERTED TRAFFIC. AT 9:35 A.M. CHEVRON PIPE LINE PERSONNEL WERE ON THEIR WAY TO THE SCENE, AND TO CLOSE M.P. 220 BLOCK VALVE. DON PITTMAN ANDRICK FILLINGER ARRIVED ON THE SCENE AT 10:10 A.M. PRODUCT WAS SPRAYING 20 FT. INTO AIR. FIRE DEPT WAS DAMMING BAR DITCH TO CONTAIN PRODUCT, SITUATION WAS UNDER CONTROL. M.P. 220 BLOCK VALVE CLOSED AT 10:15 A.M. DON PITTMAN CALLED ASST.MGR. VALENCIA COUNTY (MRS. BARBARA BEATTIE). DON PITTMAN SHOWED ALL PARTIES PRESENT (COUNTY SHERIFF, FIRE AND HIGHWAY PATROL) THE IN PLACE MARKER SIGNS AT ROAD CROSSING. WITH CONTRACT AND COMPANY CREWS LINE WAS REPAIRED AND BACK IN SERVICE BY 8:00P.M. 6/16/86. THE AMOUNT OF PRODUCT SPILLED WAS 1140 BBLS., NO PRODUCTWAS RECOVERED FROM THE GROUND.
2017-09-29 08:50 | YES | NO | 19860109 |  | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1986-06-22 | 2040 | CA | ALAMEDA |  | NO |  | NO | 1/4 CORNER BETWEEN SECTIONS 13 AND 24, T.2S.R.3E. 1 MILE NORTHWEST OF HWY. 580 AT GRANTLINE ROAD |  | LINE PIPE | PIPE |  | 1968 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 47315.1484 | 95453.7657 | CRUDE OIL | 1 | 7000 |  | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 940 | 0 | YES | 8 | 1175 | 1 | 67 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | G. G. HOHNSTEIN, PIPELINE SUPERINTENDENT | 8053270110 | DURING AN AUTOMATIC SHUT-DOWN OF THE PIPELINE A 6" DIAMETER CORROSION CELL FAILED CAUSING A 3-FOOT SPLIT IN THE PIPE.
2017-09-29 08:50 | YES | NO | 19860110 |  | 17062 | RANCHO PIPELINE SYSTEM | YES | 1986-05-27 | 1723 | TX | TRAVIS | OAK HILL | NO |  | NO | RANCHO 24-INCH PIPELINE 8451 FEET EAST OF FM 1826 J. M. BRIGHT SURVEY |  | LINE PIPE | NO DATA |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2350000 | 2223811.9746 | 4486326.9858 | CRUDE OIL | 1 | 2300 | 2055 | NO | NO | 24 | 0.31 | 52000 | WELDED |  | 975 | 350 | YES | 12 | 1121 | 1 | 53 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | YES | M. J. EICHLER, MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262 | A CONTRACTOR, GAREY CONSTRUCTION CO, CLEARING LAND WITH A DOZER AND RIPPER FOR AN INDUSTRIAL DEVELOPER HOOKED THE 24-INCH PIPELINE. CLEANUP IS STILL IN PROGRESS. A SUPPLEMENTAL REPORT WILL BE FILED WHEN CLEANUP IS COMPLETE. THE LEAK OCCURRED NEAR SLAUGHTER CREEK AND THE EDWARDS AQUIFER. A SKETCH IS ATTACHED TO SHOW THE LOCATION OF THE LEAK SITE AND THE EDWARDS AQUIFER.
2017-09-29 08:50 | YES | NO | 19860111 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-06-14 | 1623 | OK | PAYNE | CUSHING | NO |  | NO | ONE-FOURTH MILE SOUTH OF CUSING CITY LIMITS CUSHING TANK FARM |  | TANK FARM | NO DATA |  | 1941 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 378521.1872 | 763630.1252 | CRUDE OIL | 1 | 5577 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | M. J. EICHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262 | LIGHTNING STRUCK TANK 2 AT CUSHING TANK FARM. TANK WAS COMPLETELY DESTROYED, INCLUDING THE OIL IN THE TANK AT THE TIME.
2017-09-29 08:50 | YES | NO | 19860112 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-06-30 | 1430 | TX | LOVING | EL PASO | NO |  | NO | SECTION 38, BLOCK 54, T&P RAILROAD SURVEY, LOVING COUNTY TX |  | LINE PIPE | PIPE |  | 1957 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1419.4545 | 2863.613 | CRUDE OIL | 1 | 2000 | 1426 | NO | NO | 20 | 0.25 | 52 | WELDED |  | 520 | 161 | YES | 8 | 650 | 10 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | TV, NEWSPAPER | NO | NO | R. L. DOWNIE, MANAGER | 9156877551 | AT APPROXIMATELY 2:30 PM ON JUNE 30, 1986, THE 20" LINE FROM WINK TO EL PASO WASAS RUPTURED AT MP 168.28 BY A ROAD GRADER OWNED BY ORLA CONSTRUCTION CO WHILE WORKING ON THE DITCH BESIDE A COUNTY ROAD IN LOVING COUNTY, TX. THE BLADE OF THEROAD GRADER OPENED A GASH IN THE PIPE APPROXIMATELY 1-1/2" WIDE BY 8" LONG WHICH RESULTED IN A SPILL ESTIMATED AT NEAR 2,000 BARRELS. THE 20" LINE WAS QUICKLYSHUT DOWN AND VALVES CLOSED AT MP 162 (MASON STATION) AND MP 170 (PORTERVILLE JUNCTION) TO ISOLATE THE RUPTURED SECTION. MAINTENANCE PERSONNEL WERE DISPATCHEDFROM WINK, TX APPROXIMATELY 40 MILES AWAY. ORLA CONSTRUCTION CO PERSONNEL AND EQUIPMENT ALSO QUICKLY BEGAN CONSTRUCTION OF A CONTAINMENT BERM AROUND THE SPILLSITE. SEVEN VACUUM TRUCKS LOADED APPROXIMATELY 1,426 BARRELS OF CRUDE OIL FROMTHE CONTAINMENT AREA AND 574 BARRELS OF CRUDE OIL WERE SOAKED INTO THE SAND IN AN AREA APPROXIMATELY 300 FEET WIDE BY 600 FEET LONG. AT APPROXIMATELY 9:30 P.M. THE 20" LINE WAS PLACED BACK IN SERVICE AFTER TEMPORARY REPAIRS CONSISTING OF INSTALLATION OF A THREE-FEET LONG SECTION OF HALF-WRAP HELD IN PLACE WITH FOUR U-BOLT CLAMPS. PERMANANT REPAIRS WILL REQUIRE PIPE REPLACEMENT AS SOON AS EQUIPMENT AND SUPPLIES CAN BE ASSEMBLED AND SUFFICIENT DOWN TIME CAN BE SCHEDULED. THE TEMPORARY REPAIR WILL BE CLOSELY MONITORED UNTIL PERMANANT REPAIRS CAN BE AFFECTED. ORLA CONSTRUCTION CO WAS IN THE PROCESS OF IMPROVING AND WIDENING A COUNTYROAD. THE SURFACE OF THE ROADWAY HAD BEEN LOWERED ABOUT 18" BELOW NATURAL GRADEAND A DITCH OF MORE THAN TWO FEET DEPTH WAS BEING CUT BESIDE THE ROADWAY. THESPILL LOCATION HAS ADJACENT CROSSINGS OF NAVAJO PIPELINE CO., SHELL PIPELINECO. AND ALL AMERICAN PIPELINE CO. A PIPELINE MARKER WAS IN PLACE AND CLEARLYVISIBLE WITHIN TWENTY-ONE FEET OF THE DAMAGE LOCATION.
2017-09-29 08:50 | YES | NO | 19860113 |  | 2552 | COLONIAL PIPELINE CO | YES | 1986-06-13 | 1030 | MD | ANNE ARUNDEL |  | NO |  | NO | SEE ATTACHED |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 71000 | 67187.5107 | 135544.3472 | KEROSENE | 3 | 106 | 87 | NO | NO | 6 | 0.28 | 2960 | WELDED |  | 1200 | 270 | YES | 8 | 1810 | 7 | 81 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | J. S. SORROW, SENIOR ADMINISTRATOR | 4042611470 | AT 1030 HOURS ON 6/13/86 A TELEPHONE CALL WAS RECEIVED AT COLONIAL'S DORSEY JCT, MD, FACILITY FROM A CONTRACTOR ADVISING THAT HE HAD JUST RUPTURED A COLONIAL PIPELINE IN A NEW DEVELOPMENT NEAR THE BALTIMORE WASHNGTON INTERNATIONAL AIRPORT(BWI). CONSTRUCTION ACTIVITIES AT THE SITE HAVE BEEN IN PROGRESS FOR MORE THANSIX MONTHS AND THE PIPELINES HAVE BEEN LOCATED AND MARKED BY COLONIAL AT THE REQUEST OF REMOVE SPOIL FRON THE R/W WITH A FRONT-END LOADER WITHOUT GIVING NOTICETO COLONIAL AND MISJUDGED THE DEPTH OF THE PIPELINE CAUSING THE ACCIDENT. THREE PIPELINES ARE LOCATED IN THE R/W. THE 6" DIA. BWI DELIVERY PIPELINE WAS IDLE AT THE TIME AND THE OTHER TWO OPERATING PIPELINES WERE SHUT DOWN AND ISOLATED BECAUSE THE CONTRACTOR REPORTED A GASOLINE SPILL. IT WAS FOUND THAT THE 6" BWI HAD BEEN STRUCK BY AVIATION KEROSINE. THE CONTRACTOR USED HIS MACHINE TO CONSTRUCT AN EARTHEN DIKE AROUND THE LEAK SITE TO CONTAIN THE OIL. COLONIAL EMERGENCY PERSONNEL RECOVERED 87 BBLS. OF THE SPILLED OIL LEAVING A NET LOSS OF 19 BBL. THE ANNE ARUNDEL COUNTY FIRE AND POLICE DEPT. WERE NOTIFIED BY COLONAL AND RESPONDED TO THE SCENE. THE FEDERAL EPA AND MARYLAND DEPT. OF WATER RESOURCES WERE NOTIFIED AND RESPONDED TO THE SITE. A REPAIR CLAMP WAS BOLTED AROUND THE DAMAGED PIPE TO PREVENT ADDITIONAL PRODUCT LEAKAGE UNTIL THE AREA WAS MADE SAFE FOR WELDING. THE REPAIR CLAMP WAS THEN WELDED TO THE PIPE TO SERVE AS A TEMPORARY REPAIRUNTIL THE DAMAGED SECTION OF PIPE CAN BE REMOVED AND REPLACED.
2017-09-29 08:50 | YES | NO | 19860115 |  | 12127 | MARATHON PIPE LINE CO | YES | 1986-06-26 | 1610 | IN | LA PORTE |  | NO |  | NO | APPROXIMATELY 1500 FT. EAST OF COUNTY RD300W AT THE SECTION LINE BETWEEN SECTION NO. 27 AND 34. |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 540625 | 511595.042 | 1032093.8411 | FUEL OIL | 3 | 1113 | 557 | YES | NO | 10 | 0.25 | 42000 | WELDED |  | 1407 | 1050 | YES | 24 | 1792 | 9 | 71 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H. E. MILLER, VICE PRESIDENT | 4194222121 | AT APPROXIMATELY 1601 CDT, THURSDAY, JUNE 26, THE LOTTAVILLE PUMPING UNIT ON THE MUSKEGON 10" PRODUCTS PIPELINE SHUT DOWN ON LOW SUCTION PRESSURE. THE UNIT WAS RESTARTED BUT WAS SHUT BACK DOWN WHEN FLOW RATE AND PRESSURE INDICATED A PROBABLE LEAK. A SURFACE AND AERIAL SURVEILLANC EOF THE LINE WAS INTIATED AT 1634 AND AN ALL NIGHT SEARCH OF CREEK AND ROAD CROSSINGS DID NOT LOCATE THJE ESCAPED PRODUCT. ON FRIDAY, JUNE 27, AT 0640, IN HEAVY RAIN, AND WITH A LEAK LOCATION PREDICTED FROM OPERATING DATA OBTAINED FROM RECORDING CHARTS, CREWS STARTED WALKINGTHE LINE. AT 0830 TH ELEAK SITE WAS LOCATED. THE SITE WAS ABOUT 8 MILES EAST OF MICHIGAN CITY, INDIANA IN A PIPE SPAN OVER A DRAINAGE DITCH. A SEARCH WAS THEN STARTED TO FIND THE LEADING EDGE OF THE FUEL OIL WHICH HAD ENTERED A TRIBUTARY TO THE EAST BRANCH OF TRAIL CREEK. CONTAINMENT BOOMS AND PICKUP POINTS WERE SET UP ABOUT 5 AND 7 MILES DOWNSTREAM FROM THE LEAK SITE. HOWEVER, HEAVY RAINS AND RESULTING RUNOFF SWELLED AND STREAMS AND HAMPERED PICKUP. ON SATURDAY MORNING, JUNE 28, THE COAST GUARD PLACED THREE BOOMS ACROSS TRAIL CREEK APPROXIMATELY 13 MILES FROM THE LEAK SITE NEAR DOWNTOWN MICHIGAN CITY. PRODUCT WAS CONTAINED BY ONE OF THE BOOMS UNDER THE "E" STREET BRIDGE AND A FIRE OF UNKNOWN ORIGIN ENSUED. THE FIRE DID MINOR DAMAGE TO COMMUNICATION CABLES SUSPENDED ON THE BRIDGE. THE BRIDGE WAS CLOSED TO TRAFFIC AND REMAINS CLOSED AWAITING INSPECTION BY THECOUNTY HIGHWAY DEPT. NO PERSONAL INJURY OCCURRED. THE DAMAGED PIPELINE SPAN WASREPLACED WITH NEW HYDROSTATICALLY TESTED PIPE AND THE LINE LOWERED UNDER THEDITCH. THE LINE WAS PLACED BACK IN SERVICE SUNDAY EVENING 1815. IN ORDER TOASSURE THE INTEGRITY AND STRENGTH OF THIS PIPELINE SYSTEM, AND INSPECTION OFOTHER PIPE SPANS IN THE SYSTEM HAS BEEN CONDUCTED. 557 BARRELS WERE RECOVEREDAND RETURNED TO MARATHON TERMINAL. AN ESTIMATED 146 BARRELS WERE PICKEDUP WITH SORBENT BOOMS AND PADS. ALSO, IT IS ANTICIPATED THAT ABOUT 56BARRELS WOULD HAVE REMAINED IN THE FLEET OF 14 VACUUM AND TRANSPORT TRUCKSUSED TO PICK UP AND HAUL THE PRODUCT TO THE MARATHON TERMINAL. AN ESTIMATED129 BARRELS WERE LOST IN FIRE AND 147 EVAPORATED DURING THE 12-DAY CLEANUP.
2017-09-29 08:50 | YES | NO | 19860116 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1986-07-20 | 430 | TX | HUTCHINSON | FRITCH | NO |  | YES | SECTION 15 - 3/4 MILE WEST OF HIGHWAY 136 |  | LINE PIPE | NO DATA |  | 1968 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 22911 | 21680.7473 | 43738.8245 | NATURAL GAS LIQUID | 2 | 2519 | 0 | NO | NO | 5 | 0.13 | 1944 | WELDED |  | 1400 | 1225 | YES | 24 | 1750 | 3 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S. F. ISAACS, PRESIDENT | 9185811800 | BRINE VALVE WAS INADVERTENTLY CLOSED AT THE WELLHEAD.
2017-09-29 08:50 | NO | NO | 19860117 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-07-09 | 1530 | TX | ERATH |  | NO |  | NO | 1/4 MILE NORTH OF HWY. 20 11 1/2 MILES EAST OF THE CITY OF RANGER, EASTLAND COUNTY, TX |  | LINE PIPE | NO DATA |  | 1929 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 40 |  | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  | 0000000000
2017-09-29 08:50 | YES | NO | 19860118 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-06-07 | 1945 | TX | FREESTONE | WORTHAM | NO |  | NO | 1 MILE EAST OF WORTHAM DIRECTLY 40' NORTH OF STOCK POND NEAR HWY. 246 |  | LINE PIPE | PIPE |  | 1924 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 85 | 18 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 750 | 600 | YES | 24 | 1800 | 0 | 0 | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH, DIVISION MANAGER | 4098393100 | LANDOWNER NOTIFIED THE STATION ATTENDANT ABOUT THE LEAK AT 7:45 P.M. REPAIR CREW ARRIVED AT THE LEAK SITE AT 8:30 P.M. AND STARTED LOOKING FOR THE EXACT LOCATION OF THE LEAK. THE PIPELINE LEAK WAS TEMPORARILY REPAIRED WITH SADDLES, 3-10"WITH PLATE AND #3 RUBBER PLUG. STATION WAS NOTIFIED AND SYSTEM WAS BACK TO NORMAL OPERATION AT 10:45 P.M. ELECTRIC INSPECTION IS BEING RUN IN THIS SECTION FOR EVALUATION OF THE LINE PIPE'S INTEGRITY. RAILROAD COMMISSION OF TEXAS ORDEREDAND SO CONTAMINATED SOIL IS BEING HAULED BY CHEMICAL WASTE MANAGEMENT TO A DUMPSITE AT CARLYSS, LOUISIANA. HAULING OPERATION IS STILL GOING ON. SLOWDOWN IS CAUSED BY THE RECENT HEAVY RAINS IN THE AREA.
2017-09-29 08:50 | NO | NO | 19860119 |  | 2731 | CHEVRON PIPELINE CO | YES | 1986-06-11 | 1230 | TX | ANGELINA | LUFKIN | NO |  | NO |  |  | PUMPING STATION | SCRAPER TRAP |  | 1985 | OTHER | O RING IN SCRAPER TRAP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1250 | 1182.8787 | 2386.3441 | L. P. G. | 1 | 25 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH, DIVISION MANAGER | 4098393100 | O" RING IN SCRAPER TRAP LID BLEW OUT CAUSING LPG TO ESCAPE TO ATMOSPHERE. THEL.P.G. DISSIPATED INTO THE ATMOSPHERE LEAVING NO RESIDUE TO BE CLEARED UP. INCIDENT OCCURRED AT OUR LUFKIN STATION. REPAIR WAS COMPLETE AND SYSTEM BACK IN NORMAL OPERATION AT 3:00 P.M.
2017-09-29 08:50 | YES | NO | 19860120 |  | 26134 | MOBIL OIL CORP - WEST COAST PIPELINES | Null | 1986-06-23 | 220 | CA | TORRANCE |  | NO |  | NO | PRAIRIE AVENUE AT 185TH STREET |  | NO DATA | PIPE |  | 1977 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 283890.8904 | 572722.5939 | CRUDE OIL | 1 | 150 | 130 | NO | NO | 10 | 0.37 | 2377 | WELDED |  | 1440 | 733 | YES | 5 | 1800 | 10 | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. E. ROBBINS, MANAGER WEST COAST PIPE LINE | 2133282550 | THE SEAM OF A TRANSITION NIPPLE APPARENTLY FAILED DURING THE PRESSURIZING OF THE PIPELINE IN PREPAREATION FOR A HYDROSTATIC TEST.
2017-09-29 08:50 | YES | NO | 19860121 |  | 443 | AMOCO PIPELINE CO | YES | 1986-07-11 | 845 | WY | UINTA |  | NO |  | NO | LEAK OCCURRED AT AMOCCO PIPELINE'S ANSCHUTZ RANCH EAST PUMP IN UINTA CO. WY. SITE IS APPROX/16MI SOUTH OF EVANSTON |  | PUMPING STATION | PUMP |  | 1986 | OTHER | PACKING ON PD PUMP FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1900 | 1797.9756 | 3627.2431 | CRUDE OIL | 1 | 140 | 140 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. W. WHITE, AREA MANAGER, WEST OPERATIONS | 3072662119 | THE LEAK WAS DISCOVERED AT ABOUT 8:45 A.M., JULY 11, 1986. THE PACKING FAILED ON PD PUMP NUMBER 4 AT ANSCHUTZ RANCH EAST STATION. ALL SPILLED OIL WAS CONTAINED INSIDE THE DIKE SURROUNDING THE STATION. APPROXIMATELY 140 BARRELS EITHER WERE PICKED UP AND PUT BACK INTO THE PIPELINE SYSTEM WITH VAC TRUCKS OR EVAPORATED. REPAIR WAS MADE BY REPLACING PACKING.
2017-09-29 08:50 | YES | NO | 19860122 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1986-07-09 | 650 | NY | ERIE | CHEEKTOWAGA | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1962 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 21200 | 20061.6229 | 40472.3966 | CRUDE OIL | 1 | 406 | 400 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 775 | 400 | YES | 24 | 1696 | 5 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | W. C. COCHRANE, PRESIDENT & GENERAL MANAGER | 7153925631 | AN ADJACENT LANDOWNER WAS EXCAVATING WITH A D-8 DOZER ON THE PIPE LINE RIGHT-OF-WAY TO BURY DEBRIS. WHILE DIGGING A DISPOSAL PIT HE STRUCK THE PIPE LINE, RESULTING IN A SPILLAGE OF 406 BARRELS OF OIL. THE OIL WAS CONTAINED IN THE DISPOSAL PIT. TANKER TRUCKS WERE USED TO RECOVER 400 BARRELS OF OIL, WHILE 6 BARRELS OF OIL BECAME SATURATED IN ADJACENT SOIL. THE SATURATED SOIL WAS EXCAVATED AND REMOVED TO AN APPROVED LANDFILL SITE. THE PIPE LINE WAS REPAIRED WITH A 12'-4' SECTION OF PRETESTED LINE PIPE AND TWO WELD + COUPLINGS.
2017-09-29 08:50 | NO | NO | 19860123 |  | 443 | AMOCO PIPELINE CO | YES | 1986-06-10 | 1800 | OK | CREEK | DRUMRIGHT | NO |  | NO | NE 1/4 SW 1/4 33 T18N - R7E. 1 MI E & 1/4 MI N OF DRUMRIGHT, OK |  | NO DATA | NO DATA |  | 1944 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6624.1208 | 13363.5272 | CRUDE OIL |  | 0 | 0 | Null | Null | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | J. W. WILHELM, AREA MANAGER OPERATIONS | 9182252243 | TANK 6695, A HIDECK FLOATING ROOF, 80M BBL CAPACITY TANK WAS FULL OF "C" CRUDE. LIGHTNING HIT THE TANK SETTING THE ROOF SEAL OF FIRE. COMPANY PERSONNEL AND DRUMRIGHT FIRE DEPT. RESPONDED AND PUT THE FIRE OUT IN ABOUT ONE HOUR. NO CRUDE WAS SPILLED OR LOST EXCEPT THE SMALL AMOUNT CONSUMED BY THE FIRE. NO ONE WAS HUR
2017-09-29 08:50 | YES | NO | 19860124 |  | 5165 | FINA OIL & CHEMICAL CO | NO | 1986-07-26 | 1800 | TX | TAYLOR |  | NO |  | NO | 8 MILES WEST OF TYE, TEXAS ON SOUTH SIDE OF IS-20 & SOUTH OF RR TRACK |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 66241.2078 | 133635.2719 | GASOLINE | 3 | 2500 | 1600 | NO | NO | 9 | 0.2 | 42000 | WELDED |  | 1423 | 330 | YES | 0 | 0 | 1 | 58 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | SIGNS & PERSONAL | NO | YES | T. M. YEATS, PRODUCTS PIPELINE SUPERINTENDENT | 9152637661 | B E & K COMMUNICATIONS WAS TRENCHING IN A COMMUNICATION CABLE. THE TRENCHING PLOW PENETRATED A 12" CASING AND CUT INTO THE 8" PRODUCT LINE.
2017-09-29 08:50 | YES | NO | 19860125 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1986-07-24 | 1138 | AR | PULASKI | LITTLE ROCK | NO |  | NO | ON TX EASTER 20-INCH PIPELINE P-2; 4100 FEET SOUTH OF ASHER RD/FOURCHE BAYOU, AND APPROXIMATELY 12 MILES SOUTH OF LITTLE ROCK, AR |  | LINE PIPE | PIPE |  | 1944 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KEROSENE | 3 | 100 | 60 | NO | NO | 20 | 0.31 | 35000 | WELDED |  | 690 | 125 | YES | 24 | 1149 | 1 | 57 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | YES | NO | BERT PURGATORIO, VICE PRESIDENT & CHIEF ENGINEER | 7137595454 | ON JULY 24, 1986, AT APPROXIMATELY 11:38 HOURS, A ROAD GANG AT THE DEPT OF CORRECTIONS FACILITY AT WRIGHTSVILLE, AR, PUNCTURED TEXAS EASTERN'S 20-INCH P-2 PIPELINE WITH A ROAD GRADER. PERSONNEL AT THE FACILITY IMMEDIATELY NOTIFIED TEXAS EASTERN AND THE LINE WAS SHUT DOWN WITHIN A FEW MINUTES. THE UPSTREAM VALVE WAS CLOSED AT APPROXIMATELY 1200 HOURS AND THE DOWNSTREAM VALVE AT APPROXIMATELY 1332 HOURS. APPROXIMATELY 100 BARRELS WERE SPILLED, BUT WAS TOTALLY CONTAINED IN DRAINAGE DITCHES AND RETURNED TO TEXAS EASTERN TANKAGE. IN ACCORDANCE WITH THE ARKANSAS EPA OFFICIALS, THE EARTH ON WHICH THE PRODUCT SPILLED WAS PICKED UP AND SPREAD OUT TO AERATE. THE LINE WAS REPAIRED BY WELDING A FULL ENCIRCLEMENT SLEEVE OVER THE DAMAGED AREA. THE PIPELINE WAS LACED BACK IN SERVICE AT 0023 HOURS ON JULY 25, 1986.
2017-09-29 08:50 | YES | NO | 19860126 |  | 7063 | HARBOR PIPELINE CO | NO | 1986-08-04 | 337 | NJ | MIDDLESEX | NEW BRUNSWICK | NO |  | NO | INTERSECTION OF ROUTE 1 AND ROUTE 18 IN NEW BRUNSWICK, NEW JERSEY (SEE ATTACHED MAPS). |  | LINE PIPE | PIPE |  | 1955 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9463.0297 | 19090.7531 | DIESEL FUEL | 3 | 2505 |  | NO | NO | 16 | 0.28 | 52 | WELDED |  | 1100 | 700 | YES | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. AYERS, MANAGER ADMIN/OPERATION COORDINATOR | 5138988101 | ON AUGUST 4, 1986, AT 0130, THE LINDEN TERMINAL ON THE HARBOR 16" STARTED A DELIVERY TO THE TEXAS PIPE LINE COMPANY IN NEWARK, NEW JERSEY. AT APPROXIMATELY 0337, THE TEXAS PIPE LINE COMPANY SWUNG TO A DIFFERENT TANK AND A VALVE FAILURE CLOSED IN ON THE DELIVERY LINE. THE SCADA SYSTEM AND THE RELIEF SYSTEM OPERATED PROPERLY, WHICH CAUSED THE HARBOR 16" PUMPS TO SHUT DOWN, THE LINDEN INLET AND OUTLET BLOCK VALVES TO CLOSE, AND THE STATION RELIEF VALVE, WHICH PROTECTS THE 12"AND THE STATION PIPING AND IS SET AT 450 PSIG, TO RELIEVE. THE 16" RELIEF VALVE DID NOT RELIEVE BECAUSE IT IS SET AT 705 PSIG AND THE PRESSURE DID NOT GET THAT HIGH. THE DECISION WAS MADE TO TEST THE 16" LINE BEFORE START UP AND THE LEAKWAS FOUND.THE FAILED SECTION OF PIPE WILL BE ANALYZED BY AN OUTSIDE LAB AND THE RESULTS SENT TO THE DOT'S MR. RALPH KUBITZ PER HIS REQUEST.
2017-09-29 08:50 | YES | NO | 19860127 |  | 4906 | EXXON PIPELINE CO | NO | 1986-07-11 | 1030 | LA | WEBSTER |  | NO |  | NO | THE LEAK WAS LOCATED ON EXXON PIPELINE COMPANY'S WELLER TO RED CHUTE 8" CRUDE OIL TRUNK LINE, 6 MILES NORHTWEST INTERSECTION OF HIGHWAYS 80 AND 7. |  | LINE PIPE | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 14420 | 13645.6888 | 27528.866 | CRUDE OIL | 1 | 255 | 250 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 600 | 85 | YES | 8 | 660 | 0 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT 1030 HOURS ON JULY 11, 1986, A LOGGING CREW HIT OUR LINE WITH A BLADE ON THEFRONT OF THEIR TRACTOR. THE OPERATOR IMMEDIATELY NOTIFIED HIS SUPERVISOR, BOBBY GREEN, OF MINDEN, LA., WHO CONTACTED EPC'S HOUSTON DISPATCHER BY PHONE AT 1100HOURS AND GAVE A BRIEF DESCRIPTION OF THE ACCIDENT. THE DISPATCHER THEREBY SHUT DOWN THE WELLER TO RED CHUTE LINE AT 1115 HOURS. THE OIL WAS CONTAINED BY NATURAL SURROUNDINGS.EPC PERSONNEL AND CONTRACTED EQUIPMENT AND VACUUM TRUCK WERE DISPATCHED TO THE LEAK SITE AT ABOUT 1300 HOURS. THE LINE WAS PERMANENTLY REPAIRED BY REPLACING A5-FOOT SECTION OF 8" PIPING. THE LINE WAS RESTORED TO SERVICE AT 1930 HOURS ON7/14/86.FINAL CLEANUP OPERATIONS ARE STILL PENDING SOIL SAMPLES BEING SENT FOR ANALYSIS.
2017-09-29 08:50 | NO | NO | 19860128 |  | 2162 | CAYUSE PIPELINE CO | YES | 1986-05-31 | 700 | LA | CALCASIEU | EDGERLY | NO |  | NO | LEAK SITE LOCATED ONE (1) MILE WEST OF EDGERLY, 289 FEET SOUTH OF HIGHWAY 90 AND 1,235 FEET WEST OF LISA DRIVE. |  | LINE PIPE | PIPE |  | 1943 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | L. P. G. | 3 | 37 | 0 | NO | NO | 10 | 0.37 | 30000 | WELDED |  | 600 | 360 | YES | 24 | 860 | 2 | 80 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | HAROLD MESCHKE, OPERATIONS SUPERVISOR | 5043898821 | A LINE LEAK WAS REPORTED TO DOW BY A PASSERBY AT 7:00 A.M. ON MAY 31, 1986. THE CONTROL ROOM THEN NOTIFIED SUPERVISION AND DISPATECH A TECHNICIAN TO THE POSSIBLE LEAK SITE. THE LOCAL OFFICIALS WERE NOTIFIED AT THIS TIME. THEY WERE AWAREOF IT BUT THOUGHT IT WAS A CITY SERVICE LINE. AT 7:30 A.M. WE RECEIVED A LOW PRESSURE ALARM AT OUR EAST VINTON STATION JUST UPSTREAM OF THE REPORTED LEAK. THE STATION BLOCK WAS REMOTELY CLOSED AT THIS TIME. AT 8:00 A.M. THE DOW TECHNICIAN REPORTED HE WAS AT THE LEAK SITE AND IT WAS OUR LINE. ANOTHER TECHNICIAN WASDISPATCHED TO THE NEAREST DOWNSTREAM STATION TO BLOCK IT IN MANUALLY. AT 8:46 A.M. THE DOWNSTREAM VALVE WAS REPORTED CLOSED. PREPARATIONS WERE THEN MADE TO PURGE THE AFFECTED SECTION WITH NITROGEN TO REMOVE THE PROPANE FROM THE LINE. AT5:30 P.M. THE LEAK WAS STOPPED. INVESTIGATION OF THE LEAK SHOWED IT TO BE LOCATED IN AN OLD EXTERNAL CORROSION SITE. THE LINE IS COATED AND UNDER CATHODIC PROTECTION. WE HAVE NO FURTHER EXPLANATION FOR THE CAUSE AT THIS TIME, THOUGH FURTHER INVESTIGATION IS STILL UNDER WAY AND THIS SECTION OF LINE IS BEING REPLACEDWITH NEW PIPE.
2017-09-29 08:50 | YES | YES | 19860129 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-07-08 | 420 | MN | RAMSEY | MOUNDS VIEW | NO |  | NO | LONG LAKE ROAD AND WOODCREST DRIVE, MOUNDS VIEW, MN. |  | LINE PIPE | LONGITUDINAL WELD |  | 1957 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 2 | 0 | 2 | 1 | 0 | 1 | 1400000 | 1324824.1551 | 2672705.4383 | GASOLINE | 2 | 493 | 15 | YES | NO | 8 | 0.25 | 2435 | WELDED |  | 1500 | 1434 | YES | 8 | 1900 | 0 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.K. MCCAW, VICE PRESIDENT | 9185883248 | ON JULY 7, UNLEADED GASOLINE WAS BEING PUMPED THROUGH THE #2-8" PIPELINE FROM MINNEAPOLIS, MN TO THE DULUTH/SUPERIOR AREA. AT 0400 HOURS ON JULY 8 A PRODUCT SWITCH FROM UNLEADED GASOLINE TO #2 FUEL OIL WAS MADE. AT ABOUT 0420 HOURS THE MINNEAPOLIS STATION OPERATOR NOTICED RELAYS DROPPING IN THE UNIT CONTROL CABINET AND PROCEEDED TO INSPECT THE PUMP UNIT AND PIPING. AT 0421 HOURS, THE TULSA DISPATCHER RECEIVED AN ALARM THAT INDICATED A PRESSURE DROP ON THE STATION DISCHARGE. HE CONTACTED THE STATION OPERATOR TO CONFIRM READINGS AND AT 0424 HOURS, EXECUTED AN EMERGENCY STOP OF THE PUMP UNIT, THEN PROCEEDED TO CLOSE THE MAINLINE GATE VALVES. EMERGENCY RESPONSE PERSONNEL WERE CALLED TO LOOK FOR A SUSPECTED LEAK. AT 0500 HOURS, RAMSEY COUNTY SHERIFF'S DEPARTMENT CALLED AND REPORTED A FIRE ON LONG LAKE ROAD IN MOUNDS VIEW.
2017-09-29 08:50 | YES | NO | 19860130 |  | 1845 | BUCKEYE PIPELINE CO LP | YES | 1986-07-14 | 1120 | NY |  | KINGS (BROOKLYN) | NO |  | NO | SEE ATTACHED SHEET |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 44476.2395 | 89726.5397 | GASOLINE | 1 | 159 | 60 | NO | NO | 12 | 0.38 | 3529 | WELDED |  | 1000 | 580 | YES | 36 | 1175 | 3 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | NO | NO | JAMES J. KELLY, MANAGER, ENVIRONMENTAL CONTROL AND SAFETY | 2158208300 | ON MONDAY, JULY 14, 1986, AT 1120 HOURS, A MODEL 983 CATERPILLAR FRONT-END LOADER RUPTURED THE PIPELINE BY STRIKING IT WITH A TOOTH OF THE BUCKET CAUSING A 4-INCH LONG OPENING IN OUR 12-INCH PIPELINE WHICH ORIGINATES IN LINDEN, NJ, AND TERMINATES IN LONG ISLAND CITY, NY. THIS OCCURRED IN BROOKLYN, KINGS COUNTY, NEW YORK. AT THE TIME OF THE RUPTURE, THE PIPELINE WAS NOT OPERATING BUT WAS UNDER NORMAL CLOSED IN PRESSURE. THIS ALLOWED GASOLINE TO ESCAPE AND VAPORIZE. NO IGNITION OF VAPORS OCCURRED. APPROXIMATELY 159 BARRELS WERE RELEASED AND TO DATE WE HAVE RECOVERED 60 BARRELS. A SCAVENTER-TYPE INITIAL RUPTURE, MANY BARRELS WERE VAPORIZED, AND, THEREFORE, THERE WILL NOT BE A TOTAL RECOVERY.
2017-09-29 08:50 | YES | NO | 19860131 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-07-28 | 940 | MO | CLAY | KANSAS CITY | NO |  | NO | THE SOUTHEAST CORNER OF THE INTERSECTION OF HIGHWAY 169 AND BARRY ROAD. THE SPILL WAS APPROXIMATELY 1/4 MILE SOUTH OF A LARGE SHOPPING MALL(METRO NORTH). |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 94630.2968 | 190907.5313 | GASOLINE | 2 | 1749 |  | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 1250 | 636 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PIPELINE MARKINGS AND SUR | YES | YES | C.K. MCCAW, VICE PRESIDENT | 9185883248 | ON MONDAY, JULY 28, 1986, AT 0940 HOURS, DAMON PURSELL CONSTRUCTION COMPANY, NOTIFIED THE DIVISION OFFICE THAT A DOZER OPERATOR STRUCK WPL'S #6-12" PIPELINE. THE DOZER WAS REMOVING SOIL IN PREPARATION FOR AN 8' X 9' BOX CULVERT AT THE SOUTHEAST CORNER OF BARRY ROAD AND HIGHWAY 169 INTERSECTION IN KANSAS CITY, MO. THEDOZER BLADE LEFT AN 8" GOUGE IN THE LINE, RESULTING IN A LEAK OF APPROXIMATELY 1749 BARRELS OF UNLEADED GASOLINE. THE LINE WAS SHUTDOWN AND THE GATE VALVE AT MP 12+18 WAS CLOSED IMMEDIATELY. A CHECK VALVE IS IN PLACE AT MP 2+52 WHICH ISOLATES ON THE SOUTH SIDE OF THE LEAK. THREE (3) MAINTENANCE CREWS AND ONE (1) ENVIRONMENTAL CONTRACTOR WERE DISPATCHED TO THE SITE FOR LEAK CONTAINMENT, CLEANUP AND LINE REPAIRS. A 200' SECTION OF LINE WAS SPOOLED IN SO THAT REPAIRS COULD BEMADE IN A GASOLINE VAPOR-FREE ENVIRONMENT. THE KANSAS CITY FIRE DEPT., SANITATION DEPARTMENT, FEDERAL EPA, AND THE MISSOURI DEPT. OF NATURAL RESOURCES WERE COOPERATIVE AND WERE COMPLIMENTARY OF OUR RESPONSE AND CLEANUP EFFORTS. THE REGIONAL OFFICE OF THE FEDERAL EPA WAS NOTIFIED OF THE ACCIDENT AT 1047 HOURS, THE MISSOURI DNR AT 1054 HOURS, AND THE NATIONAL RESPONSE CENTER AT 1615 HOURS. THE DAMAGED PIPE HAS BEEN REMOVED AND WILL BE KEPT ON HAND FOR 60 DAYS AT THE KANSAS CITY WAREHOUSE. THE LINE WAS REPAIRED AND RETURNED TO SERVICE AT 0445 HOURS ON JULY 29,1986. CLEANUP SHOULD BE COMPLETED BY AUGUST 4, 1986.
2017-09-29 08:50 | YES | NO | 19860132 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1986-08-15 | 1045 | TX | NEWTON | CALL JUNCTION | NO |  | NO | ON TEXAS EASTERN 2-INCH PIPELINE P-2; APPROXIMATELY 2 MILES SOUTH OF FM 1004 AND 3 MILES WEST OF HIGHWAY 87; NEWTON COUNTY, TEXAS; NEAR CALL JUNCTION, TX; LOCAT |  | LINE PIPE | PIPE |  | 1944 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 28389.089 | 57272.2594 | L. P. G. | 3 | 17294 |  | YES | NO | 20 | 0.31 | 35000 | WELDED |  | 700 | 233 | YES | 24 | 1113 | 0 | 57 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | BERT R. PURGATORIO, JR. | 7137595454 | ON FRIDAY, AUGUST 15, 1986, AT APPROXIMATELY 10:45 HOURS, TEXAS EASTERN 20-INCHP-2 PIPELINE WAS PUNCTURED BY A ROAD GRADER (ROAD MAINTAINER) AT PIPELINE MILE POST 43.3, NEAR THE JUNCTION OF HIGHWAY 87 AND FM 1004 IN NEWTON COUNTY, TEXAS APPROXIMATELY 13 MILES SOUTH OF TEXAS EASTERN'S NEWTON STATION. THE PIPELINE WASMARKED WITH A CONCRETE PIPELINE MARKER, LOCATED DIRECTLY OVER THE PIPELINE AND APPROXIMATELY TEN (10) FEET FROM THE POINT WHERE THE PIPELINE WAS STRUCK.THE ROAD GRADER OPERATOR NOTIFIED THE COUNTY SHERIFF; THE SHERIFF THEN NOTIFIEDTEXAS EASTERN'S REMOTE STATION OPERATOR AT 11:03 HOURS, AND THE 20-INCH P-2 PIPELINE WAS SHUT DOWN AT 11:15 HOURS.AFTER THE SHERIFF HAD EVACUATED AND SECURED THE AREA; AND HAVING INFORMED THE STATE POLICE, LOCAL FIRE DEPARTMENT, AND FOREST SERVICE; THE PROPANE CLOUD EMITTING FROM THE PIPELINE WAS INTENTIONALLY SET OFF WITH A FLARE GUN BY TEXAS EASTERNPERSONNEL AT 15:14 HOURS. THE SOUTH ISOLATION VALVE AT MILE POST 28.13 WAS CLOSED AT 13:28 HOURS, AND THE NORTH ISOLATION VALVE AT MILE POST 56.11 WAS CLOSED AT 14:40 HOURS. PIPELINE STOPPLES WERE SET AT 20:25 HOURS, ON SATURDAY, AUGUST 16, 1986, NEAR THE BREAK TO FURTHER ISOLATE THE AREA. THE DAMAGED SECTION OF THEPIPELINE WAS REPLACED, AND THE PIPELINE WAS RETURNED TO SERVICE ON MONDAY, AUGUST 18, 1986, AT 2:35 HOURS.
2017-09-29 08:50 | YES | NO | 19860134 |  | 26125 | CALNEV PIPELINE CO | NO | 1986-08-13 | 1500 | WY | CARBON | RAWLINS | NO |  | NO | 2 MILES EAST OF THE UNION PACIFIC STATION IN RAWLINS, ALONG THE RAILROAD TRACKS AND NEAR THE I-80 OVERPASS. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 14194.5445 | 28636.1297 | DIESEL FUEL | 1 | 225 | 70 | NO | NO | 4 | 0.13 | 1950 | WELDED |  | 550 | 100 | YES | 8 | 900 | 0 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | PAUL B. STRENGELL, MGR/ENGINEERING | 7148887771 | PIPE WAS DAMAGED BY A RIPPER PREPARING TO INSTALL AN OPTIC-FIBER CABLE. OPERATOR SAYS HE WAS UNAWARE OF THE PIPELINE OR THAT HE HIT IT. NEAREST MARKER WAS 175 FEET AWAY AND IN PLAIN VIEW. STATE DOES NOT HAVE A ONE-CALL SYSTEM IN EFFECT, AND PIPELINE OPERATOR WAS UNAWARE OF THE CONSTRUCTION ACTIVITY. RAILROAD ATTEMPTEDTO PUMP DIESEL THROUGH THE LINE NEXT DAY (LINE WAS SHUT DOWN WHEN DAMAGED). PUMP RAN FOR LESS THAN ONE HOUR WHEN REPORTS OF A SPILL CAME IN. LINE WAS SHUT DOWNAND SECURED IMMEDIATELY, AND 70 BARRELS OF PRODUCT WERE RECOVERED FROM THE SURFACE. REPAIRS WERE MADE THE FOLLOWING DAY, AND SERVICE RESUMED. CONTAMINATED SOILWAS REMOVED AND CLEAN UP FINISHED BY 08/20/86.
2017-09-29 08:50 | YES | NO | 19860135 |  | 443 | AMOCO PIPELINE CO | YES | 1986-08-17 | 100 | TX | HOCKLEY | SUNDOWN | NO |  | NO | 5 MILES SOUTHEAST OF SUNDOWN, TEXAS ON HWY-41 ZAVALLON COUNTY SCHOOL LAND, KLEAGUE-37, LABOR-76. |  | TANK FARM | PIPE |  | 1982 | OTHER | BROKEN 3/4" NIPPLE IN THR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 832.7466 | 1679.9863 | CRUDE OIL | 1 | 61 | 55 | NO | NO | 1 | 0 | 0 | NO DATA |  | 150 | 70 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALBERT L. WOOD, JR. PIPELINE MAINT. FOREMAN | 8068946187 | BROKEN 3/4" NIPPLE IN PIPE THREADS GOING TO SAMPLER. REPLACED NIPPLE AND WELDED BRACING ON SAMPLER POT.
2017-09-29 08:50 | YES | NO | 19860136 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-07-31 | 1117 | KS | WYANDOTTE | KANSAS CITY | NO |  | NO | THE LEAK OCCURRED ON DONOVAN ROAD, 600 FEET EAST OF FAIRFAX TRAFFICWAY |  | NO DATA | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9463.0297 | 19090.7531 | GASOLINE | 2 | 435 | 309 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 353 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | LINE MARKINGS | Null | YES | C.K. MCCAW, VICE PRESIDENT | 9185883248 | ON THURSDAY, JULY 31, 1986, THE DIVISION OFFICE RECEIVED A CALL FROM BOHRER EXCAVATING, WHO STATED THAT WHILE REMOVING STREET ASPHALT ON DONOVAN ROAD IN FAIRFAX, KANSAS, THEIR LINE BELT BACKHOE HAD PUNCTURED ONE OF OUR PIPELINES. UPON INVESTIGATION, IT WAS DETERMINED THAT OUR #3-8", KANSAS CITY-IRVINGTON LINE HAD BEEN PUNCTURED. GATE VALVES AT THE KANSAS CITY STATION AND 18TH STREET JCT. WERE CLOSED IMMEDIATELY. TOTAL BARRELS OF UNLEADED GASOLINE OUT OF THE LINE WAS 435, AND 309 BARRELS WERE RECOVERED. THE LEAK WAS CONTAINED IN THE ASPHALT ROAD EXCAVATION AREA; THEREBY LIMITING THE SURFACE AREA OF THE SPILL AND LOSS OF PRODUCT. THE PIPELINE WAS REPAIRED AND RETURNED TO SERVICE AT 2010 HOURS ON JULY 31, 1986. PRODUCT WAS RECOVERED BY A LOCAL TRANSPORT AND DISPOSED OF AT THE WILLIAMS PIPE LINE KANSAS CITY TERMINAL.
2017-09-29 08:50 | YES | NO | 19860137 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1986-08-14 | 1056 | CA | CONTRA COSTA | MARTINEZ | NO |  | NO | 200 FEET SOUTH OF WATERFRONT ROAD, 6 FEET EAST OF SOLANO ROAD, ACROSS FROM TOSCO REFINERY OFFICE BUILDING. |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 1345 | 1290 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 1040 | YES | 24 | 1450 | 1 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | BARRY R. PEARL, VICE PRESIDENT-OPERATIONS | 2134867860 | OUR INPUT PUMP STATION AT CONCORD SHUT DOWN AFTER A DOWN-LINE BOOSTER STATION SHUT DOWN. IMMEDIATELY FOLLOWING THIS, THE PRESSURE WAS OBSERVED TO BE EXTREMELYLOW. THIS CAUSED A SUSPICION OF THE POSSIBILITY OF A LINE BREAK AND LINE WAS LEFT DOWN AND PERSONNEL WERE SENT TO INVESTIGATE AND FOUND LEAK. THE NEXT DOWN-LINE BLOCK VALVE WAS CLOSED AS SOON AS POSSIBLE TO MINIMIZE LOSS OF PRODUCT, AND TOSCO REFINERY PERSONNEL IMMEDIATELY USED THEIR ON-HAND EQUIPMENT AT THE SITE TOCONTAIN THE SPILL. APPROXIMATELY 60 FEET OF PIPE REMOVED AND REPLACED WITH NEWPIPE. EVIDENCE SHOWS THAT THE PIPE AT THE POINT OF BREAK HAD PREVIOUSLY BEEN DAMAGED BY SOME KIND OF HEAVY EQUIPMENT AND THE DAMAGE WAS UNKNOWN TO OPERATOR.
2017-09-29 08:50 | YES | NO | 19860138 |  | 18273 | SHELL PIPE LINE CORP | NO | 1986-09-01 | 900 | TX | CRANE | CRANE | NO |  | NO | SE1/4, SW1/4, SECTION 31, BLOCK 32, PSL SURVEY 15 MILES WEST OF CRANE BARNSLEY STATION |  | TANK FARM | TANK |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9850 | 9321.0842 | 18804.3918 | CRUDE OIL | 1 | 2800 | 2300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.J. EICHLER, MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262 | TANK BOTTOM RUPTURED - CAUSE UNKNOWN - ASSUME CORROSION WAS THE CAUSE OF THE SPILL. THE OIL WAS CONTAINED WITHIN THE TANK FIREWALL.
2017-09-29 08:50 | YES | NO | 19860139 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-08-18 | 1200 | TX | HOCKLEY | SUNDOWN | NO |  | NO | SW1/4 SW1/4, SECTION 21, BLOCK LGE 52 FOUR MILES SOUTH OF SUNDOWN |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1892.6059 | 3818.1506 | CRUDE OIL | 1 | 530 | 480 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 880 | 500 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | M.J. EICHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262 | HOCKLEY COUNTY ROAD DEPARTMENT PERSONNEL WERE GRADING ROAD BEDS WHEN THEY STRUCK LINE IN BOTTOM OF BAR DITCH. LINE WAS WELL MARKED BUT LINE HAS BECOME SHALLOWDUE TO EROSION. THE PIPE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19860140 |  | 2731 | CHEVRON PIPELINE CO | YES | 1986-09-17 | 1100 | UT | DUCHESNE |  | NO |  | NO | SOUTHEAST 1/4, NORTHWEST 1/4, SECTION 9 TOWNSHIP 2 SOUTH, RANGE 4 WEST, US MERIDIAN, DUCHESNE COUNTY UTAH. |  | NO DATA | VALVE |  | 1974 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 804.3575 | 1622.714 | CRUDE OIL | 1 | 250 | 225 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.V. SMITH, SALT LAKE DIVISION MANAGER | 8015397200 | A 10-INCH CRUDE LINE OWNED AND OPERATED BY CHEVRON PIPE LINE COMPANY WAS BEING PRESSURED UP TO MOVE A PIPELINE "PIG" THROUGH THE SYSTEM. THE OPERATOR NEGLECTEDTO BLOCK IN A RELATED INJECTION LINE TO ISOLATE THE INJECTION LINE FROM THE MAIN LINE PRESSURE.THE CHECK VALVE PROTECTING THE INJECTION SYSTEM FAILED, AND THE PRESSURE SURGE CAUSED THE INJECTION PUMP RELIEF VALVES TO OPEN AND RELEASE CRUDE OIL. THE INJECTION SYSTEM IS IN A REMOTE, UNMANNED AREA, AND 250 BARRELS WERE RELEASED BEFORE THE LEAK WAS DISCOVERED AND STOPPED.THE CRUDE OIL WAS CONTAINED IN AN EXISTING BERM, AND DAMAGE WAS CONFINED TO THEINJECTION PUMPS. THE WAXY, SOLIDIFIED CRUDE WAS 90% RECOVERABLE, AND THE REMAINING OILY DIRT WAS REMOVED FOR DISPOSAL.THE INJECTION SYSTEM WHERE THE LEAK OCCURRED IS A NON-REGULATED GATHERING LINE.THIS REPORT HAS BEEN SUBMITTED BECAUSE THE IMPROPER OPERATING PROCEDURE WHICH CAUSED THE LEAK OCCURRED IN A REGULATED LIQUID PIPELINE.
2017-09-29 08:50 | YES | NO | 19860141 |  | 4906 | EXXON PIPELINE CO | NO | 1986-08-04 | 2000 | TX | HARRIS |  | NO |  | NO | LEAK OCCURRED ON EXXON'S WEBSTER STATION PROPERTY. LEAK OCCURRED ON BOLING-WEBSTER 8-INCH CRUDE OIL PIPELINE. |  | LINE PIPE | WELDING FITTING |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 14300 | 13532.1324 | 27299.777 | CRUDE OIL | 1 | 412 | 410 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 600 | 50 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | YES | YES | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | PHILLIPS PIPELINE WAS WORKING ON THEIR PROPYLENE LINE BEHIND WEBSTER STATION. AT 2020 ON AUGUST 4, THEY NOTIFIED EPC'S OIL TRAFFIC CONTROL CENTER THAT THE PIPELINE HAD BEEN HIT BY A DOZER. GAUGING SUPERVISOR SENT GAUGER TO SHUT OFF PRODUCTION IN GATHERING FIELDS. MEANWHILE, PHILLIPS BUILT A PIT TO CONTAIN THE OIL.EPC EQUIPMENT, CONTRACT LPERSONEL WERE DISPATCHED TO THE SCENE AT 2020. THE LINE WAS TEMPORARILY REPAIRED BY USING DRESSER SLEEVE BY 0220 THE NEXT MORNING AND CLEAN-UP OPERATION WAS COMPLETED. PERMANENT REPAIRS WERE FINISHED ON AUGUST 6, 1986.
2017-09-29 08:50 | YES | NO | 19860142 |  | 5075 | FARMERS UNION CENTRAL EXCHANGE INC - CENEX PIPELIN | YES | 1986-09-04 | 1200 | MT | YELLOWSTONE | LOCKWOOD | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 700 | 150 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1400 | 1000 | YES | 24 | 1950 | 6 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | 14 DAY AERIAL SURVEY | NO | YES | JAMES D. LAWSON, MANAGER, CENEX PRODUCTS PIPELINE | 4066284311 | AT APPROXIMATELY 1200 HOURS (24 HOUR CLOCK) ON SEPTEMBER 4, 1986, OPERATOR AT LAUREL STATION STARTED UP STATION TO PACK THE LINE FOLLOWING A ROUTINE SHUTDOWN TO PASS A PIG AT BILLINGS STATION. STARTUP WAS NORMAL. APPROXIMATELY 3 MINUTES AFTER STARTUP, BILLINGS STATION LOST SUCTION PRESSURE FROM LAUREL - SYSTEM IMMEDIATELY WAS SHUTDOWN AND BILLINGS STATION WAS NOTIFIED TO BLOCK IN LINE. MAINTENANCE GANG WORKING AT TANK FARM UPSTREAM CLOSED BLOCKVALVE SHORTLY THEREAFTER. PERSONNEL WERE DISPATCHED FROM THREE SOURCES TO LOCATE LEAK. NO OUTSIDE SOURCES REPORTED AN OBSERVED LEAK. AT 1215 HOURS LEAK WAS LOCATED BY OUR FORCES, CONTAINMENT PROCEDURES AND EMERGENCY PROCEDURES WERE INVOKED IMMEDIATELY. THE LEAK OCCURRED IN THE BOTTOM OF AN IRRIGATION DITCH, CONSEQUENTLY ALL OF THE GASOLINE WAS DISCHARGED INTO THE DITCH, AND RAN NEARLY ONE MILE DOWNSTREAM BEFORE IT WAS STOPPED. NEARBY BUSINESSES AND RESIDENCES WERE EVACUATED BY THE SHERIFF'S DEPARTMENT FOR 24 HOURS. PROPER AUTHORITIES WERE NOTIFIED, AND CLEANUP BEGAN 1500 HOURS OF THE SAME DAY. NO GASOLINE WAS DISCHARGED TO THE YELLOWSTONE RIVER, NO GASOLINE HAS BEEN ALLOWED INTO NEARBY WATER WELLS. SPILL SITE CLEANUP CONTINUES AS OF THIS DATE(9/15/86) AND WILL CONTINUE TO SATISFACTION OF ALL AUTHORITIES.
2017-09-29 08:50 | YES | NO | 19860143 |  | 24003 | YELLOWSTONE PIPELINE CO | YES | 1986-09-03 | 1130 | MT | SANDERS |  | NO |  | YES | SECTION 5, TOWNSHIP 18 NORTH, RANGE 23 WEST, SANDERS COUNTY, MONTANA 2 MILES EAST OF PERMA, MT. |  | LINE PIPE | PIPE |  | 1954 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 47315.1484 | 95453.7657 | JET FUEL | 3 | 107 | 107 | NO | NO | 10 | 0.25 | 0 | WELDED |  | 1540 | 800 | YES | 0 | 0 | 0 | 54 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWIGHT D. JACKSON, DIRECTOR OF ENVIRONMENTAL AFFAIRS, CONTIN | 7132932100 | CONTINENTAL PIPE LINE COMPANY (OPERATOR OF YELLOWSTONE PIPE LINE) WAS NOTIFIED AT APPROXIMATELY 11:30 A.M. ON WEDNESDAY, SEPTEMBER 3, 1986 BY THE SANDERS COUNTY SHERIFF THAT OIL HAD BEEN SIGHTED IN THE FLATHEAD RIVER NEAR A YPL OVERHEAD CROSSING. THE PIPELINE WAS SHUT IN AT THE TIME OF THIS NOTIFICATION. COMPANY PERSONNEL LOCATED THE LEAK AND CLOSED THE ADJACENT BLOCK VALVES. THE LEAK, WHICH OCCURRED IN A PIPE OVERBEND, WAS REPAIRED BY COMPANY AND CONTRACT PERSONNEL, AND CLEANUP EFFORTS WERE BEGUN IMMEDIATELY.
2017-09-29 08:50 | YES | YES | 19860144 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1986-09-03 | 1600 | TX | GAINES | SEMINOLE | NO |  | YES | 5 MILES EAST OF TEXAS-NEW MEXICO STATE LINE, 2.5 MILES NORTH OF HIWAY 62. |  | PUMPING STATION | PIPE |  | 1981 | OTHER | VALVE MALFUNCTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 2 | 0 | 25000 | 23657.5742 | 47726.8828 | NATURAL GAS LIQUID | 3 | 5 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISSACS, PRESIDENT | 9185811800 | VALVE MALFUNCTIONED.
2017-09-29 08:50 | YES | NO | 19860145 |  | 443 | AMOCO PIPELINE CO | YES | 1986-09-07 | 1900 | TX | COOKE |  | NO |  | YES | RED RIVER CROSSING - P.W. HUMPHREY SURVEY (A-446) - COOKE COUNTY, TEXAS APPROX. 5 MI. NW OF DEXTER, TEXAS. |  | LINE PIPE | GIRTH |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9463.0297 | 19090.7531 | CONDENSATE - WATER | 1 | 3000 | 0 | NO | NO | 8 | 0.34 | 5200 | WELDED |  | 1400 | 450 | YES | 8 | 1750 | 0 | 65 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | JOE NELSON, AREA MANAGER, OPERATIONS | 2147597131 | THE PIPELINE ON THE SOUTH BANK OF THE RED RIVER WAS INSTALLED WITH AN OVER-BENDMAKING A FIXED POINT WHERE THE LINE ENTERED THE RIVER. THE RIVER CURRENT HAS SCOURED OUT THE COVER OVER THE LINE, AND A TREE WAS HUNG-UP ON THE LINE. IT IS ASSUMED THAT THE VIBRATION OF THE LINE DUE TO THE CURRENT AND THE TREE CREATED FATIQUE IN THE GIRTH WELD NEAREST THE SOUTH BANK AND CAUSED THE FAILURE.DUE TO THE CONDENSATE BEING 70 DEGREES API, NO CLEAN-UP WAS REQUIRED AS THE PRODUCT RAPIDLY EVAPORATED.IT WAS REPORTED IN THE NEWSPAPERS THAT 14 OR 15 PERSONS WENT TO THE EMERGENCY ROOM AT THE GAINSVILLE, TX. HOSPITAL. THEY WERE REPORTEDLY RELEASED. THIS MATTER IS BEING INVESTIGATED.THE CONDENSATE HAS 5-10 PPM MERCAPTAN IN IT AND THIS PRESENTED A LARGE STENCH AND MINOR EYE BURNING.THE LINE WAS REPAIRED USING PRE-TESTED PIPE AND WELD TENDS. A PRESSURE TEST WASAPPLIED TO VERIFY THE INTEGRITY OF THE LINE. GROUT BAGS WILL BE INSTALLED IN THE RIVER STARTING 9-15-86 AND THE TREE REMOVED.
2017-09-29 08:50 | YES | NO | 19860146 |  | 18718 | SUN PIPELINE CO | YES | 1986-08-29 | 2400 | TX | LIBERTY |  | NO |  | NO | WM. HARRIS LEAGUE SURVEY AT TRINITY RIVER |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 270075 | 255572.7741 | 515593.5152 | CRUDE OIL | 1 | 90 | 85 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | RIVER CROSSING SIGNS "DO | YES | NO | E.F. MCKINLEY, JR., AREA MANAGER, COMPLIANCE, SAFETY & HEALT | 2147570220 | AGENCIES NOTIFIED & SEQUENCE OF EVENTS: RECEIVED CALL AT 2:30 A.M., AUGUST 30,1986, FROM RAYMUNDO GARZA, DREDGING COMPANY. CALL WAS TAKEN BY SOUR LAKE TRUNK STATION OPERATOR, TOMMY BROWN. DREDGING COMPANY WAS DREDGING TRINITY RIVER WHEN THEY GOT INTO OUR LINE AT APPROXIMATELY 12:00 MIDNIGHT. TOMMY BROWN REPORTED PROBLEM TO BENNY HERFORD AT 2:35 A.M. BENNY CALLED: HARVEY DUTY AT 2:50 A.M., BUCKYCRISP AT 2:55 A.M., SIMPSON VACUUM SERVICE AT 3:10 A.M. VALVE ON WEST SIDE OF TRINITY RIVER WAS CLOSED AT 3:30 A.M. VALVE ON EAST SIDE OF TRINITY RIVER WAS CLOSED AT 3:50 A.M.AGENCIES NOTIFIED: NATIONAL RESPONSE CENTER-PETTY OFFICER O'BRIEN AT 3:35 A.M.800-424-8802, TEXAS DEPT. OF WATER RESOURCES-PRISCILLA AT 4:25 A.M. 512-463-7727, TEXAS RAILROAD COMMISSION-MARK GERDING AT 3:45 A.M. 713/460-0631, UNITED STATES COAST GUARD-PETTY OFFICER JAMES AT 3:48 A.M. 409/724-4358, U.S. COAST GUARD, GALVESTON-PETTY OFFICER REYES AT 4:30 A.M. 409/766-3687, ENVIRONMENTAL PROTECTION AGENCY-MCCLEARY AT 4:08 A.M. 214/767-2666, LONGVIEW OFFICE-BUDDY MCKINLEY AT 4:20 A.M., 6:00 A.M.-SIMPSON VACUUM ARRIVED AT LIBERTY, 7:00 A.M.-BOOM IN WATER AT IH 10 BRIDGE. 7:13 A.M.-TEXAS PARKS & WILDLIFE CALLED. WHEN WE KNOW SOMETHING DEFINITE, WE MUST CALL PHILIP CARLETON AT 512/479-4848(AUSTIN). 7:20 A.M.-HELICOPTER LEFT LIBERTY MUNICIPAL AIRPORT W/BUCKY AND FOSTER TO VIEW RIVER. 7:45 A.M.-CCIWA(CAROL JIGOUT) CALLED TO REPORT THIN SKIM OF OIL SHOWING UP AT THEIR WATERPLANT. BOOMS DISPATCHED TO THIER LOCATION. (TRINITY RIVER PLANT AT LIBERTY,409/258-3272). 8:00A.M.-MARK GERDING W/RRC CALLED BACK TO ADVISE HE IS SENDINGREPRESENTATIVE TO LIBERTY. 8:10A.M.- BUDDY MCKINLEY CALLED AND IS HEADED TO SOURLAKE. ADVISED TO HOLD HELICOPTER AFTER BUCKY & FOSTER RETURN TO TAKE RRCREPRESENTATIVE AND BUDDY MCKINLEY UP TO VIEW THE AREA. 8:20A.M.-ED LEWIS CALLEDTO ADVISE BUDDY WAS ON HIS WAY. IF WE NEED ANY HELP WHILE BUDDY IS IN ROUTE, WEARE TO CALL PAT GALLAGHER, 214/758-8814. ALSO IF THERE IS ANY PROBLEM WITH NEWS MEDIA TO CALL FORREST BROKAW, 918/584-3967. MR. LEWIS' PHONE NUMBER IS214/663-1854.
2017-09-29 08:50 | YES | NO | 19860147 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1986-08-18 | 1350 | CA |  | LOS ANGELES | NO |  | NO |  |  | NO DATA | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 313000 | 296192.829 | 597540.573 | CRUDE OIL | 1 | 1845 | 0 | YES | NO | 14 | 0.38 | 1875 | WELDED |  | 1058 | 915 | YES | 8 | 1323 | 5 | 1982 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | R.B. KUPREWICZ, VICE PRESIDENT | (213)428-9 | A MOTOR PATROL AND SCRAPPER WERE WORKING AT THE BOTTOM OF A FLOOD CONTROL CANALPRIOR TO LINING IT WITH CONCRETE. THE SCRAPPER STRUCK FOUR CORNERS PIPE LINE LINE NUMBER 63, RELEASING OIL. THE OIL CAUGHT ON FIRE, BURNED THE OIL RELEASED, THE SCRAPPER AND THE MOTOR PATROL. FOUR CORNERS HAD BEEN IN REGULAR CONTACT WITH THE CONTRACTORS AND LAND OWNER SINCE LATE 1985. LINE WAS RESTAKED THE MORNING OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19860148 |  | 26134 | MOBIL OIL CORP - WEST COAST PIPELINES | NO | 1986-08-19 | 500 | CA | KERN |  | NO |  | NO | MIDWAY PUMP STATION, 1/4 MILE EAST OF HWY 33, SEC. 13, T315, R22E |  | PUMPING STATION | PIPE |  | 1968 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 12301.9386 | 24817.9791 | CRUDE OIL | 1 | 984 | 700 | NO | NO | 2 | 0.22 | 35000 | WELDED |  | 100 | 60 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. ROBBINS, MANAGER, WEST COAST PIPE LINES | 2133282550 | PIPE FAILURE IN 2" RELIEF LINE TO PUMP SUCTION.
2017-09-29 08:50 | YES | NO | 19860149 |  | 395 | AMOCO OIL CO | YES | 1986-08-24 | 1500 | IA | HARRISON |  | NO |  | NO | SE 1/4, SECTION 18, R44W, T78N, HARRISON COUNTY, IOWA (SKETCH ATTACHED) |  | NO DATA | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 473.1515 | 954.5377 | DIESEL FUEL | 2 | 74 | 48 | NO | NO | 6 | 0.25 | 35000 | WELDED |  | 1440 | 870 | YES | 24 | 1800 | 4 | 70 | EXTERNAL | Null | YES | OTHER | SHORTED RAILROAD CASING | NO DATA |  | Null | NO DATA |  | Null | Null | M.B. WEISS, AREA MANAGER, OPERATIONS, FREEMAN MO. | 8163311673 | A SHORTED CASING UNDER THE CHICAGO NORTHWESTERN RAILROAD TRACK RUNNING BETWEEN MISSOURI VALLEY, IOWA AND CALIFORNIA JUNCTION, IOWA RESULTED IN AN EXTERNAL PIT LEAK AT THE SIX O'CLOCK POSITION ON THE 6-INCH CARRIER PIPE, 18 FEET INSIDE THE SOUTH END OF THE CASING.COMPANY OPERATIONS PERSONNEL SUSPECTED A POSSIBLE LEAK BECAUSE OF SLIGHT METERING VARIANCES. THE LINE WAS SHUT DOWN AND THE APPROPRIATE SEGMENT WAS IDENTIFIED BY STATIC PRESSURE OBSERVATIONS BETWEEN CLOSED BLOCK VALVES. LOW LEVEL OBSERVATION FLIGHTS BY THE COMPANY PATROL PLANE AND A RENTED HELICOPTER WERE INCONCLUSIVE. THE ACTUAL LEAK LOCATION WAS IDENTIFIED BY A DRIPPING CASING VENT FOUND BY COMPANY PERSONNEL WALKING THE SUSPECT 25 MILE SECTION OF PIPELINE.THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 1821 HRS. EDT. THE IOWA DEPARTMENTOF NATURAL RESOURCES WAS NOTIFIED AT 1740 CDT AND TWO ENVIRONMENTAL SPECIALIST WERE ON SITE THAT EVENING.
2017-09-29 08:50 | YES | NO | 19860150 |  | 26096 | SUNNILAND PIPELINE CO INC | NO | 1986-08-28 | 1831 | FL | BROWARD | ANDYTOWN | NO |  | NO | ANDYTOWN, FLORIDA NEAR INTERSECTION OF U.S. HIGHWAY #27 AND FLORIDA STATE ROAD #84. |  | LINE PIPE | PIPE |  | 1964 | CORROSION | OTHER | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 473151.484 | 954537.6565 | CRUDE OIL | 1 | 119 | 0 | NO | NO | 4 | 0.13 | 42000 | WELDED |  | 750 | 135 | YES | 2 | 500 | 10 | 85 | NO DATA | Null | YES | OTHER | UNDER INVESTIGATION | OTHER | UNDER INVESTIGATION | Null | NO DATA |  | Null | Null | L.B. BRASHIER, JR., VICE-PRESIDENT | 3056461375 | SCADA SYSTEM EFFECTED SHUT DOWN. LEAKS DISCOVERED BY HELICOPTER ON 8/30/86 AT 1600 HOURS. 12 LEAKS IN THE 4 1/2" PIPE AND 18 LEAKS IN THE 6 5/8" PIPE. NO EVIDENCE OF PRESSURE SURGE OR OTHER ABNORMAL OPERATIONS. SAMPLES OF THE PIPES WERE REMOVED AND SENT TO AN INDEPENDENT METALURGICAL LABORATORY AND TO ENRON CORP. LABORATORY IN OMAHA, NEB.
2017-09-29 08:50 | YES | NO | 19860151 |  | 26096 | SUNNILAND PIPELINE CO INC | NO | 1986-08-27 | 1821 | FL | BROWARD | ANDYTOWN | NO |  | NO | ANDYTOWN, FLORIDA NEAR INTERSECTION OF U.S. HIGHWAY #27 AND FLORIDA STATE ROAD #84. |  | PUMPING STATION | OTHER | RELIEF VALVE | 1977 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 189260.5936 | 381815.0626 | CRUDE OIL | 1 | 15 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.B. BRASHIER, JR., VICE PRESIDENT | 3056461375 | FOR UNKNOWN REASONS THE RELIEF VALVE OPENED AND DID NOT RESEAT, SUMP TANK OVERFLOWED INTO THE STATION FIREWALL. RAIN-WATER DRAIN LEAKED OIL INTO AN ADJACENT DEAD END BORROW DITCH.
2017-09-29 08:50 | YES | NO | 19860152 |  | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1986-09-13 | 600 | NE | OTOE |  | NO |  | NO | UNDILLA PUMP STATION APPROXIMATLY 6 MILES SOUTH OF THE TOWN OF UNDILLA, NE |  | PUMPING STATION | OTHER | PROBALY PUMP SEAL | 1971 | OTHER | PUMP SEAL LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 700000 | 662412.0775 | 1336352.7192 | NATURAL GAS LIQUID | 2 | 409 |  | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J C SMITH - VP OPER | 4026334209 | UNIT #1 WAS RUNNING ON THE 102 LINE. AT 0545, THE UNIT WENT DOWN. AN ALARM WAS RECEIVED AS A SEAL LEAK IN OUR CENTRAL CONTROL ROOM. WE ALSO RECEIVED A VAPOR ALARM AND WE ARE UNABLE TO TELL WHICH OCCURED FIRST. AT 0546, CONTROL EQUIPMENT SHUT IN THE STATION. THIS IS INDICATED BY AN EMERGENCY SHUTDOWN ALARM IN THE CONTROL CENTER. PERSONNEL WERE DISPATCHED TO THE SCENE ND WHILE APPROCHING, HEARD THEEXPLOSIONS AND SAW THE RESULTING FIRE AT APPROXIMATLY 060. DATA FROM THE CONTROL CENTER HOURLY LOG AT 0600 HRS. INDICATES THAT ALL VALVES WERE CLOSED AT THR STAVAPORS FROM THE SEAL LEAK ACCUMULATED ACROSS THE STATION SITE AND IN THE CONTROL AND HIGH POWER EQUIPMENT BUILDINGS. WEATHER CONDITIONS WERE WARM AND MUGGY ANDIT IS SPECULATED THAT AIR CONDITIONERS IN EACH BUILDING IGNITED THE FIRE AS THEY WERE STARTED. PERSONNEL AT THE SCENE AT THE TIME OF THE EXPLOSION INDICATED TWO DISTINCT EXPLOSIONS AND BOTH BUILDINGS WERE EXPLODED OUTWARD NEAR THE AIR CONDITIONER CONTROLS.
2017-09-29 08:50 | YES | NO | 19860153 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-09-18 | 1400 | TX | HOUSTON |  | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1945 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | DIESEL FUEL | 3 | 350 | 95 | NO | NO | 10 | 0.37 | 2375 | WELDED |  | 750 | 250 | YES | 24 | 1930 | 0 | 71 | NO DATA | Null | Null | NO DATA |  | OTHER | DAMAGE BY CNTY RD GRADER | Null | ONE CALL |  | Null | Null | A E SMITH - DIV MGR | 4098393100 | COUNTY ROAD GRADER STRUCK PIPELINE AT ABOUT 2:00PM, CAUSING A HOLE AND A LEAK, IN SPITE OF LINE MARKERS ON BOTH SIDES OF THE ROAD. LEAK DRAINED TO THE DITCH, TO AN UNNAMED , 2 FEET WIDE, NATURAL SPRING CREEK. DAMS WERE SET UP ALONG THE FLOW TO CONTAIN THE SPILL. BECAUSE OF RECENT RAINS, SOIL AT THE SPILL SITE. WAS SATURATED WITH WATER. THIS HELPED PREVENT SIGNIFICANT SOIL CONTAMINATION. VACUUM TRUCKS PICKED UP SPILL AND RETURNED IT TO THE SLOP TANK AT OUR LUFKIN STATION. PIPELINE WAS REPAIRED WITH 10" PLIDCO SLEEVES. CLEAN-UP OPERATIONS IS STILL UNDERWAY
2017-09-29 08:50 | YES | NO | 19860154 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1986-09-03 | 700 | TX | SCURRY | UNION | NO |  | YES | SCURRY COUNTY, BLOCK 97, SECTION 195 3/4 MILE EAST OF FARM TO MARKET ROAD 1606 |  | LINE PIPE | LONGITUDINAL WELD |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 254.5555 | 513.5413 | NATURAL GAS LIQUID |  | 2000 | 0 | NO | NO | 7 | 0.16 | 1980 | WELDED |  | 960 | 1380 | YES | 24 | 1200 | 4 | 86 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | S F ISAACS - PRES | 9185811800 | GALVANIC CORROSION
2017-09-29 08:50 | YES | NO | 19860155 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1986-09-06 | 837 | MN | POLK |  | NO |  | NO | SEC 1, T149N R39W, POLK CTY, MN, ADJACENT TO NORTH-SOUTH TOWN ROAD, APPROXIMATLY .5 MILE SOUTH OF STATE HIGHWAY 92. |  | LINE PIPE | BOLTED FITTING |  | 1986 | OTHER | CONTR. FAILED TO TIGHTEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9463.0297 | 19090.7531 | CRUDE OIL | 1 | 265 | 264 | NO | NO | 48 | 0.41 | 52000 | FLANGED |  | 633 | 120 | YES | 8 | 792 | 8 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W C COCHRANE - PRES & GEN MGR | 7153925631 | NEW 48" LOOP WAS BEING FILLED WITH CRUDE OIL WHEN THE FLANGED CONNECTION TO THEEXISTING 48" VALVE BEGAN TO LEAK. THE OIL WAS CONTAINED TO THE EXCAVATION SURROUNDING THE SITE. THE GASKET WAS REPLACED AND THE FLANGE BOLTS TIGHTENED. THE LINE HAS BEEN HYDROSTATICALLY TESTED USING A TEMPORARY SCRAPER TRAP. THE TRAP HAD BEEN REMOVED AND REPLACED WITH A PRETESTED PIECE OF PIPE WITH A FLANGE TO FIT UP TO THE EXISTING VALVE.
2017-09-29 08:50 | YES | NO | 19860156 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-09-20 | 1120 | OK | OKLAHOMA |  | NO |  | NO | NE1/4 S26 T12N R1W OKLAHOMA COUNTY |  | LINE PIPE | NO DATA |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | GASOLINE | 2 | 120 | 105 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 750 | 150 | YES | 8 | 1000 | 1 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | C K MCCAW - VP OPER | 9185883248
2017-09-29 08:50 | YES | NO | 19860157 |  | 18718 | SUN PIPELINE CO | NO | 1986-10-06 | 101 | TX | SCURRY | SNYDER | NO |  | NO | APPROX 8 MI W OF SNYDER, TX - H&TC CO SURVEY 97, SEC 195 IN SNYDER GATHERING SYSTEM AT SPLSCO STATION 6B - STATION MANIFOLD LINE |  | PUMPING STATION | PIPE |  | 1962 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 75 | 73 | NO | NO | 4 | 0.14 | 36000 | WELDED |  | 45 | 25 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL ANAROBIC CORR | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK J GALLAGHER - SAF & ENVIR COOR | 2147570223 | LEAK WAS REPORTED TO SPLSCO BY A CHEVRON PUMPER AT 5:30PM ON 10/6/86. THIS WAS CAUSED BY INTERNAL CORROSION IN THE STATION MANIFOLD LINE AT GATHERING STATION 6B. A TEMPORARY LEAK CLAMP WAS INSTALLED, AND THE PIPE WAS REPLACED ON 10/7/86. THE OIL WAS CONTAINED IN A DITCH BY PUMPED BACK INTO OUR SYSTEM. A SKIM OF OIL ONSAL SITE.
2017-09-29 08:50 | YES | NO | 19860158 |  | 22907 | WYCO PIPE LINE CO | YES | 1986-09-08 | 1330 | CO | WELD |  | NO |  | NO | 25 YDS N OF COLORADO HIGHWAY 52 & EAST OF INTERSTATE I-25, SEC 35, T2N, 686W |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1892.6059 | 3818.1506 | FUEL OIL | 1 | 75 | 0 | NO | NO | 8 | 0.25 | 2150 | WELDED |  | 1440 | 625 | YES | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | H C OLIVER - AREA MGR | 3038304770 | AT 1:30 PM ON 9/8/86, A ROAD GRADER OPERATED BY CONSOLIDATED LOWER BOULDER RESERVOIR AND DITCH CO HIT OUR PIPELINE WITH THE GRADER. THE SYSTEM WAS SHUTDOWN BY 1:40 PM AND THE SEGMENT WAS ISOLATED BY 3:10PM. THE LINE WAS REPLACED AND SHUT BACK INO SERVICE BY 2:15, NO BBLS RECOVERED.
2017-09-29 08:50 | YES | YES | 19860159 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1986-09-04 | 1600 | IN | LAKE | EAST CHICAGO | NO |  | NO | E CHICAGO TERMINAL 400 COLUMBUS DREAST CHICAGO, IN 46312 |  | TANK FARM | TANK |  | 1939 | OTHER | STILL UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 26 | 0 | 26 | 500000 | 473151.484 | 954537.6565 | GASOLINE | 3 | 55000 |  | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.J. HEINZ - VICE PRESIDENT | 9186615371 | THE FLOOR OF TANK NO. 805 FAILED SPILLING UNLEAD MOTOR FUEL INTO THE DIKE SYSTEM. THE AREA SURROUNDING THE TERMINAL WAS EVACUATED DUE TO GASOLINE ODOR. PRODUCTWAS RECOVERED USING VACUUM TRUCKS AND A TERMINAL TRANSFER PUMP. THE COMMUNITY RETURNED TO THEIR HOMES WITHIN 48 HOURS. ALL THE PRODUCT LOSS WAS DUE TO EVAPORATION. INSIGNIFICANT PRODUCT SOAKED INTO THE GROUND.
2017-09-29 08:50 | YES | NO | 19860160 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-09-10 | 930 | OK | GARVIN | PAULS VALLEY | NO |  | NO | SE1/4, SW1/4,SEC 25, T-4-N,R-1-W TWO MILES NORTH OF PAULS VALLEY PAULS VALLEY PUMP STATION |  | PUMPING STATION | TANK |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 66241.2078 | 133635.2719 | CRUDE OIL | 1 | 365 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | M J EICHLER - MGR REG & MAIN STD | 7132416262 | LIGHTNING STRUCK TANK 141 CAUSING AN EXPLOSION AND FIRE. THE TANK WAS COMPLETELY DESTROYED AND THE ADJACENT TANK 140 WAS DAMAGED.
2017-09-29 08:50 | NO | NO | 19860161 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1986-10-02 | 1230 | MN | PENNINGTON |  | NO |  | NO | APPROXIMATELY 1750 FEET SE OF PENNINGTON CTY RD NO 15 ION SE, RANGE 44 WEST |  | LINE PIPE | LONGITUDINAL WELD |  | 1967 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 11355.6356 | 22908.9038 | CRUDE OIL | 1 | 3 | 2 | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 642 | 570 | YES | 8 | 810 | 8 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W C COCHRANE - PRES & GEN MGR | 7153925631 | LAKEHEAD'S AERIAL PATROL PILOT NOTED A SIGN OF OIL AT THE LEAK SITE. MAINTENANCE PERSONNEL EXCAVATED THE 34" LINE AND DISCOVERED A CRACK APPROXIMATELY 1/2" LONG IN THE LONGITUDINAL SEAM. A 34" X 14.5" LONG PLIDCO REPAIR SLEEVE WAS INSTALLED AND PERMANENTLY WELDED ON TH THE LINE. THE ENTIRE LONGITUDINAL SEAM OF THE AFFECTED JOINT WAS ULTRASONICALLY INSPECTED. NO OTHER DEFECT WAS DISCOVERED.
2017-09-29 08:50 | YES | NO | 19860162 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-09-26 | 1345 | WI | CLARK |  | NO |  | NO | NE1/4 S18 T28N R3W CLARK COUNTY WI |  | LINE PIPE | NO DATA |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | GASOLINE | 2 | 140 | 107 | NO | NO | 8 | 0.17 | 52000 | WELDED |  | 1450 | 500 | YES | 24 | 1830 | 0 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | C K MCCAW - VP OPER | 9185883248
2017-09-29 08:50 | YES | NO | 19860163 |  | 443 | AMOCO PIPELINE CO | YES | 1986-10-01 | 845 | WY | SWEETWATER |  | NO |  | NO | NE1/4, SEC 11, T19N, R100W, SWEETWATER COUNTY, WY. |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 9550 | 9037.1933 | 18231.6692 | CRUDE OIL | 1 | 300 | 100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | WRITTEN AGREEMENT | NO | NO | G W WHITE - AREA MGR WEST OPER | 3072662119 | WILLIAMS TELECOMMUNICATIONS CO (WITEL) CONTRACTOR, HENKELS AND MCCOY, WAS INSTALLING A FIBER OPTICS CABLE FOR WITEL WITH A CAT/RIPPER PARALLEL TO AND ABOUT 85 FEET SOUTH OF AMOCO PIPELINE'S (APL) WAMSUTTER-GRANGER 8" PIPELINE WHEN THE OPERATOR MADE A RIGHT TURN AND RAN INTO APL'S LINE PUTTING A HOLE IN IT. ABOUT 100 BARRELS OF CRUDE OIL WERE RECOVERED BY VAC TRUCK AND PUT BACK INTO THE PIPELINE SYSTEM. THE REST OF THE OIL EITHER SOAKED INTO THE GROUND OR EVAPORATED. AN ATTEMPT TO BUR THE REMAINING OIL UNDER PERMIT WILL BE MADE. NONE OF THE OIL REACHED WATER. THE DAMAGED SECTION OF PIPE WAS REPLACED. ACCIDENT WAS REPORTED TO AMOCO PIPELINE AT 9:15AM, 10/1/86
2017-09-29 08:50 | YES | NO | 19860164 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-10-07 | 800 | TX | HARDIN | SOUR LAKE | NO |  | NO | SEE ATTACHED |  | TANK FARM | NO DATA |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 14000 |  | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A E SMITH - DIV MGR | 4098393100 | THIS LEAK WAS DUE TO OPERATOR ERROR. A STATION OPERATOR FAILED TO OPEN A VALVE ON A CRUDE BREAKOUT TANK, ALLOWING PRESSURE TO BUILD ON A TRANSFER LINE AND RESULTING IN A RUPTURE OF THE LINE. THE RUPTURE ON THE TRANSFER LINE WAS NOT DISCOVERED UNTIL THE NEXT DAY. WHEN AN ASSOCIATED PUMP SHUT DOWN ON HIGH PRESSURE, THE OPERATOR LIED AS TO THE CAUSE AND THE OPENED THE TANK VALVE TO CONCEAL HIS ERROR. APPROXIMATELY 14,000 BBLS. OF OIL LEAKED FROM THE TANK THROUGH THE SPLIT IN THETRANSFER LINE DURING THE NIGHT. THE LEAK WAS DISCOVERED EARLY THE NEXT MORNING.THE TRANSFER LINE HAS BEEN REPAIRED. DAMS WERE CONSTRUCTED AND BOOMS DEPLOYEDTO CONTAIN THE OIL. VACUUM TRUCKS WERE USED TO RECOVER THE OIL. THIS OIL WASBY CITIES SERVICE COMPANY AND ONTO A PRIVATE LANDOWNER'S PROPERTY. FINAL CLEANUP OPERATIONS ARE EXPECTED TO CONTINUE FOR THE NEXT SEVERAL WEEKS. DUE TO HEAVYRAINS BEFORE AND AFTER THE LEAK, THERE IS VERY LITTLE OIL SATURATED EARTH.ALMOST ALL OF THE OIL REMAINED ON THE SURFACE OF THE SOIL.
2017-09-29 08:50 | NO | NO | 19860165 |  | 443 | AMOCO PIPELINE CO | YES | 1986-09-25 | 1930 | MO | CASS | FREEMAN | NO |  | NO | NE/4, SECTION 18, T 44N, R 32W, CASS CTY, MO |  | TANK FARM | BOLTED FITTING |  | 1986 | INCORRECT OPERATION BY OPERATOR PERSONNEL | OVER PRESSURING/PIPING | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | FLANGED |  | 275 | 500 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MITCHELL B. WEISS, AREA MANAGER | 8163311673 | A SMALL SPILL WITHIN THE STATION MANIFOLD OCCURRED ON 9/24/86. IT RESULTED FROMOVER PRESSURING A BOLTED FLANGE ASSEMBLY THAT WAS PART OF A TEMPORARY SECTION OF PIPE INSTALLED TO ACCOMODATE CERTAIN CONSTRUCTION ACTIVITIES. THIS INCIDENT DID NOT MEET ANY OF THE CRITERIA FOR ACCIDENT REPORTING IN CFR 195.50. HOWEVER, THE NEXT DAY SMALL TRACES OF OIL AND A SLIGHT SHEEN APPEARED ON NEARBY PONY CREEK.ABSORBENT BOOMS AND PADS WERE UTILIZED TO CONTAIN AND RECOVER THE HYDROCARBONS.APPARENTLY UNRECOVERED OIL FROM THE MANIFOLD SPILL ENTERED AND ABANDONED DRAIN TILE WHICH EVENTUALLY DISCHARGED TO THE CREEK. AFTER TWO WEEKS OF ALMOST CONTINUOUS RAIN AND NEAR FLOODING CONDITIONS, THE LOCAL MAINTENANCE CREW HAS LOCATED, UNCOVERED, BROKEN, AND WILL PERMANENTLY PLUG THE DRAIN LINE WHERE IT LEAVES THE PUMPING STATION PROPERTY TO PREVENT SIMILAR OCCURENCES.
2017-09-29 08:50 | YES | NO | 19860166 |  | 443 | AMOCO PIPELINE CO | YES | 1986-09-21 | 1620 | MO | CLAY | LIBERTY | NO |  | NO | SE/4, SECTION 36, T 52N, R 31W, CLAY CTY, MO. |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 47315.1484 | 95453.7657 | GASOLINE | 3 | 1137 | 90 | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 1333 | 300 | YES | 24 | 1666 | 5 | 72 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | OTHER | AMOCO PUBLIC EDUCTION | NO | NO | MITCHELL B. WEISS, AREA MANAGER, OPERATIONS | 8163311673 | ONE-CALL' IS JUST STARTING IN MO. FLAIR, INC. OF SIKESTON, MO. WAS INSTALLING A FIBER OPTIC CABLE FOR SOUTHWESTERN BELL ACROSS A PASTURE OWNED BY LEWIS TAPPS.A DOZER PULLING A LARGE RIPPER BAR MISTOOK THE PIPELINE FOR AN UNDERGROUND ROCKSTRUCTURE AND PUNCHED A 4"X6" ELLIPTICAL HOLE INTO THE SIDE OF THE 12-INCH LINE. THE WORK WAS BEING DONE ON A SUNDAY AND APPARENTLY THE CONSTRUCTION DRAWINGS MADE NO REFERENCE TO AMOCO'S BURIED LINE. AMOCO HAD NOT BEEN NOTIFIED. THE PIPELINES LOCATION WAS PROMINENTLY MARKED WITH THE APPROPRIATE WARNING SIGNS AND BRIGHTLY COLORED POSTS AT THE POINTS IT CROSSED THE PROPERTY OWNERS' FENCE LINES. THEPIPELINE CONTROL CENTER IDENTIFIED THE LEAK ALMOST IMMEDIATELY WITH A CONFIRMING PHONE CALL RECEIVED FROM THE CONTRACTOR AT 1627 CDT, 7 MINS. AFTER THE INCIDENT OCCURRED. THE LINE WAS SHUT DOWN, THE CLAY CO. SHERIFF'S OFFICE WAS NOTIFIED, AND A PIPELINE EMPLOYEE WAS DISPATCHED TO CLOSE MANUALLY OPERATED BLOCK VALVES ON EACH SIDE OF THE LEAK SITE. THE VALVE 3 MILES NORTH (UPSTREAM) OF THE LEAK WASCLOSED AT 1710 CDT WITH THE VALVE 6 MILES SOUTH OF THE LEAK CLOSED 45 MINS. LATER. A VACUUM TRUCK WAS DISPATCHED TO THE LEAK SITE, BUT THE BULK OF THE GASOLINEHAD EITHER SOAKED INTO THE GROUND OR EVAPORATED (90 DEGREES AMBIENT TEMPERATURES. CONTAINMENT STRUCTURES WERE PLACED IN A ADJOINING DRY CREEK BED. TWO WEEKS OFEXTENSIVE RAINFALL IN THE AREA HAVE BROUGHT SMALL AMOUNTS OF HYDROCARBONS TO THESURFACE AND RECOVERY OPERATIONS ARE CONTINUING. A SUBSURFACE DRILLING PROGRAMIS PLANNED TO DETERMINE THE LATERAL AND VERTICAL EXTENT OF RESIDUAL HYDROCARBONSIN THE SOIL WITH REMEDIAL ACTION TO BE TAKEN AS APPROPRIATE.
2017-09-29 08:50 | YES | NO | 19860167 |  | 12628 | MOBIL PIPELINE CO | NO | 1986-10-12 | 900 | TX | ANDREWS |  | NO |  | NO | NW/4 SEC.19, BLK.41, TWP 2N, G&M & MB&A SURVEY IN ANDREWS CTY, TX. |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3312.0604 | 6681.7636 | CRUDE OIL | 1 | 170 | 120 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 592 | 125 | YES | 2 | 650 | 1 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | ISOLATED ECTERNAL CORROSION PITTING PENETRATED PIPE WALL RESULTING IN THE CRUDEOIL SPILL. PIPELINE WAS REPAIRED BY WELDING A PATCH.
2017-09-29 08:50 | YES | YES | 19860168 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1986-10-13 | 940 | OK | CIMARRON |  | NO |  | NO | 6" MCCULLOCH-BORGER-MP 83-01+58, 2782' WEST OF NORTHWEST CORNER OF SEC.28, T1N, R7E |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 1 | 0 | 1 | 0 | 0 | 0 | 115000 | 108824.8413 | 219543.661 | NATURAL GAS LIQUID | 3 | 2300 |  | YES | YES | 6 | 0.19 | 42000 | WELDED |  | 1440 | 860 | YES | 8 | 2085 | 5 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | LINE MARKERS | NO | NO | B.L. THORMAN, VICE PRESIDENT | 9186614721 | CINMARRON CTY. EMPLOYEE WAS REMOVING SOIL FROM THE BAR DITCH OVER OUR PIPELINE WHEN MAINTAINER BLADE PUNCTURED 6" NGL PIPELINE.
2017-09-29 08:50 | YES | NO | 19860169 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-10-26 | 1500 | TX | JEFFERSON | BEAUMONT | NO |  | NO | 2-1/2 MILES S.E. OF U.S. HWY.96 ON W. PT. ARTHUR ROAD IN BEAUMONT, TEXAS |  | TANK FARM | NO DATA |  | 0 | OTHER | BOOSTER PUMP SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2580 | 2441.4617 | 4925.4143 | CRUDE OIL | 1 | 50 | 48 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH, DIVISION MANAGER | 4098393100 | BOOSTER PUMP SEAL FAILED LEAKING ABOUT 50BBLS. OF COASTAL CRUDE IN THE GROUND. CLEAN-UP OPER. RECOVERED 48BBLS. THE PUMP ASSEM. WAS BY-PASSED AVOIDING ANYOPERATIONS INTERRUPTION. THE PUMP SEAL WILL BE REPLACED.
2017-09-29 08:50 | YES | NO | 19860170 |  | 395 | AMOCO OIL CO | YES | 1986-09-26 | 935 | MN | WRIGHT |  | NO |  | NO | SECTION 9, TOWNSHIP 121N, RANGE 25W |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | GASOLINE | 3 | 583 | 0 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1440 | 660 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LANDOWNER CONTACT | NO | NO | R.E. PETERSON, AREA MANAGER | 6124254750 | PIPELINE WAS RUPTURED BY A LANDSCAPE CONTRACTOR WHO WAS IN THE PROCESS OF REMOVING A TREE WITH A HYDRAULIC TREE SPADE. THE MACHINE PUNCTURED THE LINE ALLOWING APPROXIMATELY 583 BBLS OF UNLEADED GASOLINE TO ESCAPE. THE PRODUCT WAS CONTAINEDIN AN AREA 30' X 200', AND DID NOT GET ON ANY WATER. THE CONTRACTOR WAS AWARE THE PIPELINE WAS IN THE AREA, BUT DID NOT BOTHER TO CALL TO HAVE IT LOCATED. NO INJURIES OR DAMAGES WERE SUSTAINED. CLEAN-UP OPERATIONS ARE IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19860171 |  | 26134 | MOBIL OIL CORP - WEST COAST PIPELINES | NO | 1986-09-13 | 1200 | CA | KERN |  | NO |  | NO | MIDWAY PUMP STATION, 1/4 MILE EAST OF HWY. 33. SEC.13. T-31-S. R-22-E |  | PUMPING STATION | OTHER | 3/4" THREADED PIPE NIPPLE | 1967 | OTHER | FAILURE/THREADED NIPPLE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9463.0297 | 19090.7531 | CRUDE OIL | 1 | 750 | 700 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. ROBBINS, MANAGER | 2133282550 | FAILURE AT THREADED CONNECTION OF 3/4" PIPING USED FOR THERMAL RELIEF.
2017-09-29 08:50 | YES | NO | 19860172 |  | 18718 | SUN PIPELINE CO | YES | 1986-10-07 | 955 | PA | MONTGOMERY | KING OF PRUSSIA | NO |  | NO | PHILADELPHIA GEAR CORP, SOUTH GULPH ROAD, KING OF PRUSSIA |  | LINE PIPE | PIPE |  | 1966 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 5250 |  | YES | NO | 14 | 0.25 | 52000 | WELDED |  | 1200 | 860 | YES | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | OTHER | CRACK IN PIPE | Null | OTHER | LINE MARKERS, AIR PATROL | Null | Null | CLARENCE J. YABLONSKI, MANAGER COMPLIANCE, SAFETY & HEALTH | 2159642523 | AT APPROX. 9:55 AM ON 10/07/86 A PRESSURE DROP WAS OBSERVED AT SPL'S TWIN OAKS STATION. AT APPROX. 10:00AM TWIN OAKS OPERATOR ADVISED GLENHARDIE AND BY 10:04 GLENHARDIE DISPATCHER ADVISED TWIN OAKS TO SHUT DOWN THE LINE AFTER CHECKING LINEBALANCES. AT APPROXIMATELY 10:40 AM PHILADELPHIA GEAR CALLED SPL AND REPORTED PRODUCT COMING OUT OF THE GROUND AT THEIR PLANT. CONCURRENTLY, SPL PERSONNEL WEREDISPATCHED TO SHUT DOWN THE MAIN LINE BLOCK VALVES. THE NATIONAL RESPONSE CENTER WAS IMMEDIATELY NOTIFIED AND COMPANY AND CONTRACT PERSONNEL WERE CALLED TO THESCENE. APPROPRIATE FEDERAL, STATE AND LOCAL AGENCIES ADVISED. REQUESTS FOR ADDITIONAL SPL AND CONTRACTUAL PERSONNEL. POLICE AND FIRE PERSONNEL DIRECTED SECURITY AND EVACUATION EFFORTS. EARTHEN DAMS CONSTRUCTED ACROSS ABRAMS CREEK TO PREVENT MIGRATION OF FREE PRODUCT INTO THE SCHUYLKILL RIVER AND TO ASSIST IN CLEANUP OF PRODUCT. THROUGHOUT THE NIGHT, STATE, FEDERAL AND LOCAL OFFICIALS WORKED ALONGWITH SPL TO MONITOR THE SITUATION AND CONTINUED CLEANUP AND WATER FLUSHING OPERATIONS. THIS PIPELINE WAS RELOCATED IN 1965 AND 66, AND OUR ENGINEERING DEPARTMENT STATES THAT THE PIPE WAS TESTED; HOWEVER, THE PRESSURE TEST CHARTS ARE NOT AVAILABLE.
2017-09-29 08:50 | YES | NO | 19860173 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1986-10-25 | 145 | IL | GRUNDY |  | NO |  | YES | 3 MILES SOUTH, 1 MILE WEST OF LISBON, IL. TOWNSHIP 34 NORTH - RANGE 6 EAST. |  | NO DATA | PIPE | CHECK VALVE | 1986 | OTHER | LOST PACKING/CHECK VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5028 | 4758.0113 | 9598.8307 | NATURAL GAS LIQUID | 2 | 780 | 0 | NO | NO | 10 | 0.19 | 1819 | WELDED |  | 1300 | 360 | YES | 24 | 1764 | 8 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | DEFECTIVE CHECK VALVE.
2017-09-29 08:50 | NO | NO | 19860174 |  | 15786 | PORTLAND PIPELINE CORP | YES | 1986-10-08 | 1800 | NH | COOS | JEFFERSON | NO |  | NO | SEE ATTACHED SKETCH |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | CRUDE OIL | 1 | 2 | 1 | NO | NO | 24 | 0.25 | 52000 | WELDED |  | 690 | 440 | YES | 24 | 923 | 10 | 65 | EXTERNAL | Null | YES | OTHER | ANEROBIC BACTERIAL CORR | NO DATA |  | Null | NO DATA |  | Null | Null | W.R. MCGREW, PRESIDENT | 2077673231 | TEMPORARY CONTAMINATION OF ADJACENT LANDOWER'S PROPERTY. APPROX. TWO BARRELS OFCRUDE OIL LEAKED FROM THE 24 INCH MAIN LINE BECAUSE OF A PINHOLE BREAK CAUSED BY EXTERNAL CORROSION. THE CORROSION OCCURRED IN AN AREA WHERE THE PIPE COATING APPEARS TO HAVE BEEN MISSING SINCE THE ORIGINAL CONSTRUCTION IN 1965. THE TOTAL AREA OF MISSING COATING WAS 20-30 SQUARE INCHES. AN INSPECTION OF THE AFFECTED PIPE, BEFORE A CLAMP WAS INSTALLED AROUND THE DEFECT, INDICATES THE LIKELY CAUSE OF THE CORROSION TO BE ANEROBIC BACTERIA ATTACK. DUE TO THE RAPID RESPONSE BY COMPANY AND CONTRACT WORK FORCES IN DEPLOYING BOOM AND ABSORBENT MATERIAL, THE OIL WHICH ESCAPED THE PIPELINE CAUSED NO SIGNIFICANT DAMAGE TO THE ENVIRONMENT. ALL LAND INVOLVED IN THE CONTAMINATION HAS BEEN RESTORED TO GOOD CONDITION.
2017-09-29 08:50 | YES | NO | 19860175 |  | 809 | ARCO PIPE LINE CO | NO | 1986-10-20 | 1230 | OK | CARTER | ARDMORE | NO |  | NO | SE/4 SEC 13, T4S, R1E, APPROX. 1/2 MILE NORTH OF HWY 142 AND 162 FEET WEST OF HIGH 77, NEAR CITY OF ARDMORE, OKLAHOMA |  | LINE PIPE | PIPE |  | 1975 | OUTSIDE FORCE DAMAGE | CORROSION, EXTERNAL | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 13248.2416 | 26727.0544 | GASOLINE | 1 | 935 | 454 | NO | NO | 8 | 0.2 | 52000 | WELDED |  | 870 | 550 | YES | 24 | 2012 | 0 | 75 | EXTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | N.R. BENNETT, MANAGER | 3163311300 | AN OUTSIDE CONTRACTOR HIT LINE WITH DITCHING MACHINE CAUSING A GOUGE IN THE PIPE
2017-09-29 08:50 | NO | NO | 19860176 |  | 14295 | OLYMPIC PIPE LINE CO | YES | 1986-09-25 | 0 | WA | KING | RENTON | NO |  | NO | VALVE ON S.E. 5TH STREET, RENTON WASHINGTON, SEE ATTACHED MAP. |  | NO DATA | NO DATA | 1" PRESSURE SENSING LINE | 1973 | OTHER | CRACK IN THREADED SECTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.C. DURBIN, PRESIDENT | 2146582400 | ON SEPT. 25, 1986, OLYMPIC PIPE LINE CO. WAS NOTIFIED BY THE WASHINGTON STATE DEPARTMENT OF ECOLOGY (DOE) THAT SOME TYPE OF FUEL PRODUCT WAS LEAKING AT A SLOW RATE INTO THE CEDAR RIVER, APPROX. ONE MILE EAST OF INTERSTATE 405 NEAR THE MAPLE VALLEY HWY(HWY 169). AS OLYMPIC OPERATES A REFINED PETROLEUM PRODUCTS PIPELINESYSTEM IN THE APPROX. AREA, IT IMMEDIATELY DISPATCHED PERSONNEL TO THE SITE FORINVESTIGATION AND EVALUATION. WHILE THE SOURCE WAS UNDETERMINED AT THAT TIME, OLYMPIC COOPERATED WITH THE DOE IN ITS INVESTIGATION. THE DOE INVESTIGATION INCLUDED SAMPLING OF THE PRODUCT TO ANALYZE THE CONTENT. THE SAMPLING DETERMINED THATTHE MIXTURE WAS COMPRISED OF GASOLINE, DIESEL FUEL AND AVIATION FUEL. ADDITIONALLY, OLYMPIC CONDUCTED A PRESSURE TEST WHICH ESTABLISHED THAT NO LEAKAGE IS PRESENTLY OCCURRING ON ITS PIPELINE SYSTEM. OLYMPIC HAS SECURED THE SERVICES OF A PRIVATE ENVIRONMENTAL CONSULTING FIRM TO ASSIST IN THE INVESTIGATION AND EVALUATION OF THE EXISTING PROBLEM, WHILE CONTINUING TO WORK WITH THE DOE. APPROPRIATE MONITORING, CLEAN-UP AND RECOVERY OPERATIONS ARE BEING CONDUCTED WITH CONCURRENCE FROM THE DOE.
2017-09-29 08:50 | YES | NO | 19860177 |  | 2687 | COMYN PIPELINE CO | YES | 1986-08-28 | 110 | TX | EASTLAND | RANGER | NO |  | NO | NORTH FEEDER ROAD ACROSS FROM SUN PIPELINE TANK FARM I-S. HWY 20, RANGER, TEXAS |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 568 | 50 | NO | NO | 6 | 0.28 | 25000 | THREADED |  | 75 | 60 | YES | 24 | 530 | 10 | 85 | NO DATA | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | F. BEVARD, GENERAL MANAGER | 9156772223 | 6" PIPELINE OWNED BY COMYN PIPELINE COMPANY WAS HIT BY EG&K CONSTRUCTION OF ABILENE, TEXAS WHILE INSTALLING AN UNDERGROUND TELEPHONE CABLE.
2017-09-29 08:50 | YES | NO | 19860178 |  | 2687 | COMYN PIPELINE CO | YES | 1986-07-26 | 1000 | TX | JONES | HAMLIN | NO |  | NO | APX. 6 MILES SOUTHWEST OF HAMLIN, TEXAS ON SOUTH SIDE OF FM57. OWNERS' NAME IS A.E. KILLION OF HAMLIN TEXAS. |  | LINE PIPE | PIPE |  | 1925 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 283.8909 | 572.7226 | CRUDE OIL | 1 | 336 | 50 | NO | NO | 5 | 0.24 | 25000 | THREADED |  | 325 | 325 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | F. BREVARD, GENERAL MANAGER | 9156772223
2017-09-29 08:50 | YES | NO | 19860179 |  | 2687 | COMYN PIPELINE CO | YES | 1986-07-05 | 1030 | TX | EASTLAND | RANGER | NO |  | NO | NORTH FEEDER ROAD OFF I-20 NEAR SUN PIPELINE TANK FARM AT RANGER, TEXAS |  | LINE PIPE | PIPE |  | 1945 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | CRUDE OIL | 1 | 145 | 0 | NO | NO | 6 | 0.28 | 25000 | THREADED |  | 75 | 60 | YES | 24 | 530 | 10 | 85 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | F. BEVARD, GENERAL MANAGER | 9156772223 | 6" PIPELINE OWNED BY COMYN PIPELINE COMPANY WAS HIT WHILE JOE BOB CONSTRUCTION OF EASTLAND, TEXAS WAS CONSTRUCTING A TANK BATTERY LOCATION FOR SUN PRODUCTION. IT WAS HIT BY A DOZER WHILE MAKING THIS TANK LOCATION.
2017-09-29 08:50 | YES | NO | 19860180 |  | 2687 | COMYN PIPELINE CO | NO | 1986-10-22 | 300 | TX | EASTLAND | RANGER | NO |  | NO | W.C. BOSWELL SURVEY, SEC.A-29, BLK 9 OF EASTLAND CTY, TX; APX. 4 MILES NW OF CITY OF RANGER |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 189.2606 | 381.8151 | CRUDE OIL | 1 | 99 | 0 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 75 | 20 | YES | 6 | 513 | 3 | 78 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | F. BEVARD, GENERAL MANAGER | 9156772223 | LOCK CONSTRUCTION OF ODESSA, TX. WHILE CLEARING RIGHT-OF-WAY FOR NEW PIPELINE (SUN PIPELINE) KNOCKED A HOLE WITH LOW-BOY TRAILER WHILE CROSSING OVER PIPELINE.
2017-09-29 08:50 | YES | NO | 19860181 |  | 18386 | SOHIO PIPELINE CO | YES | 1986-10-29 | 1537 | OH | MONTGOMERY | MAD RIVER TOWNSHIP | NO |  | NO | INTERSECTION OF SMITHVILLE RD. AND SPRINGFIELD ST. (SEE ATTACHED MAP) |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2838.9089 | 5727.2259 | DIESEL FUEL | 3 | 119 | 115 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1230 | 1200 | YES | 24 | 1540 | 9 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | D.L. AYERS, MANAGER, ADM. & OPERS. COORDINATION | 5138988101 | THE PIPELINE WAS LOCATED EARLIER FOR THE COUNTY ENGINEERS WHO WERE PERFORMING SOME CONSTRUCTION IN THE AREA. THEY RESPONDED THAT THEY WOULD NOT BE WORKING NEARTHE PIPELINE. THE PIPELINE WAS DAMAGED BY CONSTRUCTION WHICH RESULTED IN THE LEAK. THIS WAS THE SECOND LEAK IN THE AREA ON THIS PIPELINE CAUSED BY THE CONSTRUCTION. THE OPERATOR WAS NOT CALLED TO INSPECT DURING THE CONSTRUCTION. THE PIPELINE WAS EXPOSED FOR APPROXIMATELY 700 FEET AND SEVERAL OTHER AREAS OF DAMAGE WEREFOUND. APPROX. 40 FEET OF PIPE WAS REPLACED. AN INTERNAL INSPECTION DEVICE IS SCHEDULED TO BE RUN DURING THE MONTH OF NOVEMBER, 1986 TO LOOK FOR OTHER DAMAGE.THIS INSPECTION WAS DETERMINED NECESSARY AFTER THE PREVIOUS LEAK CAUSED BY THIRD-PARTY DAMAGE.
2017-09-29 08:50 | YES | NO | 19860182 |  | 12628 | MOBIL PIPELINE CO | YES | 1986-10-24 | 230 | TX | CLAY |  | NO |  | NO | APPROX. 4 MILES WEST AND 3/4 MILES SOUTH OF HENRIETTA, TX, HT&BBR CO. SURVEY, ABS. 232, BLK.69. |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 44476.2395 | 89726.5397 | CRUDE OIL | 1 | 4000 | 3500 | NO | NO | 8 | 0.32 | 1792 | WELDED |  | 400 | 300 | YES | 2 | 586 | 10 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | EXTERNAL CORROSION PENETRATED THE PIPE WALL RESULTING IN THE CRUDE OIL SPILL. REPAIRS WERE MADE BY WELDING A FULL ENCIRCLEMENT WRAP TO THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19860183 |  | 4805 | EXPLORER PIPELINE CO | YES | 1986-10-31 | 600 | LA | CALCASIEU |  | NO |  | NO | 1.09 MILES EAST OF STATE HIGHWAY 1133, 50 YDS. NORTH OF DAVE DOUGAS ROAD, ON EXPLORER PIPELINE LAKE CHARLES STATION SITE. SEE ATTACHED MAP |  | PUMPING STATION | VALVE | THERMAL RELIEF VALVE | 1971 | OTHER | TOP/THERMAL VALVE UNSCREW | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 23657.5742 | 47726.8828 | FUEL OIL | 2 | 220 | 219 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. SANDS, VICE PRESIDENT OPERATIONS | 9184935100 | AT 6:19 ON OCTOBER 31, 1986, EXPLORER'S DELIVERYMAN ARRIVED AT LAKE CHARLES PUMP STATION AND DISCOVERED #2 FUEL OIL ESCAPING FROM A THERMAL RELIEF VALVE ON THE#1 PUMP UNIT. FUEL OIL WAS RUNNING INTO A DRAINAGE DITCH ON THE EAST SIDE OF THE STATION. THE STATION WAS SHUT DOWN IMMEDIATELY AND THE RELIEF VALVE ISOLATED. COMPANY DISPATCHING AND SUPERVISORY PERSONNEL WERE NOTIFIED AND EMERGENCY CLEAN-UP CREWS AND VACUUM TRUCKS WERE DISPATCHED. SPILL CONTAINMENT BOOMS WERE IN PLACE ON THE DRAINAGE DITCH APPROX. 1/2 MILE FROM THE STATION BY 7:00. AN EARTHEN DAM WAS ALSO BUILT ACROSS THE DITCH TO ASSURE NO PRODUCT ESCAPED INTO THE CALCASIEU RIVER. VACUUM TRUCKS AND CONTRACT PERSONNEL FINISHED CLEAN-UP BY 15:00 ON NOVEMBER 2, 1986. ALL OIL WAS CONTAINED IN THE DRAINAGE DITCH AND SUBSEQUENTLY RECOVERED. CAUSE OF THE SPILL IS ATTRIBUTED TO THE TOP PORTION OF A THERMAL RELIEF VALVE UNSCREWING AS A RESULT OF PUMP VIBRATIONS, ALLOWING PRODUCT TO ESCAPE.
2017-09-29 08:50 | YES | NO | 19860184 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-10-22 | 509 | KS | MIAMI | PAOLA | NO |  | NO | MIAMI CTY, SE1/4 SW1/4 T17S R23E |  | LINE PIPE | GIRTH |  | 1946 | FAILED WELD | DEFECTIVE WELD | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9463.0297 | 19090.7531 | FUEL OIL | 2 | 1901 | 0 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 1096 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.K. MCCAW, VICE PRESIDENT-OPERATIONS | 9185883285 | THE LINE WAS OPERATING NORMALLY PRIOR TO THE ACCIDENT. WATER VELOCITY AND STREAM BOTTOM EROSION CREATED STRESSES ON THE GIRTH WELD CAUSING A FAILURE OF A DEFECTIVE WELD.
2017-09-29 08:50 | YES | NO | 19860185 |  | 443 | AMOCO PIPELINE CO | YES | 1986-11-13 | 1645 | TX |  | DENVER CITY | NO |  | NO | 3 MILES WEST & 1/2 MILE NORTH OF DENVER CITY, TEXAS |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 88 | 82 | NO | NO | 6 | 0.13 | 0 | WELDED |  | 250 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | JAMES L. HOMER, P/L MAINT. FOREMAN | 5053962817 | CONTRACT BACKHOE WAS DIGGING WORKOVER PIT FOR PRODUCER - WHILE DIGGING PIT HE HIT & PUNCTURED P/L. ALL OIL WAS CONTAINED IN PIT. P/L WAS REPAIRED & RETURNED TO
2017-09-29 08:50 | YES | NO | 19860186 |  | 19536 | TOTAL PIPELINE CORP | NO | 1986-11-13 | 1015 | OK | COTTON |  | YES | SE1/4 SW1/4 14/4W-13W | NO | 2 MILES NORTH AND 1/2 MILE WEST OF THE JUNCTION OF STATE HIGHWAY 70 AND 36 (SEE ATTACHED MAP) |  | LINE PIPE | PIPE | COLLAR COUPLING | 1919 | FAILED PIPE | OTHER | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4731.5148 | 9545.3766 | CRUDE OIL | 1 | 400 | 385 | NO | NO | 8 | 0.32 | 35000 | COUPLED |  | 600 | 50 | YES | 8 | 1006 | 4 | 86 | NO DATA | Null | YES | OTHER | IMPRESSED RECTIFIERS | OTHER | SUDDEN DROP IN TEMP. | Null | ONE CALL |  | NO | NO | W.O. DELANO, GENERAL MANAGER | 4052291638 | ON 11-13-86 AT 10:00 A.M. TOTAL PIPELINE PERSONNEL STARTED PUMPING DEVOL STATION. WHEN THE LINE DISCHARGE PRESSURE FAILED TO INCREASE FROM 50PSI, THEY SHUT DOWN THE STATION AT 10:10A.M. AT 10:15A.M. TOTAL PIPELINE'S BURKBURNETT OFFICE WAS NOTIFIED OF A LEAK 3 MILES EAST OF DEVOL STATION ON 8" MAINLINE. TOTAL PIPELINE PERSONNEL BEGAN IMMEDIATELY AND WERE CARRIED ON THROUGHOUT THE DAY. UPON VISUAL INSPECTION OF THE PIPELINE IT WAS FOUND THAT A THREADED COUPLING IN THE LINE TEMPERATURE HAD DROPPED DRASTICALLY FROM ABOUT 75 DEGREES F TO 16 DEGREES F THE PREVIOUS NIGHT. THE PIPELINE WAS REPAIRED BY INSTALLING 6' OF PRE-HYDROSTATIC TESTED PIPE AND 2-8" WELD + END COUPLINGS. LEAK WAS REPORTED TO THE FOLLOWING:1. NATIONAL RESPONSE CENTER 1-800-424-8802 AT 8:45P.M. ON 11/13/86 TALKED TO LIEUTENANT ZELL.2.OKLAHOMA CORPORATION COMMISSION 1-405-255-0103 AT 8:00A.M. ON 11/14/86 TALKEDTO WADENE HAYES3. OKLAHOMA CORP COMMISSION PIPELINE SAFETY DIVISION 1-405-521-2258 AT 10:00A.M. ON 11/14/86 TALKED TO PAM COYNE.
2017-09-29 08:50 | YES | NO | 19860187 |  | 2731 | CHEVRON PIPELINE CO | YES | 1986-11-10 | 2030 | UT | DUCHESNE | MYTON | NO |  | NO | CHEVRON PIPELINE CO, MYTON PUMP STATION, MYTON BEACH ROAD, NEAR MYTON, UTAH |  | PUMPING STATION | PUMP |  | 1962 | OTHER | FAILED PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 89898.782 | 181362.1547 | CRUDE OIL | 1 | 70 | 30 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.V. SMITH, DIVISION MANAGER | 8015397200 | A 3/4" OIL COOLING LINE TO PUMP BEARING ON A MAIN LINE BOOSTER PUMP FAILED, RELEASING OIL AROUND THE BOOSTER PUMP AREA. THIS OIL IS CRUDE OIL FROM THE MAIN PIPELINE WHICH IS CIRCULATED THROUGH THE PUMP BEARINGS TO DISSIPATE EXCESS HEAT IN THE BEARING. THE OIL IS THEN RETURNED TO THE MAIN LINE. THE SUPERVISING DISPATCHER WAS ALERTED TO THE SPILL BY ALARMS IN THE DIVISION CONTROL CENTER, AND FIELD PERSONNEL WERE DISPATCHED TO THE STATION. THIS STATION IS REMOTELY OPERATED AND IS NORMALLY NOT MANNED. THE OIL SPILL WAS CONFINED TO THE STATION SITE. RECOVERED OIL WAS RETURNED TO THE MAIN PIPELINE AND THE CONTAMINATED SOIL WAS HANDLED ASAGREED TO WITH THE UTAH STATE WATER POLLUTION CONTROL AGENCY.
2017-09-29 08:50 | YES | NO | 19860188 |  | 4805 | EXPLORER PIPELINE CO | YES | 1986-10-27 | 1035 | TX | DALLAS | DALLAS | NO |  | NO | APPROX. 1500 FT. SOUTH OF ROYAL LANE AND 2 MILES WEST OF INTERSTATE I35. JOHN SPOON SURVEY A-1632, DALLAS CTY, TX. (SEE ATTACHED MAP) |  | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 14194.5445 | 28636.1297 | GASOLINE | 1 | 805 | 805 | NO | NO | 12 | 0.22 | 52000 | WELDED |  | 1286 | 71 | YES | 77 | 1702 | 0 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | YES | NO | R.E. SANDS, VICE PRESIDENT/OPERATIONS | 9184935100 | A CONTRACTOR EMPLOYED BY A MAJOR LOCAL DEVELOPER WAS CLEANING OUT A DRAINAGE DITCH WITH A BACKHOE. THE CONTRACTOR ALSO HAD DUG A HOLE ADJACENT TO THE DRAINAGE DITCH TO DISPOSE OF SILT AND SOIL FROM THE DITCH. WHILE ENLARGING THE DISPOSAL PIT, THE CONTRACTOR HIT EXPLORER'S 12" DIAMETER PETROLEUM PRODUCTS PIPELINE WITH THE BACKHOE BUCKET. THE PIPELINE WAS APPROX. 9 FT. DEEP AT THE LOCATION OF THE DISPOSAL PIT. THE TEETH ON THE BACKHOE BUCKET RIPPED AN 8" LONG, 2" WIDE HOLE IN THE SIDE OF THE PIPELINE AT APPROX. 5:00 O'CLOCK POSITION. THE PIPELINE WAS SHUTDOWN AT THE TIME WITH 71 PSIG PRESSURE. NOLEAD GAS SPILLED FROM THE P/L AND WAS CONTAINED IN THE DISPOSAL PIT. THE CONTRACTOR CALLED EXPLORER'S DISPATCHER IN TULSA, OK SEVEN MINUTES AFTER HITTING MAINTENANCE CONTRACTOR AND VACUUM TRUCKS, LOCAL FIRE AND POLICE DEPTS WERE ALSO CONTACTED. DRAIN-UP WAS ALMOST IMMEDIATE, REPAIRS WERE MADE WITH A NEW SECTION OF PIPE CONNECTED WITH WELD + ENDS. PERMANENTWELDINGS WAS DELAYED UNTIL GAS VAPORS WERE COMPLETELY ELIMINATED. THE NEAREST P/L MARKER WAS APPROX. 150 FT. FROM THE LEAK. HOWEVER, THE CONTRACTOR HAD TO DRIVE BY SEVERAL P/L MARKERS LOCATED IN THE FIELD WHILE GAINING ACCESS TO THE DRAINAGE DITCH. EXPLORER HAD NOT BEEN PREVIOUSLY CONTACTED ABOUT THE NATURE OR DATE OFTHE CONTRACTOR'S WORK.
2017-09-29 08:50 | NO | NO | 19860189 |  | 2552 | COLONIAL PIPELINE CO | YES | 1986-10-29 | 845 | VA | PITTSYLVANIA |  | NO |  | NO | AT A POINT APPROX. .25 MILES SOUTH OF U.S. HIGHWAY 58 AND 1 MILE WEST OF THE CITY LIMITS DANVILLE, VA (SEE ATTACHED MAP) |  | NO DATA | PIPE |  | 1963 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9700 | 9179.1388 | 18518.0305 | GASOLINE |  | 12 | 11 | NO | NO | 32 | 0.28 | 52000 | WELDED |  | 632 | 330 | YES | 24 | 885 | 11 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | J.S. SORROW, SENIOR ADMINISTRATOR | 4042611470 | AT 8:45 ON NOVEMBER 29, 1986, TELEPHONE NOTICE WAS RECEIVED AT THE COLONIAL WITT, VA. PUMPING STATION THAT A SMALL AMOUNT OF PETROLEUM PRODUCT WAS ON THE SURFACE OF A CREEK NEARBY. TRACES OF GAS WERE FOUND, AND THREE CONTAINMENT DAMS WERE CONSTRUCTED ACROSS THE CREEK TO CONTAIN THE PRODUCT. THE PIPELINE WAS EXCAVATED TO FIND A 1/8" DIAMETER HOLE IN THE PIPE WALL CAUSED BY ABRASION FROM A ROCK THAT HAD BECOME LODGED UNDER THE PIPELINE. AN ESTIMATED 12 BARRELS OF GAS HAD BEEN LOST FROM THE P/L WITH 11 BARRELS OF THAT AMOUNT BEING RECOVERED. THE ROCK WAS REMOVED FROM BENEATH THE PIPE AND A REPAIR CLAMP WAS BOLTED AROUND THE PIPE TO STOP THE LEAK. THE CLAMP WAS LATER WELDED TO THE PIPE WHEN THE AREA WAS CLEARED AND MADE SAFE FOR HOT WORK PROCEDURES. THE FEDERAL EPA AND VA. WATER QUALITY CONTROL BOARD WERE NOTIFIED OF THE SPILL.
2017-09-29 08:50 | YES | NO | 19860190 |  | 320 | ALLEGHENY PIPELINE CO | YES | 1986-11-11 | 845 | PA | YORK | MECHANICSBURG | NO |  | NO | MECHANICSBURG, PA. EAST OF TWP ROAD 979 - M.P. 22.7 - 6" LINE A3 (SKETCH ATTACHED) |  | NO DATA | SCRAPER TRAP |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 15 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | PENNSYLVANIA ACT | Null | YES | B.R. PURGATORIO, JR, VICE PRESIDENT | 7137595454 | AN ALLEGHENY PIPELINE COMPANY MAINTENANCE UNIT WAS WORKING ON SCHEDULED PIPELINE EXCAVATION FOR LOCATION OF EXISTING 2 INCH LINE TAP NEAR A BLOCK VALVE. THE EXISTING TAP WAS TO BE UTILIZED FOR DRAINING THE 6 INCH LINE FOR A SCHEDULED RELOCATION PROJECT WITHIN THE AREA. THE BACKHOE OPERATOR WAS EXCAVATING ALONG SIDE OFTHE PIPE, WHILE LABORERS WERE REMOVING THE DIRT AWAY FROM THE PIPE WITH HAND SHOVELS. AN IN LINE CHECK VALVE WAS ALSO LOCATED WITHIN THE SUBJECT LINE SECTION APPROX. 6 FT. WEST OF THE BLOCK VALVE. THE CHECK VALVE PACKING NUT FOR THE CLAPPER STEM WAS PROTRUDING OUTSIDE THE CHECK VALVE BODY THE NUT WAS HIT AND THE SCREWTHREADS WERE BROKEN CAUSING NORMAL BUTANE TO BE RELEASED TO THE ATMOSPHERE. A PIT WAS ESTABLISHED TO CONTAIN ALL LIQUID. LOCAL AUTHORITY WAS NOTIFIED AND A SAFETY PRECAUTION TWO RESIDENTIAL DWELLINGS EVACUATED. A PIPELINE WAS BACK IN NORMAL SERVICE AT 1600 HRS. NOVEMBER 12, 1986. DURING THE DURATION OF STOPPLE AND REPAIR THE NORMAL BUTANE DISSIPATED TO THE ATMOSPHERE.
2017-09-29 08:50 | NO | NO | 19860191 |  | 4906 | EXXON PIPELINE CO | YES | 1986-10-16 | 850 | TX | WOOD |  | NO |  | NO | LEAK OCCURRED AT STATION 11+30 ON STATE HIGHWAY 14 ROAD CROSSING APPROX. 1130 FT. EAST OF EPC'S HAWKINS STATION ON THE HAWKINS-LONGVIEW 16 INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 13976 | 13225.5303 | 26681.2366 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 16 | 0.28 | 42000 | WELDED |  | 960 | 110 | YES | 0 | 960 | 6 | 72 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY | 7136565956 | EXXON CO., U.S.A.(HAWKINS PRODUCTION) REPORTED A LEAK TO SHARON TROWBRIDGE, EPCPIPELINER, AT APPROX. 8:50A.M. ON 10/16/86, ON OUR HAWKINS-LONGVIEW MAINLINE WEST OF HWY.14. THE LEAK WAS CAUSED BY EXTERNAL CORROSION CAUSED BY A SHORTED CASING. APPROX. 1/2 BARREL OF HAWKINS CRUDE WAS OUT. THE SOIL WAS TURNED DURING THE REPAIRS, BUT NO OTHER CLEANUP WAS NECESSARY. NATURAL DITCHES WERE USED TO CONFINE THE OIL. ONE HUNDRED FEET OF 16" PIPE WAS USED TO REPLACE THE PIPE. THE EXACTTIME THAT THE LEAK STARTED IS UNKNOWN. EPC PERSONNEL AND A MCMAHAN CONSTRUCTIONBACKHOE WERE DISPATCHED TO THE LEAK SITE IMMEDIATELY. OTHER CONTRACTORS USED WERE: SIGMON CONSTRUCTION (TRACKHOE AND SIDEBOOM), MCCORD-LANE CO.(TANK TRUCK), MURPHY CONSTRUCTION(BACKHOE AND WELDER). ACID ENGINEERING WAS ALSO USED FOR REPAIRS. PERMANENT REPAIRS WERE COMPLETED AT 12:30 A.M. ON 10/18/86. THE LINE WAS PUT BACK IN SERVICE AT 1:00A.M. ON 10/18/86.
2017-09-29 08:50 | NO | NO | 19860192 |  | 443 | AMOCO PIPELINE CO | Null | 1986-11-20 | 900 | TX | JEFFERSON | BEAUMONT | NO |  | NO | NORTH LOADING DOCK, BEAUMONT TANK FARM |  | TANK FARM | PUMP |  | 0 | OTHER | PUMP SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 2 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOE NELSON, AREA MANAGER | 2147597131 | THE COAST GUARD MADE AN UNANNOUNCED INSPECTION OF THE DOCK AREA AT BEAUMONTAT 9:00A.M. ON NOV. 20, 1986. UNFORTUNATELY WE HAPPENED TO HAVE A LEAK ON THESUMP PUMP AT THE TIME. I WAS MADE AWARE OF THE PROBLEM ABOUT 9:30A.M. ANDIMMEDIATELY WENT TO INVESTIGATE. AFTER CHECKING THE SITUATION WE DID THEFOLLOWING: 1.PUMPED OUT THE DRAIN PAN UNDER THE SUMP WHICH STOPPED FURTHERSPILLAGE. TIME:9:45A.M. 2. DEPLOYED THE CONTAINMENT BOOM AND TRAPPED OILAROUND THE DOCK FROM ESCAPING. TIME:10:10A.M. 3. WASHED OIL BENEATH DOCK INTOBOOM AND PICKED UP ALL SIGNIFICANT AMOUNTS WITH ABSORBANT SHEETS. TIME 12:30P.M.MADE REPAIRS TO THE SUMP PUMP SEAL. TIME 12:00P.M. 5.RETRIEVED CONTAINMENTBOOM FOLLOWING CLEANUP AND DISPOSED OF OIL ABSORBANT MATERIALS. TIME 2:00P.M.THIS SPILL OCCURED ON THE NORTH DOCK WHERE THE MECHANICAL PUMP SEAL HAD FAILEDAND #2 FUEL OIL WAS LEAKING OUT AROUND THE SHAFT AND INTO THE DRIP PAN BENEATHTHE DRIP PAN HAD OVERFLOWED AND OIL HAD GOTTEN INTO THE RIVER BELOW. THE RIVERCURRENT CARRIED A 30FT. WIDE SHEEN DOWNSTREAM APPROX. A QUARTER MILE. I WOULDESTIMATED BET 20-30GALS. OF PRODUCT HAD GOTTEN ON THE WATER. THE SUMP PUMP WASNOT OPERATING AT THE TIME OF THE SPILL. THE COAST GUARD REPRESTATIVES' MARKHOWARD AND MIKE HAYNIE PRESENTED ME WITH A WRITTEN NOTICE OF POLLUTION INCIDENTAT THE TIME. A COPY OF WHICH IS ATTACHED.
2017-09-29 08:50 | YES | NO | 19860193 |  | 443 | AMOCO PIPELINE CO | YES | 1986-11-03 | 830 | OK | POTTAWATOMIE |  | NO |  | NO | 1/2 MILE N. & 1/4 E. OF TRIBBEY, OK |  | LINE PIPE | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2365.7574 | 4772.6883 | CRUDE OIL | 1 | 275 | 250 | NO | NO | 12 | 0 | 35000 | WELDED |  | 700 | 15 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J. W. WILHELM, AREA MANAGER OPERATIONS | 9182257271 | THE POTTAWATOMIE COUNTY ROAD GRADER WAS GRADING AN E-W GRAVEL ROAD WHEN ITSTRUCK THE 12" PIPELINE IN THE DITCH BOTTOM. LINE MARKERS ARE LOCATED PLAINLYVISIBLE IN THE FENCE LINE ON EACH SIDE OF THE ROAD AND THE GRADER OPERATORKNEW THE LINE WAS THERE. NO ONE WAS HURT.
2017-09-29 08:50 | YES | NO | 19860194 |  | 2745 | CONTINENTAL PIPELINE CO | YES | 1986-11-21 | 1045 | OK | OKLAHOMA | DALE | NO |  | NO | 250 YEARS NORTH OF RENO & VICKIE ON THE EAST SIDE OF VICKIE ROAD IN THE BANK OF CRUTCHO CREEK. |  | LINE PIPE | PIPE |  | 1962 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1892.6059 | 3818.1506 | GASOLINE | 1 | 965 | 573 | NO | NO | 8 | 0.16 | 52000 | WELDED |  | 1354 | 260 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | DWIGHT JACKSON, DIR. OF ENVIRONMENTAL AFFAIRS | 7132932100 | OKEMAH PIPELINE CONSTRUCTION COMPANY WAS WORKING ON REMOVING AN OLD SUN OIL PIPELINE THAT RAN PERPENDICULAR TO OUR EIGHT INCH LINE. IN THE PROCESS OF DIGGING,THEIR BACKHOE HIT OUR LINE THAT CROSSES THE CRUTCHO CREEK. OUR LINE WAS BURIEDSOME +24" BELOW THE BOTTOM OF CREEK. THEY HIT OUR LINE IN THE SOUTH BANK OF THE CREEK. THE LINE WAS HIT AROUND 10:45 AM AND WE WERE NOTIFIED IMMEDIATELY BY CONTRACTOR. BOOMS WERE DEPLOYED ON EACH SIDE OF LEAK AND TWO EARTHEN DAMS WERE INSTALLED ABOUT 400 YDS. DOWN STREAM OF THE DOWN STREAM BOOM. PRODUCT IS BEING PICKED UP. AFTER INSPECTION OF LEAK AREA, THE PIPE WILL BE REPLACED.
2017-09-29 08:50 | YES | NO | 19860195 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-10-24 | 900 | MN | KANDIYOHI | WILLMAR | NO |  | NO | KANDIYOHI COUNTY NW 1/4 SW 1/4 S32 T12ON R36W |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 14194.5445 | 28636.1297 | GASOLINE | 2 | 274 | 242 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | YES | NO | C.K. MCCAW, VICE PRESIDENT - OPERATIONS | 9185883285 | ON OCTOBER 23, 1986, AT 1545 HOURS, A LANDOWNER CALLED WPL'S NORTHWEST DIVISIONOFFICE REQUESTING US TO LOCATE THE PIPELINE ON HIS PROPERTY. WPL ARRANGED TO MEET THE LANDOWNER THE FOLLOWING DAY AT 0930 HOURS AND STAKE THE LINE. ON OCTOBER 24, AT 0845 HOURS, THE LANDOWNER STARTED PLOWING (BECAUSE OF RAIN) BEFORE OUR PERSONNEL ARRIVED AT THE SITE. AT 0900 HOURS, HE STRUCK OUR #1-8" LINE. THIS LINE WAS NOT OPERATING AT THE TIME IT WAS STRUCK. A TOOTH ON THE TILING MACHINE PUNCTURED THE LINE CREATING A HOLE APPROXIMATELY 2 INCHES IN DIAMETER. THE TOOTH STRUCK IN THE PIPE WHICH MINIMIZED THE PRODUCT LOSS.
2017-09-29 08:50 | YES | NO | 19860196 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-11-25 | 1400 | TX | CRANE |  | NO |  | NO | 5 MILES SOUTH OF PENWELL TX, THEN 150 FT WEST OF STATE ROAD 1601. SECTION 4, BLOCK 26, PSL LAND SURVEY. |  | PUMPING STATION | TANK |  | 1985 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 320 | 300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. L. DOWNIE, DIVISION MANAGER | 9156877551 | HIGH LEVEL SWITCH FAILED TO SHUTOFF FLOW INTO TANK. REPAIRED HIGH LEVEL SWITCHON TANK.
2017-09-29 08:50 | YES | NO | 19860197 |  | 2731 | CHEVRON PIPELINE CO | YES | 1986-11-24 | 900 | TX | CRANE |  | NO |  | NO | SAND HILLS STATION LOCATED SECTION 21, BLOCK 27 PSL LAND SURVEY. THE STATEION IS ABOUT 16 MILES WEST OF CRAIN, TX, JUST OFF OF STATE ROAD 1053 |  | TANK FARM | TANK |  | 1977 | OTHER | TANK MIXER VIBRATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 420 | 400 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. L. DOWNIE, DIV. MANAGER | 9156877551 | TANK (1839) MIXER VIBRATION CAUSED FLANGE NUTS TO LOOSEN, CAUSING THE LEAK. MIXER SUPPORT & BOLTS RE-ADJUSTED.
2017-09-29 08:50 | YES | NO | 19860198 |  | 26086 | SEADRIFT PIPELINE CORP | NO | 1986-11-06 | 1400 | TX | JACKSON |  | NO |  | NO | 7 MILES N OF HWY 35 AND 2 MILES E OF FM 1593. |  | LINE PIPE | PIPE |  | 1961 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 21600 | 20440.1441 | 41236.0268 | L. P. G. | 1 | 650 | 0 | NO | NO | 6 | 0.25 | 42000 | WELDED |  | 1864 | 900 | YES | 24 | 2660 | 0 | 61 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. L. WYATT, ENGINEER | 5125527511 | DURING A ROUTINE AERIAL INSPECTION OF THE PIPELINE RIGHT-OF-WAY, THE PILOT OBSERVED AN ICE BALL ON THE GROUND IN THE IMMEDIATE VICINITY OF THE PIPELINE. THE PIPELINE WAS REMOVED FROM SERVICE AND VENTED THROUGH PORTABLE FLARES. A FIVE-FOOT SECTION OF PIPE CONTAINING A MILL DEFECT WAS CUT AND REPLACED. A SMALL ELLIPTICAL HOLE EXISTED AT THE MILL DEFECT. THE DURATION OF THE MINOR LEAK IS UNKNOWN.
2017-09-29 08:50 | YES | NO | 19860199 |  | 10319 | KOCH GATHERING SYSTEMS INC | YES | 1986-10-11 | 900 | TX | BURLESON |  | NO |  | NO | LEAK OCURRED OF F.M. 60 IN BURLESON CO., JAMES BUCKHANNAN A-7 |  | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 236.5757 | 477.2688 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 6 | 0.19 | 300 | WELDED |  | 300 | 300 | YES | 24 | 1000 | 0 | 81 | INTERNAL | Null | YES | OTHER | SALTWATER | NO DATA |  | Null | NO DATA |  | Null | Null | GARY MAYFIELD,DISTRICT FOREMAN | 4095425559
2017-09-29 08:50 | YES | NO | 19860200 |  | 10319 | KOCH GATHERING SYSTEMS INC | YES | 1986-10-16 | 900 | TX | BURLESON |  | NO |  | NO | LEAK OCCURED OFF F.M. 60 BURLESON CO. JOSEPH HENSON A-136 |  | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1892.6059 | 3818.1506 | CRUDE OIL | 1 | 1000 | 995 | NO | NO | 6 | 0.19 | 300 | WELDED |  | 300 | 300 | YES | 24 | 1000 | 1 | 81 | INTERNAL | Null | YES | GALVANIC | SALTWATER | NO DATA |  | Null | NO DATA |  | Null | Null | GARY MAYFIELD, DISTRICT FOREMAN | 4095425559
2017-09-29 08:50 | YES | NO | 19870001 |  | 2552 | COLONIAL PIPELINE CO | YES | 1986-11-14 | 2307 | NC | GUILFORD | GREENSBORO | NO |  | NO | COLONIAL TANK FARM AT THE INTERSECTION OF I-40 AND GALLIMORE DAIRY ROAD |  | TANK FARM | TANK |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 946.303 | 1909.0753 | GASOLINE | 3 | 200 | 200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. S. SORROW | 4042611470 | MAINTENANCE ON THE ROOF OF TANK 845 AT THE COLONIAL TANK FARM LOCATED IN GREENSBORO, NC, INVOLVED THE USE OF A PUMP CONNECTED T0 THE WATER DRAW AND FLOATING ROOF DRAIN LINES AT THE SHELL OF THE TANK. THE PUMP WAS DETACHED AND REMOVED FROM THE EMPTY TANK, BUT THE WATER DRAW AND ROOF DRAIN VALVES WERE INADVERTENTLY LEFTOPEN. THE STATION OPERATOR CHECKED THE TANK WHILE A DELIVERY OF GASOLINE WAS BEING MADE INTO THE TANK AND FOUND PRODUCT IN THE TANK DIKE.THE VALVES WERE DLOSEDAND THE SPILLED PRODUCT WAS RECOVERED AND PUMPED BACK INTO THE TANK. COLD TEMPERATURE AND WET SOIL IN THE TANK DIKE FACILITATED THE RECOVERY OF ALL SPILLED PROD
2017-09-29 08:50 | YES | NO | 19870002 |  | 809 | ARCO PIPE LINE CO | YES | 1986-11-29 | 1400 | TX | PARKER |  | NO |  | NO | APPROX. 1 MILE SOUTH AND 3 MILES WEST OF ALEDO, TEXAS |  | LINE PIPE | NO DATA |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 80435.7523 | 162271.4016 | CRUDE OIL | 1 | 2751 | 1454 | NO | NO | 18 | 0.28 | 52000 | WELDED |  | 720 | 100 | YES | 24 | 950 | 1 | 56 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | V.P. DRISKI | 3163311300 | ON NOV. 29, 1986, ALEDO CONSTRUCTION, INC. WAS EXCAVATING A DITCH WITH A VEMEERT-800B ROCK DITCHER ACROSS ARCO PIPE LINE CO.'S JACKSBORO-TEAGUE 18" PIPELINE.THE DITCHER HIT THE LINE KNOCKING A HOLE (APPROX. 1" ROUND) IN THE PIPE AT THE 2 O'CLOCK POSITION. ARCO PIPE LINE CO.'S JACKSBORO TO TEAGUE 18" PIPELINE WAS LOCATED AND FLAGGED ON NOV. 13, 1986, AND ALEDO CONSTRUCTION CO. WAS NOTIFIED TO GIVE ARCO NOTIFICATION BEFORE WORKING IN THE VICINITY OF THIS 18" LINE SO THAT ARCO COULD HAVE A REPRESENTATIVE ON SITE. NO NOTIFICATION WAS RECEIVED FROM ALEDO CONSTRUCTION, INC.
2017-09-29 08:50 | YES | NO | 19870003 |  | 26125 | CALNEV PIPELINE CO | YES | 1986-12-09 | 1030 | CA | SAN BERNARDINO |  | NO |  | YES | BAKER BOOSTER STATION, APPROXIMATELY 2.5MILES ENE OF BAKER, CALIFORNIA |  | PUMPING STATION | PUMP |  | 1969 | OTHER | PUMP SEAL FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 100 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PAUL B. STRENGELL | 7148887771 | ACCIDENT OCCURRED AT AN UNMANNED, REMOTE PUMP STATION. THE PUMP OUTBOARD SEAL BEGAN LEAKING AND THE SEAL FAILURE DEVICE FAILED TO SHUT DOWN THE PUMP. THE SUMP HIGH LEVEL ALARM ALSO FAILED AND THE SEAL RAN TO COMPLETE DESTRUCTION. PRODUCT LEAKED FROM THE PUMP UNDER PRESSURE UNTIL DISCOVERED BY THE LINE PILOT.
2017-09-29 08:50 | YES | NO | 19870006 |  | 4906 | EXXON PIPELINE CO | NO | 1986-11-30 | 1300 | TX | NUECES |  | NO |  | NO | LEAK OCCURRED AT STATION 428+73*JUST INSIDE (SOUTH) OF THE KING RANCH NORTH LAURELES FENCE SOME 8 1/2 MILES EAST-SOUTHEAST OF BISHOP, TEXAS(SEE ATTACHES MAP). |  | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2300 | 2176.4968 | 4390.8732 | CRUDE OIL | 1 | 75 | 65 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 818 | 100 | YES | 24 | 900 | 1 | 59 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. P. MURRAY | 7136565956 | ON NOVEMBER 30, 1986 AT 1:00 P.M., A FARMER REPORTED A LEAK IN EXXON PIPELINE COMPANY'S ALAZAN-JCT. ON 390 INTRASTATE TRUNKLINE TO EXXON'S DISPATCHER IN HOUSTON,TEXAS. THE DISPATCHER NOTIFIED THE APPROPRIATE GAUGING SUPERVISOR, WHO THEN DISPATCHED A GAUGER AT 4:30 P.M. THE LINE WAS SHUT DOWN AT 6:00 P.M. NOTE: THE SINGLE LINE PUMP WAS ALREADY DOWN WHEN GAUGER ARRIVED. LINE IS NOT UNDER PRESSURE CONTINUOUSLY. ALL RELEASED OIL (75 BBLS.) WAS CONTAINED IN A MAN-MADE DRAINAGE DITCH. ON DECEMBER 1, 1986, TEMPORARY REPAIRS WERE MADE BY CLAMPING THE LINE AND 65 BARRELS OF OIL WAS RECOVERED WITH VACUUM TRUCKS.ON DECEMBER 2, 1986, PERMANENT REPAIRS WERE MADE BY WELDING 10' OF FULL WRAP ON THE LINE. THE LINE WAS RESTORED TO SERVICE DURING THE AFTERNOON. CLEAN-UP OPERATIONS (TURNING THE SOIL) CONTINUED THROUGHOUT THE WEEK, AND WERE COMPLETED ON DECEMBER 5, 1986.
2017-09-29 08:50 | YES | NO | 19870007 |  | 26084 | SAN DIEGO PIPELINE CO | NO | 1986-11-22 | 1230 | CA | ORANGE | TUSTIN | NO |  | NO | BETWEEN RED HILL AVENUE AND MYFORD ROAD ON SANTA FE RAILROAD RIGHT-OF-WAY PARALLELING MOULTON PARKWAY IN TUSTIN, CALIFORNIA |  | LINE PIPE | PIPE |  | 1962 | OTHER | PIPE SEAM FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 33120.6039 | 66817.636 | GASOLINE | 2 | 11077 | 3180 | NO | NO | 10 | 0.22 | 52000 | WELDED |  | 1525 | 1466 | YES | 24 | 1979 | 1 | 63 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BARRY R. PEARL | 2134867860 | APPROXIMATELY 1250, 11-22-86, ORANGE STATION PERSONNEL ADVISED OUR PRODUCTS MOVEMENT SECTION OF ABNORMAL LINE PRESSURE AND FLOW RATES. APPROXIMATELY 1305, 11-22-86, PRODUCTS MOVEMENT RECEIVED A CALL FROM SHELL OIL COMPANY VIA THE LOS ANGELES BASIN LEAK WHEEL OF A PIPELINE LEAK SOUTH OF RED HILL AVENUE, ON SANTE FE RAILROAD RIGHT-OF-WAY PARALLELING MOULTON PARKWAY IN TUSTIN, CALIFORNIA. LINE WAS SHUT DOWN AT 1311, 11-22-86, AND FIELD FORCES NOTIFIED. BLOCK VALVES WERE CLOSED ON BOTH SIDES OF RUPTURED SECTION OF PIPE. THE ORANGE COUNTY FIRE DEPARTMENT WASTHE FIRST EMERGENCY RESPONSE PERSONNEL AT THE LEAK SITE AND ARRANGED TO CONSTRUCT AN EARTHEN DAM IN A FLOOD CONTROL CHANNEL WHERE MOST OF THE ESCAPING GASOLINEWAS FLOWING. VACUUM TRUCKS RECOVERED SOME OF THE GASOLINE AT THE LEAK SITE AND DAM SITE. THE RUPTURED PIPELINE SECTION WAS REMOVED AND NEW SECTION INSTALLED.
2017-09-29 08:50 | YES | NO | 19870008 |  | 26124 | BEACON OIL CO | NO | 1986-07-30 | 1800 | CA | KINGS | HANFORD | NO |  | NO | AT RAILROAD CROSSING OF THE KINGS RIVER, 2.5 MILES NORTH OF HIGHWAY 198 |  | LINE PIPE | PIPE |  | 1964 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 283890.8904 | 572722.5939 | CRUDE OIL | 1 | 1250 | 0 | NO | NO | 6 | 0.22 | 35000 | WELDED |  | 570 | 200 | YES | 4 | 900 | 8 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | JAMES D. LEWIS | 2095820241 | PIPELINE WAS SHOT ON 7/30/86 AND CLEAN UP ACTIVITIES CONTINUED UNTIL 8/20/86 BETWEEN RAILROAD CROSSING AND THE JACKSON AVE. BRIDGE. DAMAGES TO PIPELINE WAS LOCATED AT THE SHORELINE OF THE KINGS RIVER (EAST SIDE).
2017-09-29 08:50 | YES | NO | 19870009 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1986-10-21 | 1100 | TX | HUTCHINSON |  | NO |  | NO | BORGER GATHERING LINE "BD" 8" STA. 154 + 88 SEC. 67, BLK.46, H&TC RR, HUTCHINSON CO., TX. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 120 | 0 | NO | NO | 8 | 0.32 | 35000 | THREADED |  | 175 | 115 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. A. HILL | 8062737941 | EXTERNAL & INTERNAL CORROSION CAUSED HOLE IN PIPELINE
2017-09-29 08:50 | NO | NO | 19870010 |  | 19212 | TESORO PIPELINE CO | NO | 1986-12-18 | 1000 | TX | JACKSON |  | NO |  | NO | LOCATED IN JACKSON COUNTY, TEXAS APPROXIMATELY 1 1/4 MILES SOUTHWEST OF INTERSECTION HIGHWAY FM 530 AND COUNTY ROAD 402. NEAREST CITY IS CORDELE, TEXAS |  | LINE PIPE | NO DATA |  | 1978 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2365.7574 | 4772.6883 | CRUDE OIL | 1 | 10 | 0 | NO | NO | 45 | 0.16 | 2900 | WELDED |  | 100 | 10 | YES | 8 | 300 | 1 | 78 | INTERNAL | Null | YES | NO DATA | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | BEN F. RUNNELS | 5128288484 | PIPELINE DEVELOPED A FATIGUE LEAK. HEAVY RAINS WASHED OILY FILM INTO "BRUSHY CREEK". USED BOOMS AND OTHER EQUIPMENT TO CONTAIN AND REMOVE OIL FROM WATER AND LAND AREA.
2017-09-29 08:50 | NO | NO | 19870011 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-12-15 | 1230 | TX | HARDIN | SOUR LAKE | NO |  | NO | 1 MILE NORTH OF HWY. 105 ON HWY. 326 |  | TANK FARM | PIPE |  | 1930 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 40 | 30 | NO | NO | 8 | 0.32 | 0 | NO DATA |  | 460 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH | 4098393100 | INPROPER ALIGNMENT OF BLOCK VALVES TOWARDS THE TANKAGE CAUSED EXCESSIVE PRESSURE ON THE PIPELINE CAUSING THE RUPTURE.
2017-09-29 08:50 | YES | NO | 19870012 |  | 22430 | WEST SHORE PIPE LINE CO | YES | 1986-11-26 | 1800 | IN | LAKE | EAST CHICAGO | NO |  | NO | SEC. 28 - T37N-R 9W IN LAKE COUNTY, INDIANA SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1961 | OTHER | DENT FROM ORIGINAL CONSTR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 141.9454 | 286.3613 | TURBINE FUEL | 3 | 320 | 320 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 270 | 40 | YES | 24 | 1625 | 1 | 61 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH C. ANDREEN | 3122573740 | AT ABOUT 1530 HRS. ON NOVEMBER 26, 1986, WEST SHORE PIPE LINE WAS NOTIFIED ALONG WITH OTHER PIPE LINE COMPANIES OF A STRONG ODOR IN THE AREA OF US REDUCTION CO., EAST CHICAGO, IND. THIS IN THE VICINITY OF THE WEST SHORE 16" SHELL/EXPLORER LATERAL TO ITS HAMMOND STATION, HAMMOND, IND. THE LINE HAD BEEN SHUT SOWN AT 1000 HRS. ON NOVEMBER 26 AFTER COMPLETION OF A RECEIPT TO WEST SHORE VIA THIS LATERAL. THE LINE WAS LAID DOWN WITH TURBINE FUEL. THE LINE, THEREFORE, WAS NOT IN OPERATION WHEN THE LEAK WAS REPORTED. THE BLOCK VALVES AT EACH END OF THIS LATERALHAD BEEN CLOSED AS PART OF WEST SHORE'S NORMAL OPERATING PROCEDURE FOLLOWING COMPLETION OF THAT LAST DELIVERY. WEST SHORE PERSONNEL WERE DISPATCHED TO THE SCENE TO EVALUATE THE SITUATION AND CONTACT PERSONNEL TO BEGIN CLEAN-UP AND REPAIR OPERATIONS. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AT 2200 HRS.ON NOVEMBER 26TH. THE LEAK WAS DETERMINED TO BE INSIDE A CASED RAILROADD CROSSING. THE CROSSING WAS REMOVED AND THE LEAK FOUND TO BE CAUSED BY MECHANICAL DAMAGEDURING ORIGINAL CONSTRUCTION. A TOTAL OF 112'9' OF PIPE WAS REPLACED AND THE LINE WAS BACK IN SERVICE DECEMBER 5, 1986. A TOTAL OF 320 BBLS. OF TURBINE FUEL WAS RECOVERED BY VAC TRUCK AND RETURNED TO SHELL OIL CO. CLEAN-UP WAS COMPLETED ONDECEMBER 8, 1986.
2017-09-29 08:50 | YES | NO | 19870013 |  | 19536 | TOTAL PIPELINE CORP | NO | 1986-12-03 | 1100 | MI | CLARE |  | NO |  | NO | COUNTY LINE ROAD, 3/4 MILE WEST OF VANDECAR ROAD, SECTION 34, SURREY TOWNSHIP, CLARE COUNTY |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 150 | 140 | NO | NO | 8 | 0.28 | 0 | WELDED |  | 800 | 600 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | NEIL LAPAUGH | 5174639612 | ISABELLA COUNTY ROAD GRADER WAS REPAIRING WASHED OUT ROAD BED. OPERATOR WAS DITCHING SHOULDER OF ROAD WITH GRADER BLADE TO OBTAIN DIRT FOR FILL FOR WASH OUTS AND TO ALLOW WATER RUN OFF IN DITCH INSTEAD OF ROAD BED. WHEN HIS DITCH INTERSECTED OUR LINE, THE LINE WAS PUNCTURED BY THE ROAD GRADER BLADE. TOTAL PIPELINE WASNOT ADVISED OF THE WORK GOING ON IN THE RIGHT OF WAY AREA. THE ORIGINAL 3 FOOT OF COVER HAD BEEN REDUCED BY THE CUTTING OF A NEW ROAD BED WHEN ROAD WAS REROUTED
2017-09-29 08:50 | YES | NO | 19870014 |  | 2731 | CHEVRON PIPELINE CO | NO | 1986-12-20 | 1500 | TX | LIBERTY |  | NO |  | NO | (SEE ATTACHED MAP) |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 90 | 80 | NO | NO | 8 | 0.32 | 0 | NO DATA |  | 460 | 0 | YES | 0 | 550 | 1 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH - DIVISION MANAGER | 4098393100 | DISPATCHER NITICED METER CHECKS WERE OUT AND SHUT DOWN OPERATIONS AT 8:30 A.M. AERIAL PATROL WAS REQUESTED IMMEDIATELY AND SPOTTED THE SUSPECTED LOCATION AT 12:40 P.M. DUE TO THE REMOTENESS OF THE LOCATION, LEAK WAS NOT CONFIRMED UNTIL 3:00P.M. RESPONSE CREWS WERE IMMEDIATELY SENT TO THE AREA AND 90% OF THE MATERIAL WAS RECOVERED WITH VACUUM TRUCKS. LEAK WAS CONFINED IN THE PIPELINE RIGHT-OF-WAY.THE COMPANY REQUESTED AND WAS GRANTED BY THE TEXAS AIR CONTROL BOARD TO BURN OFF UNRECOVERED MATERIAL. SADDLE WAS USED FOR TEMPORARY REPAIRS. CUT-OUT AND PERMANENT REPLACEMENT IS SCHEDULED AT A LATER DATE.
2017-09-29 08:50 | YES | NO | 19870015 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1986-12-11 | 2219 | KS | RENO | WILLOWBROOK | NO |  | YES | TOWNSHIP 22 SOUTH RANGE 6 WEST 1 MILE SOUTH OF WILLOWBROOK, KANSAS |  | LINE PIPE | NO DATA |  | 1964 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 267.8037 | 540.2683 | L. P. G. | 2 | 10 | 0 | NO | NO | 8 | 0.16 | 1881 | WELDED |  | 1171 | 1220 | YES | 24 | 1560 | 1 | 64 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S. F. ISAACS | 9185811800 | UNKNOWN PENDING RESULTS OF METALLURGICAL TEST.
2017-09-29 08:50 | NO | NO | 19870016 |  | 18386 | SOHIO PIPELINE CO | NO | 1986-12-14 | 630 | LA | JEFFERSON |  | NO |  | NO | BARATARIA BAY LAT. 29 DEGREES 16'53" LONG. 89 DEGREES 56'47" |  | LINE PIPE | PIPE | CRACK IN HORIZONTAL WELD | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 4 | 0 | NO | NO | 12 | 0.31 | 35000 | WELDED |  | 1100 | 750 | YES | 0 | 1375 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L. L. OWEN | 5043926601 | LEAK WAS DISCOVERED BY PASSING COMPANY BOAT. ONLY A SHEEN WAS VISIBLE AND LEAK WAS TOO SMALL FOR COMPUTERIZED LEAK DETECTION SYSTEM TO IDENTIFY. THE 4 BBL. QUANTITY IS AN ESTIMATE. THE LEAK RESULTED FROM A CRACK IN A HORIZONTAL WELD ON A PREVIOUSLY INSTALLED 10" X 12" X 3/8" REPAIR PATCH. THE DATE AND CIRCUMSTANCES OFTHE PATCH INSTALLATION IS UNKNOWN. TEMPORARY REPAIR WAS COMPLETED BY GRINDING OUT THE CRACK AND WELDING. THE SECTION OF PIPE CONTAINING THE PATCH WILL BE REPLACED TO CONSTITUTE A PERMANENT REPAIR. THIS PIPELINE SYSTEM WAS PURCHASED FROM CHEVRON PIPE LINE COMPANY ON 1 SEPT. 1986 AND COMPLETE RECORDS HAVE NOT BEEN FURNISHED BY PREVIOUS OWNER
2017-09-29 08:50 | YES | NO | 19870017 |  | 2552 | COLONIAL PIPELINE CO | YES | 1986-12-01 | 100 | TN | MARION | WHITWELL | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE | 9 | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 75704.2374 | 152726.025 | KEROSENE | 3 | 600 | 500 | NO | NO | 8 | 0.19 | 42000 | WELDED |  | 1318 | 1256 | YES | 24 | 1831 | 1 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | J. S. SORROW | 4042611470 | ON DECEMBER 1, 1986, AT 00300 HOURS, THE CHATTANOOGA TO NASHVILLE, TENNESSEE, 8"DIAMETER PIPELINE WAS SHUT DOWN BY AUTOMATIC SAFETY DEVICES DUE TO A PUMP BEARING FAILURE AT THE MURFREESBORO, TENNESSEE, PUMP STATION. THE UNIT WAS REPAIRED, AND AT 0400 HOURS AN ATTEMPT WAS MADE TO RESTART THE PIPELINE, BUT THE PUMP STATION UPSTREAM OF MURFREESBORO WOULD NOT START DUE TO LOW SUCTION PRESSURE. THE PIPELINE WAS SECURED, AND EMERGENCY PERSONNEL WERE ALERTED TO A POSSIBLE LEAK IN THE PIPELINE. THE MARION COUNTY, TENNESSEE, SHERRIFF'S OFFICE WAS NOTIFIED AT 0800 HOURS THAT A POSSIBLE KEROSENE SPILL EXISTED FROM THE PIPELINE IN THE VICINTY OF WHITWELL, TENNESSEE. AT 1000 HOURS THE LEAK SITE WAS LOCATED ON A STEEP SLOPEOF THE SOUTH SIDE OF WHITWELL MOUNTAIN AS SHOWN ON THE ATTACHED PORTION OF A USC&GS MAP. A 15 FT. LONG SPLIT IN THE PIPE LONGITUDINAL SEAM WAS THE SOURCE OF THE FAILURE. SEVERAL DENTS IN THE PIPE WERE OBSERVED ALONG THE LONGITUDINAL SEAM WHICH WAS LOCATED NEAR THE 12 O'CLOCK POSITION. IT IS BELIEVED THAT THE PIPE WAS POSSIBLY DAMAGED BY CONTRACTOR EQUIPMENT ENGAGED IN CONSTRUCTING AN ADJACENT PARALLEL COLONIAL 10" DIAMETER PIPELINE IN 1972. APPROXIMATELY 600 BBLS. OF KEROSENE HAD SPRAYED FROM THE PIPE ONTO TREES AND ROCKS AND WAS APPEARING ON THE SURFACE OF THE MOUNTAIN SLOPE BELOW THE LEAD SITE. ALL OF THE 60 FT. LONG JOINT OF PIPE CONTAINING THE SPLIT WAS REMOVED FROM THE PIPELINE AND REPLACED WITH PRE-HYDROS
2017-09-29 08:50 | YES | NO | 19870018 |  | 443 | AMOCO PIPELINE CO | YES | 1986-12-25 | 1400 | IL | WILL | JOLIET | NO |  | NO | 300 FEET WEST OF THE INTERSECTION OF OLIN ROAD AND WEST TREATMENT ROAD IN JOLIET, IL |  | LINE PIPE | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 141945.4452 | 286361.297 | FUEL OIL | 3 | 429 | 379 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 1090 | 890 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. A. STAHL - AREA MANAGER- OPERATIONS | 2197382359 | ON THE AFTERNOON OF DECEMBER 25, 1986, THE COAST GUARD REPORTED A SHEEN ON THE DES PLAINES RIVER. AFTER SEVERAL HOURS OF CHECKING IT WAS DETERMINED THAT WE HADA LEAK ON THE WHITING TO DUBUQUE LINE. PRODUCT FROM THIS LINE HAD SEEPED INTO AN OUT FALL FROM A NEARBY SEWAGE TREATMENT PLANT WHICH CARRIED THE PRODUCT OUT ONTO THE DES PLAINES RIVER
2017-09-29 08:50 | YES | NO | 19870019 |  | 26141 | SHELL OIL CO | YES | 1986-12-30 | 719 | OK | GARVIN | PAULS VALLEY | NO |  | NO | SW 1/4, SW 1/4, SECTION 25, T-4-N, R-1-W, SURVEY 4639+50 SOUTHWEST BANK OF WASHITA RIVER HAEALDTON-CUSHING 10-INCH |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 283890.8904 | 572722.5939 | CRUDE OIL | 1 | 400 | 400 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 850 | 470 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | M. J. EICHLER | 7132416262 | THE PIPE APPEARED TO HAVE BEEN HIT BY A BACKHOE SOMETIME IN THE PAST- THE TIME AND WHO HIT THE PIPELINE ARE UNKNOWN. THIS INCIDENT APPARENTLY CAUSED A WEAKNESSIN THE PIPE RESULTING IN THE LEAK.
2017-09-29 08:50 | YES | NO | 19870020 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1986-12-30 | 1120 | CA | CONTRA COSTA | MARTINEZ | NO |  | NO | ON RAILROAD RIGHT-OF-WAY, APPROXIMATELY 1/2/ MILE EAST OF THE MARTINEZ AMTRACK STATION. P.L.M.P. 8.27 (MEASURED FROM UNION JUNCTION) |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | JET FUEL | 2 | 445 | 400 | NO | NO | 8 | 0.19 | 1800 | WELDED |  | 1440 | 900 | YES | 4 | 1800 | 4 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | BARRY R. PEARL, VICE PRESIDENT-OPERATIONS | 2134867860 | THE RUPTURE WAS AT A POINT WHERE LINE HAD BEEN DAMAGED SOMETIME IN THE PAST ANDDAMAGE WAS NEVER REPORTED
2017-09-29 08:50 | YES | NO | 19870021 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-01-19 | 1115 | TX | JEFFERSON | BEAUMONT | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | NO DATA |  | 1924 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 150 | 130 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 200 | 0 | YES | 24 | 900 | 1 | 73 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH, DIVISION MANAGER | 4098393100 | LEAK WAS SPOTTED BY AERIAL PATROL AND PILOT REPORTED TO LUCAS STATION IMMEDIATELY. CLEAN-UP CREW WAS DISPATCHED QUICKLY AND WAS ON SITE IN ONE HOUR. RAILROAD COMMISION OF TEXAS (OIL AND GAS DIVISION) REPRESENTATIVE INSPECTED THE CLEAN-UP OPERATION. SPILL IS CONTAINED, SITE CLEAN-UP OPERATION IS EXPECTED TO BE COMPLETEBY END OF THE WEEK. PIPELINE IS TEMPORARILY CLAMPED AND PERMANENT REPAIRS WILL BE MADE BY INSTALLING FULL WRAP.
2017-09-29 08:50 | YES | NO | 19870022 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1986-12-26 | 1145 | CA | KERN |  | NO |  | NO | SEC 9 T11 NORTH R21 WEST |  | LINE PIPE | PIPE | ACETYLENE WELD BROKE | 1924 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 33120.6039 | 66817.636 | CRUDE OIL | 1 | 380 | 225 | NO | NO | 10 | 0.38 | 1560 | WELDED |  | 520 | 70 | YES | 8 | 650 | 7 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | R. B. KUPREWICZ VICE PRESIDENT OF OPERATIONS | 2134289017 | FAILED ACETYLENE WELD WAS LOCATED IN WELL COMPACTED SOIL UNDER A FARM ROAD. THESOIL UNDER THE ROAD SETTLED DIFFERENTLY FROM THE SURROUNDING IRRIGATED LAND.
2017-09-29 08:50 | YES | NO | 19870023 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1986-12-16 | 1600 | OK | KAY | PONCA | NO |  | NO | SE/4 OF THE SE/4 OF SECTION 4, T25N, R2E, KAY COUNTY, OKLAHOMA |  | TANK FARM | BOLTED FITTING |  | 1968 | OTHER | PIPE IN DRESSER COUPLING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 126 | 96 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. K. MCCAW VICE PRESIDENT - OPERATIONS | 9185883285 | APPROXIMATELY 7 HOURS AFTER STARTUP, A PIPE PULLED OUT OF THE 6 INCH DRESSER COUPLING ON THE 50 H.P. TANK PUMP DISCHARGE. IT WAS DISCOVERED IMMEDIATELY, THE OPERATION WAS SHUTDOWN AND THE VALVES CLOSED. A TOTAL OF 126 BARRELS OF LEADED GASOLINE WAS SPILLED, BUT IT WAS CONTAINED WITHIN TANK #608'S FIREWALL. A TOTAL OF 96 BARRELS WERE RECOVERED. THE NET LOSS WAS 30 BARRELS.
2017-09-29 08:50 | YES | NO | 19870024 |  | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1986-12-31 | 1620 | TX | RUNNELS | BALLINGER | NO |  | NO | APPROX. 5 MI. NW OF TOWN OF BALLINGER, TX. LEAK OCCURRED 3,042' E. OF STATE HWY. 158 SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 37852.1187 | 76363.0125 | CRUDE OIL | 3 | 110 | 55 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1060 | 850 | YES | 24 | 1273 | 1 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT K. (BOB) REED - REGULATORY COMPLIANCE SUPV. | 5127583571 | LEAK WAS CAUSED BY A SMALL OUTSIDE CORROSION PIT. PIPE MAY HAVE BEEN LEAKING FOR SOME TIME, AS LINE HAD NOT BEEN UNDER PRESSURE. IT IS POSSIBLE THAT LEAK BECAME NOTICEABLE ONLY WHEN PIPELINE WAS PRESSURED UP, RECENTLY.
2017-09-29 08:50 | YES | NO | 19870025 |  | 12624 | MOBIL OIL CORP | NO | 1986-12-04 | 655 | TX | HARDIN |  | NO |  | NO | APPROXIMATELY 8 MILES WEST OF SOUR LAKE, TEXAS, G&BN RAILROAD COMPANY SURVEY, SECTION 4, ABSTRACT 246. |  | LINE PIPE | PIPE |  | 1917 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 42583.6336 | 85908.3891 | NATURAL GAS LIQUID | 2 | 850 | 0 | NO | NO | 8 | 0.32 | 24000 | THREADED |  | 580 | 630 | YES | 24 | 890 | 5 | 77 | EXTERNAL | Null | YES | OTHER | LOCALIZED PITTING ON TOP | NO DATA |  | Null | NO DATA |  | Null | Null | B. H. BLACKMON, GENERAL MANAGER, BEAUMONT REFINERY | 4098393802 | THE MR2 - 8" TRANSFER PIPELINE FROM BEAUMONT TO HULL WAS SHUT DOWN WHILE A NORMAL BUTANE DELIVERY WAS BEING PUMPED TO MT. BELVIEU. LEAKAGE THROUGH A CLOSED BLOCK VALVE AND A CLOSED CONTROL VALVE INTO THE MR-2 PIPELINE CAUSED A GRADUAL PRESSURE RISE FROM 190 PSIG TO 630 PSIG. THE FAILURE OCCURRED AT 630 PSIG AT MP 185.2 IN AN AREA OF LOCALIZED CORROSION PITTING ON THE TOP OF THE PIPELINE. THE FAILURE WAS REPAIRED BY REPLACING THE SECTION OF PIPE WITH NEW LINE PIPE.
2017-09-29 08:50 | YES | NO | 19870028 |  | 3012 | D - S PIPELINE CORP | NO | 1986-12-11 | 1000 | TX | HASKELL |  | NO |  | NO | MATHEW DUNN A-120, BLOCK 64, HASKELL COUNTY, TEXAS |  | LINE PIPE | PIPE |  | 1927 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 13248.2416 | 26727.0544 | OIL AND GASOLINE | 3 | 1800 | 1080 | NO | NO | 10 | 0.37 | 25000 | THREADED |  | 480 | 178 | YES | 24 | 600 | 5 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PIPELINE PUBLIC AWARENESS | NO | NO | W. C. TURNER, GENERAL MANAGER | 8063783940 | AT APPROXIMATELY 10:00 A.M. ON DECEMBER 11, 1986, A HASKELL COUNTY EMPLOYEE WASOPERATING A MOTOR GRADER AND STRUCK OUR 10" CRUDE OIL PIPELINE. THE PIPELINE RUPTURED AND ALLOWED 1800 BARRELS OF BLENDED GAS OIL TO ESCAPE, OF WHICH, 1080 BARRELS WAS SUBSEQENTLY RECOVERED. THE PIPELINE WAS SHUT-DOWN FROM THE CONTROL CENTER IN DUMAS, TEXAS. CREWS WERE DISPATCHED TO CONTAIN THE SPILL AND REPAIR THE DAMAGE. PIPELINE WARNING SIGNS WERE IN PLACE AND VISIBLE ON BOTH SIDES OF THE COUNTY ROAD.
2017-09-29 08:50 | YES | NO | 19870030 |  | 19315 | TEXAS PIPELINE CO | NO | 1986-12-13 | 1252 | TX | MCLENNAN | WACO | NO |  | NO | ABOUT ONE (1) MILE NORTH OF FM NO. 2491, JUST EAST OF LOOP 340, JOHN HARMON SURVEY, A-20, MCCLENNAN COUNTY, NEAR THE CITY OF WACO, TEXAS |  | LINE PIPE | PIPE |  | 1948 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1419.4545 | 2863.613 | DIESEL FUEL | 1 | 2092 | 1341 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1170 | 500 | YES | 24 | 1000 | 1 | 48 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER |  | NO | NO | J. S. MINER, DISTRICT MANAGER | 7134322765 | THE TEXAS PIPELINE COMPANY WAS PUMPING DIESEL FROM ITS HEARNE STATION TO ITS WACO STATION ON SATURDAY, DEC. 13,1986. AT A LOCATION OF ABOUT 1 MILE NORTH OF FM 2491, JUST EAST OF LOOP 340, A BULLDOZER (OPERATED BY OTHERS) WAS GRADING A PRIVATE SERVICE ROAD. THE DRAINAGE DITCH ALONG THE SIDE OF THE ROAD WAS BEING DEEPENED, ABOUT 20 FEET FROM THE TEXAS PIPE LINE CO. PIPELINE MARKER AND 40 FEET FROM AN EXXON PIPE LINE CO. PIPELINE MARKER, WHEN THE LINE WAS STRUCK AND BROKEN BY THE BULLDOZER AT 12:52. THE TEXAS PIPELINE COMPANY HAD BEEN OPERATING AT ABOUT 500 PSIG AT THAT LOCATION. BECAUSE OF THE LINE BREAK, THE SUCTION PRESSURE AT THE DOWNSTREAM WACO BOOSTER PUMP DROPPED AND THE ENTIRE LINE WENT DOWN AT ABOUT 12:55P.M. BY THE TIME THE OPERATOR OF THE BULLDOZER GOT TO A TELEPHONE TO REPORT THEMATTER AT 1:30 P.M., PERSONNEL OF THE TEXAS PIPE LINE CO. HAD BEEN DISPATCHED TOTHE WACO STATION VALVE TO CLOSE IT DOWN, THUS PREVENTING DIESEL FROM BACKING DOWN THE PIPELINE AND OUT THE BREAK. ONCE THE MAJORITY OF DIESEL OIL HAD BEEN CONTAINED IN A DRY DRAW LEADING INTO A GRAVEL PIT BY CONSTRUCTING A LEVEE OR DAM, VACUUM TRUCKS WERE DISPATCHED TO THE SITE TO BEGIN PICK-UP OPERATIONS. THE PIPELINE WAS EXCAVATED, THE DAMAGED SECTION WAS REMOVED AND A NEW JOINT OF PIPE WAS INSTALLED WITH TWO "WELD PLUS ENDS". THE LINE WAS PUT BACK INTO SERVICE AND CLEANUPOPERATIONS WERE SUSPENDED BECAUSE OF DARKNESS. ON SUNDAY, DEC. 14, 1986, VACUUM
2017-09-29 08:50 | YES | NO | 19870031 |  | 4906 | EXXON PIPELINE CO | NO | 1986-12-26 | 400 | TX | PECOS |  | NO |  | NO | LEAK OCCURRED IN EXXON PIPELINE COMPANY'S YATES PECOS STATION ON THE 12" DISCHARGE LINE BETWEEN THE PUMP UNIT AND SCRAPER TRAP |  | LINE PIPE | PIPE |  | 1972 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 3406.6907 | 6872.6711 | CRUDE OIL | 1 | 320 | 285 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 965 | 800 | YES | 24 | 1800 | 2 | 72 | INTERNAL | Null | YES | OTHER |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. P. MURRAY, OPERATONS MANAGER | 7136565956 | AT APPROXIMATILY 0400 HOURS ON DECEMBER 26, 1986, EPC'S DISPATCHER NOTIFIED FIELD PERSONNEL THAT THE PUMP UNIT AT YATES PECOS STATION HAD LOCKED OUT. AN EPC EMPLOYEE WAS DISPATCHED TO THE REMOTE SITE AND ARRIVED AT 1000 HOURS. UPON ARRIVAL,HE DISCOVERED AND REPORTED A CRUDE OIL LEAK. A REPAIR AND CLEAN-UP CREW WERE DISPATCHED TO THE SITE AND BEGAN REPAIR OPERATIONS AT 1230 HOURS. IT WAS DETERMINED THAT THE LEAK WAS CAUSED BY INTERNAL CORROSION. THE BAD SECTION OF PIPE WAS REPLACED WITH NEW PIPE. OPERATIONS WERE RESUMED AT 1830 HOURS, DECEMBER 27, 1986. CLEAN-UP OPERATIONS WERE COMPLETED ON DECEMBER 29, 2986.
2017-09-29 08:50 | YES | NO | 19870032 |  | 4906 | EXXON PIPELINE CO | NO | 1986-12-24 | 2300 | TX | ATASCOSA |  | NO |  | NO | LEAK OCCURRED AT STATION SUCTION PIPING CHECK VALVE GASKET AT IMOGENE STATION. IMOGENE STATION IS LOCATED APPROXIMATELY 4 MILES SOUTH-SOUTHEAST OF PLEASANTON, T |  | PUMPING STATION | OTHER | GASKET ON 10" WAFER VALVE | 1985 | OTHER | INSUFFICIENT SURFACE AREA | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 63300 | 59900.9779 | 120844.4673 | CRUDE OIL | 1 | 1300 | 1200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT APPROXIMATELY 11:00 P.M. ON 12/24/86 A GASKET ON A 10" WAFER CHECK VALVE GAVEWAY ON THE SUCTION PIPING AT EXXON PIPELINE CO.'S (EPC) IMOGENE STATION. THE LEAK WAS REPORTED TO EPC'S DISPATCHER IN HOUSTON AT 11:00 A.M. ON 12/25/86 BY EXXON COMPANY, U.S.A. PERSONNEL. THE LEAK WAS STOPPED AT 3:00 P.M. ON 12/25/86/ BY IPC'S GAUGER BY CLOSING THE INCOMING MAINLINE BLOCK VALVE, (NOTE: THE STATION WAS NOT RUNNING WHEN LEAK OCCURRED.) OIL GRAVITATED TO A "WET WEATHER" CREEK (METATTE CREEK) WHICH IS APPROXIMATELY 300' FROM THE LEAK SITE. THE OUL FLOWED APPROXIMATELY 2 MILES DOWN THE CREEK BED. OIL WAS CONTAINED BY PUTTING OUT BOOMS AND BUILDING A FLUME TO RECOVER ALL AVAILABLE OIL. CLEAN UP ACTIVITIES BEGAN 12/26/86/AT 8:00 A.M. BY USING SKIMMERS, VACUUM TRUCKS AND BULLDOZERS. BACKHOES WERE USED FOR TURNING THE SOIL. CLEAN UP ACTIVITIES WERE COMPLETED AT 3:00 P.M. ON 1/7/87PERMANENT REPAIRS WERE MADE BY REMOVING THE WAFER CHECK VALVE AND MAKING A FLANGE-TO-FLANGE CONNECTION. IT APPEARS THAT THE CHECK VALVE DESIGN DOES NOT PROVIDESUFFICIENT SURFACE AREA FOR APPROPRIATE SEALING OF THE GASKETS. THE STATION WASRESTORED TO SERVICE AT 8:00 P.M. ON 12/26/86.
2017-09-29 08:50 | YES | NO | 19870033 |  | 26141 | SHELL OIL CO | NO | 1986-12-18 | 930 | CA | KERN | BAKERSFIELD | NO |  | NO | ROUND MOUNTAIN 6-INCH LATERAL, SECTION 34, T-28-S, R-28-E, MDB&M SURVEY 1.5 MILES EAST OF INTERSECTION OF ROUND MOUNTAIN ROAD |  | LINE PIPE | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5250 | 4968.0906 | 10022.6454 | CRUDE OIL | 1 | 120 | 115 | NO | NO | 6 | 0.3 | 42000 | WELDED |  | 1440 | 0 | YES | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | M. J. EICHLER, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262 | PIELINE WAS HIT BY EQUIPMENT BEING USED BY OUTSIDE COMPANY
2017-09-29 08:50 | YES | YES | 19870034 |  | 6856 | GULF CENTRAL PIPELINE CO | YES | 1987-02-04 | 1930 | MO |  | LOUISIANA | NO |  | NO | IN IRECO, INC. AMMONIA NITRATE PLANT LOCATED APPROXIMATELY ONE MILE SE OF LOUISIANA, MO. |  | TANK FARM | VALVE |  | 1986 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 3 | 2 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DALE D. HOLDER | 9184910300 | AT APPROXIMATELY 7:30 P.M. ON FEBRUARY 4, 1987, A TWO MINUTE POWER FAILURE OCCURRED IN IRECO, INC'S LOUISIANA, MISSOURI PLANT CAUSING A BREAKER TO TRIP AND A CONTROL VALVE TO CLOSE. THIS CAUSED PRESSURE TO BUILD UP ON GULF CENTRAL'S METER SKID WHICH SHOULD HAVE TRIPPED A PRESSURE SWITCH SET AT 275#. HOWEVER, THE PRESSURE SWITCH FAILED, CAUSING PRESSURE TO BUILD UP ON IRECO'S PIPING WHICH ACTIVATEDTHEIR RELIEF VALVE SET AT 300#, ALLOWING PRODUCT TO ESCAPE TO THE ATMOSPHERE FOR APPROXIMATELY TWO MINUTES OR UNTIL THEIR OPERATOR RESET THE BREAKER AND THE SYSTEM WAS THEN PLACED BACK IN OPERATION.
2017-09-29 08:50 | YES | NO | 19870035 |  | 4906 | EXXON PIPELINE CO | NO | 1987-02-02 | 1100 | TX | REAGAN |  | NO |  | NO | LEAK OCCURRED ON EXXON PIPELINE COMPANY'S YATES PECOS TO KEMPER #1 - 8" TRUNKLINE APPROXIMATE STATION NUMBER 1650 + 46(SEE ATTACHED SKETCH |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2314.1467 | 4668.5686 | CRUDE OIL | 1 | 1700 | 1630 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 741 | 50 | YES | 24 | 1050 | 1 | 74 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. P. MURRAY | 7136565956 | AT APPROXIMATELY 1400 HOURS ON FEBRUARY 2, 1987 AN AIR PATROL FOR THE PERMIAN CORPORATION REPORTED AN OIL LEAK ON EXXON PIPELINE COMPANY'S YATES PECOS TO KEMPER TRUNKLINE SYSTEM. AN EXXON PIPELINE COMPANY REPAIR CREW WAS DISPATCHED TO THE LEAK SITE AND BEGAN REPAIR OPERATIONS AT 1500 HOURS. IT WAS DETERMINED THE LEAK WAS CAUSED BY EXTERNAL CORROSION. THE BAD SECTION OF PIPE WAS REPLACED WITH NEW PIPE AND OPERATIONS WERE RESUMED AT 1530 HOURS, FEBRUARY 4, 1987. CLEAN-UP OPERATIONS WERE COMPLETED ON FEBRUARY 4, 1987.
2017-09-29 08:50 | YES | NO | 19870036 |  | 9175 | JAYHAWK PIPELINE CORP | YES | 1987-01-23 | 1140 | KS | OSBORNE |  | NO |  | NO | NE/4 SEC. 25, TWP. 10S, R14W APPROXIMATELY 2 3/4 MILES NORTH OF PARADISE, KANSAS |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13884.88 | 28011.4113 | CRUDE OIL | 1 | 1600 | 1200 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1300 | 1160 | YES | 24 | 1740 | 9 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | WARNING SIGNS AT RR XINGS | NO | NO | DENNIS E. SMITH | 3162679669 | AT 1140, JANUARY 23,1887, 3 UNITS AT LATON STATION DELIVERING OIL TO A STORAGE TANK AT CHASE STATION THROUGH 10" LINE SHUT DOWN. THE JAYHAWK OPERATOR AT CHASE CONTACTED JAYHAWK EMPLOYEE AT LATON WHO WAS PROVING A ACT METER AT THIS LOCATION.THE UNITS FAULTS INDICATED LOW SUCTION ON THE SHUTDOWN. THE BOOSTER PUMP AT THISSTATION IS THROTTLED BACK DURING THIS ACT METER PROVING TO ALLOW A FULL FLOW RATE DELIVERY FROM ACT INTO THE PUMP SUCTION MANIFOLD. AT TIMES IN THE PAST, THIS THROTTLING OPERATING HAS RESTRICTED TOO MUCH OIL TO PUMP SUCTION AND SHUTDOWN THESTATION. ATTRIBUTING THIS SHUTDOWN TO THE BOOSTER PUMP THROTTLING AND THE ACT METER PROVING, THE 3 UNITS WERE STARTED BACK UP AND RAN FOR 30 MINUTES. THE LINE PRESSURE DID NOT RESPOND NORMALLY AND THE STATION WAS SHUT DOWN AT 1250. A FURTHER CHECK AN THE SYSTEM WAS MADE BY RUNNING ONE UNIT FOR 45 MINUTES AT LATON WITHBLOCK VALVE CLOSED AT CHASE TO REPACK THE LINE. UNIT WAS SHUT DOWN AT 1350 AND LINE PRESSURE DID NOT HOLD. AERIAL PATROL PILOT WAS CALLED OUT AND LOCATED LEAK AT APPROXIMATELY 1400. PERSONNEL AND EQUIPMENT WERE DISPATCHED TO THE LEAK LOCATION. EMPLOYEE AT LATON ARRIVED AT THE SITE AT 1510 AND REPORTED CONDITIONS AT THELEAK LOCATION . LEAK WAS IN PASTURE LAND AND ESCAPED OIL HAD RUN DOWN HILLSIDE AND TRAVELED ON FROZEN GROUND APPROXIMATELY 1/2 MILES IN NARROW DRY GULLY. VACUUM TRUCKS BEGAN RECOVERING SURFACE OIL THAT EVENING. EXCAVATION AND REPAIR OF LEAK
2017-09-29 08:50 | YES | NO | 19870037 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-02-12 | 2330 | TX | FREESTONE | WORTHAM | NO |  | NO | SEE ATTACHED |  | TANK FARM | NO DATA | PROVER LOOP FITTING | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 300 | 275 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH, DIVISION MANAGER | 4098393100 | LOOP LINES WERE RECONNECTED AFTER WORKING ON THE MASTER METER PROVER. DRAIN LINE TO SUMP PIT WAS APPARENTLY LEFT OPEN. PRODUCT WAS PICKED UP BY VACUUM TRUCK ANDHAULED TO LUFKIN SLOP TANK #1592 AND LATER REINJECTED INTO THE PIPELINE..
2017-09-29 08:50 | YES | NO | 19870038 |  | 12628 | MOBIL PIPELINE CO | YES | 1987-01-08 | 1430 | KS | BUTLER | BENTON | NO |  | NO | SW 1/4, SEC. 33, TWP. 25 SOUTH, RANGE 3 EAST |  | LINE PIPE | PIPE | 6 | 1953 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1650 | 1527.3368 | 3081.2552 | CRUDE OIL | 1 | 60 | 20 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 720 | 100 | YES | 2 | 830 | 1 | 69 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | WHILE CUTTING BRUSH, COMPANY PERSONNEL DISCOVERED A PIN HOLE IN A GIRTH WELD OFTHE 10" PIPELINE. INVESTIGATION REVEALED THE LEAK WAS CAUSED BY INTERNAL CORROSION. THE PIN HOLE WAS REPAIRED BY WELDING A WELD SLEEVE TO THE PIPELINE, ENCASING THE WELD WITH THE PIN HOLE.
2017-09-29 08:50 | YES | NO | 19870039 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1987-02-03 | 300 | OK | CARTER |  | NO |  | NO | 1 1/4 MILES SOUTH OF POOLEVILLE, 1 MILE WEST, 1 MILE SOUTH INTO SITE |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 925.6587 | 1867.4274 | CRUDE OIL |  | 150 | 148 | NO | NO | 4 | 0.75 | 0 | NO DATA |  | 400 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | YES | YES |  | 4058674822 | MOBIL OIL COMPANY WAS PLUGGING A WELL AND HAD A DOZER OUT FROM BRADY CONSTRUCTION, WHICH WAS PULLING A TRUCK AROUND THE LOCATION. AT SUCH TIME THE TRUCK RAN OVE
2017-09-29 08:50 | NO | NO | 19870040 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1987-01-06 | 930 | CA | KERN |  | NO |  | NO | LINE 50 WEST OF GATE VALVE #133 AT NORTH COLES LEVEE PUMP STATION (22 MILES SW OF BAKERSFIELD ON HWY119 |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 5553.952 | 11204.5645 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 8 | 0.25 | 2180 | WELDED |  | 724 | 400 | YES | 8 | 906 | 7 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.B. KUPREWICZ | 2134289017 | LEAK CAUSED BY EXTERNAL CORROSION ON LINE 50
2017-09-29 08:50 | NO | NO | 19870041 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1987-01-08 | 125 | CA | LOS ANGELES | LAKEWOOD | NO |  | NO | 5107 DEE BOYER ROAD, LAKEWOOD, CALIFORNIA (LINE 17) |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 27769.76 | 56022.8226 | CRUDE OIL | 1 | 7 | 5 | NO | NO | 10 | 0.25 | 1750 | WELDED |  | 720 | 520 | YES | 4 | 900 | 1 | 85 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | R.B. KUPREWICZ | 2134289017 | LEAK CAUSED BY INTERNAL CORROSION ON LINE 17
2017-09-29 08:50 | YES | NO | 19870042 |  | 4906 | EXXON PIPELINE CO | YES | 1987-02-23 | 2000 | TX | CRANE |  | NO |  | NO | LEAK OCCURRED IN CRANE STATION, LOCATED 3 MILES NORTH OF THE CITY OF CRANE, TX ON EAST SIDE OF HWY. 385. (SEE ATTACHED MAP) |  | TANK FARM | TANK |  | 1927 | OTHER | ROOF DRAIN HOSE BROKE APA | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3690 | 3415.6805 | 6890.8072 | CRUDE OIL | 1 | 125 | 85 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT 10:00 HOURS ON FEBRUARY 24, 1987, AN EXXON PIPELINE EMPLOYEE DROVE BY CRANE STATION AND DISCOVERED OIL WITHIN TANK NO. 485'S FIREWALL. AFTER INVESTIGATING, HE NOTED THE OIL COMING FROM THE TANK ROOF DRAIN VALVE WHICH HE CLOSED. THE LEAKWAS CAUSED BY THE INTERNAL ROOF DRAIN HOSE BREAKING APART. EPC PERSONNEL, VACUUM TRUCKS AND A BACKHOE WERE DISPATCHED TO CRANE STATION AND BEGAN CLEAN-UP OPERATIONS AT 11:00 HOURS. CLEAN-UP WAS COMPLETED ON FEBRUARY 24,1987, AT 16:00 HOURS.THE TANK HOSE WAS PERMANENTLY REPAIRED ON FEBRUARY 27, 1987, BY INSTALLING A NEW HOSE
2017-09-29 08:50 | YES | NO | 19870043 |  | 443 | AMOCO PIPELINE CO | NO | 1987-01-01 | 600 | TX | HARRIS | HOUSTON | NO |  | NO | SURVEY-JUAN SUTTON A-751 LOT 24, 9100 CURLEE, HOUSTON, TX |  | NO DATA | VALVE | SUMP | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 500 | 495 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | NO DATA | DRAIN LINE NOT CLOSED | Null | NO DATA |  | Null | Null | MICHAEL P. CLANG | 7133322476 | IN THE PROCESS OF CLEANING OUT A STRAINER THE DRAIN LINE VALVE INADVERTENTLY REMAINED OPEN CAUSING THE SUMP TO RUN OVER DURING THE NIGHT. THE SUMP PUMP WAS UNABLE TO KEEP UP WITH THE INCOMING FLOW RATE.
2017-09-29 08:50 | YES | NO | 19870044 |  | 26141 | SHELL OIL CO | NO | 1987-02-01 | 600 | CA | KERN | WASCO | NO |  | NO | ONE-HALF MILE NORTH OF HWY 46, SECTION 2, T-27-S, R-22-E, MDB SURVEY |  | LINE PIPE | VALVE |  | 1970 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 12033.5627 | 24276.5565 | CRUDE OIL | 1 | 345 | 325 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 747 | YES | 24 | 1600 | 1 | 70 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | OTHER | UNDERGROUND SERVICE ALERT | Null | Null | J.W. HOLDEN, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870045 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-02-03 | 1100 | TX | UPTON | MCCAMEY | NO |  | NO | BARNSLEY-MCCAMEY NO. 2-6-INCH SW 1/4, SW 1/4, SECTION 11, BLOCK R, TCRR SURVEY 2.75 MILES NORTHWEST OF MCCAMEY |  | LINE PIPE | PIPE |  | 1920 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2776.976 | 5602.2823 | CRUDE OIL | 1 | 825 | 750 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 850 | 450 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870046 |  | 18273 | SHELL PIPE LINE CORP | YES | 1986-12-20 | 1100 | LA |  |  | YES | X-2792608, Y-167094 | NO | SOUTH PASS BLOCK 65 8-INCH PIPELINE (500 YARDS SOUTHEAST OF BLOCK 65A) IN A DEPTH OF 300 FEET OF WATER OFF THE COAST OF LA., GULF OF MEXICO LONGITUDE - W88 51'2 |  | LINE PIPE | PIPE |  | 1969 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1108000 | 1048503.6885 | 2115255.4469 | CRUDE OIL | 1 | 90 | 0 | NO | NO | 8 | 0.38 | 56000 | WELDED |  | 1440 | 300 | YES | 24 | 2400 | 1 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN | 7132416262 | ON DECEMBER 30, 1987, A LEAK WAS DISCOVERED ON SHELL OIL COMPANY'S 8-INCH CRUDEOIL GATHERING PIPELINE BETWEEN SOUTH PASS BLOCK 65 AND SOUTH PASS BLOCK 62, LOCATED ABOUT 15 MILES SOUTHEAST OF THE MOUTH OF THE MISSISSIPPI RIVER. THE LINE WAS SHUT DOWN AND THE INCIDENT WAS IMMEDIATELY REPORTED BY SHELL OFFSHORE INC. TO THE NATIONAL RESPONSE CENTER, THE MINERALS MANAGEMENT SERVICE AND THE UNITED STATES COAST GUARD AND BY SHELL PIPE LINE CORPORATION TO THE STATE OF LOUISIANA. THE OBSERVED OIL SPILL WAS ESTIMATED AND REPORTED AT 80 TO 100 BARRELS WHICH WAS MOVING OUT TO SEA. SHELL OFFSHORE INC. MOBILIZED A CLEAN GULF ASSOCIATES FAST RESPONSE UNIT AND RECOVERED 50 BARRELS OF EMULSION(APPROXIMATELY 45 BARRELS OF WATER AND 5 BARRELS OF OIL). NO INDICATION OF OIL WAS OBSERVED FROM THE SPILL AFTER DECEMBER 31, 1986 FROM HELICOPTER SURVEILLANCE FLIGHTS. THE LINE HAS BEEN REPAIRED, AND A DAMAGED PIECE OF PIPE WHICH WAS CUT OUT OF THE LINE IS BEING EXAMINED IN AN EFFORT TO DETERMINE THE CAUSE OF THE LEAK. THE INFORMATION FROM LABORATORYLEAK TESTS ON THE PIECE OF PIPE REMOVED FROM THE PIPELINE AND OUR REVIEW OF OILMEASUREMENT RECORDS INDICATE THAT A THEORETICALLY LARGER AMOUNT OF OIL WAS SPILLED; PERHAPS AS MUCH AS 23,000 TO 29,000 BARRELS BEGINNING AS EARLY AS DECEMBER 27, 1986. HOWEVER, THE CONSIDERABLE BOAT AND HELICOPTER TRAFFIC IN THE AREA DURING THIS PERIOD REPORTED NO VISUAL OBSERVATION OF A SPILL IN AN AMOUNT LARGER THAN
2017-09-29 08:50 | YES | NO | 19870047 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-02-14 | 700 | NM | LEA | MONUMENT | NO |  | NO | SE 1/4, NW 1/4, SECTION 28, T-20-S, R-37-E, 4.5 MILES SOUTHWEST OF MONUMENT LEA STATION |  | PUMPING STATION | PIPE |  | 1936 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3650 | 3378.6541 | 6816.1101 | CRUDE OIL | 1 | 695 | 595 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 600 | 325 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262 | INTERNAL CORROSION IN STUB OF 6-INCH DISCHARGE MANIFOLD
2017-09-29 08:50 | YES | NO | 19870048 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-02-08 | 701 | LA | PLAQUEMINES | PILOTTOWN | NO |  | NO | SECTION 27, T-21-S, R-19-E, PILOTTOWN STATION, LATITUDE 29_11'09", LONGITUDE 80_15'09" |  | PUMPING STATION | LONGITUDINAL WELD | ONE-HALF INCH NIPPLE | 1958 | OTHER | VIBRATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 62400 | 57761.1009 | 116527.4711 | CRUDE OIL | 1 | 110 | 110 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870049 |  | 26085 | SCURLOCK OIL CO | Null | 1987-02-01 | 1730 | TX | SMITH |  | NO |  | NO | 5 MILES EAST OF THE INTERSECTION OF HWY 31 AND 850. ON 850 AND 3.4 MILE NORTH OF 850. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2776.976 | 5602.2823 | CRUDE OIL |  | 100 | 50 | NO | NO | 8 | 0.25 | 24000 | WELDED |  | 720 | 100 | NO | 0 | 0 | 1 | 79 | EXTERNAL | Null | YES | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | JAMES H. MCBETH, DISTRICT SUPERVISOR | 2149845252
2017-09-29 08:50 | YES | NO | 19870050 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-01-22 | 1442 | TX | NUECES |  | NO |  | NO | APPROXIMATELY 5 MILES SOUTHWEST OF ROBSTOWN NEAR FARM TO MARKET ROAD 1694 IN THE GREGORIO FARIAS SURVEY, ABSTRACT 6. |  | LINE PIPE | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1600 | 1481.0539 | 2987.8839 | GASOLINE | 3 | 71 | 0 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 806 | 150 | YES | 24 | 1006 | 1 | 73 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D L DENNARD, V P OPER | 2146582226 | TRUAL GASOLINE SPILL. A TEMPORARY LEAK CLAMP WAS INSTALLED TO STOP THE LEAK, THE
2017-09-29 08:50 | YES | NO | 19870051 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-02-28 | 1000 | TX | PALO PINTO |  | NO |  | NO | SEE ATTACHED REPORT |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 400 | 100 | NO | NO | 8 | 0.37 | 0 | WELDED |  | 900 | 600 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH, DIVISION MANAGER | 4098393100 | AT APPROXIMATELY 6 P.M. FRIDAY, FEBRUARY 27, 1987, CHEVRON PIPE LINE COMPANY SHUT DOWN THE SECTION OF ITS PIPELINE THAT DELIVERS MOTOR GASOLINE TO EASTLAND, LOCATED APPROXIMATELY 100 MILES WEST OF FORT WORTH. THE COMPANY'S METERING SYSTEM HAD SHOWN A SHORTAGE OF PRODUCT DELIVERY INDICATING A PROBLEM, WHICH LATER WAS DISCOVERED TO BE A LEAK. INSPECTION OF THE PIPELINE BEGAN IMMEDIATELY, BUT WAS HINDERED BY HEAVY RAIN AND RESULTING HIGH WATER. RESPONSE CREWS WERE ALERTED. SPILLCONTAINMENT EQUIPMENT WAS DEPLOYED, AND APPROPRIATE GOVERNMENTAL AGENCIES NOTIFIED. AT DAYLIGHT SATURDAY MORNING, CREWS CONTINUED INSPECTING THE PIPELINE BY WALKING THE RIGHT-OF-WAY AND BY AERIAL SURVEILLANCE. AT 10 A.M. SATURDAY, FEBRUARY28, 1987, THE LEAK WAS CONFIRMED AND LOCATED SOME 20 MILES SOUTHWEST OF MINERALWELLS, TEXAS, 35 MILES WEST OF FORT WORTH. THE LEAK WAS STOPPED AND VISIBLE SURFACE GASOLINE WAS CONTAINED AND RECOVERED USING VACUUM TRUCKS, IT IS ESTIMATED AT LEAST 400 BARRELS OF LEADED GASOLINE WAS SPILLED. THE PIPELINE LEAK OCCURRED IN A FLOODED CREEK THAT FLOWED INTO OTHER TRIBUTARIES. CLEAN UP EFFORTS WERE INITIATED USING THE SPILL CONTAINMENT EQUIPMENT AND VACUUM TRUCKS. AS LATE AS 9 P.M.SATURDAY, INSPECTIONS BY CHEVRON WITH THE EPA AND CITY WATER DEPARTMENT SHOWED NO GASOLINE BEYOND THE SPILL LOCATION. AT 6 A.M. SUNDAY, MARCH 1, 1987, THE WATERTREATMENT PLANT OF THE CITY OF MINERAL WELLS DETECTED THE ODOR OF GASOLINE. AROUND 10 A.M., THREE INDIVIDUALS IN ONE OF THE OUTLYING COMMUNITIES REPORTED A GASOLINE ODOR IN THEIR WATER. AS A PRECAUTIONARY MEASURE, LOCAL CITIZENS WERE ADVISED TO NOT DRINK THE WATER. THIS INFORMATION WAS COMMUNICATED BY LOCAL TELEVISIONAND RADIO STATIONS. CHEVRON ARRANGED THE DELIVERY OF BOTTLED WATER TO MINERAL WEELLS AND ASSISTED THE CITY IN DISPENSING IT TO AREA CITIZENS. SPECIAL ARRANGEMENTS WERE MADE FOR DELIVERIES TO NURSING HOMES AND TO PEOPLE CONFINED TO THEIR HOMES. WATER WAS ALSO SET ASIDE FOR THE DELIVERY TO LOCAL SCHOOL DISTRICTS. CHEVRON WILL CONTINUE TO PROVIDE BOTTLED WATER UNTIL CHEVRON AND THE CITY OF MINERAL WELLS WITH THE STATE DEPARTMENT OF HEALTH ARE ASSURED THE WATER SUPPLY IS SAFE TODRINK. CHEVRON SENT WATER SAMPLES COLLECTED SUNDAY TO A FORT WORTH LABORATORY FOR CHROMATOGRAPHIC ANALYSIS. THE RESULTS OF THESE ANALYSES SHOWED LESS THAN 1 PPM GASOLINE. ADDITIONAL TESTING WILL BE CONDUCTED TO CONFIRM THESE RESULTS. CHEVRON CONTINUES AROUND-THE-CLOCK MONITORING FOR THE PRESENCE OF GASOLINE AT THE CITY'S WATER TREATMENT PLANT AND THE LEAK SITE. CHEVRON IS ALSO PROVIDING PERSONNELWITH RADIO-EQUIPPED TRUCKS TO ASSIST THE MINERAL WELLS WATER DEPARTMENT. CHEVRON IS ALSO CONTINUING TO WORK WITH THE CITY IN A COOPERATIVE EFFORT TO RESOLVE THE PROBLEM. THE CITY OF MINERAL WELLS LAST NIGHT, MARCH 2, 1987, STARTED AN EXTENSIVE TREATMENT PROCESS ON ADVICE OF THEIR NEWLY HIRED CONSULTANT, AID CONSULTING ENGINEERS, INC. OF DALLAS, TEXAS. THE PROCESS WILL ESTABLISH A BASE LINE EVALUATION OF THE TOTAL WATER SYSTEM BY COMPREHENSIVE SAMPLING. ACTIVATED CARBON(CHARCOAL) WAS ADDED AT THE WET WELL WHICH TAKES SUCTION FROM PALO PINTO CREEK, THE MAJOR SOURCE OF THE CITY'S WATER SUPPLY. CHARCOAL WAS ALSO ADDED AT THE WEIRS IN THE MAIN WATER TREATMENT PLANT. THE CHARCOAL REMOVES IMPURITIES FROM THE WATER, AROMATICS IN PARTICULAR. THE CONSULTANT ALSO ADVISED THAT THE WATER SYSTEM BE FLUSHED, AFTER THE CHARCOAL IS IN PLACE, BY OPENING FIRE HYDRANDS AT THE MOST DISTANT POINTS FROM THE MAIN TREATMENT PLANT. PROGRESS WILL BE MEASURED BY ADDITIONAL SAMPLING. AT MIDNIGHT SUNDAY, MARCH 2, 1987, THE CITY PUT INTO OPERATION ITS AUXILIARY WATER TREATMENT FACILITY WHICH UTILIZES WATER FROM MINERAL WELLS LAKE NEARBY. THIS SYSTEM, HOWEVER, IS ONLY CAPABLE OF SUPPLYING ABOUT ONE-THIRD OF THETOTAL CITY WATER USAGE. TOLERANCE LIMITS OBTAINED BY THE CITY FROM THE TEXAS DEP
2017-09-29 08:50 | YES | NO | 19870052 |  | 4906 | EXXON PIPELINE CO | NO | 1987-02-13 | 1120 | TX | MONTGOMERY |  | NO |  | NO | LEAK OCCURRED AT STATION 237+02 (SOUTH SIDE OF RIVER ROAD) ABOUT ONE MILE SOUTHWEST OF CONROE STATION ON THE CONROE TO SATSUMA NO. 1-8 INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1932 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 38000 | 35175.0294 | 70962.242 | CRUDE OIL | 1 | 2200 | 2188 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 700 | 125 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER |  | NO | NO | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | INCH BY 3 INCH HOLE IN OUR PIPELINE. THE CONTRACTOR HAD BEEN CLEANING OUT A DRAMORE DAMS/BERMS TO CONTAIN THE OIL. CONTRACTED EQUIPMENT AND VACUUM TRUCKS ARRIVED AT THE SITE AT 13OO HOURS. THE LINE WAS PERMANENTLY REPAIRED BY REPLACING A 6-FOOT SECTION OF PIPING. THE LINE WAS RESTORED TO SERVICE AT 0340 HOURS ON FEBRUARY 14, 1987. CLEAN-UP OPERATIONS WERE COMPLETED FEBRUARY 19, 1987.
2017-09-29 08:50 | YES | NO | 19870053 |  | 10012 | KANEB PIPELINE CO | YES | 1987-02-06 | 1815 | KS | BUTLER |  | NO |  | NO | EL DORADO, KANSAS 1624 SUNSET ROAD |  | LINE PIPE | TANK |  | 1954 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 466 | 437 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MACK E. BROWN, VICE PRESIDENT OF ENGINEERING & OPERATIONS | 3162621408 | STATION OPERATOR FAILED TO CORRECTLY CALCULATE FILL TIME OF TANK AND THE TANK OVERFLOWED.
2017-09-29 08:50 | YES | NO | 19870054 |  | 443 | AMOCO PIPELINE CO | YES | 1987-02-02 | 1000 | MO | CASS | FREEMAN | NO |  | NO | NW/4, SECTION 8, T 44N, R 32W CASS COUNTY, MISSOURI (SKETCH ATTACHED) |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 69424.4001 | 140057.0566 | GASOLINE | 1 | 2895 | 1420 | NO | NO | 16 | 0.25 | 42000 | WELDED |  | 788 | 500 | YES | 24 | 1185 | 5 | 72 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AMOCO PUBLIC EDUCATION | NO | NO | MITCHELL B. WEISS, AREA MANAGER, OPERATIONS | 8163311673 | ON FEBRUARY 2, 1987, AT 0900 HRS. CST A SCRAPER WAS LAUNCHED FROM FREEMAN STATION WHICH IS APPROXIMATELY 1.4 MILES SOUTH OF THE LEAK SITE. PRIOR TO THIS, THE LAST SCRAPER WAS RUN ON FEBRUARY 4, 1986. AT ABOUT THE TIME THE SCRAPER REACHED WHAT TURNED OUT TO BE THE LEAK SITE, OUR INSTRUMENTATION INDICATED A DROP IN PRESSURE AT SUGAR CREEK TERMINAL WHICH IS 34 MILES DOWNSTREAM (NORTH) OF THE LEAK SITE. SIMULTANEOUSLY, AN INCREASE IN FLOW RATE OCCURRED AT MAYVIEW STATION , THE NEAREST UPSTREAM PUMPING STATION. THE OPERATOR ON DUTY IMMEDIATELY BEGAN SHUTTINGDOWN THE LINE DOWN AT 1014 HRS. CST. ABOUT 5 MINUTES LATER A CALL WAS RECEIVED FROM MR. GARY RICHARDSON INDICATING A LEAK WAS OCCURRING ON HIS PROPERTY. AFTER OUR INITIAL RESPONSE, SUBSEQUENT INSPECTION OF THE BREAK SHOWED A TELEPHONE CABLE PARALLEL TO AND DIRECTLY ABOVE OUR PIPELINE. CONCLUSIVE SIGNS OF EXTERNAL MECHANICAL DAMAGE WERE APPARENT ON THE PIPELINE. FURTHER INVESTIGATION REVEALED THATIN JULY OF 1986 A CONTRACTOR FOR THE LOCAL TELEPHONE COMPANY PLOWED IN A DIRECTBURIAL CABLE TO PROVIDE SERVICE TO THE RICHARDSON HOME WHICH WAS THEN UNDER CONSTRUCTION. THE SPLIT WHICH WAS 21 INCHES LONG AND RAN DIRECTLY ALONG A 10 FT. TRACK OF OVERLAPPING DENTS OR PEEN MARKS ON THE PIPELINE. A CROSS SECTIONAL VIEW THROUGH THE SPLIT SHOWED A FLATTENING OF THE LINE. OUR RECORDS INDICATE THAT WE DID NOT RECEIVE A LINE LOCATION REQUEST FROM EITHER THE TELEPHONE COMPANY OR THEIR
2017-09-29 08:50 | YES | NO | 19870055 |  | 809 | ARCO PIPE LINE CO | YES | 1987-02-14 | 1600 | IL | LIVINGSTON |  | NO |  | NO | TANK FARM LOCATED AT COMPANY'S FLANAGAN STATION, LIVINGSTON COUNTY, NEAR PONTIAC, ILLINOIS |  | TANK FARM | OTHER | LEAK IN ROOF DRAIN | 1980 | OTHER | GASKET FAILURE IN SWIVEL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 550 | 535 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | N.R. BENNETT, MANAGER-NORTHERN AREA OPERATIONS | 3163311300 | ROOF DRAIN ON TANK #1404 DEVELOPED A LEAK CAUSING AN OIL SPILL IN THE TANK DIKEOF APPROXIMATELY 550 BBLS. 535 BBLS WERE RECOVERED
2017-09-29 08:50 | YES | NO | 19870056 |  | 2731 | CHEVRON PIPELINE CO | Null | 1987-02-21 | 430 | TX | NAVARRO | WORTHAM | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 18513.1734 | 37348.5484 | GASOLINE | 3 | 400 | 50 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 750 | 600 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH | 4098393100
2017-09-29 08:50 | YES | NO | 19870057 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-01-07 | 1230 | TX | JIM WELLS |  | NO |  | NO | APPROXIMATELY 2 MILES SOUTHEAST OF PREMONT IN THE A. CANALES SURVEY, BLK. 182. |  | LINE PIPE | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1350 | 1249.6392 | 2521.027 | GASOLINE | 3 | 51 | 0 | NO | NO | 4 | 0.24 | 35000 | WELDED |  | 801 | 200 | YES | 24 | 1001 | 2 | 74 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | ISOLATED EXTERNAL CORROSION PITTING PENETRATED THE PIPE WALL RESULTING IN THE NATURAL GASOLINE SPILL. A TEMPORARY LEAK CLAMP WAS INSTALLED TO STOP THE LEAK, THE DAMAGED SECTION OF PIPE WILL BE REPLACED WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 19870058 |  | 22907 | WYCO PIPE LINE CO | YES | 1987-02-08 | 500 | CO | ADAMS | DUPONT | NO |  | NO |  |  | TANK FARM | TANK |  | 1948 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 557 | 460 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.D. SEALOCK, FIELD SUPERVISOR | 3038304695 | A MICROCOMPUTER AND BACKUP SYSTEM FAILED.
2017-09-29 08:50 | YES | NO | 19870059 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-02-10 | 715 | TX | LIBERTY |  | NO |  | NO | 3 1/2 MILES SOUTH OF DAISETTA & 4 MILES WEST OF DEVERS |  | PUMPING STATION | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4628.2933 | 9337.1371 | CRUDE OIL | 1 | 290 | 289 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH, DIVISION MANAGER | 4098393100 | CORROSION ON A CAPPED 10" LINE IN THE UNDERGROUND STATION PIPING CAUSED A PIT HOLE. THE OIL RAN INTO A DRAINAGE DITCH AND INTO A SMALL CREEK. THE OIL RAN ABOUT1 MILE DOWN THE CREEK BEFORE BEING CONTAINED. THE COLLECTED OIL WAS RECOVERED BY VACUUM TRUCKS AND RETURNED TO THE STATION TANK. A NEW WELD CAP WAS WELDED AT THE END OF THE 10" LINE. TEXAS RAILROAD COMMISSION AND ENVIRONMENTAL PROTECTION AGENCY INSPECTED THE SITE DURING CLEAN-UP OPERATIONS
2017-09-29 08:50 | YES | NO | 19870060 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-01-11 | 1910 | TX | JASPER |  | NO |  | NO | THREE MILES EAST OF JASPER ON FARM TO MARKET ROAD 1408, APPROXIMATELY ONE MILE EAST OF THE INTERSECTION OF FM 1408 AND STATE HIGHWAY 63. |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7516 | 6957.2505 | 14035.5845 | NATURAL GAS LIQUID | 2 | 5 | 0 | YES | NO | 4 | 0.24 | 35000 | WELDED |  | 1440 | 500 | YES | 8 | 1848 | 11 | 52 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC, INSIDE CASIN | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | A LANDOWNER WAS BURNING PASTURE GRASS AT THE CROSSING OF THE 4" NGL PIPELINE AND FARM TO MARKER ROAD 1408, WHICH IGNITED THE VAPORS FROM A SMALL LEAK IN THE PIPELINE. UPON NOTIFICATION OF THE FIRE, THE PIPELINE SYSTEM WAS IMMEDIATELY SHUT DOWN AND BLOCK VALVES CLOSED TO ISOLATE THE LEAKING SECTION. THE SMALL FIRE WHICH WAS BURNING ON THE GROUND SURFACE WAS EASILY EXTINGUISHED. INVESTIGATION REVEALED THE LEAK WAS CAUSED BY ATMOSPHERIC CORROSION INSIDE THE CASING UNDER THE ROAD CROSSING. A SECTION OF THE CASING WAS REMOVED FROM THE LEAK AREA AND A FULL ENCIRCLEMENT PATCH WELDED TO THE PIPELINE, ENCASING THE SECTION OF PIPE WITH A PIN HOLE. THE PIPE UNDER THE ROAD CROSSING WILL BE REPLACED.
2017-09-29 08:50 | YES | NO | 19870061 |  | 1036 | BADGER PIPELINE CO | YES | 1987-03-12 | 1110 | WI | DANE | STOUGHTON | NO |  | NO | NEAR HAMMOND AND HANNERVILLE ROADS ABOUT 3 MILES SOUTHEAST OF STOUGHTON |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 55539.5201 | 112045.6452 | FUEL OIL | 1 | 70 | 30 | NO | NO | 12 | 0.25 | 46000 | WELDED |  | 1800 | 680 | YES | 24 | 1250 | 1 | 54 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS | NO | NO | W. WESLEY HOGAN, DISTRICT MANAGER | 3124390270 | ON MARCH 12, 1987 AT 11:10 A.M. BADGER PIPELINE WAS NOTIFIED BY A MR. CRAIG FULLER, OWNER OF FULLER EXCAVATING, THAT HE HAD PUNCTURED OUR PRODUCTS PIPELINE ANDTHAT PRODUCT WAS LEAKING FROM THE PIPE. MR. FULLER HAD BEEN DIGGING IN CONNECTION WITH THE PERFORMANCE OF PERCOLATION TESTS PRIOR TO DEVELOPMENT OF THE SITE NEAR WHERE OUR PIPELINE CROSSES HAMMOND ROAD AT MP 161.6 NEAR STOUGHTON, WISCONSIN. OUR TULSA CONTROL CENTER WAS NOTIFIED OF THE LEAK AND WERE TOLD TO SHUT DOWN THE LINE, LEAVING AS LITTLE PRESSURE AS POSSIBLE. THE LINE SECTION WAS ISOLATED BY CLOSING THE JANESVILLE STATION DISCHARGE VALVE AND THE MADISON MAINLINE BLOCK VALVE. THE LINE WAS SHUTDOWN AND ISOLATED BY 11:14 A.M. THE LEAK SITE WAS FURTHERISOLATED BY CLOSING AT 12:45 P.M. THE ISOLATED SECTION CONTAINING THE DAMAGED PIPE IS APPROXIMATELY 14.5 MILES IN LENGTH. BADGER PERSONNEL WERE DISPATCHED BY RADIO TO SECURE THE SITE AND TO MAKE TEMPORARY REPAIRS. DUE TO THE REMOTENESS OF THE SITE THERE WAS NO DANGER TO POPULATED AREAS. SUPPORT GROUPS CALLED BY BADGERARRIVED AT 4:30 P.M. AND A TEMPORARY REPAIR WAS COMPLETED AT 5:30 P.M. APPROXIMATELY 1275 GALLONS OF #2 FUEL OIL WAS RECOVERED FROM THE SITE. FULLER EXCAVATIONWAS AWARE THAT THE LINE WAS IN THE AREA; HOWEVER, NEGLECTED TO CALL NEITHER BADGER PIPELINE NOR THE WISCONSIN ONE CALL SYSTEM. THE LINE PUNCTURE OCCURRED IN A CORN FIELD APPROXIMATELY 800 FEET SOUTH OF HAMMOND ROAD WHICH IS 3 MILES SOUTHEAST OF STOUGHTON, WISCONSIN. A SHALLOW TRENCH WAS DUG AROUND THE PERIMETER OF THE SITE WITH SOME DEEPER CATCH PITS. THERE WAS A SMALL CREEK OUT-SIDE OF THE PERIMETER WHICH WAS CLEANED OF DEBRIS AND A BOOM WAS INSTALLED IN THE EVENT THE PRODUCT SHOULD REACH IT. THE PRODUCT WAS CONTAINED PRIOR TO REACHING THE SHALLOW TRENCH. CLEAN-UP OF THE SITE INVOLVED THE REMOVAL OF ALL OF THE CONTAMINATED SOIL WHICH WAS HAULED TO THE DANE COUNTY LANDFILL. REPAIRS TO THE LINE WERE MADE BY INSTALLING TWO STOPPLE TEES, FOLLOWED BY WELDING OF A 10'6" SECTION OF 12-3/4 O.D.LINE PIPE. THIS COMPLETED THE LINE REPAIR.
2017-09-29 08:50 | YES | NO | 19870062 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1987-03-04 | 130 | OH | ALLEN | LIMA | NO |  | NO | 10' SOUTH OF MID-VALLEY PIPELINE COMPANY'S SCRAPER TRAP LOCATED ACROSS FROM 1776 BUCKEYE ROAD, LIMA,OHIO(PHOTO ATTACHED) |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13884.88 | 28011.4113 | CRUDE OIL |  | 5225 | 5031 | NO | Null | 22 | 0.38 | 35000 | WELDED |  | 860 | 830 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT A. ARNET, ENVIRONMENTAL & SAFETY COORDINATOR, SUN PIP | 3132928850 | ON MARCH 4, 1987 AT APPROXIMATELY 0130 HOURS (EST), MID-VALLEY PIPELINES' LIMA TERMINAL PUMP VIBRATION MONITOR ALARM #4 ACTIVATED AUDIBLY AND VISUALLY, RESULTING IN PUMP #3 AND #4 SHUTTING DOWN. PUMP #1, A SMALLER UNIT, CONTINUED TO OPERATE. THE TERMINAL OPERATOR, DON ROOP, AFTER PHYSICALLY CHECKING THE PUMPS AND RESETTING THE ALARMS, RESTARTED PUMP #3. UPON RESTART, THE OPERATOR WITNESSED THE FLOW CHART MOVEMENT TO AN INCREASED RATE AND REDUCED PRESSURE. UPON DETERMINATION THAT LOW SUCTION WAS INDICATED AT THE UPSTREAM STATION IN CYGNET, THE LIMA STATION OPERATOR SHUT DOWN THE STATION. TERMINAL OPERATOR, DOUG MOORMAN, HAD BEEN DISPATCHED TO ASSIST WITH THE DIFFICULTIES AND ARRIVED AT APPROXIMATELY 0215 HOURS (EST). AT THIS TIME THE TERMINAL FOREMAN, GEORGE FLETCHER WAS CONTACTED AND HE ADVISED DOUG TO BEGIN LOOKING FOR A LEAK IN THE SYSTEM. AS DOUG WAS LEAVING THE TERMINAL, THE LEAK WAS SPOTTED NEAR THE SCRAPER TRAP. CRUDE OIL WAS COVERING A LARGE SECTOR OF DITCH. MID-VALLEY PIPELINE PERSONNEL AND SPILL CONTRACTORS WERE DISPATCHED TO THE SCENE AND CLEAN UP OPERATIONS WERE BEGUN IN THE DRAINAGE DITCH AND THE IMMEDIATE VICINITY OF THE LEAK TO "SAFE UP" THE AREA IN PREPARATION FOR EXCAVATION. AT APPROXIMATELY 1700 HOURS(EST), THE AFFECTED AREA OF THE LINE WAS EXCAVATED, AND A LONGITUDINAL RUPTURE WAS IDENTIFIED ON THE UNDERSIDE (SIX O'CLOCK) OF THE 22" LINE. AT APPROXIMATELY 1930 (EST), THE RUPTURED PIPE WAS CUT OUT AS A 7' SECTION. THE RUPTURE ITSELF WAS MEASURED TO BE APPROXIMATELY 24" IN LENGTH AND APPROXIMATELY 5" IN WIDTH AT THE WIDEST POINT. EXAMINATION INDICATED THAT THE PIPE HAD FAILED DUE TO CORROSION. THE AFFECTED SECTION WAS REPLACED WITH TESTED PIPE, WELDS WERE PROPERLY X-RAYED, AND THE LINE WAS RETURNED TO SERVICE AT AREDUCED PRESSURE AT APPROXIMATELY 1300 HOURS (EST) MARCH 5, UNTIL FURTHER INSPECTION OF IMMEDIATE DISCHARGE PIPING COULD BE MADE. UPON FURTHER INSPECTION IT WASDECIDED TO REPLACE THE ENTIRE 800' SECTION OF IMMEDIATE DISCHARGE PIPING. THISJOB WAS COMPLETED ON MARCH 23, 1987. A CORROSION CONSULTANT WAS ENGAGED TO INSPECT THE OLD PIPE AND TO MAKE RECOMMENDATIONS ON PROTECTING THE NEW PIPE.
2017-09-29 08:50 | YES | NO | 19870063 |  | 19335 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1987-03-14 | 1015 | TX | HARRIS |  | NO |  | NO | LYONDELL PETROCHEMICAL REFINERY, PASADENA, TEXAS |  | LINE PIPE | PIPE |  | 1937 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3702.6347 | 7469.7097 | CRUDE OIL | 1 | 140 | 138 | NO | NO | 12 | 0.41 | 0 | WELDED |  | 850 | 50 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.V. OWENS, DISTRICT MANAGER | 9159497019 | THE CRUDE OIL LEAK WAS REPORTED TO OUR OZONA STATION BY REFINERY PERSONNEL. THEMAIN LINE WAS SHUT DOWN, PERSONNEL WERE DISPATCHED, THE LEAK WAS CONTAINED AND OIL WAS RECOVERED. CAUSE OF THE LEAK WAS TRACED TO A LINE FAILURE. EVIDENCE INDICATES THAT EXTERNAL STRESSES, RESULTING FROM NUMEROUS EXCAVATIONS IN THE IMMEDIATE AREA, HAD BEEN PLACED ON THIS LINE SEGMENT. THE LINE LAYS IN WHAT HAS BECOME A PIPELINE CORRIDOR, WITH NUMEROUS LINES CROSSING AND LAYING PARALLEL IT. PERMANENT REPAIRS WERE MADE AND THE EXTERNAL STRESSES RELIEVED.
2017-09-29 08:50 | YES | NO | 19870064 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-03-25 | 140 | TX | ECTOR |  | NO |  | NO | JUDKINS STATION TANK FARM SECTION 1 BLK 16 PUBLIC SCHOOL LAND SURVEY APPROX. 15 MILES WEST OF ODESSA TX 1 MILE SOUTH OF INTERSTATE HIGHWAY I-20(SEE ATTACHED MAP |  | TANK FARM | TANK |  | 0 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 91000 | 84234.9387 | 169935.8953 | CRUDE OIL | 1 | 50 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | R.L. DOWNIE, DIVISION MANAGER | 9156877551 | TATION SIGHTED TANK ON FIRE (APPROX. 24:40). REPORTED TO MONAHANS STATION OPERATOR WHO CONTACTED ALL PARTIES CONCERNED. WEST ODESSA VOLUNTEER FIRE DEPT. RESPONDED WITH 2 PUMPERS. FIRE WAS EXTINGUISHED WITH FOAM BLANKET IN SEAL AREA.
2017-09-29 08:50 | YES | NO | 19870065 |  | 395 | AMOCO OIL CO | NO | 1987-03-05 | 1900 | TX | TERRY |  | NO |  | NO | 3 1/2 MI. NE & 2 MI. EAST OF SEAGRAVES, TX |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3239.8053 | 6535.996 | CRUDE OIL | 1 | 55 | 35 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 650 | 200 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER |  | NO | NO | JAMES L. HOMER, P/L MAINTENENCE FOREMAN | 5053962817 | P/L HAD PREVIOUSLY BEEN DAMAGED BY FARM PLOW-AFTER UNKNOWN LENGTH OF TIME METALFATIGUE RESULTED IN RUPTURED.
2017-09-29 08:50 | YES | NO | 19870066 |  | 395 | AMOCO OIL CO | YES | 1987-02-20 | 1200 | MO | CASS | FREEMAN | NO |  | NO | NW/4, SECTION 18, T 44N, R 32W, CASS COUNTY, MISSOURE (SKETCH ATTACHED) |  | LINE PIPE | OTHER | COLLAR THREADS | 1923 | OTHER | COLLAR FAILURE, THREADS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 23141.4667 | 46685.6855 | CRUDE OIL | 1 | 285 | 238 | NO | NO | 12 | 0.38 | 25000 | THREADED |  | 695 | 680 | YES | 24 | 869 | 1 | 75 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MITCHELL B. WEISS, AREA MANAGER, OPERATIONS | 8163311673 | THE #2 SYSTEM IS A BI-DIRECTIONAL SYSTEM BETWEEN DRUMRIGHT, OKLAHOMA AND FREEMAN, MISSOURI. IT WAS LAST OPERATED ON APRIL 11, 1986 FROM DRUMRIGHT TO FREEMAN. AT 1400 CST ON FEBRUARY 16, 1987, THE LINE WAS STARTED AND OPERATED FROM FREEMAN TO DRUMRIGHT AT A REDUCED PRESSURE, 600 PSI. AT 0900 CST ON FEBRUARY 19, 1987, THE COMPANY PILOT BEGAN HIS AERIAL PATROL OF THE PIPELINE. AT 1550 CST ON FEBRUARY 19, THE PATROL PILOT COMPLETED HIS RUN AND REPORTED NO PROBLEMS. AT 1550 CST ON FEBRUARY 19, 1987, THE FREEMAN DISCHARGE PRESSURE WAS INCREASED TO 690 PSI. ONFRIDAY, FEBRUARY 20, 1987, A COLLAR LEAK WAS REPORTED. REPAIR AND RECOVERY EFFORTS WERE PROMPTLY INITIATED
2017-09-29 08:50 | YES | NO | 19870067 |  | 5320 | FLORIDA POWER CORP | NO | 1987-03-10 | 920 | FL | PINELLAS |  | NO |  | NO | UNDER HIGH TENSION POWER LINE APPROXIMATELY 1/2 MILE NORTH OF COUNTY ROAD 95 EAST OF U.S. 19 |  | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 46282.9334 | 93371.371 | CRUDE OIL | 1 | 200 | 125 | NO | NO | 14 | 0.25 | 52000 | WELDED |  | 1080 | 800 | YES | 48 | 1200 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER |  | NO | NO | R.W. REED, SUPERVISOSR OF SYSTEM FUEL OPERATIONS | 8132233026 | A LAND OWNER APPARENTLY STRUCK AND DAMAGED THE PIPELINE WHEN EXCAVATING THE GROUND FOR THE PURPOSE OF RECESSING ON ABOVE GROUND TYPE SWIMMING POOL. AT THAT TIME THE PIPELINE WAS SECURED WITH OIL IN THE LINE. THE LAND OWNER WAS APPARENTLY UNAWARE THAT HE WAS EXCAVATING IN THE TRANSMISSION LINES' RIGHT OF WAY, WHERE THEPIPELINE IS BURIED ABOUT FOUR FEET BELOW THE SURFACE. HE DID NOT HAVE A BUILDING PERMIT. A POOL SUPPORT WAS LESS THAN A FOOT AWAY FROM THE PIPELINE. PUMPING STARTED AT 8:05 MARCH 10TH AND THE LEAK WAS REPORTED TO THE PUMPING STATION AND THE PIPELINE WAS IMMEDIATELY SECURED AT 9:20
2017-09-29 08:50 | YES | NO | 19870068 |  | 381 | AMBER PIPELINE CO | NO | 1986-12-21 | 1030 | TX | TARRANT | COLLEYVILLE | NO |  | NO | 6700 PLEASANT RUN ROAD, COLLEYVILLE, TEXAS |  | LINE PIPE | GIRTH |  | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 68000 | 64348.6018 | 129817.1213 | GASOLINE | 1 | 1000 | 600 | NO | NO | 8 | 0.28 | 45000 | WELDED |  | 500 | 60 | YES | 8 | 700 | 4 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MAX HORNSBY | 8178725413 | THE CAUSE OF THE ACCIDENT, WAS A BROKEN GIRTH WELD. THIS PARTICULAR WELD SHOWEDTO HAVE NO WELDING PENETRATION ON THE INSIDE OF THE PIPE. THIS WAS NOT A RECENTWELD, BUT LOOKED TO HAVE BEEN DONE IN THE LAST 25 YEARS.
2017-09-29 08:50 | YES | NO | 19870069 |  | 26141 | SHELL OIL CO | NO | 1987-02-11 | 800 | CA | KERN | SHAFTER | NO |  | NO | SECTION 13, T-28-S, R-24-E, MDB&M SURVEY THREE MILES WEST OF SHAFTER BAKERSFIELD 14-INCH MAINLINE |  | LINE PIPE | VALVE |  | 1971 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 27769.76 | 56022.8226 | CRUDE OIL | 1 | 400 | 350 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1140 | 769 | YES | 24 | 1600 | 1 | 71 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870070 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-02-16 | 100 | SD |  | SIOUX FALLS | NO |  | NO | HAYWARD SCHOOL PROPERTY WHICH WAS FROM ITS TANK FARM ON 12TH ST. IN SIOUX FALLS; ACTUAL RELEASE DATE WAS 9/23/85. |  | TANK FARM | TANK |  | 1950 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000000 | 3702634.6702 | 7469709.6828 | GASOLINE | 3 | 715 | 19 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | CORROSION FROM TANK SEDIM | NO DATA |  | Null | NO DATA |  | Null | Null | C.K. MCCAW, VICE PRESIDENT, OPERATIONS | 9185883285 | TANK #1341 ON WILLIAMS' 12TH STREET TERMINAL IN SIOUX FALLS, SOUTH DAKOTA, WAS CONVERTED FROM JP-4 SERVICE TO UNLEADED GASOLINE SERVICE IN SEPTEMBER 1985. A SMALL CORROSION LEAK DEVELOPED IN THE TANK BOTTOM DURING FILLING OPERATIONS 9/22/85-9/23/85. HOWEVER, THIS LEAK WAS NOT DETECTED UNTIL A NEARBY RESIDENT, MRS. DUBBLE, REPORTED GASOLINE VAPORS IN HER BASEMENT ON MAY 30, 1986. THE TANK WAS EMPTIED, AND A SMALL PINHOLE LEAK WAS FOUND ON THE TANK BOTTOM NEAR THE RIM. A FIBERGLASS BOTTOM WAS INSTALLED AFTER THE TANK WAS CLEANED AND INSPECTED. SIZE OF THERELEASE UNKNOWN; ONLY 19 BARRELS HAVE BEEN RECOVERED THROUGH 3/1/87. ON SEPT....EMBER 17, 1986, HAYWARD ELEMENTARY SCHOOL REPORTED GASOLINE VAPORS AND WAS EVACUATED. SITE INVESTIGATIONS FROM SEPTEMBER 18, 1986 THROUGH FEBRUARY 15, 1987, INDICATED THAT TANK 1341 WAS ALSO THE SOURCE OF GASOLINE UNDER THE SCHOOL PROPERTY(INITIALLY A NEARBY GASOLINE STATION WAS THOUGHT TO BE THE SOURCE). THE CONSULTANTS (BAY WEST) ALSO ESTIMATED ON FEBRUARY 16 THAT APPROXIMATELY 20,000 GALLONS WERE UNDER THE SCHOOL SITE AND 10,000 GALLONS UNDER MRS. DUBBE'S FORMER PROPERTY.
2017-09-29 08:50 | YES | NO | 19870071 |  | 395 | AMOCO OIL CO | YES | 1987-03-10 | 1345 | WY | FREMONT |  | NO |  | NO | LEAK OCCURRED IN THE NW 1/4, SECTION 3, T.38., R.90W., FREMONT COUNTY, WYOMING AT AMOCO PIPELINE'S LOST CABIN STATION. STATION SITE IS ABOUT 3/8 MILE N.E. OF LO |  | TANK FARM | TANK |  | 1948 | OTHER | WATER DRAIN LINE FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 694.244 | 1400.5706 | CRUDE OIL | 1 | 75 | 72 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.W. WHITE, AREA MANAGER, WEST OPERATIONS | 3072662119 | AT 13:45, MARCH 10, 1987, AN AMOCO PIPELINE COMPANY EMPLOYEE SPOTTED OIL INSIDEA TANK DIKE AT OUR LOST CABIN STATION. HE IMMEDIATELY CLOSED A VALVE, WHICH STOPPED THE LEAK, AND NOTIFIED THE MAINTENANCE FOREMAN. ABOUT 72 BARRELS OF CRUDE OIL WERE PICKED UP BY VACUUM TRUCK AND PUT BACK INTO OUR TANKAGE. THE REMAINING 3BARRELS WERE MIXED WITH DIRT DURING CLEANUP AND SPREAD THROUGHOUT THE TANK DIKEAREA. ALL WORK WAS COMPLETE BY 16:00 MARCH 11, 1987. THE LEAK WAS CAUSED BY A FAILURE IN A FLOATING ROOF TANK WATER DRAIN LINE, WHICH ALLOWED OIL TO ENTER IT AND DRAIN TO THE GROUND. ALL OF THE LEAKED OIL WAS CONTAINED INSIDE THE TANK DIKE. NO OIL REACHED WATER. THE FAILED WATER DRAIN LINE WILL BE REPAIERED AT A LATERTIME AS SOON AS THE TANK CAN BE EVACUATED.
2017-09-29 08:50 | YES | NO | 19870072 |  | 12628 | MOBIL PIPELINE CO | YES | 1987-02-23 | 1720 | TX | TAYLOR | MERKEL | NO |  | NO | SECTION 6, BLK. 18, T&PRR CO. SURVEY LOCATED 1 MILE SOUTH OF THE CITY OF MERKEL, WEST OF COUNTY ROAD FM 126 AND LITTLE BITTER CREEK. |  | LINE PIPE | PIPE |  | 1944 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 27000 | 24992.784 | 50420.5404 | CRUDE OIL | 1 | 358 | 324 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 825 | 350 | YES | 2 | 908 | 4 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | ISOLATED EXTERNAL CORROSION PITTING PENETRATED PIPE WALL RESULTING IN THE CRUDEOIL SPILL. REPAIRS WERE MADE BY WELDING A SADDLE TO THE PIPELINE. PIPE-TO-SOIL POTENTIAL TAKEN AT THE PIPE SURFACE WAS DETERMINED TO BE VERY GOOD AT THIS SITE.
2017-09-29 08:50 | YES | NO | 19870073 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1987-02-23 | 700 | IL | WHITE |  | NO |  | NO | NORRIS CITY PUMP STATION; APPROXIMATELY 1 MILE EAST OF NORRIS CITY, ILLINOIS (VICINITY MAP ATTACHED) |  | PUMPING STATION | OTHER | CONTROL VALVE | 1979 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 57650 | 53364.2222 | 107657.1908 | FUEL OIL | 3 | 149 | 149 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BERT R. PURGATORIO, JR., VICE PRESIDENT & CHIEF ENGINEER | 7137595454 | ABNORMAL OPERATION, RESULTING FROM CONTROL VALVE MALFUNCTION, CAUSED PUMP STATION PRESSURE TO RISE AND PRESSURE RELIEF VALVES RELIEVED TO STATION SUMPS. SUMP TANKS OVERFLOWED ON STATION PROPERTY AND PRODUCT WAS CONTAINED ENTIRELY ON STATION PROPERTY.
2017-09-29 08:50 | YES | NO | 19870074 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-02-25 | 1400 | KS | BUTLER | AUGUSTA | NO |  | NO | NEAR STATE AVENUE AND SHIRLEY AVENUE IN THE CITY OF AUGUSTA. |  | LINE PIPE | PIPE |  | 1937 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2314.1467 | 4668.5686 | CRUDE OIL | 1 | 60 | 50 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 413 | 70 | YES | 2 | 455 | 1 | 69 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | INTERNAL CORROSION PIT PENETRATED PIPE WALL RESULTING IN THE CRUDE OIL SPILL. PIPELINE WAS REPAIRED BY WELDING A PATCH.
2017-09-29 08:50 | YES | NO | 19870075 |  | 19536 | TOTAL PIPELINE CORP | NO | 1987-02-16 | 1400 | TX | ARCHER |  | NO |  | NO | 1 1/2 MILES SOUTH AND 1/2 MILE EAST OF U.S. POST OFFICE AT KAMAY, TEXAS. |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 462.8293 | 933.7137 | CRUDE OIL | 1 | 359 | 110 | NO | NO | 6 | 0 | 0 | WELDED |  | 300 | 0 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | OTHER | OXIDATION | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM O. DELANO, GENERAL MANAGER OF SOUTHWEST DIVISION | 4052291638 | EXTERNAL CORROSION CAUSED A LEAK IN ONE OF TOTAL PIPELINE CORPORATION'S 6" MAINFIELD GATHERING SYSTEMS. OIL WAS DISCHARGED ONTO PROPERTY AND THEN THE REMAINDER WAS BURNED. REMAINING OIL STAINED SOIL IS TO BE REMOVED AND THE LOCATION CLEANED UP AS SOON AS WEATHER PERMITS. BURN PERMIT WAS OBTAINED FROM PAUL KANDT OF THE TEXAS AIR CONTROL BOARD ON 2-17-87. LEAK WAS CALLED IN TO PETTY OFFICER, O'BRIEN, OF THE NATIONAL RESPONSE CENTER. LEAK WAS CALLED IN TO BECKY OF THE TEXAS RAILROAD COMMISSION.
2017-09-29 08:50 | YES | NO | 19870076 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-04-12 | 1415 | TX | EL PASO |  | NO |  | NO | CHEVRON PIPE LINE EL PASO STATION 6325 TROWBRIDGE ST EL PASO TX SECTION 3 ASCARATE GRANT SURVEY EL PASO COUNTY TX |  | LINE PIPE | SCRAPER TRAP |  | 0 | OTHER | D RING SEAL FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | 12496.392 | 25210.2702 | DIESEL FUEL | 2 | 700 | 500 | NO | NO | 0 | 0 | 0 | NO DATA |  | 1860 | 750 | YES | 8 | 2325 | 4 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L. DOWNIE (DIVISION MANAGER) | 9156877551 | D" RING SEAL FAILED ON EL PASO TO ALBUQ 8" PRODUCTS TRUNK LINE'S SCRAPER TRAP CAUSING DIESEL FUEL TO SPILL.RECOVERED FUEL WAS RETURNED TO CHEVRON REFINERY'S SLOP TANK, CONTAMINATED SOIL WILL BE REMOVED.
2017-09-29 08:50 | YES | NO | 19870077 |  | 19536 | TOTAL PIPELINE CORP | YES | 1987-04-11 | 1800 | OK | KAY |  | NO |  | NO | CENTER OF SECTION 36, TOWNSHIP 25N, RANGE 1 W, KAY COUNTY, OKLAHOMA |  | LINE PIPE | PIPE |  | 1925 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1851.3173 | 3734.8548 | CRUDE OIL | 1 | 400 | 386 | NO | NO | 6 | 0.25 | 40700 | WELDED |  | 720 | 550 | YES | 8 | 1005 | 5 | 85 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GARY A STRACK DOT CO-ORDINATOR | 3164425100 | TIME OF ACCIDENT UNKNOWN. LANDOWNER NOTIFIED TPC WEEKEND DUTY OFFICER IMMENDIATELY AFTER LOCATING LEAK. ACCIDENT WAS ATTRIBUTED TO PIPELINE FAILURE AT A CORROSION PIT.
2017-09-29 08:50 | YES | NO | 19870078 |  | 2327 | CHEVRON USA INC | NO | 1987-03-05 | 2000 | HI | HONOLULU | EWA BEACH | NO |  | NO | LEAK WAS LOCATED IN AN UNINHABITED AREA ALONG KALAELOA BOULEVARD. NO PUBLIC OR PRIVATE BUILDINGS ARE NEAR THE LEAK SITE. THE LEAK OCCURRED AT MILEPOST 1.4. |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 925.6587 | 1867.4274 | GASOLINE | 3 | 6000 | 0 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1200 | 200 | YES | 8 | 1500 | 7 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.H. TSUJI, AREA SUPERVISOR | 8086825711 | THE PIPELINE WAS SHUT DOWN DUE TO DISCREPANCY ON A PRODUCT TRANSFER. LINE WAS PRESSURED UP TO 450 PSIG (WHICH IS BELOW DESIGN PRESSURE) AND BLOCKED IN. PRESSURE DROPPED OFF. THE PIPLINE WAS DISPLACED WITH WATER THEN PRESSURED UP TO 950 PSIG. THE LEAK WAS THEN DISCOVERED AND REPAIRED ON MARCH 5. THE NATIONAL RESPONSE CENTER, COAST GUARD AND THE STATE DEPARTMENT OF HEALTH WERE NOTIFIED OF THE LEAK.
2017-09-29 08:50 | YES | NO | 19870080 |  | 1466 | BLACK LAKE PIPELINE CO | YES | 1987-03-09 | 1100 | LA | BIENVILLE |  | NO |  | NO | SECTION 19, T-17-N, R-7-W, BIENVILLE PARISH, LOUISIANA |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 37026.3467 | 74697.0968 | NATURAL GAS LIQUID | 2 | 177 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1245 | 650 | YES | 24 | 1559 | 12 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, VICE PRESIDENT | 3163311300
2017-09-29 08:50 | YES | NO | 19870081 |  | 443 | AMOCO PIPELINE CO | YES | 1987-04-04 | 300 | WY | JOHNSON |  | NO |  | NO | NW 1/4 SECTION 26 T41N R80W; LEAK LOCATION WAS IN REMOTE RURAL AREA. |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 32398.0534 | 65359.9597 | CRUDE OIL | 1 | 180 | 149 | NO | NO | 12 | 0.38 | 0 | WELDED |  | 695 | 0 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GW WHITE, AREA MANAGER - WEST OPERATIONS | 3075770581 | ROCKY SOIL CONDITIONS HAD RUBBED A HOLE THROUGH PIPE COATING. THIS ALLOWED MOISTURE TO CORRODE PIPE WALL AND ULTIMATELY CAUSE PITTING IN PIPE AT THIS LOCATION.HOLE WAS APPROXIMATELY 3/16" DIAMETER.
2017-09-29 08:50 | NO | NO | 19870082 |  | 443 | AMOCO PIPELINE CO | YES | 1987-03-16 | 830 | OK | POTTAWATOMIE |  | NO |  | NO | NW 1/4 SE 1/4 SECTION 7 T8N - R3E POTTAWATOMIE COUNTY 4.3 MI N, 1.5 MI E OF TRIBBEY, OK |  | LINE PIPE | PIPE |  | 1918 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 231.4147 | 466.8569 | CRUDE OIL | 1 | 6 | 0 | NO | NO | 6 | 0.28 | 25000 | COUPLED |  | 690 | 600 | YES | 24 | 1038 | 5 | 76 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC CORROSION ADJ | NO DATA |  | Null | NO DATA |  | Null | Null | JW WILHELM, AREA MANAGER | 9182252243 | THE PIPELINE SPANS A CREEK AT THE LEAK LOCATION. A PIT DEVELOPED IN THE PIPE WHERE IT RESTED ON A SUPPORT. REPAIRS REQUIRED MOVING THE SUPPORT, WELDING A FULL ENCIRCLEMENT SLEEVE ON THE PIPE AND THEN REPOSITIONING THE SUPPORT.
2017-09-29 08:50 | NO | NO | 19870083 |  | 443 | AMOCO PIPELINE CO | YES | 1987-02-18 | 0 | TX | HARRIS | HOUSTON | NO |  | NO | H.L. & P. RIGHT OF WAY IN GATX TERM. N. OF SHIP CHANNEL |  | LINE PIPE | BOLTED FITTING |  | 1987 | OTHER | GASKET MISALIGNMENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 10 | 0.34 | 0 | FLANGED |  | 300 | 50 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL P CLANG | 7133322476 | ON FEB 12, 1987 A OLD VALVE WAS REMOVED AND REPLACED WITH A SPOOL PIECE. THE LINE REMAINED SHUT DOWN AND OUT OF SERVICE UNTIL FEB. 18, 1987. AT THAT TIME THE LINE WAS BEING FILLED AGAIN. A MAN WAS PRESENT AT THE SPOOL LOCATION TO INSPECT THE NEW INSTALLATION FOR ANY LEAKS. WHEN A LEAK WAS DETECTED, THE PUMP WAS SHUT DOWN AND THE VALVE UP-STREAM WERE CLOSED. THE VALVE DOWN-STREAM REMAINED OPEN TO RELIEVE LINE PRESSURE. DURING THIS TIME APPROXIMATELY 1/2 TO 3/4 BARRELS OF CRUDE OIL RAN INTO A CONTRIBUTARY LEADING TO THE HOUSTON SHIP CHANNEL. TWO BOOMS WERE SET AND OIL WAS CONTAINED AND PICKED UP BEFORE REACHING HOUSTON SHIP CHANNEL.
2017-09-29 08:50 | YES | NO | 19870084 |  | 443 | AMOCO PIPELINE CO | NO | 1987-03-06 | 630 | TX | REAGAN |  | NO |  | NO | 4 MI EAST OF HIGHWAY 33, ALONG SIDE FM 2600 |  | LINE PIPE | NO DATA |  | 1966 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 185.1317 | 373.4855 | CRUDE OIL | 1 | 350 | 350 | NO | NO | 8 | 0.19 | 0 | WELDED |  | 60 | 50 | NO | 0 | 0 | 3 | 87 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIMMY M. HUNTER, PIPELINE MAINT. FOREMAN | 9155733589
2017-09-29 08:50 | YES | NO | 19870085 |  | 443 | AMOCO PIPELINE CO | NO | 1987-02-26 | 2100 | TX | IRION |  | NO |  | NO | SECTION 2, BLOCK 2, H & TC RR SURVEY 2, BLOCK 2 7.5 MI S/W OF ARDEN TEXAS |  | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 462.8293 | 933.7137 | CRUDE OIL | 1 | 1900 | 1880 | NO | NO | 16 | 0.25 | 0 | WELDED |  | 800 | 500 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIMMY M. HUNTER, MAINT. FOREMAN | 9155733589
2017-09-29 08:50 | YES | NO | 19870086 |  | 395 | AMOCO OIL CO | YES | 1987-03-31 | 0 | IA | MONONA | ONAWA | NO |  | NO | SW/4, SECTION 35, T84N, R45W, MONONA COUNTY, IOWA (SKETCH ATTACHED) |  | LINE PIPE | OTHER | TEMPORARY PIPING | 1987 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 4165.464 | 8403.4234 | DIESEL FUEL | 2 | 300 | 295 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | OTHER | FAILURE IN TEMPORARY VALV | Null | NO DATA |  | Null | Null | MITCHELL B. WEISS, AREA MANAGER | 8163311673 | 169 MILES OF 6-INCH LINE BETWEEN COUNCIL BLUFFS, IOWA AND SIOUX FALLS, SOUTH DAKOTA IS CURRENTLY BEING PREPARED FOR AN INTERNAL INSPECTION SURVEY. LIMITATIONS ON THE INSTRUMENT REQUIRE IT TO BE REMOVED AND REINSERTED AT THE APPROXIMATED THIRD POINTS. TO ACCOMMODATE THIS, TEMPORARY RECEIVERS AND LAUNCHERS MUST BE PROVIDED. THE SITE OF THE SPILL WAS THE FIRST OF THESE LOCATIONS.TWO 1.5-INCH FORGED STEEL 2000 WOG NEEDLE VALVES, USED FOR VENTING, CRACKED THROUGH THE MALE THREADS AT THE POINT THEY WERE ADAPTED TO COUPLINGS ON THEIR RESPECTIVE BARRELS. ALL THE DIESEL FUEL WHICH ESCAPED WAS CONTAINED AND RECOVERED FROM THE CONSTRUCTION DITCH WHICH MEASURED 180 FT. LONG X 8 FT. WIDE X 6 TO 8 FT. DEEP.AFTER COMPLETION OF THE INTERNAL INSPECTION IN MAY, ALL TEMPORARY PIPING WILL BE REMOVED AND THE NORMAL CONFIGURATION RESTORED.
2017-09-29 08:50 | YES | NO | 19870090 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-03-06 | 930 | NM | VALENCIA |  | NO |  | NO | BELEN PIPE LINE TERMINAL LOCATED ON JARRALE RD. (STATE RD 109) IN BELEN N.M. SECTION 19 RZE TS 5N SURVEY (SEE TWO ATTACHED MAPS) |  | PUMPING STATION | OTHER | SALT DRYER | 1964 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 8330.928 | 16806.8468 | DIESEL FUEL | 3 | 350 | 300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L. DOWNIE, DIVISION MANAGER | 9156877551 | WHEN DIESEL STREAM WAS DIVERTED FROM MAIN EL PASO TO ALBUQUERQUE PRODUCTS TRUNKLINE TO THE BELEN TERMINAL TRUNK LINE THE SANTA FE MANIFOLD VALVE WAS NOT OPENED BY RAILROAD EMPLOYEES CAUSING OVER PRESSURE AT THE LOW PRESSURE SALT DRYER AT THE BELEN TERMINAL. THE SALT DRYER RUPTURED CAUSING THE SPILL.THE LOW PRESSURE SALT DRYER HAS BEEN REMOVED FROM THE SYSTEM.
2017-09-29 08:50 | YES | NO | 19870091 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-03-27 | 900 | TX | CRANE |  | NO |  | NO | APPROXIMATELY 2 MI NORTH OF CRANE, TX. &1 MI WEST OF TX HWY 385 SECTION 9, BLOCK X, CCSD & RGNG SURVEY 4" RUN AROUND LINE TO SAND HILLS TO CRANE 8" CRUDE TRUNK |  | NO DATA | PIPE |  | 1973 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 370.2635 | 746.971 | CRUDE OIL | 1 | 60 | 45 | NO | NO | 4 | 0.16 | 35000 | WELDED |  | 840 | 160 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L. DOWNIE, DIVISION MANAGER | 9156877551 | HOLE IN LINE DUE TO EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19870092 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-04-02 | 930 | TX | NAVARRO |  | NO |  | NO | ONE MILE WEST-NORTHWEST OF FM 642SEE ATTACHED MAPS |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6479.6107 | 13071.9919 | DIESEL FUEL |  | 80 | 25 | NO | NO | 10 | 0 | 0 | THREADED |  | 675 | 640 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.D. BRUBAKER | 8177653261 | AT 9:30 AM IT WAS DETERMINED, DUE TO A VARIATION IN BARREL COUNTS AND SIGNIGICANT LOSE IN LINE PRESSURE, THERE WAS A LEAK ON THE 10" CPL PRODUCTS MESQUITE LINE. THE LEAK WAS ISOLATED BETWEEN THE PUMP STATION AT WORTHAM, TEXAS AND THE PRODUCTS TERMINAL AT DAWSON, TEXAS. THE PATROL PLANE WAS NOTIFIED, AND PERSONNEL WERESENT OUT TO WALK THE LINE. AT 11:30 AM THE LEAK WAS FOUND AT M.P. 11.42. THE AMOUNT OF PRODUCT (DIESEL FUEL) ON THE SURFACE WAS ESTIMATED TO BE ABOUT 80 BBLS. AN APPROXIMATED AREA OF 400' X 400' OF PASTURE LAND WAS AFFECTED.THE LEAK APPEARED TO HAVE BEEN CAUSED BY EXTERNAL CORRISION WITH THE HOLE IN THE PIPE APPROXIMATELY 1/8 OF AN INCH IN DIAMETER. REPAIRS WERE MADE USING CLAMPS,AND THE PIPELINE WAS BACK IN SERVICE AT 2:00 P.M.
2017-09-29 08:50 | NO | NO | 19870093 |  | 4906 | EXXON PIPELINE CO | NO | 1987-03-20 | 1055 | TX | HARRIS |  | NO |  | NO | LEAK OCCURRED AT STATION 1820+21, WHICH IS LOCATED IN THE EASTERN HALF OF THE SAN JACINTO RIVER @ 1-10 ON THE BAYTOWN #1-NORTH HOUSTON 10" LINE. |  | LINE PIPE | WELDING FITTING | WELD ON STOPPLE FITTING | 1968 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 23141.4667 | 46685.6855 | GASOLINE | 3 | 1 | 0 | NO | NO | 10 | 0.37 | 42000 | THREADED |  | 1440 | 750 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY | 7136565956 | CONTAIN THE LEAK. IT WAS NOT APPARENT THAT THE SHEEN WAS CAUSED BY A PIPELINE LEAK, SO THE BAYTOWN-IRVING PRODUCTS LINE AND THE SATSUMA-BAYTOWN 20" CRUDE LINERESUMED OPERATIONS AT 1430 HOURS. THE CAUSE OF THE SHEEN WAS CONFIRMED TO BE A PIPELINE LEAK AT 1630 HOURS. THE LEAK WAS FOUND TO BE A BAILED ASBESTOS-TYPE GASKET IN A STOPPLE FITTING ON THE BAYTOWN-ALDINE PRODUCTS LINE. THE GASKET WAS REPLACED WITH A METAL, SPIRAL WOUND GASKET TO PREVENT A RECURRENT LEAK. THE LINE WAS PLACED BACK INTO SERVICE AT 1825 HOURS ON MARCH 21. WHILE REPAIRING THIS LEAK,WE ELECTED TO INSPECT OTHER ADJACENT PIPELINES. WE FOUND AN EXTREMELY SMALL "SEEP" COMING FROM THE WELD OF STOPPLE FITTING ON THE BAYTOWN-IRVING PRODUCT LINE. THE STOPPLE FITTING WAS CUT OUT AND REPLACED WITH NEW PIPE. THE BAYTOWN-IRVING PRODUCTS LINE RESUMED SERVICE AT 1741 HOURS ON MARCH 26. CLEANUP OPERATIONS WERE COMPLETE ON MARCH 27,1987.
2017-09-29 08:50 | NO | NO | 19870095 |  | 4906 | EXXON PIPELINE CO | NO | 1987-03-20 | 1055 | TX | HARRIS |  | NO |  | NO | LEAK OCCURRED AT STATION 1819+25, WHICH IS LOCATED IN THE EASTERN HALF OF THE SAN JACINTO RIVER @ 1-10 ON THE BAYTOWN-ALDINE 8" LINE. |  | LINE PIPE | WELDING FITTING | GASKET ON STOPPLE FITTING | 1968 | OTHER | FAILED "ASBESTOS-TYPE" GA | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 19000 | 17587.5147 | 35481.121 | GASOLINE | 3 | 1 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1200 | 200 | YES | 24 | 2008 | 7 | 71 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | THE US. COAST GUARD CALLED JESSE SHEAD (EUSA) TO REPORT A 20' X 20' SHEEN ON THE WEST BANK OF THE SAN JACINTO RIVER, NORTH OF THE I-10 CROSSING. MR. SHEAD CALLED EPC'S OIL TRAFFIC CONTROL CENTER AT 1055 HOURS. THE SATSUMA-BAYTOWN 20" CRUDELINE, THE BAYTOWN-IRVING 10" PRODUCTS LINE, AND THE BAYTOWN-ALDINE 8" PRODUCTS LINE WERE IMMEDIATELY SHUTDOWN. EPC FIELD PERSONNEL ARRIVED ON THE SCENE AT 1115HOURS AND THE SHEEN WAS LOCATED AT 1200 HOURS. BOOMS WERE IMMEDIATELY PUT OUT TOCONTAIN THE LEAK. IT WAS NOT APPARENT THAT THE SHEEN WAS CAUSED BY A PIPELINE LEAK, SO THE BAYTOWN-IRVING PRODUCTS LINE AND THE SATSUMA-BAYTOWN 20" CRUDE LINE RESUMED OPERATIONS AT 1430 HOURS. THE CAUSE OF THE SHEEN WAS CONFIRMED TO BE A PIPELINE LEAK AT 1630 HOURS. THE LEAK WAS FOUND TO BE A FAILED ASBESTOS-TYPE GASKET IN A STOPPLE FITTING ON THE BAYTOWN-ALDINE PRODUCTS LINE. THE GASKET WAS REPLACED WITH A METAL, SPIRAL WOUND GASKET TO PREVENT A RECURRENT LEAK. THE LINE WASPLACED BACK INTO SERVICE AT 1825 HOURS ON MARCH 21. CLEANUP OPERATIONS WERE COMPLETED ON MARCH 27, 1987.
2017-09-29 08:50 | YES | NO | 19870096 |  | 4906 | EXXON PIPELINE CO | YES | 1987-04-01 | 1130 | TX | UPTON |  | NO |  | NO | LEAK OCCURRED AT APPROXIMATE STATION 772 + 45 SOME 6.24 MILES NORTH OF MCCAMEY STATION ON THE CRANE TO MCCAMEY #1 - 8" PIPELINE. |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12360 | 11441.1411 | 23081.4029 | CRUDE OIL | 1 | 600 | 0 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 722 | 300 | YES | 0 | 794 | 0 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565957 | AT 1130 HOURS ON APRIL 1, 1987 * EXXON PIPELINE COMPANY'S AIR PATROL REPORTED ACRUDE OIL LEAK ON OUR NUMBER 1-8 INCH CRANE TO MCCAMEY TRUNKLINE. AN EXXON PIPELINE COMPANY REPAIR CREW WAS DISPATCHED TO THE LEAK SITE. UPON ARRIVAL IT WAS DETERMINED THE LEAK WAS CAUSED BY EXTERNAL CORROSION. 600 BARRELS OF CRUDE OIL WERE SPILLED WITH NONE RECOVERED DUE TO THE ROUGHNESS OF THE TERRAIN. THE CRUDE OILHAD FLOWED DOWN A DRY WASH FOR APPROXIMATLELY 1.75 MILES. CLEAN UP OPERATIONS WERE STARTED IMMEDIATELY. OIL SPILLAGE WAS STOPPED BY SHUTTING DOWN THE FLOW AND INSTALLING A PIPELINE CLAMP. PERMANENT REPAIRS WERE COMPLETED ON APRIL 3, 1986 BY INSTALLING 10 FEET OF FULL WRAP.* AS INDICATED UNDER B 2.), THE LEAK PROBABLY STARTED MARCH 31, 1987.
2017-09-29 08:50 | YES | NO | 19870097 |  | 5165 | FINA OIL & CHEMICAL CO | YES | 1987-03-13 | 400 | TX | WICHITA | WICHITA FALLS | NO |  | NO | 75 YDS, WEST OF FM171 (CHARLEY ROAD) AND 7 YDS SOUTH OF SINCLAIR BLVD. |  | PUMPING STATION | OTHER | A 3/4 INCH X 6 INCH PIPE | 1983 | OTHER | PUMP VIBRATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13884.88 | 28011.4113 | DIESEL FUEL | 3 | 135 | 120 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | T.M. HIATS, SUPT. PRODUCTS PIPLINE | 9152637661 | 1. TERMINAL OPERATOR DISCOVERED LEAK AT 0432. HE SHUT DOWN AND BLOCKED IN THE PUMP. HE ALSO ATTEMPTED TO CONTAIN THE SPILL AND NOTIFIED THE TERMINAL MANAGER.2. THE PIPELINE SUPERVISOR WAS IN THE AREA AND ARRIVED AT THE SCENE AT 0720.3. THE CLEANUP COMPANY, THE WICHITA COUNTY EMERGENCY MANAGER AND THE WICHITA FALLS FIRE DEPARTMENT WERE NOTIFIED AS WELL AS DOT, NRC, TWC, AND TRC.4. DIESEL FLOWED INTO THE DITCHES ALONG SINCLAIR AND FM171 AND THROUGH A CULVERT EAST OF FM171 ON TOP OF WATER STILL STANDING FROM RECENT RAINS. MOST OF THE DIESEL WAS PICKED UP USING VACUUM TRUCKS AND A SMALL AMOUNT WAS ABSORBED WITH HAY,(MAP ATTACHED).5. A VIBRATION DAMPNER HAS BEEN INSTALLED ON THE PUMP AND THE LINE WILL BE CHANGED FROM SCHEDULE 80 TO SCHEDULE 160 PIPE.
2017-09-29 08:50 | YES | NO | 19870098 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1987-03-06 | 1340 | MN | CLEARWATER |  | NO |  | NO | APPROXIMATELY 1/2 MILES DOWNSTREAM OF OPERATOR'S CLEARBROOK, MINNESOTA TERMINAL IN SECTION 33, TOWNSHIP 149 N, RANGE 37W. |  | LINE PIPE | PIPE |  | 1954 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 70600 | 65351.5019 | 131840.3759 | CRUDE OIL | 1 | 500 | 490 | NO | NO | 26 | 0.28 | 52000 | WELDED |  | 762 | 760 | YES | 24 | 965 | 9 | 74 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.E. STAUDOHAR, COORDINATOR - OPERATIONS | 7153925631 | A REPORT OF A SHOW OF OIL WAS REPORTED AT 1340 MST ON MARCH 6. THE LINE WAS SHUTDOWN AND MAINTERANCE CREWS EXCAVATED THE LINE AND DISCOVERED A CRACK APPROXIMATELY 1/2" LONG IN THE LONGITUDINAL SEAM. A 26" X 14" LONG PLIDCO REPAIR SLEEVE WAS INSTALLED AND PERMANENTLY WELDED ONTO THE LINES. THE ENTIRE LONGITUDINAL SEAM OF THE AFFECTED JOINT WAS ULTRASONICALLY INSPECTED. NO OTHER DEFECT WAS DISCOVERE
2017-09-29 08:50 | YES | NO | 19870099 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-04-10 | 1606 | WY | SWEETWATER |  | NO |  | YES | TOWNSHIP 12 NORTH RANGE 105 WEST SECTION15 |  | LINE PIPE | NO DATA |  | 1980 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 361.9325 | 730.1641 | NATURAL GAS LIQUID | 2 | 11911 | 0 | NO | NO | 13 | 0.25 | 2350 | WELDED |  | 1820 | 1804 | YES | 24 | 2483 | 11 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | LINE PIPE RUPTURED. PIPE APPEARS TO HAVE BEEN PREVIOUSLY GOUGED.
2017-09-29 08:50 | YES | NO | 19870100 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-04-16 | 906 | MN | MARTIN |  | NO |  | YES | TOWNSHIP 103 NORTH RANGE 33 WEST SECTION 31 |  | LINE PIPE | LONGITUDINAL WELD |  | 1960 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 290.6568 | 586.3722 | L. P. G. | 2 | 5374 | 0 | NO | NO | 9 | 0.22 | 2640 | WELDED |  | 1269 | 925 | YES | 10 | 1830 | 10 | 60 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | LINE RUPTURED AT PREMATURE PRESSURE. WAITING FOR METALLURGY REPORT.
2017-09-29 08:50 | YES | NO | 19870101 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-04-04 | 1630 | IA | JOHNSON | IOWA CITY | NO |  | YES | 5 MILES EAST OF IOWA CITY, IOWA ON HIGHWAY 6 |  | PUMPING STATION | OTHER | RECOMPRESSOR AND CAVERN H | 1967 | OTHER | EQUIPMENT FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 122000 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S F ISAACS | 9185811800 | UKNOWN AT THIS TIME
2017-09-29 08:50 | YES | NO | 19870102 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1987-04-13 | 1800 | OK | GARVIN | ELMORE CITY | NO |  | NO | TWO MILES WEST ON ELMORE CITY ON HWY 29.FOUR MILES SOUTH 1/4 MILE WEST ON NORTH SIDE OF ROAD |  | PUMPING STATION | VALVE |  | 0 | OTHER | SUN PRESSURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1851.3173 | 3734.8548 | CRUDE OIL | 1 | 130 | 115 | NO | NO | 0 | 0 | 1440 | FLANGED |  | 800 | 100 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HERBERT M CONNELL | 4058674822 | A " W K M HIGH PRESSURE F E STEEL VALVE AT OUR EOLA STATION SEPARATED AT THE TOPWHERE BODY AND STEM JOINTS TOGETHER FROM SUN PRESSURE IN THE BOTTOM CAVITY OF THE VALVE.
2017-09-29 08:50 | YES | NO | 19870103 |  | 12628 | MOBIL PIPELINE CO | YES | 1987-03-12 | 337 | TX | NAVARRO |  | NO |  | NO | NEAR THE INTER SECTION OF INTERSTATE 45 AND SOUTH 15TH STREET SOUTH OF CORSICANA TEXAS |  | LINE PIPE | WELDING FITTING |  | 1958 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 238000 | 220306.7629 | 444447.7261 | CRUDE OIL | 1 | 2237 | 260 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D L DENNARD | 2146582226 | THE HORIZANTAL WELD ON A 20" T. D. WILLIAMSON STOPPLE FITTING DUE TO INADEQUATEPENETRATION IN THE WELD. THE FAILURE ALLOWED CRUDE OIL TO ESCAPE FROM THE IPELINE AND THE PRESSURE TO DROP. THE PRESURE DROP WAS IMMEDIATELY OBSERVED BY THEOPERATIONS CONTROLLER, AND THE LINE WAS SHUT DOWN. FORTY MINUTES AFTER THE ACCIDENT OCCURRED AFIRE WAS REPORTED AT THE SITE. THE SOURCE OF IGNITION COULD NOTTHE FAILED FITTING AND THE ADJOINING PIPE WERE REMOVED FROM THE PIPELINE AND REPLACED WITH NEW LINE PIPE.
2017-09-29 08:50 | YES | YES | 19870104 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1987-03-26 | 1933 | VA | CAROLINE |  | NO |  | NO | APPROXIMATELY 300 FEET EAST OF A POINT ON 664 ABOUT ONE HALF MILE SOUTH OF ITS INTERSECTION WITH VA 601 IN BALTY VA LOCATED IN THE MADISON DISTRICT OF COLUMBIA |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 2 | 0 | 2 | 118000 | 109227.7228 | 220356.4356 | JET FUEL | 3 | 952 | 52 | YES | NO | 13 | 0.2 | 1655 | WELDED |  | 1080 | 168 | YES | 24 | 1490 | 10 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R M CROOK | 4042612137 | THE ACCIDENT OCCURRED IN A RURAL AREA OF CAROLINE COUNTY VA AT 7:30 P.M. EST ON MARCH 26 1987. A CONTRACTOR WAS BURYING DEBRIS AFTER HAVING PERFORMED A CONTROLLED BURNING OF A HOUSE APPROXIMATELY 75 FEET FROM PLANTATION'S 12 INCH, .203 WALL THICKNES, X-52 GRADE PETROLEUM PRODUCTS PIPELINE. THE CONTRACTOR HAD DUG A 30' X 3.5' HOLE WITH AN FEET OF COVER. A 3.5" X 2" HOLE WAS TORNIN THE PIPELINE AT THE 9 O CLOCK POSITION LOOKING DOWNSTREAM. THE JP-5 FEUL INTHE LINE IMMEDIATELY CAUGHT FIRE. THE SOURCE OF IGNITION WAS THE REMAINS OF THEBURNED STRUCTURE WHEN THE PRODUCT (JP-5) UNDER PRESSURE REACHED IT. TWO PERSONSREQUIRED HOSPITAL TREATMENT. THE OWNER OF THE LOADER WHO WAS STANDING BEHIND ITSUFFERED MINOR BURNS TO HIS ARM. THE OPERATOR WHO HAD INGESTED FUEL WAS RETAINED AT THE HOSPITAL FOR OBSERVATION. THE APPLICABLE " ONE CALL" CENTER HAD NOT BEEN NOTIFIED OF THE EXCAVATION. THE CLOSET LINE MARKER WAS 75 FEET FROM THE POINT OF DAMAGE AND THREE OTHER LINE MARKER WITHIN LINE OF SIGHT.
2017-09-29 08:50 | YES | NO | 19870105 |  | 18273 | SHELL PIPE LINE CORP | NO | 1987-03-21 | 930 | TX | YOAKUM | DENVER CITY | NO |  | NO | SE 1/4 SE1/4 SECTION 826 BLOCK DJOHN H GIBSON SURVEY ONE MILE NORTH OF DENVERWASSON-MCCAMEY 16 INCH SCRAPPER LAUNCHER |  | LINE PIPE | SCRAPER TRAP |  | 1968 | OTHER | O RING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2260 | 2091.9886 | 4220.386 | CRUDE OIL | 1 | 750 | 650 | NO | NO | 16 | 0.31 | 52000 | WELDED |  | 1440 | 1300 | YES | 24 | 1890 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN | 7132416262
2017-09-29 08:50 | YES | NO | 19870106 |  | 18273 | SHELL PIPE LINE CORP | NO | 1987-03-19 | 940 | OH | ALLEN | LIMA | NO |  | NO | LIMA TERMINAL TANK L-19 1500 W. BUCKEYEROAD |  | TANK FARM | TANK |  | 1938 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 60167.8134 | 121382.7823 | GASOLINE | 2 | 223 | 222 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN | 7132416262 | TANK BOTTOM HAD CORRODED
2017-09-29 08:50 | YES | NO | 19870107 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-03-11 | 1237 | SD | MINNEHAHA | SIOUX FALLS | NO |  | NO |  |  | TANK FARM | WELDING FITTING | DRESSER COUPLING - P | 1950 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 462829.3338 | 933713.7104 | GASOLINE | 2 | 200 | 5 | NO | NO | 10 | 0.22 | 35000 | WELDED |  | 275 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C K MCCAW | 9185883285 | THE 10 INCH LINE THAT RUPTURED IS LOCATED ON WILLIAMS 12TH STREET TERMINAL INSIOUX FALLS, SOUTH DAKOTA. THE LINE BEGINS AT THE POINT WHERE OUR 12" MAINLINEENDS AND EXTENDS THROUGH THE TERMINAL TANK FARM TO TANK #1341. THE LINE WAS INA STATIC CONDITION AND VALVES WERE CLOSED AT EACH END OF THE LINE WHEN IT RUPTURED ON MARCH 11. THE RUPTURE IS BELIEVED TO HAVE BEEN CAUSED BY THE ISOLATION OFA 1/2" THERMAL RELIEF VALVE AT TANK #1341. THE DEVELOPING PRESSURE CAUSED THE FAILURE OF A DRESSER COUPLING, LINE PIPE ADJACENT TO A 90 DEGREE WELD ELBOW ANDTHE SPLITTING OF A PORTION OF PIPE ATTACHED TO A CONCRETE SUPPORT. THESE FAILURES RESULTED IN THE LOSS OF THE ENTIRE 200 BARREL LINE FILL OF WHICH WE WERE ONLY ABLE TO RECOVER APROXIMATELY 5 BARRELS.
2017-09-29 08:50 | YES | NO | 19870108 |  | 2327 | CHEVRON USA INC | NO | 1987-03-03 | 815 | HI | HONOLULU |  | NO |  | NO | LEAK OCCURED IN AN UNINHAITED AREA 50 FEET FROM THE EDGE OF PEARL HARBOR AT MILEPOST NO PUBLIC OR PRIVATE BUILDINGS ARE NEAR THE LEAK SITE |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 925.6587 | 1867.4274 | FUEL OIL | 3 | 85 | 85 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1610 | 600 | YES | 0 | 2050 | 0 | 60 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | CALL OPERTOR | YES | YES | WAYNE H TSUJI | 8086825711 | THE PIPE LINE WAS BEING REFURBISHED. THE BUCKET OF THE BACKHOE REMOVING SOILAROUND THE LINE SNAGGED AND TORE A HOLE IN THE PIPELINE. THE PIPELINE WAS SHUT DOWN AND REPAIRED ON MARCH 3 THE NATINAL RESPONSE CENTER AND COAST GUARD WERE NOTIFIED OF THE LEAK.
2017-09-29 08:50 | NO | NO | 19870109 |  | 2327 | CHEVRON USA INC | NO | 1986-12-10 | 1800 | HI | HONOLULU |  | NO |  | NO | LEAK OCCURRED ON THE BANK OF KALAUAO STREAM MP14.14 NO PUBLIC OR PRIVATE BUILDINGS ARE LOCATED WITHIN 100 FEET OF THE LEAK SITE. |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1892.6059 | 3818.1506 | FUEL OIL | 3 | 1 | 0 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1610 | 600 | YES | 0 | 2050 | 0 | 60 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W H TSUJI | 8086825711 | LEAK OCCURED DURING A ROUTINE SHIPMENT OF FUEL OIL. EXTERNAL CORROSION CAUSED APNHOLE LEAK IN THE PIPELINE. OIL ENTERED STREAM FROM THE LEAK SITE ON THE BANK.THE PIPELINE SHUTDOWN AND REPAIRED. THE NATIONAL RESPONSE CENTER THE COAST GAURD AND THE NAVY'S PEARL HARBOR PORT OPERATIONS WERE NOTIFIED.
2017-09-29 08:50 | NO | NO | 19870110 |  | 2327 | CHEVRON USA INC | NO | 1987-02-01 | 1615 | HI | HONOLULU |  | NO |  | NO | LEAK OCCURRED AT THE WAIMALU STREAM JOGGING BRIDGE MP13.75 THE PIPELINE IS SUPPORTED ALONG THE SIDE OF THE BRIDGE |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1851.3173 | 3734.8548 | DIESEL FUEL | 3 | 1 | 0 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1200 | 700 | YES | 8 | 1500 | 7 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W H TSUJI | 8086825711 | EXTERNAL CORROSION CAUSED A PINHOLE LEAK IN THE PIPELINE AND OIL LEAKED INTO WAIMALU STREAM. THE PIPELINE WAS SHUT DOWN AND REPAIRED. THE NATIONAL RESPONSE CENTER THE COAST GAURD ANT THE NAVY'S PEARL HARBOR PORT OPERATIONS WERE NOTIFIED.
2017-09-29 08:50 | YES | NO | 19870111 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-04-08 | 1520 | SD | MINNEHAHA | SIOUX FALLS | NO |  | NO | NW 1/4 NWW 1/4 SECT 28 T102N R49W |  | LINE PIPE | PIPE |  | 1946 | OTHER | THE COATING HAD APPARENTL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 231414.6669 | 466856.8552 | GASOLINE | 3 | 25 | 0 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 250 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S L CROPPER | 9185883381 | THE COATING HAD APPARENTLY BEEN DAMAGED WHEN THE PIPE WAS INSTALLED IN THE CASSING; EVENTUALLY CAUSING THE LEAK.
2017-09-29 08:50 | YES | NO | 19870112 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-04-09 | 743 | KS | MIAMI |  | NO |  | NO | NE1/4 NW1/4 SECT 30 T16S R24E |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 14810.5387 | 29878.8387 | GASOLINE | 3 | 580 | 276 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 244 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PHYSICAL LINE STAKING | NO | YES | C K MCCAW | 9185883381 | A BACK HOE OPERATOR EMPLOYED BY KILLOUGH INC OTTAWA KANSAS STRUCK THE #3-8' LINE PUNCTURING IT THE LINE HAD BEEN MARKED BY WILLIAMS PIPE LINE COMPANY PRIOR TO CONTRACTOR BEGINNING WORK
2017-09-29 08:50 | YES | NO | 19870113 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1987-05-01 | 807 | VA | CHESTERFIELD |  | NO |  | NO | TWO THIRDS OF A MILE NORTH OF VA 604(GENITO ROAD) AND APPROXIMATELY 700 FEET SOUTH OF THE CENTERLINE OF VA 76(POWHITE PARKWAY) CURRENTLY UNDER CONSTRUCTION. |  | LINE PIPE | LONGITUDINAL WELD |  | 1964 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 101822.4534 | 205417.0163 | GASOLINE | 3 | 1647 | 325 | NO | NO | 13 | 0.2 | 1655 | WELDED |  | 1080 | 1096 | YES | 26 | 1331 | 6 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R M CROOK | 4042612137 | THE ACCIDENT OCCURRED IN CHESTERFIELD COUNTY VIRGINIA AT 8:07 A.M., EDT ON MAY 11987. PLANTATION'S 12-INCH, .203 WALL THICKNESS, X-52 GRADE PETROLEUM PRODUCTSPIPELINE RUNS NORTH, PARALLEL TO A VIRGINIA POWER HIGH VOLTAGE TRANMISSION LINEBETWEEN THE POWER LINE AND A HEAVILY WOODED AREA. THE LEAK OCCURED JUST SOUTH OF THE CONSTRUCTION AREA FOR VA HIGHWAY 76. THE PIPELINE RUPTURED AT THE 10 O'CLOCK POSITION LOOKING NORTH. THE SPLIT WAS 32 INCHES LONG AND 3 INCHES WIDE AT ITS BROADEST POINT. THE ERW PIPE SEAM WAS AT THE 12 O'CLOCK POSITION. THERE WASNO OPERATIONAL UPSETS AND THE PIPELINE WAS OPERATING WITH IN DESIGN CRITERIA.THE FAILED SECTION OF PIPE REVEALED EVIDENCE OF LAMINATIO. THE ENTIRE JOINT OFPIPE WAS REPLACED. 1647 BARRELSSOF UNLEADED REGULAR GASOLINE ESCAPED INTO THE WOODED AREA. A PORTION OF THE PRODUCT TRAVERSED APPROXIMATELY ONE HALF MILE ALONG A CREEK AND WAS CONTAINED ON EVERGREEN LAKE. THERE WERE NO INJURIES.AS REQUESTED BY DR. DOUGLAS CHISHOLM, CHIEF, RESEARCH UNIT OF THE OFFICE OF PIPELINE SAFETY, A LAB ANALYSIS SF THE FAILED SECTION OF 12 INCH PIPE WILL BE FORWARDED UNDER SEPARATE COVER AS SOON AS IT IS RECIEVED.
2017-09-29 08:50 | NO | NO | 19870114 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1987-05-12 | 1330 | MI | ST CLAIR |  | NO |  | NO | BETWEEN M-29 & MICHIGAN AVENUE AT 18TH STREET EXTENSION MARYSVILLE, MICHIGAN (WEST OF RAILROAD TRACKS) |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 16200 | 14995.6704 | 30252.3242 | CRUDE OIL | 1 | 2 | 0 | NO | NO | 30 | 0.25 | 52000 | WELDED |  | 649 | 200 | YES | 24 | 763 | 11 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J E STAUDOHER | 7153925631 | A SMALL PATCH OF OIL WAS NOTED DURING A ROUTINE AERIAL PATROL BY OPERATOR'S PILOT. MAINTENANCE CREWS RESPONDED EXCAVATED THE LINE AND DISCOVERED A SMALL CORROSION PIT WEEPING OIL. A 30" PLIDCO REPAIR SLEEVE WAS BOLTED ON THE LINE AND WELDED AFTER THE ENTIRE JOINT WAS EXAMINED.
2017-09-29 08:50 | YES | NO | 19870115 |  | 19536 | TOTAL PIPELINE CORP | Null | 1987-04-16 | 700 | OK | CARTER |  | YES | SW1/2 18-4S-1W | NO | FROM LONE GROVE OKLAHOMA 2 MILES NORTH OF HWY 70 ON NEWPORT ROAD AND 4.8 MILES WEST ON PRARIE VALLEY ROAD. |  | TANK FARM | TANK |  | 1960 | OTHER | POWER FAILURE SHUTDN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 6942.44 | 14005.7057 | CRUDE OIL | 1 | 18000 | 150 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM O DELANO | 4052291638
2017-09-29 08:50 | YES | NO | 19870116 |  | 443 | AMOCO PIPELINE CO | NO | 1987-05-19 | 830 | WY | PARK |  | NO |  | YES | LEAK OCCURRED IN THE NW1/4 SW1/4 SECTION 1 T47N R100W PARK COUNTY WYOMING NEAR AMOCO PRODUCTION COMPANY LACT EMBAR #3 LITTLE BUFFALO BASIN APPROXIMATELY 10 MILE |  | PUMPING STATION | PUMP |  | 1983 | OTHER | PUMP PACKING & PLUNGER FA | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 786.8099 | 1587.3133 | CRUDE OIL | 1 | 160 | 157 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD W WHITE | 3072662119 | THE LEAK WAS REPORTED AT 08:30 MAY 19,1987. THE PACKING AND PLUNGER FAILED ON APL'S PUMP AT LACT UNIT EMBAR NO. 3. ABOUT 157 BARRELS OF CRUDE OIL WERE PICKED UP AND PUT BACK INTO THE PIPE LINE SYSTEM WITH VAC TRUCKS. THE REMAINING THREE BARRELS, WHICH MIXED WITH THE SOIL, WERE SCOOPED UP AND SPREAD OUT INSIDE A TANKDIKE AT APL'S LITTLE BUFFALO STATION. THIS DISPOSAL METHOD WAS APPROVED BY THE WYOMING DEQ. NO OIL REACHED WATER. REPAIRS WERE MADE BY REPLACING THE PACKING AND PLUNGER.
2017-09-29 08:50 | YES | NO | 19870117 |  | 443 | AMOCO PIPELINE CO | Null | 1987-05-06 | 1430 | TX | HOCKLEY |  | NO |  | NO | 16 MILES NORTH OF LEVELLAND TEXASON HWY-FM-1490 TURNWEST 1 1/2 MILE STATE CAPITAL LAND LEAGUE 705 LABOR 24 |  | LINE PIPE | TANK | PRODUCER | 0 | OTHER | CHECK VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 150 | 130 | NO | NO | 0 | 0 | 0 | NO DATA |  | 10 | 10 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALBERT L WOOD | 8068946187 | WASHED TANK REPAIRED CHECK VALVE PICKUP OIL & CLEANUP.
2017-09-29 08:50 | YES | NO | 19870118 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-04-04 | 2100 | TX | LIBERTY | EASTGATE | NO |  | NO | THE ACCIDENT WAS AT EASTGATE STATION, WHICH IS LOCATED ON TEXAS STATE HIGHWAY 1960 APPROXIMATELY ONE MILE SOUTHEAST OF EASTGATE. |  | PUMPING STATION | VALVE |  | 1961 | OTHER | CRACK IN CHECK VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4628.2933 | 9337.1371 | CRUDE OIL | 1 | 130 | 110 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D L DENNARD | 2146582226 | AT 2100 ON APRIL 4 1987 THE SEALY TO BEUMONT CRUDE OIL SYSTEM WAS SHUT DOWN DUETO A SHORTAGE TRENS WHICH HAD DEVELOPED. AN UNSUCCESSFUL PRESURE TEST WAS PUT ON THE PIPELINE TO INVESTIGATE THE SHORTAGE. WHILE SEGMENTS OF THE PIPELINE WERE BEING ISOLATED TO FUTHER INVESTIGATE THE SHORTAGE, THE LIBERTY COUNTY SHERIFFSDEPARTMENT REPORTED A CRUDE OIL SPILL EXISTED AT OUR EASTGATE STATION. THE PIPELINEWAS IMMEDIATELY ALLOWED TO DRAIN INTO TANKAGE AT BEAUMONT TO RELIEVE THE PRESSURE ON THE STATION PIPING. INSPECTION REVEALED THAT A CHECK VALVE ON THE DISCHARGE OF THE STATION HAD CRACKED. THE CRACK IN THE CHECK VALVE WAS CAUSED BY EXTERNAL STRESSES. THE CHECK VALVE WAS REPLACED WITH A NEW ONE.THE CRUDE OIL WAS PICKED UP WITH A VACUM TRUCK FROM THE STATION PROPERTY AND A ROADSIDE DITCH PLACED IN THE TANK AT EASTGATE STATION AND REINJECTED INTO PIPELIN
2017-09-29 08:50 | YES | NO | 19870123 |  | 2327 | CHEVRON USA INC | NO | 1987-05-13 | 600 | HI | HONOLULU | PEARL CITY | NO |  | NO | LEAK OCCURRED AT WAIWA SPRINGS BRIDGE MP11.66. THE PIPELINE IS SUPPORTED ALONG THE SIDE OF THE BRIDGE. |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | JET FUEL | 3 | 2500 | 0 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1200 | 700 | YES | 8 | 1500 | 7 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | E K PANEE | 8086825711 | WHITE OIL LINE RUP[TURED SPILLING JET A FEUL INTO WAIAWA SPRINGS WHICH FLOWS INTO PEARL HARBOR MIDDLE LOCK AREA. THE PIPEL;INE WAS SHUTDOWN AND PERMANENT REPAIRS WERE MADE. THE COAST GUARD THE NATIONAL RESPONSE AND THE NAVY'S PEARL HARBOR PORT OPERATIONS WERE NOTIFIED.
2017-09-29 08:50 | YES | YES | 19870124 |  | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1987-04-18 | 1550 | TX | ECTOR | ODESSA | NO |  | NO | APPROX. 0.85 MI NORTH OF ODESSA, TX AND APPROX. 420' EAST OF ANDREWS HWY.(US HWY 385) APPROX. 0.13 MILES SOUTH OF HWY 385/YUKON RD INTERSECTION 6718 ANDREWS HWY |  | LINE PIPE | PIPE |  | 1927 | OTHER | EXACT CAUSE IS UNDER IVES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | CRUDE OIL | 1 | 0 | 0 | YES | NO | 10 | 0.37 | 28000 | WELDED |  | 1000 | 0 | YES | 24 | 650 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT K REED | 5127853571 | THE PIPELINE RUPTUREED AT APPROXIMATELY 3:50 P.M. ON SASTURDAY, APRIL 18, 1987,CAUSING LEAKAGE AND A SUBSEQUENT FIRE. THE PIPELINE WAS INACTIVE T THE TIME THE LATEST PUMPING OPERATION HAVING BEEN COMPLETED ON MARCH 29 1987. THE PIELINE'SPRESSURE, AT THE TIME OF THE RUPTURE, SHOULD HAVE BEEN NO MORE THAN APPROX. 175#THE RUPTURE (21" IN WIDTH) OCCURREDBENEATH THE BACK END OF AN OCCUPIED MOBILEHOME. DEPTH OF COVER OVER THE PIPELINE AT THAT POINT IS APPROX. 35". FUMES FROM THE LEAKAGE RESULTING FROM THE RUPTURE APPARENTLY IGNITED IN THE VICINITY OF THE MOBILE HOME, THE SOURCE OF THE IGNITION BEING UNDETERMINED AT THIS TIME.THE FIRE THAT RESULTED DESTROYED 10 MOBILE HOMES (2 OF WHICH WERE OCUPPIED), INJURED THE OCCUPANTS OF ONE MOBILE HOME AND 7 FIRE FIGHTERS.THE ODESSA FIRE DEPARTMENT WAS NOTIFIED OF THE FIRE AT 3:57 PM 4/18 BY ALARM CALLIN FROM THE PUBLIC SECTOR. AMERICAN PETROFINA PIPE LINE CO WAS NOTIFIED BY THE FIRE DEPARTMENT AT 5:15 PM THROUGH 24-HR CO NUMBER MONITERED AT ITS MIDLAND TEXAS CONTROL CENTER AT 5:20 PM THE MIDLAND CONTROL CENTER NOTIFIED CO. PERSONNEL TO RESPOND. AT 5:53 PM THE NEAREST BLOCK-VALVE EAST OF THE LEAK SITE 1.63 MI WAS CLOSED -OFF AND AT 6:00 PM THE FIRST CO REPRSENTATIVW WAS AT THESCENE OF THE
2017-09-29 08:50 | YES | NO | 19870125 |  | 395 | AMOCO OIL CO | YES | 1987-04-21 | 930 | MO | JACKSON | SUGAR CREEK | NO |  | NO | NW/4 SECTION 27 T50N R32W SUGAR CREEK JACSON COUNTY MO |  | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | LANDSLIDE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 23141.4667 | 46685.6855 | GASOLINE | 2 | 590 | 309 | NO | NO | 8 | 0.25 | 52000 | WELDED |  | 1440 | 1016 | YES | 24 | 1800 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | LANDSLIDE |  | Null | NO DATA |  | Null | Null | MITCHELL B WEISS | 8163311673 | A HEAVY RAINSTORM WHICH OCCURRED EARLY THE MORNING OF APRIL 21 1987TRIGGERED A SERIES OF SLOPE FAILURES RESULTING IN THE FRACTURE OF AMOCOS 8 INCHPIPELINE WITHIN THE CITY LIMITS OF SUGAR CREEK MOINSTRUMENTATION AT THE SUGAR CREEK CONTROL CENTER DETECTED THE POSSIBILITY OF ALEAK AND THE VALVES AND THE SYSTEM WAS SHUT DOWN. PERSONNEL WERE DISPATCH TO CLOSE GATE VALVES AND TO PHYSICALLY WALK THE PIPELINE IN THE SUSPECT AREA BECAUSEOF UNUSUAL GEOLOGICAL CONDITIONS, THE LEAK WAS NOT LOCATED UNTIL 0930 HRS CDT.THE PIPE WAS UNCOVERED AND THE FRACTURED WAS CONFIRMED AT 1145 CDTTHE HIGHLY UNSTABLE NATURE OF THE SOIL CONDITIONS NECESSITATED A 427 FT PIPELINE RELOCATIONS. THE LINE WAS RETURNED TO OPERATION ON APRIL 25, 1987.
2017-09-29 08:50 | YES | NO | 19870126 |  | 26102 | TEXACO INC | YES | 1987-05-12 | 1130 | OK | KAY |  | NO |  | NO | GO NORTH FROM THE TOWN OF MARYLAND TO COWBOY CEMETARY TURN EAST FOR 2 MILE TURN NORTH 1/2 ON WEST SIDE OF ROAD |  | LINE PIPE | VALVE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 185.1317 | 373.4855 | CRUDE OIL | 1 | 370 | 340 | NO | NO | 8 | 0.32 | 1000 | THREADED |  | 600 | 100 | YES | 8 | 750 | 0 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR | Y | Null | NO DATA |  | Null | Null | BOYD C VRATIL | 9182253469 | TEXECO EMPLOYEES WERE IN THE PROCESS OF RECONDITIONING AND LOWERING THIS SECTION OF LINE WHEN OUR BACKHOE STRUCK AN UNKNOWN 2" VALVE ON THE PIPELINE CAUSING THE LEAK
2017-09-29 08:50 | YES | NO | 19870127 |  | 18718 | SUN PIPELINE CO | YES | 1987-04-17 | 1840 | NY | BROOME |  | NO |  | NO | 677 FEET NORTH OF CENTERLINE OFROUTE 79 TOWN OF LISLE BROOM COUNTY NEW YORK |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 316 | 217 | NO | NO | 6 | 0.28 | 30000 | WELDED |  | 1200 | 1085 | YES | 24 | 1800 | 10 | 65 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CLARENCE J YABLONSKI | 2159642523 | SUN PIPE LINE COMPANY DISPATCHER RECIEVED PHONE CALL FROM NEW YORK DEPARTMENTOF ENVIROMENTAL CONSERVATION SPILL ENGINEER INFORMING US THAT THERE WAS A POSSIBLE LEAK NEAR LISLE, NEW YORK.PETROLEUM PRODUCT WAS OBSEVERVED ON DUDLEY CREEKLISNORTH OF LISLE NEW YORK. THE PIPELINE WAS IMMEDIATELY SHUT DOWN AND THE LEAK WAS EVENTUALLY UNCOVERED AND CLAMPED NORTH OF DUDLEY CREEK. APPROXIMATELY 1500 FEET OF NEW PIP INSTALLED REPLACING EXISTING PIPE ON STEEP HILLSIDE
2017-09-29 08:50 | YES | NO | 19870128 |  | 805 | ATLANTIC PIPELINE CORP | YES | 1987-03-31 | 800 | PA | DELAWARE | RIDLEY | NO |  | NO | 200' NORTH OF MACDADE BLVD., PARALLEL TO CRUM CREEK, ON THE NEW INTERSTATE 95 (BLUE ROUTE PROPERTY) |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9256.5867 | 18674.2742 | FUEL OIL | 1 | 119 | 2 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1753 | 7 | YES | 0 | 0 | 12 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | JOHN MUNCE | 2156788005 | AT APPROXIMATELY 0915 HOURS ON MARCH 31,1987, ATLANTIC WAS NOTIFIED THAT FUEL OIL WAS OBSERVED ON THE GROUND NORTH OF MACDADE BLVD., ADJACENT TO CRUM CREEK ON PENN DOT PROPERTY. AT THIS LOCATION, THE ATLANTIC PHILADELPHIA 8" SPUR PIPELINE AND SOHIO'S 8" PIPELINE RUN PARALLEL. THE LINE WAS NOT ACTIVE AT THE TIME. SOHIOWAS CALLED PRIOR TO ATLANTIC AND ARRIVED ON SITE AT 0945. ATLANTIC PERSONNEL ARRIVED A SHORT TIME LATER. MID-ATLANTIC REFINERY SERVICES WERE CALLED TO THE SITEAND RESPONDED WITH 2 VACUUM TRUCKS TO BEGIN SALVAGING. SPILL BOOMS WERE DEPLOYED IN CRUM CREEK AND A RETENTION TRENCH WAS DUG. SALVAGE EFFORTS BEGAN IMMEDIATELY. AT 1300 HOURS, IT WAS DETERMINED THAT THE PROBLEM WAS THE ATLANTIC LINE. IT WAS A TEAR IN THE PIPE AT THE 9:00 POSITION. INVESTIGATION HAS INDICATED THAT THEPIPELINE WAS HIT BY EXCAVATING EQUIPMENT SOMETIME IN THE FALL OF 1986 WHEN A SEWER LINE WAS CONSTRUCTED UNDER THE PIPELINE. THE FULL EXTENT OF DAMAGE TO THE PIPE WAS NOT PROPERLY EVALUATED AND SUBSEQUENTLY FAILED UNDER NORMAL OPERATIONS. TEMPORARY REPAIRS WERE MADE ON THE AFTERNOON OF MARCH 31ST, PERMANENT REPAIRS WERE COMPLETED ON APRIL 2ND. UNDER THE GUIDANCE OF DEPT. OF ENVIRONMENTAL RESOURCESSALVAGING AND CLEAN-UP OPERATIONS ARE ONGOING.
2017-09-29 08:50 | YES | NO | 19870129 |  | 18718 | SUN PIPELINE CO | NO | 1987-07-02 | 1140 | TX | GREGG | WHITE OAK | NO |  | NO | 11,200 FT. DUE NORTH OF U.S. HIGHWAY 80 AND 27, 500 FT. DUEEAST OF U.S. HIGHWAY 281, NEAR WHITE OAK, GREGG COUNTY, TEXAS, SITE OF SPILL IN UNINHABITED AREA. |  | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 46.2829 | 93.3714 | CRUDE OIL | 1 | 532 | 526 | NO | NO | 8 | 0.3 | 35000 | WELDED |  | 600 | 25 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | E.F. MCKINLEY, JR. | 2147570220 | 8" LINE GENERALLY HANDLES A RANGE OF BARRELS PER DAY BETWEEN 0 TO 2500(ESTIMATES) DEPENDING ON HAND RUNS AND/OR TRUCK DELIVERIES. LEAK OCCURRED ON BOTTOM PIPE.CAUSE WAS INTERNAL CORROSION. LEAK OCCURRED BETWEEN AERIAL PATROL FLIGHTS, POSSIBLE THE DAY AFTER THE LAST FLIGHT. THE CRUDE ESCAPED THE LINE THROUGH A SMALL PINHOLE, LEAKING INTO A LOW AREA BETWEEN THE PIPE LINE RO.W. AND A HILL. THE OIL WAS CONTAINED NATURALLY BY THE HIGH GROUND SURROUNDING THE LOW AREA. APPROXIMATELY 532 BARRELS ESCAPED FROM THE 8" PIPELINE AND INTO SAID AREA. SPILL RECOVERY OPERATION COMMENCED IMMEDIATELY UPON THE INITIAL REPORT. RECOVERY AND CLEANUP EFFORTS BEGAN AT 12:30 PM ON JULY 2, 1987 AND WERE COMPLETED WHEN THE TEXAS RAILROAD COMMISSION APPROVED THE CLEAN UP ON JULY 8, 1987. 526 BARRELS WERE RECOVERED AND PLACED BACK INTO SUN PIPE LINE'S THOMAS STATION FACILITY. SIX BARRELS WERE LOST TO OIL ABSORBENT MATERIAL AND BY SOAKING INTO DRY DIRT AREA AROUND THE SPILL AREA. AMOCO PROD. COMPANY, THE LANDOWNER, APPROVED THE CLEANUP AND WAIVED ANY DAMAGE CLAIMS.
2017-09-29 08:50 | YES | NO | 19870130 |  | 13131 | CONOCO INC | YES | 1987-03-31 | 1711 | WY | NATRONA |  | NO |  | NO | SW 1/4, NE 1/4, T30N, R81W |  | LINE PIPE | LONGITUDINAL WELD |  | 1963 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 550000 | 509112.2672 | 1027085.0814 | GASOLINE | 3 | 2172 | 87 | NO | NO | 8 | 0.19 | 52 | WELDED |  | 1631 | 1525 | YES | 24 | 2100 | 11 | 63 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWIGHT D. JACKSON | 7132932100 | AT 1711, 3/31/87, A 400-LB. DECREASE IN DISCHARGE PRESSURE, ALONG WITH AN INCREASE IN FLOW RATE, WAS NOTED AT CASPER STATION. THE PIPELINE WAS SHUT DOWN AT 1712 BY HOUSTON OIL MOVEMENTS. AIR SEARCH OF PIPELINE RIGHT-OF-WAY STARTED AT 1800 AND CONTINUED UNTIL DARK, THEN EMPLOYEES DROVE TO ALL LOCATIONS ALONG PIPELINE ACCESSIBLE BY VEHICLE BUT COULD NOT DETECT ANY PRODUCT OR PRODUCT ODOR. ON APRIL 1, AT 0530, TWO EMPLOYEES WERE DISPATCHED ON ATV'S TO M.P. 278 TO CLOSE THE BLOCK VALVE AND LOOK FOR LEAK ON SOUTH SIDE OF CASPER MOUNTAIN. AT THE SAME TIME, TWO OTHER EMPLOYEES ON SNOWMOBILES WERE DISPATCHED TO LOOK FOR THE LEAK ON CASPER MOUNTAIN. AT 1010, THE NATRONA COUNTY SHERIFF'S DEPARTMENT CONFIRMED A LEAK WITHPRODUCT IN BOLTON CREEK. PRODUCT HAD FOLLOWED BOLTON CREEK AND ENTERED THE NORTH PLATTE RIVER AT A POINT NEAR WHERE THE NORTH PLATTE RIVER CROSSED WYOMING HIGHWAY 220. NUMEROUS CONTAINMENT BOOMS WERE PLACED ACROSS BOLTON CREEK AND THE NORTH PLATTE RIVER. SIPHON DAMS WERE ALSO CONSTRUCTED ON BOLTON CREEK. PRODUCT PICK UP WITH ABSORBENT PADS AND VACUUM TRUCKS WAS STARTED ON A TWENTY-FOUR-PER-DAY SCHEDULE. NINETY-SIX FEET OF PIPE WAS REPLACED AT LEAK SITE WITH 8"-.188" WALL, X-52, ERW PIPE WHICH HAD BEEN PRETESTED. APPROXIMATELY 20' OF PIPE, WHICH INCLUDEDTHE SECTION OF PIPE THAT WAS RUPTURED, WAS SENT TO CONOCO'S RESEARCH AND DEVELOPMENT LABORATORY IN PONCA CITY, OK TO DETERMINE THE EXACT CAUSE OF FAILURE.
2017-09-29 08:50 | YES | NO | 19870131 |  | 24003 | YELLOWSTONE PIPELINE CO | YES | 1987-07-03 | 2154 | MT | SANDERS |  | NO |  | YES | TOWNSHIP 18N, RANGE 23, SECTION 14, APPROXIMATELY 100 YARDS WEST OF YELLOWSTONE PIPE LINE'S AERIAL MARKER 368. |  | LINE PIPE | LONGITUDINAL WELD |  | 1954 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4628.2933 | 9337.1371 | DIESEL FUEL | 3 | 3862 | 0 | NO | NO | 10 | 0.25 | 46000 | WELDED |  | 0 | 0 | YES | 0 | 0 | 1 | 54 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWIGHT D. JACKSON | 7132932100 | CONOCO PIPE LINE COMPANY(OPERATOR OF YELLOWSTONE PIPE LINE), WAS NOTIFIED AT 10:15 P.M., FRIDAY, JULY 3, 1987, BY A LOCAL RESIDENT THAT PRODUCT WAS ESCAPING FROM THE PIPELINEL. THE SEGMENT OF THE PIPELINE IN WHICH THE LEAK OCCURRED HAD ALREADY BEEN SHUT-IN PRIOR TO THE DISCOVERY OF THE LEAK AS A PART OF NORMAL DELIVERY OPERATIONS ALONG THE PIPELINE SYSTEM. UPON NOTIFICATION OF THE LEAK, COMPANY PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE LEAK SITE. AT 11:00 P.M. THE BLOCK VALVE AT AERIAL MARKER 368, LOCATED APPROXIMATELY 100 YARDS WEST OF THE LEAK SITE, WAS CLOSED. COMPANY PERSONNEL SHUT THE UPSTREAM BLOCK VALVE AT 12:00 MIDNIGHT TO ISOLATE THE LINE SEGMENT. CLEAN UP OPERATIONS BEGAN IMMEDIATELY AND THE PIPELINE WAS REPAIRED BY COMPANY AND CONTRACT PERSONNEL. THE HYDROGEOLOGIC CONDITIONSWHICH EXISTED AT THE LEAK SITE WERE SUCH THAT NO PRODUCT WAS RECOVERED. AN ON-SITE ASSESSMENT BY COMPANY ENVIRONMENTAL PERSONNEL INDICATED THAT NO APPARENT SURFACE WATER IMPACT OCCURRED. THE POSSIBILITY OF SOIL AND GROUND WATER IMPACTS ARECURRENTLY BEING EVALUATED BY COMPANY ENVIRONMENTAL PERSONNEL.
2017-09-29 08:50 | YES | NO | 19870132 |  | 26102 | TEXACO INC | YES | 1987-05-30 | 1345 | OK | COTTON |  | NO |  | NO | NORTH EAST QUARTER OF SECTION 14, TOWNSHIP 5 SOUTH, RANGE 10 WEST, COTTON COUNTY, OKLAHOMA |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 349487 | 323505.6708 | 652641.607 | CRUDE OIL | 1 | 19150 | 0 | NO | NO | 24 | 0.5 | 52000 | WELDED |  | 1050 | 660 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | ONE CALL |  | Null | Null | EDWIN H. GRIPP | 8177230761 | DUE TO SEVERE FLOODING, A NEW CHANNEL OF THE RED RIVER WAS FORMED APPROXIMATELY1/4 MILE NORTH OF BASIN PIPELINE'S OVERHEAD CROSSING. THE NEW CHANNEL WAS APPROXIMATELY 700 FEET OF PIPE. ONCE UNSUPPORTED, THE LEAK OCCURRED IN A WELD. ORIGINAL FORM NO. 7000-1 WAS DATED JUNE 9, 1987.
2017-09-29 08:50 | YES | NO | 19870133 |  | 809 | ARCO PIPE LINE CO | Null | 1987-06-13 | 1100 | TX | GAINES |  | NO |  | NO | SECTION 21, PUBLIC SCHOOL LAND SURVEY, BLOCK A-8 , GAINES COUNTY, TEXAS 15 MILES SW OF DENVER CITY, TEXAS, 502' WEST OF AERIAL MARKER #4; STATION 528 + 64 - RUS |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2776.976 | 5602.2823 | CRUDE OIL | 1 | 150 | 25 | NO | NO | 6 | 0.2 | 35000 | WELDED |  | 664 | 74 | YES | 12 | 865 | 12 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | V.P. DRISKI | 3163311300 | FARMER WAS USING TRACTOR WITH "AERATOR" EQUIPMENT OVER LINE. LINE WAS 9 1/2" DEEP. AERATOR WAS WORKING BETWEEN 9" AND 16" DEEP. EQUIPMENT PUNCHED A 1" DIAMETERHOLE IN THE LINE.
2017-09-29 08:50 | NO | NO | 19870134 |  | 443 | AMOCO PIPELINE CO | NO | 1987-06-22 | 1630 | TX | GALVESTON |  | NO |  | NO | 1/2 MILE SOUTH OF INTERCOASTAL WATERWAY AND 250 FT. E. OF HWY. 124 |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 462.8293 | 933.7137 | CRUDE OIL | 1 | 25 | 24 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 200 | 175 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOE NELSON | 2147597131 | LINE IS EXPOSED IN A DITCH CROSSING WHERE TIDAL ACTION CREATES A WET/DRY CONDITION. EVEN THOUGH LINE IS CATHODICALLY PROTECTED, THIS CONDITION OF ALTERNATELY WET/DRY PREVENTS PROTECTION IN THIS AREA.OIL SPILLED ON MARSH LAND, CANAL, INTERCOASTAL WATERWAY AND NATIONAL WILDLIFE REFUGE. CLEAN-UP WAS EFFECTIVVE WITH LITTLE OR NO ENVIRONMENTAL OR PROPERTY DAMAGE. DEFECTIVE PIPE WILL BE REPLACED.
2017-09-29 08:50 | YES | NO | 19870135 |  | 26141 | SHELL OIL CO | NO | 1987-06-16 | 814 | MA | MIDDLESEX | WAYLAND | NO |  | NO | MAINSTONE ROAD AND COLTSWAY IN WAYLAND, MA |  | LINE PIPE | PIPE |  | 1940 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 35 | 16 | NO | NO | 6 | 0.25 |  | WELDED |  | 1200 | 350 | YES | 24 | 1500 | 1 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | G.W. LOYD, JR. | 6186781994 | ON THE MORNING OF 6/16/1987, E.B. ROTONDI & SONS, INC. WERE OPERATING THEIR ROTARY DRILL AT THE INTERSECTION OF MAINSTONE ROAD AND COLTSWAY IN WAYLAND, MA FOR THE PURPOSE OF TRENCHING A CABLE FOR CONTINENTAL CABLEVISION. THEY WERE AWARE OUR LINE WAS THERE AND THE ROAD HAD BEEN MARKED WITH YELLOW REFLECTIVE PAINT AND REGULAR P/L MARKER POLES WERE ADJACENT. THEY FAILED TO CALL SHELL FOR THE LOCATION OF DEPTH AND WERE NOT HAND DIGGING IN A SAFETY ZONE AS PRESCRIBED BY MA ONE CALL SYSTEM (DIG SAFE). NO SHELL REPRESENTATIVE WAS ON HAND TO WITNESS THE CROSSING
2017-09-29 08:50 | YES | NO | 19870136 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1987-05-27 | 245 | WI | COLUMBIA |  | NO |  | NO | OPERATOR'S PUMP STATION LOCATED APPROXIMATELY ONE MILE NORTH OF RIO, WISCONSIN ON LOWVILLE ROAD. |  | PUMPING STATION | BOLTED FITTING |  | 1971 | OTHER | FAILURE OF FLEXITALLIC | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 345000 | 319352.2403 | 644262.4601 | CRUDE OIL | 1 | 3150 | 2450 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.E. STAUDOHARR | 7153925631 | A GASKET ON THE DOWNSTREAM SIDE OF THE STATION HEADER PIPE UPSTREAM OF THE CONTROL VALVE FAILED AT APPROXIMATELY 0245 MST ON MAY 27, 1987. THE OIL RAN ACROSS AFIELD AND ACCUMULATED IN A SMALL LOW SWAMPY AREA. RESTORATION IS CONTINUING AT THIS TIME.
2017-09-29 08:50 | YES | NO | 19870137 |  | 26134 | MOBIL OIL CORP - WEST COAST PIPELINES | NO | 1987-06-08 | 430 | CA | KERN | LEBEC | NO |  | NO | SHOULDER OF LEBEC ROAD, 1/4 MILE SOUTH OF CIRCLE DRIVE IN LEBEC, CALIFORNIA |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 601678.1339 | 1213827.8235 | CRUDE OIL | 1 | 2500 | 2000 | NO | NO | 12 | 0.25 | 2039 | WELDED |  | 1250 | 1100 | YES | 8 | 1660 | 10 | 83 | EXTERNAL | Null | YES | OTHER | LOCALIZED CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | R E ROBBINS MANGER, WEST COAST PIPE LINES | 2133282550 | THE INCIDENT OCCURRED DURNING NORMAL OPERATIONS. THE PIPE WALL HAD APPARENTLY BEEN WEAKENED BY EXTERNAL LOCALIZED CORROSION IN THE AREA WHERE THE PIPE FAILED. IT IS BELIEVED THAT SHIELDING FROM CATHODIC PROTECTION CURRENT WAS DUE TO DISBONDED COATING.
2017-09-29 08:50 | YES | NO | 19870138 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1987-05-23 | 1430 | LA | EAST BATON ROUGE |  | NO |  | NO | PLANTATION PIPE LINE COMPANY'S BATON ROUGE TANK FARM. CORNER OF LA HWY. 19 AND BLOUNT ROAD |  | TANK FARM | VALVE | 1" DRAIN VALVE | 1986 | INCORRECT OPERATION BY OPERATOR PERSONNEL | 1" DRAIN VALVE LEFT OPEN. | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 60167.8134 | 121382.7823 | TURBINE FUEL | 3 | 300 | 300 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R M CROOK V P OPERATIONS | 4042612137 | THREE COMPANY EMPLOYEES CALIBRATED THE PROVER LOOP ON AN INCOMING CONNECTING PIPLINE AT PLANTATION PIPE LINE COMPANY'S BATON ROUGE TANK FARM. AT THE CONCLUSIONOF THIS CALIBRATION PROCESS, ALL THREE EMPLOYEES FAILED TO DETECT A 1" DRAIN VALVE WHICH REMAINED OPEN. OPERATIONS PERSONNEL ALSO MADE TWO SEPARATE CHECKS OF THE PROVER SYSTEM, ONE CHECK WHEN THE WORK WAS COMPLETED AND A SECOND CHECK WHEN THE PIPELINE BEGAN RECEIVING PRODUCT, BOTH CHECKS FAILED TO REVEAL THE 1" VALVEWHICH REMAINED OPEN. THE PIPELINE STARTED AT 18:26 CDST, ON MAY 22, HOWEVER, PRODUCT INITIALLY FLOWED THROUGH THE WATER/PRODUCT SEPARATOR AND INTO THE PRODUCT SUMP. IT WAS ABOUT TWO HOURS BEFORE THIS SUMP FILLED AND FORCED PRODUCT BACK THROUGH THE SEPARATOR AND INTO THE WATER SUMP. THE DRAIN-DRY PUMP IN THE WATER SUMPTHEN EMPTIED THE PRODUCT INTO A DRAINAGE DITCH WHICH FLOWS TO THE FIELD SEPARATOR. (SEE ATTACHED SKETCH DATED 6/17/87.) THE PIPELINE WAS SHUT DOWN AT 11:55 CDST ON MAY 23, HOWEVER, IT WAS 14:30 CDST ON MAY 23 BEFORE AN EMPLOYEE NOTICED THAT THE FIELD SEPARATOR, WHICH IS DESIGNED TO CONTAIN ANY PRODUCT THAT FLOWS ONTO THE GROUND DRUING SUCH AN INCIDENT, HAD PRODUCT ON IT. ALL SPILLED PRODUCT WAS CONTAINED ON THIS FIELD SEPARATOR AND ALL THE PORDUCT WAS RECOVERED AND RETURNED TO A TANK. PLANTATION PIPE LINE COMPANY'S MANAGEMENT WAS NOT AWARE OF THE SPILL UNTIL MAY 26. INITIAL INVESTIGATION REVEALED LESS THAN 50 BARRELS SPILLED. FURTHE
2017-09-29 08:50 | YES | NO | 19870139 |  | 22907 | WYCO PIPE LINE CO | YES | 1987-05-08 | 845 | WY | NATRONA | CASPER | NO |  | NO | JUST WEST OF CITY STREET "BRYAN STOCK TRAIL" NORTH SIDE OF CITY |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 69424.4001 | 140057.0566 | GASOLINE | 2 | 100 | 10 | NO | NO | 8 | 0.19 |  | NO DATA |  | 1000 | 300 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | YES | Null | RONALD A WENKE FIELD SUPERVISOR | 3072346586 | PIPELINE WAS HIT BY A JOHN DEERE 544 FRONT END LOADER. HOLE IN PIPELINE WAS 1 1/2" WIDE BY 3" LONG.
2017-09-29 08:50 | YES | YES | 19870140 |  | 3466 | DOME PIPELINE CORP | YES | 1987-07-14 | 940 | MN | TRAVERSE |  | NO |  | NO | WHEATON STATION (SEE ATTACHED MAP) WHICH IS LOCATED 5.5 MILES NORHT OF WHEATON, MN, ON HIGHWAY 75. |  | PUMPING STATION | VALVE |  | 1978 | OTHER | INCORRECT MAINTENANCE PRO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | L. P. G. | 3 |  | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J L WILLIAMS OPERATION MANAGER | 3193547722 | STATION WAS SHUT DOWN AND THE PIPING WAS BLOWN DOWN SO VALVE MAINTENANCE COULD BE PERFORMED. FIRE OCCURRED WHEN EMPLOYEE DID NOT FOLLOW THE WRITTEN PROCEDURED FOR VALVE MAINTENANCE, AND USED A VACUUM CLEANER TO CLEAN THE INSIDE OF THE VALVE BODY. FLASH FIRE OCCURRED IMMEDIATELY UPON STARTING THE VACUUM CLEANER TO CLEAN THE INSIDE OF THE VALVE BODY. EMPLOYEE'S USE OF AN ELECTRICAL ARCING DEVICE IN AN EXPLOSIVEATMOSPHERE RESULTED IN THE EMPLOYEE OBTAINING FIRST DEGREE BURNS ON HIS FOREARMS, FACE, AND NECK. EMPLOYEE WAS TAKEN TO THE NEAREST HOSPITAL FOR TREATMENT. BECAUSE OF THE CONCERN FOR INFECTION, HE WAS HOSPITALIZED FOR APPROXIMATELY ONE WEEK
2017-09-29 08:50 | YES | NO | 19870141 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1987-05-12 | 2250 | LA | BIENVILLE | CASTOR | NO |  | NO | CASTOR, LOUISIANA PUMP STATION; VICINITY MAP, TPA-V-20 ATTACHED; 14" LINE P62 |  | PUMPING STATION | OTHER | CHECK VALVE FLANGE GASKET | 1980 | OTHER | GASKET FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3239.8053 | 6535.996 | FUEL OIL | 3 | 930 | 930 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM M OLLER EXECUTIVE V P | 7137593605 | FLANGE GASKET ON UPSTREAM SIDE OF PUMP DISCHARGE CHECK VALVE FAILED, RELEASING #2 OIL ON GROUND. PRODUCT WAS CONTAINED BY A CONTAINMENT POND ON THE PUMP STATION PROPERTY. NO PRODUCT ESCAPED FROM THE PROPERTY.
2017-09-29 08:50 | YES | NO | 19870143 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1987-06-29 | 458 | AR | LAWRENCE |  | NO |  | Null | RURAL AREA-OUR EGYPT (WALNUT RIDGE), ARKANSAS PUMP STATION FACILITY LOCATED IN LAWRENCE COUNTY T15N-R2E IN THE NORTHWEST QUARTER OF SECTION 20. VICINTY MAP TPA- |  | PUMPING STATION | OTHER | 3/4" PIPE NIPPLE ON PUMP | 1980 | OTHER | 3/4" PIPE NIPPLE, ON MAIN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3700 | 3424.9371 | 6909.4815 | FUEL OIL |  | 645 | 642 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM M OLLER EXECUTIVE V P | 7137593605 | PUMP UNIT ON OUR 16"LINE P-62 AT OUR UNMANNED REMOTE STATION IDENTIFIED AS "EGYPT STATION", WAS TAKEN DOWN BY OUR HIGH GAS VAPOR ALARM ON JUNE 29, 1987 AT 04:58 HOURS. OUR AREA REPRESENTATIVE WAS DISPATCHED TO THE STATION AND STOPPED THE PRODUCT FLOW BY CLOSING THE NECESSARY VALVES. OUR MAINTENANCE CREW ARRIVED AND DAMMED THE AREA OFF. TANK TRUCKS WERE ORDERED AND ALL OF THE RECOVERABLE FUEL OIL WAS COLLECTED AND THE AAREA WASHED DOWN.
2017-09-29 08:50 | YES | NO | 19870144 |  | 4906 | EXXON PIPELINE CO | YES | 1987-06-13 | 1730 | TX | FREESTONE | FAIRFIELD | NO |  | NO | LEAK OCCURRED AT STATION 2326+80 (NEAR MIMS CREEK) 23 MILES EAST OF GROESBECK STATION ON THE NECHES JCT.-GROESBECK 8" LINE. |  | LINE PIPE | PIPE |  | 1936 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 8330.928 | 16806.8468 | CRUDE OIL | 1 | 80 | 78 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 640 | 20 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY | 7136565956 | A LEAK WAS REPORTED BY MIKE DANIELS, SON OF PROPERTY OWNER DOYLE DANIELS, AT APROXIMATELY 5:30 P.M. ON 6-13-87 ON THE 8" NECHES JCT.-GROESBECK TRUNK LINE. THE PIPELINE WAS NOT IN OPERATION AT THE TIME AND WAS BELIEVED TO HAVE BETWEN 15-20 PSI LINE PRESSURE AT THE TIME OF THE LEAK. A MAINTENANCE CREW WAS DISPATCHED FROM LONGVIEW WHILE MR. DANIELS, OWNER OF D & W OILFIELD CONSTRUCTION, EXCAVATED THE LEAK SITE. THE OIL WAS COMING GROM A HOLE IN THE PIPE AS THE RESULT OF EXTERNAL CORROSION IN AN OVERBEND WHERE THE PIPELINE WAS EXPOSED. THE OIL RAN DIRECTLY INTO A SMALL CREEK, MIMS CREEK, AND TRAVELED APPROXIMATELY 1/2 MILE DOWNSTREAM BEFORE IT COULD BE CONTAINED. AFTER ARRIVING ON THE SCENE, THE MAINTENANCE CREW INSTALLED BOOMS AND FLUME PIPES IN THE CREEK TO PREVENT FURTHER CONTAMINATION WHILE THE LEAK WAS TEMPORARILY REPAIRED BY INSTALLING LEAK CLAMPS. PALESTINE CONTRACTORS WERE CALLED TO PROVIDE VACUUM TRUCK SERVICE FOR PICKING UP THE OIL. THE CLEAN-UP OPERATIONS HAVE SINCE BEEN COMPLETED WHILE PERMANENT REPAIRS ARE STILL PENDING.
2017-09-29 08:50 | YES | NO | 19870145 |  | 4906 | EXXON PIPELINE CO | NO | 1987-05-19 | 1130 | TX | MONTGOMERY |  | NO |  | NO | LEAK OCCURRED AT THE SCRAPER TRAP LOCATED INSIDE EXXON'S CONROE GAS PLANT. THIS SCRAPER TRAP IS ON EXXON PIPELINE'S CONROE TO SATSUMA LPG PR |  | LINE PIPE | VALVE |  | 1969 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 694.244 | 1400.5706 | L. P. G. | 2 | 45 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY | 7136565956 | AT APPROXIMATELY 1130 HOURS ON MAY 19,1987, TWO EXXON PIPELINE COMPANY (EPC) EMPLOYEES WERE USING A TAPPING MACHINE TO TAP THROUGH A ONE-INCH BALL VALVE ON THESCRAPER TRAP BARREL WHEN THE TOP SECTION BLEW OFF THE TAPPING MACHINE AND LPG WAS RELEASED TO THE ATMOSPHERE. EXXON PERSONNEL IMMEDIATELY SHUT DOWN THE SYSTEM AND CLOSED THE ONE-INCH BALL VALVE STOPPING THE RELEASE. THE EPC CREW HAD BEEN INSTALLING A VENT VALVE ON THE SCRAPER TRAP BARREL TO BRING THE TRAP INTO COMPLIANCE WITH DOT RULE 195.426. A THREAD-O-LET HAD BEEN WELDED ON THE LINE WITH THE TRAP WET, THE NIPPLE AND BALL VALVE INSTALLED AND THE TAPPING MACHINE SET TO CUT.THE TAP WAS MADE BUT THE BIT WOULD NOT WITHDRAW ENOUGH TO ALLOW CLOSURE OF THE BALL VALVE AND SECTION OF THE MACHINE UPWARD. THE THREADS AND STOP BUSHING OF THE TOP BODY SECTION FAILED AND THE TOP SECTION BLEW OFF THE TAPPING MACHINE. LPG WAS RELEASED TO THE ATMOSPHERE UNTIL THE BALL VALVE WAS CLOSED.
2017-09-29 08:50 | YES | NO | 19870146 |  | 2552 | COLONIAL PIPELINE CO | YES | 1987-05-21 | 500 | NC | MECKLENBURG | CHARLOTTE | NO |  | NO | COLONIAL PIPELINE COMPANY CHARLOTTE DELIVERY FACILITY KENSTEAD CIRCLE, PAW CREEK, NC 28130 |  | NO DATA | NO DATA | TANK EXTERNAL FLOATING RO | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1851.3173 | 3734.8548 | GASOLINE | 3 | 5770 | 3361 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | NO DATA | ATMOSPHERIC CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. SORROW | 4042611470 | THE COLONIAL OPERATOR AT THE CHARLOTTE DELIVERY FACILITY NOTED TANK GAUGE LEVELFOR TANK NO.734 HAD DROPPED 2.36 FEET SINCE COMPLETION OF A DELIVERY INTO THE TANK. UPON INVESTIGATION, A FULL STREAM OF GASOLINE WAS FOUND TO BE COMING FROM THE FLOATING ROOF DRAIN LINE AND THE DIKE FLOOR WAS COVERED WITH GASOLINE PREVENTING THE OPERATOR FROM CLOSING THE ROOF DRAIN VALVE AT THE TANK. THE DIKE DRAIN VALVE WAS ALREADY IN THE CLOSED POSITION AND ALL OF THE PRODUCT WAS CONTAINED INSIDE THE DIKE. THE OPERATOR RETURNED TO THE CONTROL ROOM AND REMOTELY TRANSFERREDTHE PRODUCT IN THE TANK TO OTHER AVAILABLE TANKS. THE GASOLINE WAS THEN COVEREDWITH FIRE FIGHTING FOAM TO REDUCE EVAPORATION AND THE POSSIBILITY OF A FIRE. THEN WATER WAS INTRODUCED INTO THE DIKE TO PREVENT THE PRODUCT FROM SOAKING INTO THE SOIL. A TOTAL OF 5,770 BARRELS OF GASOLINE WAS SPILLED INTO THE DIKE WITH 3,361 BARRELS BEING RECOVERED AND RETURNED TO THE SYSTEM. THE DEFECTIVE DRAIN LINE WILL BE REMOVED FROM THE TANK AND REPLACED WITH NEW GALVANIZED COATED PIPE.
2017-09-29 08:50 | YES | NO | 19870147 |  | 2552 | COLONIAL PIPELINE CO | YES | 1987-06-11 | 947 | VA | FAIRFAX |  | NO |  | NO | SINGLETON'S WAY IN SINGLETON'S GROVE SUBDIVISION NEAR CENTREVILLE, VIRGINIA |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 370 | 118 | NO | NO | 32 | 0.28 | 52000 | WELDED |  | 657 | 190 | YES | 24 | 789 | 12 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | J.S. SORROW | 4042611470 | A CONTRACTOR WAS OPERATING A D-9 BULLDOZER TO PULL A ROCK RIPPER (PLOW) TO FACILITATE GRADING FOR A SIDE WALK TO BE CONSTRUCTED ACROSS THE COLONIAL PIPELINE RIGHT-OF-WAY IN THE SINGLETON'S GROVE SUBDIVISION. THE RIPPER STRUCK AND PUNCTUREDTHE 32" DIAMETER GREENSBORO, NORTH COROLINA TO DORSEY JUNCTION, MARYLAND PIPELINE AT 0947 HOURS EDT ON JUNE 11, 1987. PRIOR TO THE START OF CONSTRUCTION IN THEDEVELOPMENT THE PIPELINE HAD 38" OF COVER OVER THE PIPE, BUT GRADING ACTIVITY BEFORE THE ACCIDENT OCCURRED HAD LEFT APPROXIMATELY 30" OF COVER OVER THE PIPE ATTHE TIME OF THE PUNCTURE. A LINE MARKER WAS IN PLACE AND PLAINLY VISIBLE 25.5 FET FROM THIS POINT. THE PIPELINE WAS TRANSPORTING UNLEADED GASOLINE AT A PRESSURE OF 190 PSI AND FLOW RATE OF APPROXIMATELY 14,300 BPH WHEN THE INCIDENT OCCURRED. GASOLINE SPEWED FROM THE PIPE FOR ABOUT THREE MINUTES AND WAS BLOWN BY THE WIND AWAY FORM THE TRACTOR, OVER THE CONSTRUCTION OFFICE ABOUT 100 FEET FROM THE RUPTURE AND DISPERSED INTO A WOODED AREA OF ABOUT THREE ACRES. A COLONIAL PIPELINE COMPANY EMPLOYEE HAD JUST ARRIVED AT THE CONSTRUCTION OFFICE TO INQUIRE ABOUT THE LOCATION OF ANOTHER CONSTRUCTION PROJECT WHEN THE ACCIDENT HAPPENED. THE EMPLOYEE IMMEDIATELY RAN TO EQUIPMENT BEING OPERATED IN THE GENERAL AREA WARNING THE OPERATORS TO SHUT DOWN THEIR MACHINES AND VACATE THE AREA. THE EMPLOYEE THEN OPTAINED A RIDE TO THE FIRE STATION A FEW BLOCKS AWAY TO NOTIFY THE FAIRFAX COUNTY
2017-09-29 08:50 | YES | NO | 19870148 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-06-29 | 1015 | CO | GARFIELD |  | NO |  | YES | TOWNSHIP 5 SOUTH RANGE 103 WEST |  | LINE PIPE | NO DATA |  | 1981 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 467.4576 | 943.0508 | NATURAL GAS LIQUID | 2 | 10000 | 0 | NO | NO | 10 | 0.21 | 2299 | WELDED |  | 1650 | 810 | YES | 24 | 2243 | 11 | 80 | NO DATA | Null | Null | NO DATA |  | NO DATA | GROUND SHIFT | Null | NO DATA |  | Null | Null | S.F. ISAACS | 9185811800 | LINE PIPE SEPARATED DUE TO GROUND SHIFT. METALLURGICAL REPORT PENDING
2017-09-29 08:50 | YES | YES | 19870149 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-06-26 | 1100 | IA | CEDAR | ROCHESTER | NO |  | YES | TOWNSHIP 79 NORTH, RANGE 2 WEST |  | LINE PIPE | NO DATA |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 1 | 0 | 1 | 2 | 0 | 2 | 384 | 355.4529 | 717.0921 | L. P. G. | 2 | 10 | 0 | NO | NO | 8 | 0.19 | 2266 | WELDED |  | 1504 | 170 | YES | 24 | 1962 | 9 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | S.F. ISAACS | 9185811800 | CONTRACTOR WAS DIGGING DITCH FOR INSTALLATION OF DRAIN TILE. PIPELINE WAS CUT WITH DITCHING MACHINE.
2017-09-29 08:50 | YES | NO | 19870150 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-07-11 | 845 | TX | KENT |  | NO |  | NO | KENT COUNTY, SECTION 166, BLOCK G |  | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3402 | 3149.0908 | 6352.9881 | NATURAL GAS LIQUID | 2 | 167 | 0 | NO | NO | 4 | 0.13 | 1944 | WELDED |  | 1400 | 672 | YES | 24 | 1913 | 10 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | COMPANY EMERGENCY | NO | NO | S.F. ISAACS | 9185811800 | CONTRACTOR CUT PIPE WITH DOZER
2017-09-29 08:50 | YES | NO | 19870151 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-07-09 | 2030 | TX | TYLER |  | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1945 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 7405.2693 | 14939.4194 | GASOLINE | 2 | 30 | 10 | NO | NO | 12 | 0.38 |  | WELDED |  | 650 | 260 | YES | 24 | 1174 | 6 | 71 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH | 4018393100 | NEARBY LANDOWNER REPORTED THE LEAK TO THE HOUSTON DISPATCHING OFFICE AT 5:55 P.M., AND SYSTEM WAS SHUTDOWN AT 6:00P.M. INCIDENT WAS CONFIRMED AT 8:30P.M. ALL CONCERNED FEDERAL AND STATE AGENCIES WERE INFORMED OF THE INCIDENT BY 9:30P.M. EXTERNAL CORROSION CAUSED THE INCIDENT AND PART OF IT SEEPED INTO A NEARBY CREEK BRANCH. PRODUCT WAS RECOVERED BY VACUUM TRUCKS AND ABSORBENT PADS AND WAS RETURNED FOR STORAGE. PLIDCO SLEEVE WAS WELDED TO THE PIPE FOR PERMANENT REPAIRS.
2017-09-29 08:50 | NO | NO | 19870152 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-05-27 | 610 | TX | JEFFERSON |  | NO |  | NO | 2 MILES S.E. OF HWY. 69 ON W. PT. ARTHUR ROAD |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 6 | 6 | NO | NO | 10 | 0.37 |  | WELDED |  | 0 | 450 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH | 4098393100 | LEAK WAS CAUSED BY EXTERNAL CORROSION. IT WAS CONFIRMED ON THE COMPANY PROPERTY. RECOVERED MATERIAL WAS RETURNED TO TANKAGE. LEAK WAS CLAMPED. CORRODED SECTIONIS SCHEDULED FOR CUT-OUT AND REPLACEMENT IN JUNE.
2017-09-29 08:50 | YES | NO | 19870153 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-07-23 | 1000 | TX | JEFFERSON | BEAUMONT | NO |  | NO | 2-1/2 MILES SOUTH OF HWY. 287 ON W. PT. ARTHUR ROAD |  | TANK FARM | TANK |  | 1962 | OTHER | UNKNOWN;CRACK AT BOTTOM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2314.1467 | 4668.5686 | CRUDE OIL | 3 | 100 | 99 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH | 4098393100 | LEAK WAS DISCOVERED 10:00A.M. 7/23/87 BY A TANK INSPECTOR. CRUDE WAS CONTAINED INSIDE THE FIREWALL AND RECOVERED BY VACUUM TRUCK. IT WAS RETURNED TO TANKAGE. TANK 1101 WAS EMPTIED SO THAT IT WILL GE GAS FREED, CLEANED AND REPAIRED AT A LATER DATE.
2017-09-29 08:50 | YES | NO | 19870154 |  | 443 | AMOCO PIPELINE CO | YES | 1987-06-23 | 500 | WY | PARK |  | NO |  | YES | LEAK OCCURED IN THE SW 1/4 OF SECTION 15, T51N, R101W, PARK COUNTY, WY, AT AMOCO PIPELINE'S OREGON STATION. STATION SITE IS ABOUT 13 MILES SOUTH OF CODY, WY. |  | PUMPING STATION | TANK |  | 1944 | OTHER | TANK EQUIP MALFUNCTIONED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 2591.8443 | 5228.7968 | CRUDE OIL | 1 | 2300 | 2297 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.W. WHITE | 3072662119 | THE SPILL WAS DISCOVERED AT 0500 JUNE 23,1987. THE TANK GAUGE MALFUNCTIONED ON TANK 6757 AT OREGON STATION ALLOWING THE TANK TO OVERFILL. ALL SPILLED OIL WAS CONTAINED INSIDE THE DIKE THAT SURROUNED THE TANK. APPROXIMATELY 2297 BARRELS WERE PICKED UP AND PUT BACK INTO THE PIPELINE SYSTEM WITH VAC TRUCKS. ABOUT 3 BARRELS SOAKED ONE TO TWO INCHES INTO THE GROUND, WHICH WAS VERY HARD. THIS OIL WAS SUBSEQUENTLY WORKED INTO THE SOIL. NO OIL REACHED WATER. THE TANK LEVEL GAUGE WAS
2017-09-29 08:50 | YES | NO | 19870155 |  | 443 | AMOCO PIPELINE CO | YES | 1987-05-30 | 810 | OK | LOVE |  | NO |  | NO | RED RIVER CROSSING, PW HUMPHREY SURVEY A-446 COOKE CO. TEX. 5 MI. NW, DEXTER, TEXAS. SECTION 19 T85-R2E, LOVE COUNTY OK. |  | LINE PIPE | NO DATA |  | 1965 | OTHER | PIPE BROKEN BY FLOOD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9256.5867 | 18674.2742 | CONDENSATE - WATER | 3 | 1500 | 0 | NO | NO | 8 | 0.34 | 35000 | WELDED |  | 1400 | 300 | YES | 8 | 1750 | 0 | 65 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. WILHELM | 9182257271 | AMOCO'S 8" YANTIS-HEALDTON LINE AT THE RED RIVER CROSSING WAS WASHED OUT IN THESOUTH BANK AND PULLED IN TWO DURING A TIME OF HEAVY FLOODING. THE CROSSING IS IN PROGRESS NOW OF BEING REPLACED BY THE BORING METHOD WITH APPROXIMATELY 2600 FT. OF 8 4/8" OD O.500" WALL APILX42 STEEL PIPE WITH PLASTIC COATING. THE NEW CROSSING WILL BE 25FT BELOW THE RIVER BOTTOM.
2017-09-29 08:50 | YES | NO | 19870156 |  | 443 | AMOCO PIPELINE CO | YES | 1987-05-20 | 1000 | OK | POTTAWATOMIE |  | NO |  | NO | NW/4, SEC19, T8N, R3E, POTTAWATOMIE COUNTY OKLAHOMA. 2 3/4 NORTH, AND 1 MILE EAST OF TRIBBEY OK. |  | LINE PIPE | PIPE |  | 1918 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 120 | 100 | NO | NO | 6 | 0.25 |  | NO DATA |  | 823 | 0 | YES | 24 | 1038 | 5 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | NORMAN E WEST | 8178766167 | AN EQUIPMENT OPERATOR OF FARRAH CONSTRUCTION, HIT OUR LINE WITH A LAND SCRAPER.THEY CONTAINED THE OIL SPILLED AND CONTACT AMOCO PIPELINE CO.
2017-09-29 08:50 | YES | NO | 19870157 |  | 809 | ARCO PIPE LINE CO | YES | 1987-06-29 | 1330 | TX | MONTAGUE |  | NO |  | NO | 8 MILES SOUTH OF BOWIE, TEXAS, PIPELINE STATION #1270+31 |  | LINE PIPE | NO DATA |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 1203.3563 | 2427.6556 | CRUDE OIL | 1 | 59 | 0 | NO | NO | 8 | 0.32 | 24000 | THREADED |  | 410 | 170 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | N.R. BENNETT | 3163311300 | LEAK ON LINE CAUSED BY EXTERNAL GALVANIC CORROSION. 59 BBLS CRUDE OUT AND LOST.
2017-09-29 08:50 | NO | NO | 19870158 |  | 26086 | SEADRIFT PIPELINE CORP | NO | 1987-06-18 | 1830 | TX | MATAGORDA |  | NO |  | NO | 7.5 MILES WEST OF MARKHAM, ONE MILE SOUTH OF FARM ROAD 1468. |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 17800 | 16476.7243 | 33240.2081 | L. P. G. | 2 |  | 0 | NO | NO | 6 | 0.25 | 42000 | WELDED |  | 1864 | 1100 | YES | 24 | 2330 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. WYATT | 5125533176 | THE LEAK WAS DETECTED BY A LOCAL FARMER WHO NOTICED GAS BUBBLING THROUGH THE WATER IN THE DRAINAGE DITCH. A VISUAL INSPECTION SHOWED THE LEAK TO BE IN A SECTION CONTAINING LOCALIZED CORROSION. APPROXIMATELY 15' OF PIPE WAS REPLACED WITH NEW PIPE. FURTHER INSPECTION INDICATED THE LEAK COULD NOT BE CALCULATED BUT WAS ESTIMATED TO BE ABOVE THE REPORTABLE QUANTITY OF 5 BARRELS PER DAY. THE LPG VAPORIZED INTO THE ATMOSPHERE.
2017-09-29 08:50 | YES | NO | 19870159 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-03-23 | 615 | LA | PLAQUEMINES | PILOTTOWN | NO |  | NO | PILOTTOWN STATION LAT 29-11-9 LONG 80-15-9 |  | PUMPING STATION | PUMP |  | 1958 | OTHER | MECHANICAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 8330.928 | 16806.8468 | CRUDE OIL | 1 | 80 | 80 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN | 7132416262 | CRACK DEVELOPED IN PUMP HEAD, RELEASING CRUDE OIL. OIL WAS CONTAINED ONSITE ANDRECOVERED.
2017-09-29 08:50 | YES | NO | 19870160 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-06-15 | 800 | TX | REAGAN | MIDKIFF | NO |  | NO | DRIVER PUMP STATION SW 1/4, SE 1/4, SECTION 30, T-5-S, BLOCK 36 SIX MILES EAST OF MIDKIFF ON HIGHWAY 2401 |  | PUMPING STATION | PUMP |  | 1952 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4370 | 4045.1284 | 8160.6578 | CRUDE OIL | 2 | 9092 | 0 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 700 | 350 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKINGS, AIR PATROL | NO | NO | HOWARD JANZEN | 9185883850 | AT APPROXIMATELY 1550 HOUEA ON MAY 21, 1987, WILLIAMS PIPE LINE COMPANY'S PLATTSBURG-DES MOINES #4-12" PIPELINE WAS PUNCTURED BY A ROPAD GRADER JUST SOUTH OF PATTONSBURG, MISSOURI, AT MP 68+13. THE LINE WAS DOWN AND LOCKED IN WHEN THE DAMAGE OCCURRED. GATE VALVES ON EITHER SIDE OF THE PUNCTURE WERE CLOSED, THE PUNCTURE AREA WAS ISOLATED AND THE PROPANE WAS BLED OFF. A TOTAL OF 9092 BARRELS OF PRODUCT WAS BLOWN DOWN. REPAIRS WERE COMPLETED AT APPROXIMATELY 2000 HOURS ON MAY 23, 1987, AND THE LINE WAS REPRESSURED AT THAT TIME.
2017-09-29 08:50 | YES | NO | 19870161 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-05-21 | 1550 | MO | DAVIESS |  | NO |  | NO | ACCIDENT OCCURRED AT A TOWNSHIP ROAD IN THE SW/T OF THE SE/4, SECTION 17, TOWNSHIP 60 N, RANGE 29 W, DAVIESS CO MISSOURI. CLOSEST RESIDENCE IS 1/4 MILE FROM LAK |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 92565.8668 | 186742.7421 | L. P. G. | 2 | 9092 | 0 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 700 | 350 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | LINE MARKINGS, AIR PATROL | NO | NO | HOWARD JANSEN V P | 9185883850 | AT APPROXIMATELY 1550 HOUR ON MAY 21, 1987, WILLIAMS PIPE LINE COMPANY'S PLATTSBURG-DES MOINES #4-12" PIPELINE WAS PUNCTURED BY A ROAD GRADER JUST SOUTH OF PATTONSBURG, MISSOURI, AT MP 68+13. THE LINE WAS DOWN AND LOCKED IN WHEN THE DAMAGEOCCURRED. GATE VALVES ON EITHER SIDE OF THE PUNCTURE WERE CLOSED, THE PUNCTURE AREA WAS ISOLATED AND THE PROPANE WAS BLED OFF. A 12" SECTION OF LINE WAS REMOVED AND ONE SET OF FLANGES WAS INSTALLED. A TOTAL OF 9092 BARRELS OF PRODUCT WAS BLOWN DOWN. REPAIRS WERE COMPLETED AT APPROXIMATELY 2000 HOURS ON MAY 23, 1987, AND THE LINE WAS REPRESSURED AT THAT TIME.
2017-09-29 08:50 | NO | NO | 19870162 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-05-24 | 730 | NE | BURT |  | NO |  | NO | N 1/2, NE 1/4, S8, T22N, R11E, LOCATED 3/4 MILE FROM NEAREST DWELLING. |  | LINE PIPE | BOLTED FITTING |  | 1941 | OTHER | SMALL PINHOLE IN PLIDCO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9256.5867 | 18674.2742 | L. P. G. | 2 | 1 | 0 | NO | NO | 6 | 0.22 | 35000 | WELDED |  | 1450 | 400 | YES | 8 | 1830 | 9 | 85 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN | 9185883850 | ON THE MORNING OF 5/24/87, THE IRVINGTON MAINTENANCE CREW DISCOVERED A SMALL PROPANE LEAK IN THE #2-6" OMAHA TO SIOUX CITY LINE AT MP 205+6. A SMALL PINHOLE LEAK WAS DETECTED ON A PLIDCO END COUPLING WELD. A STOPPLE MACHINE WAS USED TO INSTALL A NEW SPOOL AND THE LINE WAS RETURNED TO SERVICE ON 5/27/87.
2017-09-29 08:50 | NO | NO | 19870163 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-07-15 | 1635 | NE |  | FALLS CITY | NO |  | NO | FALLS CITY PUMP STATION |  | PUMPING STATION | OTHER | FILLET WELD ON EXISTING | 1950 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 11107.904 | 22409.129 | GASOLINE | 3 | 1 | 0 | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 1450 | 1100 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN | 9185883850 | ON JULY 15TH, 1987, A LEADED REGULAR GASOLINE LEAK WAS DISCOVERED IN THE GATE VALVE BOX AT MILE POST 95+11 ON THE MAINLINE SIDE OF THE OUTGOING STATION ISOLATION VALVE. A CRACKED FILLET WELD ON AN EXISTING PATCH WAS THE CAUSE OF THE LEAK. A FOUR FOUR (4') SPOOL OF NEW PIPE WAS INSTALLED AND THE LINE WAS RETURNED TO SERVICE ON JULY 16, 1987.
2017-09-29 08:50 | YES | NO | 19870164 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-07-12 | 1920 | MN |  | MINNESOTA | NO |  | NO | TANK #820 |  | TANK FARM | NO DATA |  | 1950 | OTHER | BURN THROUGH FLOOR PLATE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 18513.1734 | 37348.5484 | FUEL OIL | 3 | 104 | 15 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN | 9185883850 | WPL'S TANK #820 AT MINNEAPOLIS TERMINAL HAD RECENTLY BEEN CLEANED AND COATED. ON JULY 4TH, THREE(3) OF PRODUCT WAS PUT INTO THE TANK FOR A FINAL VERIFICATION OF THE INTEGRITY OF THE TANK BOTTOM. ON JULY 12TH, 1987, FUEL OIL WAS DISCOVERED AROUND THE OUTSIDE PERIMETER OF THE TANK. AN INVESTIGATION OF THE INCIDENT REVEALED A BURN THROUGH APPARENTLY OCCURRED WHILE THE CONTRACTOR WAS MODIFYING THE BASE OF THE ROOF SUPPORT COLUMN. CLEAN UP OPERATIONS ARE BEING COORDINATED WITH THE MPCA.
2017-09-29 08:50 | NO | NO | 19870165 |  | 22610 | WILLIAMS PIPELINE CO | NO | 1987-04-08 | 1405 | NE | PALMYRA |  | NO |  | NO | T9N R9E S26 SE 1/4 SE 1/4, NEAR CITY OF PALMYRA |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 23141.4667 | 46685.6855 | GASOLINE | 3 | 30 | 0 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1500 | 275 | YES | 24 | 1500 | 8 | 54 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS, AERIAL | NO | NO | H.E. JANZEN | 9185883850 | A LEAK WAS DISCOVERED ON APRIL 8, 1987, AT MILEPOST 24+19 BY A LOCAL FARMER. THE LINE WAS SHUT DOWN AND GATE VALVES WERE CLOSED TO ISOLATE THE LEAK. PREVIOUS THIRD PARTY DAMAGE WAS IDENTIFIED AS THE CAUSE OF THE FAILURE. PERMANENT REPAIRS WERE COMPLETED, AND THE LINE RESUMED OPERATION ON APRIL 10, 1987. OFFICIALS FROMTHE NEBRASKA DEPT. OF ENVIRONMENTAL CONTROL (NDEC) INSPECTED THE LEAK SITE AND REQUIRED THAT A SITE ASSESSMENT BE COMPLETED AND A WRITTEN REPORT SUBMITTED TO THEIR DEPT. FOR REVIEW. THE NDEC APPROVED OUR PROPOSAL FOR ASSESSMENT ON JUNE 5, 1987. BASED ON THIS APPROVED PLAN, THE TOTAL CLEAN UP IS ESTIMATED TO BE $25,000.UNTIL THE TIME OF THE STATE'S APPROVAL, IT WAS NOT FULLY CLEAR WHAT THE EXTENT OR COST OF THE CLEAN UP MEASURES WOULD BE.
2017-09-29 08:50 | YES | NO | 19870166 |  | 22610 | WILLIAMS PIPELINE CO | NO | 1987-06-02 | 1630 | IA | HARDIN |  | NO |  | NO | T88N, R22W, S6 NE 1/4 |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 6942.44 | 14005.7057 | L. P. G. | 2 | 108 | 0 | NO | NO | 6 | 0.26 | 35000 | WELDED |  | 850 | 300 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN | 9185883850 | A LEAK WAS DISCOVERED ON THE #1-6" DES MOINES-MASON CITY PROPANE LINE AT MP 64 BY A LOCAL FARMER. THE LINE WAS STATIC, HOLDING APPROXIMATELY 300 PSI PRIOR TO THE LEAK OCCURRENCE. STOPPLE EQUIPMENT WAS USED TO INSTALL A NEW PIPE SEGMENT, THEN THE LINE WAS RETURNED TO SERVICE ON JUNE 4, 1987.
2017-09-29 08:50 | YES | NO | 19870167 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-06-12 | 1725 | ND |  |  | NO |  | NO | T141N R49W S28 NW 1/4 |  | LINE PIPE | LONGITUDINAL WELD |  | 1946 | OTHER | DEFECT IN SEAM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 64796.1067 | 130719.9194 | FUEL OIL | 3 | 289 | 21 | NO | NO | 6 | 0.19 | 35000 | WELDED |  | 1150 | 920 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN | 9185883850 | ON JUNE 12, 1987, A LEAK WAS DISCOVERED IN A SMALL RESIDENTIAL AREA NORTH OF HARWOOD, NORTH DAKOTA ON THE #1-6" PIPELINE AT MP 113+. MAINTENANCE PERSONNEL WEREDISPATCHED TO THE SCENE AND THEY PROCEEDED TO ISOLATE THE LEAK BY CLOSING APPROPRIATE MAINLINE VALVES. THE MAJORITY OF THE FUEL OIL SPILLED WAS CONCENTRATED WITHIN CLOSE PROMIXIMTY OF THE RUPTURE; HOWEVER, SOME PRODUCT SPRAY WAS CARRIED BYTHE WIND ONTO THE PROPERTY OF FOUR RESIDENTS. THE RUPTURE WAS IDENTIFIED AS A SEAM FAILURE AND THE FAILED SECTION WAS REMOVED FOR METALLURGICAL ANALYSIS. A NEWSPOOL OF PIPE WAS INSTALLED AND THE LINE WAS RETURNED TO OPERATION ON JUNE 16, 1987. AN INTERIM OPERATING PRESSURE WAS ESTABLISHED UNTIL SUCH TIME THAT A HYDROSTATIC TEST CAN BE COMPLETED.
2017-09-29 08:50 | YES | NO | 19870168 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-06-06 | 1600 | ID | ELMORE |  | NO |  | NO | CHEVRON PIPE LINE'S GLEN FERRY STATION OFF OF BENNETT ROAD - 20 MILES EAST OF MOUNTAIN HOME, IDAHO |  | PUMPING STATION | PUMP | WELDING FITTING | 1957 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 83309.2801 | 168068.4679 | DIESEL FUEL | 3 | 2 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.V. SMITH | 8015397251 | ON THE AFTERNOON OF JUNE 6, 1987, GLENN'S FERRY OIL PUMP (#2202) LOST SUCTION ANBD RAN DRY. THE PUMP OVERHEATED AND THE SHAFT SEIZED AND SNAPPED. THE FORCE PRODUCED BY THE SHAFT SNAPPING ALSO BROKE THE WELDED FITTINGS OFF OF THE PUMP, SPILLING PRODUCT. DUE TO OVERHEATING, THE PRODUCT SPONTANEOUSLY IGNITED AND BURNED. THE FIRE WAS EXTRINGUISHED AT 1800 6-6-87. INVESTIGATION FOUND THAT THE REMOTELYOPERATED PUMP SUCTION VALVE HAD CLOSED WHILE PUMP WAS RUNNING. DAMAGE WAS SUSTAINED BY THE PUMP AND MOTOR AND SOME OF THE STATION PIPING. DUE TO THE CLOSED VALVE, A SMALL QUANTITY OF PRODUCT WAS LOST AND NONE REACHED THE GROUND DUE TO THE FIRE.
2017-09-29 08:50 | YES | NO | 19870169 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-06-22 | 1400 | UT | SALT LAKE |  | NO |  | NO | UTAH STATE ROAD 65, NEAR MOUNTAIN DELL CREEK, PARLEY'S CANYON, SALT LAKE COUNTY |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 69424.4001 | 140057.0566 | CRUDE OIL | 1 | 1500 | 0 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1114 | 50 | YES | 8 | 1393 | 9 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PRE-CONSTRUCTION MEETINGS | YES | YES | ROD V SMITH SALT LAKE DIVISION MANAGER | 8015397251 | A D-9 CATERPILLAR WAS BEING OPERATED DURNIG CONSTRUCTION OF A NEW ROAD BY KIEWITT CONSTRUCTION COMPANY, UNDER CONTRACT TO THE UTAH STATE ROAD COMMISSION. THE D-9 STRUCK A 10-INCH CRUDE LINE, RELEASING THE CRUDE OIL. THE OIL WAS CONTAINED BY EFFORTS OF THE CONTRACTOR AND CHEVRON PIPE LINE COMPANY EMPLOYEES WORKING IN THE AREA. THE INCIDENT OCCURRED IN A WATERSHED AREA SERVING SALT LAKE CITY. A SMALL SPRING WAS AFFECTED. THIS SECTION OF LINE WAS SCHEDULED TO BE OUT-OF-SERVICE WITHIN 24 HOURS OF THE INCIDENT, AS PART OF A LINE RELOCATION PROJECT CURRENTLY UNMDERWAY. THE PIPELINE IS BEING RELOCATED AS PART OF PREPARATIONS FOR THE CONSTRUCTION OF A NEW DAM IN THE AREA. THE ROADWAY CONSTRUCTION IS ALSO PART OF THESEPREPARATIONS. CLEANUP AND DISPOSAL OF MATERIAL IS BEING PERFORMED UNDER DIRECTION GIVEN BY THE SALT LAKE COUNTY HEALTH DEPARTMENT AND THE UTAH STATE HEALTH DEPARTMENT, WATER POLLUTION CONTROL BUREAU.
2017-09-29 08:50 | YES | NO | 19870170 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-07-15 | 1500 | OR | UMATILLA | ADAMS | NO |  | NO | SEC 17, T3N, R34E, WILLAMETE MERIDIAN. |  | PUMPING STATION | PIPE | 1/2 INCH BLEEDER LINE ON | 1953 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 400 | 370 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA | NEWSPAPER CAMPAIGN | YES | YES | R V SMITH DIVISION MANAGER | 8015397251 | A CONTRACTOR WAS EXCAVATING NEAR SOME VALVE BOXES AT THE ADAMS STATION UNDER THE SUPERVISION OF CHEVRON PIPE LINE COMPANY. THE BACKHOE STRUCK A 1/2 INCH BLEEDER LINE, RELEASING DIESEL FUEL. THE DIESEL FUEL WAS CONTAINED AT THE EXCAVATION SITE, AND THE FREE LIQUID PUMPED INTO TANKER TRUCKS. CLEAN-UP OPERATIONS WERE PERFORMED UNDER THE DIRECTION OF THE OREGON DIVISION OF ENVIRONMENTAL QUALITY. CHEVERON PIPE LINE COMPANY, SALT LAKE DIVISION, IS REMOVING ALL OUT-OF-SERVICE UNDERGROUND PIPING SUCH AS THIS BLEEDER LINE DURING ALL STATION RENOVATION OR EXCAVATION PROJECTS.
2017-09-29 08:50 | YES | NO | 19870171 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1987-05-06 | 210 | CA | CORONA RIVERSIDE |  | NO |  | NO | CORONA PUMP STATION, 1599 MAPLE STREET, CORONA, CALIFORNIA |  | PUMPING STATION | VALVE |  | 1980 | OTHER | OPENNED VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 54000 | 49985.568 | 100841.0807 | CRUDE OIL | 1 | 100 | 50 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R B KUPREWICZ V P OPERATIONS | 2134289017 | A BLEEDER VALVE ON AN INJECTION PUMP WAS OPENNED AND RESULTED IN CRUDE OIL BEING RELEASED. PROMPT RESPONSE FROM THE LOCAL FIRE DEPARTMENT AND COMPANY PERSONNELRESULTED IN CONTAINMENT OF THE SPILL AND MINIMIZATION OF THE IMPACTED AREA.
2017-09-29 08:50 | NO | NO | 19870172 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1987-05-23 | 1635 | CA | LOS ANGELES |  | NO |  | NO | 20 FT. NW OF DOMINGUEZ CHANNEL |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 46282.9334 | 93371.371 | FUEL OIL | 2 | 1 | 0 | NO | NO | 12 | 0.32 | 42000 | WELDED |  | 720 | 250 | YES | 8 | 900 | 0 | 82 | EXTERNAL | Null | YES | NO DATA | DEEP PIT AT 3 O'CLOCK | NO DATA |  | Null | NO DATA |  | Null | Null | R B KUPREWICZ V P OPERATIONS | 2134289017 | THE LEAK WAS CAUSED BY EXTERNAL CORROSION ON LINE 79. LESS THAN 1 BARREL OF GAS OIL WAS SPILLED. IT WAS CONTAINED BY SORBENT BOOM AND PROMPTLY CLEANED UP.
2017-09-29 08:50 | YES | NO | 19870173 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1987-09-01 | 1245 | MN | ITASCA |  | NO |  | NO | OPERATOR'S DEER RIVER, MINNESOTA PUMP STATION LOCATED ON US HIGHWAY 2, 1.5 MI E OF DEER RIVER, MN |  | PUMPING STATION | WELDING FITTING |  | 1985 | OTHER | FRACTURE OF .5 X 2" NIPPL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15500 | 14347.7093 | 28945.125 | CRUDE OIL | 1 | 50 | 48 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.E. STAUDOHARCOORDINATOR - OPERATIONS | 7153925631 | A .5 X 2" NIPPLE ATTACHED TO A 12" SPOOL PIECE IMMEDIATELY DOWNSTREAM FROM THE PRESSURE CONTROL VALVE FRACTURED. A .5" BALL VALVE AND PLUG WAS ATTACHED TO THE NIPPLE WHICH WAS USED TO OCCASIONALLY ATTACH PRESSURE GAUGES. THE NIPPLE WAS REMOVED AND REPLACED WITH A .75" THREAD-O-LET FITTING WHICH WAS PLUGGED AND BACKWELD
2017-09-29 08:50 | YES | NO | 19870174 |  | 443 | AMOCO PIPELINE CO | NO | 1987-08-18 | 1200 | TX | BRAZORIA | ALVIN | NO |  | NO | HASTINGS FIELD J.C. JOHNSON LEASE |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 150 | 145 | NO | NO | 7 |  |  | WELDED |  | 60 | 40 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MIKE P. CLANCY | 7133322476
2017-09-29 08:50 | YES | NO | 19870175 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1987-08-19 | 1343 | GA | HARALSON |  | NO |  | NO | WOODED AREA APPROXIMATELY 3 MILES EAST OF BREMEN, GEORGIA SEE DRAWING A-SOT-29-0 ATTACHED. |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 29621.0774 | 59757.6775 | TURBINE FUEL | 1 | 1100 | 1050 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 200 | 228 | YES | 24 | 1345 | 6 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | ROY M CROOK V P OPERATIONS | 4042612137 | RIGHT-OF-WAY CLEARING CONTRACTOR WAS CLEARING BRUSH ON RIGHT OF WAY USING A HYDRO-AX (HEAVY DUTY BUSHHOG). THE OPERATOR OF THE HYDRO-AX WAS CLEARING THE BANK OF OF A SMALL BRANCH WHEN THE BLADE OF THE HYDRO-AX STRUCK THE 10-INCH PIPELINE. THE UPPER 1/3 OF THE PIPE WAS EXPOSED IN THE CREEK BUT BELOW WATER LEVEL. THE BLADE OF THE HYDRO-AX CUT/TORE A GASH IN THE PIPE APPROXIMATELY 1-1/2" WIDE AND 15" LONG. BREMEN STATION WAS NOTIFIED BY RADIO AND THE PIPELINE WAS SHUT DOWN AND CLOSED OFF.
2017-09-29 08:50 | YES | NO | 19870176 |  | 2271 | CHASE TRANSPORTATION CO. | YES | 1987-08-07 | 900 | KS | SEDGWICK |  | NO |  | NO | LEAK OCCURED ON OR NEAR SECTION LINE BETWEEN SECTIONS 1 AND 2 OF T.26S - R.2W |  | LINE PIPE | NO DATA | SEE ATTACHMENT | 0 | OTHER | UNKNOWN, SEE ATTACHMENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 5553.952 | 11204.5645 | GASOLINE AND FUEL OIL | 1 | 250 | 200 | NO | NO | 10 | 0.34 | 35000 | WELDED |  | 1640 |  | YES | 24 | 2050 |  | 72 |  | Null | YES |  |  |  |  | Null |  |  | Null | Null | L. R. HENDRICKS, MANAGER | 3163216380 | CHASE TRANSPORTATION CO OPERATES TWO PETROLEUM PRODUCTS PIPELINES IN THE AREA OFTHIS REPORTED LEAK. THE LINES ARE PARALLEL TO EACH OTHER IN THE SAME RIGHT-OF-WAY. ONE LINE IS A 10.75" O.D. X.344" WALL THICKNESS, GRADE B PIPE. THE OTHER IS A IS A 8.625" X .322" WALL THICKNESS, GRADE B PIPE. BOTH LINES CARRY MOOTOR GASOLINES AND DIESEL. THE 10" LINE ALSO CARRIES JET FUEL. ON AUGUST 6TH CHASE TRANSPO
2017-09-29 08:50 | NO | NO | 19870177 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-08-22 | 2400 | TX | ELLIS |  | NO |  | NO | SEE MAP |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 92.5659 | 186.7427 | GASOLINE | 3 | 10 | 0 | NO | NO | 10 | 0.37 |  | WELDED |  | 675 | 640 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A E SMITH DIVISION MANAGER | 4098393100
2017-09-29 08:50 | NO | NO | 19870178 |  | 443 | AMOCO PIPELINE CO | YES | 1987-08-20 | 1200 | OK | CREEK |  | NO |  | NO | NW 1/4 SECTION 33 T18N-R7E. 1 1/2 MI EAST, 1 MI NORTH OF DRUMRIGHT, OK. |  | LINE PIPE | NO DATA |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 740.5269 | 1493.9419 | CRUDE OIL | 1 | 15 | 14 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 689 | 100 | YES | 8 | 864 | 12 | 82 | EXTERNAL | Null | YES | GALVANIC | EXPOSED IN CREEK BOTTOM |  |  | Null |  |  | Null | Null | J. W. WILHELM, AREA MANAGER - CUSHING | 9182257271 | THE LEAK WAS CAUSED BY AN EXTERNAL CORROSION PIT ON THE TOP OF THE #4-10" LINE WHERE IT IS EXPOSED IN THE BOTTOM OF A SMALL CREEK. A TEMPORARY LEAK CLAMP WAS INSTALLED UNTIL A PIPE REPLACEMENT CAN BE ACCOMPLISED. CREEK WAS CLEANED UP USING BOOM AND SORBENT MATERIALS.PART H - #4-10",0.83 MI N OF DRITE STA. LINE WAS NOT OPERATING AT TIME OF LEAK.
2017-09-29 08:50 | YES | NO | 19870179 |  | 26095 | STEUART PETROLEUM CO. | NO | 1987-08-19 | 1100 | MD | PRINCE GEORGES | AQUASCO | NO |  | NO | POTOMAC ELECTRIC POWER COMPANY (PEPCO) LOCATED AT CHALK POINT GENERATING STATION, EAGLE HARBOR ROAD, AQUASCO, MD. (IN TANK FARM) |  | TANK FARM | TANK |  | 1972 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COMM: PIPELINE SOLVENT (#2 OIL); CLASS: 1; LOSS: 1036; RECOV: 1014; FIRE: NO; EXP: NO; PRTST: Null; FACTD: Null; FACAT: Null; PREVT: Null; EXCAL: Null; TMPMK: Null; PNAME: JACK L. GOODMAN, TERMINAL MANAGER; PHONE: 3019941200 | THE SUBJECT PIPELINE DELIVERS #6 FUEL OIL ON AN AS NEEDED BASIS. AFTER EACH REQUIRED DELIVERY, THE #6 OIL IS DISPLACED WITH SOLVENT (#2 OIL), AND REMAINS IN A STATIC CONDITION. THE #2 OIL IS DISPLACED INTO TANKAGE AT RYCEVILLE STATION, ANDEITHER TANKAGE AT MORGANTOWN OR CHALK POINT GENERATING STATION (DEPENDENT ON WHICH HAS REQUIREMENT) BY THE NEXT REQUIRED DELIVERY OF #6 FROM THE PINEY POINT STORAGE FACILITY. INCIDENT OCCURED AFTER THE LINE WAS DISPLACED THROUGH RYCEVILLE,AND THE #6 WAS DIRECTEDTOWARD CHALK POINT. THE #2 OIL TANK AT CHALK POINT DID NOT HAVE SUFFICIENT ULLAGE TO CONTAIN THE CAPACITY OF THE PIPELINE BEING DISPLACED BY THE #6 FROM RYCEVILLE TO CHALK POINT. OPERATING PERSONNEL NEGLECTED TO VERIFY THE TANK BY MANUAL GAUGING IMMEDIATELY PRIOR TO THE TANK FILL COMMENCING; THEREFORE, THEY WERE UNAWARE THE ULLAGE WAS INSUFFICIENT TO CONTAIN THE PIPELINE DISPLACEMENT. A CONTRIBUTING FACTOR WAS THE RETIREMENT OF THE TWO (2) KEY PIPELINEOPERATING PERSONNEL DURING THE PERIOD PRECEDING THE PIPELINE DELIVERY. MEETINGSAND OPERATIONAL TRAINING WILL BE CONDUCTED WITH PERSONNEL PRIOR TO THE NEXT OPERATION; AND CONTROLS WILL BE PLACED IN EFFECT TO PREVENT ANY SUCH FUTURE OCCURENC
2017-09-29 08:50 | YES | NO | 19870180 |  | 4906 | EXXON PIPELINE CO | YES | 1987-07-11 | 930 | TX | CHEROKEE |  | NO |  | NO | STATION 1704+24 SOME 3 MILES EAST OF NECHES JUNCTION ON THE ARP - NECHES JCT. 8" TRUNKLINE. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 19180 | 17754.1332 | 35817.2579 | CRUDE OIL | 1 | 250 | 240 | NO | NO | 8 | 0.32 | 30000 | WELDED |  | 700 | 190 | NO |  |  |  |  | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | G.P. MURRAY | 7136565956 | AT 0930 HOURS ON JULY 11, 1987, A LEAK WAS REPORTED BY BARR AIR PATROL TO EXXON, USA AT THE NECHES GAS PLANT. UPON INVESTIGATION, IT WAS DETERMINED THAT THE LEAK MAY BELONG TO EXXON PIPELINE CO SO THE OTC CONTROLLER IN HOUSTON WAS NOTIFIEDAND THE LINE WAS SHUT DOWN AT 1225 HOURS. THE CONTROLLER THENNOTIFIED THE GAUGING SUPERVISRO FOR THAT AREA WHO IN TURN CALLED THE MAINTENANCE SUPERVISOR. AT 1330 HOURS EPC PERSONNEL, CONTRACTED EQUIPMENT, AND VACUUM TRUKS WERE DISPATCHEDTO THE SITE. UPON EXCAVATION, THE OIL WAS FOUND TO BE COMING FROM A SMALL HOLE RESUL;TING FROM EXTERNAL CORROSION. THE LEAK WAS AT A CREEK CROSSING AND THE OILHAD TRAVELED APPROXIMATELY 1 1/4 MI. DOWNSTREAM BEFORE BOOMS AND FLUME PIPES COULD BE INSTALLED TO PREVENT FURTHER CONTAMINATION OF WATERWAY. THE OIL HAS SINCEBEEN CLEANED UP AS OF 7-23-87, AND PERMANENT REPAIRS CONSISTING OF FULL WRAPPINGTHE CREEK CROSSING HAVE BEEN SCHEDULED.
2017-09-29 08:50 | NO | NO | 19870181 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1987-07-13 | 1140 | CA | YOLO | WEST SACRAMENTO | NO |  | NO | IN SACRAMENTO RIVER APPROXIMATELY 30 FEET FROM WEST BANK - DOWNSTREAM OF OUR SACRAMENTO STATION |  | LINE PIPE | PIPE |  | 1966 | OTHER | UNKNOWN, LINE BYPASSED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 1 | 20 | 0 | NO | NO | 10 | 0.37 |  | WELDED |  | 1440 |  | YES | 24 | 1875 |  | 66 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | BARRY R. PEARL | 2134867860
2017-09-29 08:50 | YES | NO | 19870183 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | NO | 1987-07-29 | 1930 | CA | CONTRA COSTA | RICHMOND | NO |  | NO | ON RAILROAD RIGHT-OF-WAY APPROXIMATELY 500 FEET NORTH OF HENSLEY STREET |  | LINE PIPE | LONGITUDINAL WELD | CRACK IN SEAM OF PIPE | 1963 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 100 | 85 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1365 | 610 | YES | 24 | 1800 | 4 | 63 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | BARRY R. PEARL | 2134867860 | OUR FIELD PERSONNEL FOUND A SMALL STAIN ON GROUND APPROXIMATELY .57 MILES FROM OUR RICHMOND STATION. LINE WAS ON A SCHEDULED SHUTDOWN. PRESSURE IMMEDIATELY BLED OFF LINE AND BLOCK VALVES CLOSED. LEAK WAS CAUSED BY A SEAM FAILURE (APPROXIMATE 1-1/2 INCH CRACK). APPROXIMATELY 60 FEET OF PIPE REPLACED.
2017-09-29 08:50 | YES | NO | 19870184 |  | 809 | ARCO PIPE LINE CO | YES | 1987-08-04 | 1020 | OK | WASHINGTON |  | NO |  | NO | NE/4 SEC. 19-T27N-R13E - 1 MI NORTHE OF DEWEY, WASHINGTON COUNTY, OKLAHOMA ON HIGHWAY 75 AND 1-1/4 MILE WEST |  | LINE PIPE | PIPE |  | 1929 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 18513.1734 | 37348.5484 | GASOLINE | 2 | 871 | 210 | NO | NO | 8 | 0.25 | 24000 | WELDED |  | 700 | 120 | YES | 0 | 1000 | 0 | 48 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | N.R. BENNETT, MANAGER - NORTHERN AREA OPERATIONS | 3163311300
2017-09-29 08:50 | YES | YES | 19870185 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1987-07-31 | 1805 | NC | GASTON | GASTONIA | NO |  | NO | PLANTATION PIPE LINE COMPANY'S LOWELL PUMPING STATION LOCATED AT 2740 SOUTH NEW HOPE ROAD IN GASTONIA, NORTH CAROLINA. |  | PUMPING STATION | SCRAPER TRAP |  | 1952 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 1 | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.M. CROOK, VICE PRESIDENT - OPERATIONS | 4042612137 | ON FRIDAY, JULY 31, 1987 AT APPROXIMATELY 6:05 P.M., SEVERAL COMPANY EMPLOYEES WERE RECEIVING AND LAUNCHING SCRAPERS ON THE 14-INCH PIPELINE AT LOWELL STATION IN GASTONIA, NC. A TERMINAL OPERATOR WAS MAKING PREPARATIONS TO LAUNCH THE THIRDAND FINAL SCRAPER FROM THE STATION. HE HAD DRAINED THE LAUNCHER, INSERTED THE SCRAPER, AND CLOSED THE SCRAPER LAUNCHER ENCLOSURE. HE THEN PROCEEDED TO FILL THELAUNCHER WITHOUT FIRST CLOSING THE DRAIN VALVE. HIS ACTIONS EXPOSED THE DRAIN SYSTEM TO FULL LINE PRESSURE AND GASOLINE ERUPTED FROM THREE VENT DRAINS. THE TERMINAL OPERATOR IMMEDIATELY CLOSED THE DRAIN VALVE ON THE LAUNCHER AND GASOLINE STOPPED COMING OUT THE VENT DRAINS. A VAPOR CLOUD QUICKLY FORMED AND WAS IGNITED BY A 5 HP GASOLINE POWERED WATERBLASTER WHICH THE AREA MANAGER WAS USING TO CLEAN THE ADJACENT BUILDING. THE RESULTANT FIRE WAS EXTINGUISHED IN A FEW MINUTER BYWORKERS USING PORTABLE FIRE EXTINGUISHERS. THE TERMINAL OPERATOR HAD GOTTEN GASOLINE IN HIS EYES, WAS TAKEN TO THE HOSPITAL FOR TREATMENT AND WAS LATER RELEASED. THE AREA MANAGER RECEIVED SECOND AND THIRD DEGREE BURNS TO 68% OF HIS BODY AND IS IN THE NC MEMORIAL HOSPITAL BURN CENTER AT CHAPEL HILL, NC. HIS CONDITION IS LISTED AS CRITICAL BUT STABLE.
2017-09-29 08:50 | YES | NO | 19870186 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-07-27 | 805 | MN | HENNEPIN |  | NO |  | NO | T116, R22W, SE.25, SECTION 35 |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 462829.3338 | 933713.7104 | GASOLINE | 3 | 24 | 0 | NO | NO | 12 | 0.38 | 42000 | WELDED |  | 1350 | 45 | YES | 24 | 1400 | 0 | 54 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | NO DATA |  | Null | Null | H.E. JANZEN | 9185883850 | AT 0830 HOURS FRIDAY, JULY 24, 1987, WILLIAMS PIPE LINE COMPANY WAS NOTIFIED BYTHE LOCAL POLICE DEPARTMENT THAT A 90" SEWER MAIN IN EDEN PRAIRIE HAD RUPTURED AND HAD WASHED OUT A LARGE AREA BENEATH OUR PIPELINE. THE LINE WAS IMMEDIATELY SHUT DOWN AND MAINTENANCE PERSONNEL WERE DISPATCHED TO INVESTIGATE. THE SEWER EFFLUENT HAD WASHED OUT THE SIDE OF A BLUFF JUST NORTH OF THE MINNESOTA RIVER CREATING A HOLE APPROXIMATELY 100' DEEP. VALVES WERE CLOSED ON EITHER SIDE OF THE WASHOUT TO ISOLATE THE SEGMENT. DUE TO THE STEEP GRADIENT, MAINTENANCE CREWS WERE ABLE TO TAP THE LINE AND DRAIN OFF MUCH OF THE LINE FILL. WORK CONTINUED THROUGH THE WEEKEND TO SET UP A PURGE OPERATION SO AS TO DISPLACE THE REMAINING LINE FILL WITH NITROGEN. AT 2005 HOURS ON JULY 27, 1987 WHILE THE LINE WAS BEING PURGED,THE PIPE CRACKED (AS RESULT OF FLEXING AND BENDING THAT OCCURRED DURING THE WASHOUT) AND SPILLED AN ESTIMATED 24 BARRELS OF PRODUCT. A 1250 FOOT TEMPORARY REROUTE WAS INSTALLED AND THE LINE RESUMED OPERATION ON AUGUST 14, 1987.
2017-09-29 08:50 | YES | NO | 19870187 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-08-16 | 1030 | LA | ST JAMES | ST. JAMES | NO |  | NO | ST. JAMES TERMINAL (CAPLINE SYSTEM)ONE-HALF MILE SOUTH OF HIGHWAY 18 |  | PUMPING STATION | OTHER | SUMP | 1968 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 100 | 98 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262 | UP OVERFILL - THE METER STRAINER VALVE WAS HALF OPEN. THE HIGH SUMP ALARM DID NOT ALERT CONTROLLER OF PROBLEM.
2017-09-29 08:50 | YES | NO | 19870188 |  | 24003 | YELLOWSTONE PIPELINE CO | YES | 1987-07-23 | 937 | ID | KOOTENAI |  | NO |  | YES | TOWNSHIP 49 NORTH, RANGE 1 WEST, SECTION7, KOOTENIA COUNTY IDAHO |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4628.2933 | 9337.1371 | GASOLINE | 3 | 644 | 47 | NO | NO | 10 | 0.31 | 42000 | WELDED |  | 1727 | 892 | YES | 0 | 0 | 0 | 54 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKER; NEAREST MARK | NO | NO | DWIGHT D. JACKSON DIRECTOR, ENVIRONMENTAL AFFAIRS | 7132932100 | CONOCO PIPE LINE (OPERATOR OF YELLOWSTONE PIPE LINE), WAS NOTIFIED AT 9:37 A.M.(PDT) ON THURSDAY, JULY 23, 1987, THAT PRODUCT WAS LEAKING FROM THE PIPELINE ATFOURTH OF JULY PASS. THE PIPELINE WAS IMMEDIATELY SHUTDOWN BY OPERATING PERSONNEL IN HOUSTON, TEXAS AND LOCAL PERSONNEL WERE DISPATCHED TO THE LEAK SITE. THE LEAK WAS REPAIRED BY COMPANY AND CONTRACT PERSONNEL AND CLEANUP OPERATIONS BEGAN IMMEDIATELY. THE LEAK WAS CAUSED BY THE PIPE BEING STRUCK BY A ROAD GRADER DURING ROAD CONSTRUCTION BY A PRIVATE CONTRACTOR DOING WORK FOR THE STATE OF IDAHO.
2017-09-29 08:50 | YES | NO | 19870190 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-07-16 | 1600 | TX | NUECES | CORPUS CHRISTI | NO |  | NO | NUECES BAY BLVD., NEAR LIFT BRIDGE, HELDENFELS DITCH |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 32398.0534 | 65359.9597 | GASOLINE | 3 | 105 | 5 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 1070 | 950 | YES | 2 | 1184 | 9 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | THE CORPUS CHRISTI TO SAN ANTONIO REFINED PRODUSTS PIPELINE WAS SHOWING A SHORTAGE WHICH COULD NOT BE RESOLVED. WHILE THE SYSTEM WAS SHUT DOWN FOR OTHER WORK, THE SOUTH SECTION OF THE PIPELINE WAS PRESSURE TESTED. IT WAS DETERMINED FROM THIS TEST THAT THERE WAS A LEAK. BY WALKING THE PIPELINE, A SMALL AMOUNT OF REGULAR GASOLINE WAS FOUND ON HELDENFELS DITCH. THIS GASOLINE WAS CONTAINED WITH A BOOM AND PICKED UP WITH A VACUUM TRUCK, ABSORBANT PADS WERE USED TO CLEAN UP THAT PROTION OF THE GASOLINE THAT REMAINED.THREE SMALL PINHOLES WERE FOUND IN THE PIPE WHICH WERE CAUSED BY EXTERNAL CORROSION. THE DAMAGED SECTION OF PIPE HAS BEEN REPLACED WITH NEW COATED LINE PIPE.
2017-09-29 08:50 | YES | NO | 19870191 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-07-17 | 1400 | TX | FAYETTE | SCHULENBURG | NO |  | NO | ONE-HALF MILE WEST OF SCHULENBURG, TEXAS, NEAR US HWY. 90 (MP 41.6 ON THE PIPELINE) |  | LINE PIPE | PIPE |  | 1924 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 8500 | 7868.0987 | 15873.1331 | CRUDE OIL | 1 | 281 | 25 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 800 | 250 | YES | 2 | 880 | 12 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE MARKERS;PUBLIC & | NO | NO | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | MAINTAINER OPERATOR WAS BUILDING A NEW ROADBED ON SUNDAY AFTERNOON WHEN HE STRUCK AND RUPTURED THE 8" PIPELINE. HE IMMEDIATELY CALLED THE CONTROL CENTER TO REPORT THE ACCIDENT. THE 8" PIPELINE WAS SHUT DOWN AND ALLOWED TO DRAIN INTO TANKAGE AT THE NEXT DOWNSTREAM TANK FARM.THE SECTION OF PIPELINE WAS ISOLATED AND TEMPORARILY REPAIRED WITH A LEAK CLAMPAND CLEAN-UP OPERATIONS WERE STARTED.THE NEST MORNING, 10 FEET OF DAMAGED LINE PIPE WAS REPLACED WITH NEW COATED ANDWRAPPED PIPE.MOBIL PIPE LINE HAD NOT BEEN NOTIFIED THAT THE MAINTAINER WOULD BE WORKING NEAROUR PIPELINE.
2017-09-29 08:50 | YES | NO | 19870192 |  | 13131 | CONOCO INC | YES | 1987-07-27 | 930 | CO | WELD | PIERCE | NO |  | NO | ONE MILE WEST OF PIERCE, CO, SE 1/4, SE 1/4, SEC. 21, T8N,R66W, |  | LINE PIPE | PIPE |  | 1940 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 925.6587 | 1867.4274 | CRUDE OIL | 1 | 2981 | 897 | NO | NO | 8 | 0.22 |  | WELDED |  | 800 | 470 | YES | 24 | 1000 | 0 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKER | Null | Null | DWIGHT D. JACKSON | 7132932100 | A FARMER, PLOWING HIS FIELD, HIT THE PIPELINE WITH A BLADE OF THE PLOW. COVERAGE FOR THE LINE WAS SHALLOW IN THE AREA DUE TO WIND EROSION, LAND LEVELING, ETC. THE FARMER IMMEDIATELY NOTIFIED CONOCO PIPE LINE AND THE PIPELINE WAS SHUT DOWN.A COMPANY EMPLOYEE THEN CLOSED A DOWNSTREAM BLOCK VALVE. EQUIPMENT WAS BROUGHT IN AND THE LINE DRAINED DOWN TO RELIEVE STATIC HEAD PRESSURE AT THE LEAK LOCATION. THE DAMAGED PIPE WAS CUT OUT AND RELACED WITH NEW PRE-HYDROSTATIC TESTED PIPE.NO CRUDE OIL ENTERED WATER. THE OILY DIRT RESULTING FROM THE LEAK WAS CLEANED UP AND DISPOSED OF AT WELD LANDFILL, INC., FOLLOWING APPROVAL BY THE WILD COUNTY HEALTH DEPARTMENT.
2017-09-29 08:50 | YES | NO | 19870193 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1987-08-20 | 135 | TX | UPTON |  | NO |  | NO | LINE 80-1-2-3 EXT.- CRANE-BENEDUM-MP 77-43+74 6.8 MILES NORTH OF RANKIN, TX, ON STATE HWY. 349, THEN APPROX. 10 MILES EAST ON RANCH RD 1555, THEN APPROX. 3/4 OF |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 24000 | 22215.808 | 44818.2581 | NATURAL GAS LIQUID | 3 | 2173 | 0 | NO | NO | 6 | 0.19 | 35000 | WELDED |  | 1430 | 422 | YES | 24 | 1934 | 6 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | B L THORMAN MANAGER OF ENGINEERING & TECNICAL SERVICES | 9186614721 | CONTRACTOR FOR PHILLIPS PETROLEUM COMPANY HIT LINE WITH DIRT SCRAPER.
2017-09-29 08:50 | YES | NO | 19870194 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-09-04 | 430 | TX | WARD |  | NO |  | NO | MONAHANS PUMP STATION 1/2 MILE WEST OF TEXAS HIGHWAY 18, SEC. 78, BLK. A G&MMN&A |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 500 | 485 | NO | NO | 10 | 0.37 | 1710 | WELDED |  | 300 | 400 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R C KINNEAR DIVISION MANAGER | 9156877551 | CRUDE OIL WAS PUMPED INTO WRONG TANK AGAINST A PARTLY CLOSED VALVE. THE HIGHER PRESSURE AGAINST A HOLE IN PIPE, DUE TO EXTERNAL CORROSION, CAUSED THE LEAK.
2017-09-29 08:50 | YES | NO | 19870195 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-08-22 | 700 | MO | ST CHARLES |  | NO |  | NO | NE 1/4, SE 1/4, SECTION 24, T-47-N, R-4-E, SURVEY 205 OZARK 22-INCH PIPELINE |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 31180 | 28862.0373 | 58226.387 | CRUDE OIL | 1 | 3900 | 3841 | NO | NO | 22 | 0.34 | 46000 | WELDED |  | 885 | 138 | YES | 12 | 1000 | 0 | 49 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | YES | J W HOLDEN MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262 | A SUPPLEMENTAL REPORT WILL BE FILED. CLEANUP IS STILL IN PROGRESS.
2017-09-29 08:50 | NO | NO | 19870196 |  | 443 | AMOCO PIPELINE CO | YES | 1987-08-28 | 945 | OK | CARTER |  | NO |  | NO | SE 1/4 NW 1/4 SECTION 8 T3S-R3W |  | LINE PIPE | PIPE |  | 1932 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 462.8293 | 933.7137 | NATURAL GAS LIQUID | 3 | 16 | 15 | NO | NO | 8 |  | 35000 | WELDED |  | 660 | 230 | Null | 24 | 832 | 11 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W WILHELM AREA MANAGER OPERATONS | 9182257271 | LEAK OCCURRED AT THE EDGE OF A SMALL CREEK DUE TO AN EXTERNAL PIT. PRODUCT WAS CONTAINED IN CREEK ABOUT 1/4 MILE DOWNSTREAM OF PIPELINE CROSSING WHERE CONTAINMENT DAM & FLUME WAS INSTALLED. CREEK WAS FLUSHED WITH WATER AND PRODUCT PICKED UP. RESIDUE WAS BURNED. LINE WILL BE RECONDITIONED AT THIS POINT.
2017-09-29 08:50 | YES | NO | 19870197 |  | 443 | AMOCO PIPELINE CO | NO | 1987-09-07 | 1045 | TX | BRAZORIA |  | NO |  | NO | HWY 35 SOUTH OF DIXIE FARMS RD NORTH OF AMOCO PRODUCTION BUILDING |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 500 | 500 | NO | NO | 6 |  |  | WELDED |  | 0 | 40 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL P CLANCY | 7133222476 | CLAMP WAS INSTALLED AND LINE REMAINS SHUT IN
2017-09-29 08:50 | YES | NO | 19870198 |  | 9175 | JAYHAWK PIPELINE CORP | YES | 1987-09-08 | 1520 | KS | MORTON |  | NO |  | YES | SE/4 SEC. 33, TWP. 34S, R42W APPR 2.25 MI NORTH OF ELKHART KANSAS |  | LINE PIPE | NO DATA |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 6942.44 | 14005.7057 | CRUDE OIL | 1 | 480 | 320 | NO | NO | 6 | 0.19 | 35000 | WELDED |  | 1000 | 200 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | WARNING- ROAD CROSSING SI | NO | NO | DENNIS E. SMITH, PRESIDENT | 3162679669 | CONTRACTOR DITCHING MACHINE STRUCK AND PUNCTURED JAYHAWK'S 6" LINE 2 1/4 MILES NORTH OF ELKHART, KANSAS AT APPROXIMATELY 1515, SEPTEMBER 8, 1987. NOTIFICATION OF THE LEAK WAS RECEIVED BY TELEPHONE AT 1520 FROM SUPERVISOR OF OIL COMPAMY WHO HAD EMPLOYEE WORKING IN THE AREA. LINE WAS SHUT DOWN AT 1530 AND VACUUM TRUCKSWERE DISPATCHED TO LEAK. PUNCTURE WAS ON TOPSIDE OF PIPE AND CRUDE OIL WAS CONTAINED IN OPEN PIPE LINE DITCH THAT WAS BEING DUG AT TIME OF THE ACCIDENT. THREE HUNDRED TWENTY (320) BARRELS OF CRUDE OIL WAS RECOVERED WITH AN ESTIMATE OF ONE HUNDRED (160) BARRELS SOAKED INTO LOOSE SOIL IN NEW PIPE LINE DITCH. DAMAGED PIPE WAS REMOVED AND REPLACEMENT JOINT, 7' 4" WAS INSTALLED. TWO REPLACEMENT WELDS ON TESTED AT 025, SEPTEMBER 9, 1987. TO SERVICE AT 0125, SEPTEMBER 9, 1987.
2017-09-29 08:50 | YES | NO | 19870199 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-09-18 | 1530 | CO | GARFIELD |  | NO |  | NO | 20 MI NORTH OF MAC, COLORADO, SECTION 35, TOWNSHIP 5 SOUTH, RANGE 104 WEST |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 132326 | 122488.7088 | 247109.2009 | NATURAL GAS LIQUID | 2 | 11145 | 0 | NO | NO | 10 | 0.21 | 2300 | WELDED |  | 1650 | 485 | YES | 24 | 2262 | 11 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COMPANY EMERGENCY RESPONS | NO | NO | S.F. ISAACSPRESIDENT | 9185811800
2017-09-29 08:50 | YES | NO | 19870200 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1987-09-02 | 1050 | OK | OKLAHOMA | OKLAHOMA | NO |  | NO |  |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 23141.4667 | 46685.6855 | CRUDE OIL | 1 | 370 | 340 | NO | NO | 8 | 0.32 |  | NO DATA |  | 720 | 45 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | DANNY NEAL MAINTANENCE FOREMAN | 4052426612 | OPERATRO OF FRONT END LOADER WORKING @ NEW REMINGTON PARK RACEWAY, HIT AN 8" LINE, CAUSING SPILL TO OCCUR. OPERATOR WAS IN WRONG LOCATION AND WAS DISMISSED FOLLOWING THE INCIDENT. OIL WAS PICKED UP AND LINE CLAMPED OFF TO STOP OIL.
2017-09-29 08:50 | YES | NO | 19870202 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-10-03 | 1330 | TX | JEFFERSON | BEAUMONT | NO |  | NO | 3 MILES SOUTH OF HWY. 69 ON WEST ARTHUR ROAD |  | TANK FARM | NO DATA | VITAULIC COUPLING | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3800 | 3517.5029 | 7096.2242 | CRUDE OIL | 1 | 120 | 114 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA | INCIDENT OCCURRED INSIDE | Null | Null | A E SMITH DIVISION MANAGER | 4098393100 | A CONTRACTOR'S MOWING EQUIPMENT STRUCK A PARTIALLY BURIED VITAULIC COUPLING CAUSING THE CRUDE OIL TO LEAK. THE LEAK WAS CONTAINED INSIDE THE PROPERTY AND RECOVERED BY VACUUM TRUCKS. RECOVERED MATERIAL WAS RETURNED TO TANKAGE.
2017-09-29 08:50 | YES | NO | 19870203 |  | 19213 | TEXACO CHEMICAL CO - A DIV OF TEXACO INC | YES | 1987-09-19 | 1400 | TX | JEFFERSON | PT. ARTHUR | NO |  | NO | TANK FARM IS LOCATED NW OF STATE HWY. 73, NE OF F.M. 823 AND W. OF ROOSEVELT AVE. APPROXIMATE COORDINATE: 290 53' 30" N 930 59' 30" W. |  | TANK FARM | TANK | FITTING IN ROOF DRAIN FAI | 1971 | INCORRECT OPERATION BY OPERATOR PERSONNEL | FAILED FITTING IN ROOF DR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 160 | 157 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ASST. DISTRICT MANAGER | 7134322765 | A FAILURE IN A JOINT OF A ROOF DRAIN ON TANK 1501 CAUSED PRODUCT OT LEAK INTO ROOF DRAIN AND UPON GROUND. PRODUCT FOLLOWED NATURAL DRAINAGE TO FLOOD PUMP RESERVOIR. EMPLOYEE MAKING ROUND PUMPED RAINWATER OUT OF RESERVOIR AND APPROXIMATELY 2 BARRELS OF PRODUCT MIXED WITH WATER. THIS MIXTURED WAS PUMPED UPON DRAINAGE DISTRICT #7 DRAIN DITCH FOR APPROXIMATELY 1-1/2 MILES TO D.D. #7 CATCH BASIN.
2017-09-29 08:50 | YES | NO | 19870204 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-09-18 | 2330 | ND | CASS | FARGO | NO |  | NO | FARGO TERMINAL |  | TANK FARM | NO DATA | TRANSFER HOSE | 0 | OTHER | TRANSFER HOSE RUPTURED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4628.2933 | 9337.1371 | TOLUENE |  | 110 | 100 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA | HOSE RUPTURE | Null | NO DATA |  | Null | Null | H E HANZEN VICE PRESIDENT- OPERATIONS | 9185883850 | ON SEPTEMBER 18 AT 1800 HOURS, LOCATION PERSONNEL BEGAN DRAWING WATER FROM THE BOTTOM OF TANK #1352 (X-GRADE) AND TRANSFERRING IT TO TANK #164 (X-9) VIA A PORTABLE PUMP AND A FLEXIBLE 2" HOSE. THIS WAS BEING DONE IN PREPARATION FOR TURNINGTANK #1352 TO THE RACK. THE TRANSFER OPERATION WAS BEING MONITORED EVERY HALF HOUR. AT APPROXIMATELY 2400 HOURS, IT WAS DISCOVERED THAT THE DISCHARGE HOSE HAD RUPTURED. HEAVY RAIN AT THE TIME, MADE IT DIFFICULT TO ESTIMATE THE AMOUNT OF BOTTOM WATER LOSS. AN OVER/SHORT CALCULATION LATER REVEALED THAT 110 BARRELS HAD ESCAPED. THE BOTTOM WATER COLLECTED IN A SMALL LOW-LYING AREA JUST NORTH OF THE TERMINAL FENCE. MAINTENANCE CREW WERE ABLE TO RECOVER APPROXIMATELY 310 BARRELS OF BOTTOM WATER AND RAIN WATER MIX AND PUMP IT BACK INTO TANK #164. TEST SAMPLES TAKEN IN THE RECOVERY AREA INDICATED SPECIFICA GRAVITIES RANGING FROM 1.006 TO 1.045. FUTHER SAMPLING IS BEING CONDUCTED IN COOPERATION WITH THE NORTH DAKOTA HEALTH DEPARTMENT.
2017-09-29 08:50 | YES | YES | 19870205 |  | 443 | AMOCO PIPELINE CO | NO | 1987-09-08 | 800 | TX | GALVESTON | KEMAH | NO |  | NO | 1/4 MILE SOUTH OF CLEAR CREEK AND 300' WEST OF HWY 146 |  | LINE PIPE | GIRTH |  | 1943 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | NATURAL GAS LIQUID | 3 | 280 | 0 | YES | YES | 6 | 0.28 |  | WELDED |  | 500 | 484 | YES | 8 | 750 | 12 | 85 | NO DATA | Null | YES | NO DATA |  | NO DATA | WELD FAILED DO TO ADJACEN | Null | NO DATA | INSPECTOR AT LOCATION | Null | Null | MICHAEL P CLANG | 7133322476
2017-09-29 08:50 | YES | NO | 19870206 |  | 809 | ARCO PIPE LINE CO | YES | 1987-09-28 | 1530 | IL | COOK |  | NO |  | NO | 1/4 MILE WEST OF HIGHWAY 30 ALONG PENN CENTRAL RAILROAD TRACKS NEAR LYNWOOD, ILLINOIS |  | LINE PIPE | PIPE |  | 1905 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 4998.5568 | 10084.1081 | GASOLINE | 3 | 516 | 356 | NO | NO | 8 | 0.32 | 24000 | COUPLED |  | 632 | 210 | YES | 24 | 875 | 7 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | N R BENNETT NORHTERN AREA OPERATIONS MANAGER | 3163311300 | AN OPERATOR FOR AN EXCAVATING COMPANY STRUCK OUR LINE WITH A DOZER
2017-09-29 08:50 | YES | NO | 19870210 |  | 18718 | SUN PIPELINE CO | Null | 1987-09-29 | 800 | TX | ORANGE |  | NO |  | NO | 1/2 MILE NORTH OF HWY.105 AND 3 MILES EAST OF ORANGEFIELD TOWNSITE. |  | TANK FARM | VALVE |  | 1930 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 7120 | 6590.6897 | 13296.0832 | CRUDE OIL | 1 | 500 | 499 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E F MCKINLEY JR AREA MANAGER COMPLIANCE SAFETY & HEALTH | 2147570220 | VALVE LINEUP WAS MADE INCORRECTLY. WHEN TRYING TO FILL TANK, PRESSURE CAUSED VALVE TO BREAK. SPILL WAS REPORTED TO BENNY HERFORD, FOREMAN, BY NILS STRANG, GAUGER, AT 8:15 A.M., 9/29/87. NATIONAL RESPONSE CENTER AND TEXAS RAILROAD COMMISSION WERE NOTIFIED.
2017-09-29 08:50 | YES | NO | 19870211 |  | 13131 | CONOCO INC | YES | 1987-10-26 | 950 | WY | NATRONA |  | NO |  | YES | NE1/4, NE1/4, SEC 2, T3IN, R81W MILE POST 268 |  | LINE PIPE | LONGITUDINAL WELD |  | 1963 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 138848.8001 | 280114.1131 | GASOLINE | 3 | 1000 | 0 | NO | NO | 8 | 0.19 | 52 | WELDED |  | 1632 | 1454 | YES | 24 | 2100 | 11 | 63 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L G HUBBARD |  | PIPELINE HAD BEEN SHUT DOWN FROM OCTOBER 21 TO OCTOBER 26 FOR SCHEDULED MAINTENANCE. IT WAS RESTARTED AT 1812 HOURS ON OCTOBER 26. LINE CONDITIONS HAD STABLIIZED BY 1845 HOURS WITH A FLOW RATE OF 800 BPH, CASPER DISCHARGE PRESSURE WAS 1620PSI AND SINCLAIR BACKPRESSURE WAS 220 PSI. AT 2053 HOURS, THE SINCLAIR PUMP WASSHUT DOWN IN PREPARATION TO RECEIVE A SCRAPER. PIPELINE WAS STABLIZED BY 2148 HOURS WITH CASPER DISCHARGE PRESSURE 1806 PSI AND SINCLAIR BACKPRESSURE 600 PSI. AT 2150 HOURS, THE CASPER VARIABLE SPEED DRIVE (VSD) UNIT WENT INTO SEQUENCE ANDRPM'S DECREASED FROM 3592 TO 1988 INDICATING THAT THE UNIT HAD CONTROLLED BACK.THE CASPER (VSD) CONTINUED TO CONTROL BACK AND WOULD NOT RESPOND TO SETPOINT COMMANDS FROM HOUSTON. CASPER STATION WAS SHUT DOWN AT 2237 HOURS AND THE CASPER SUPERVISOR WAS CALLED OUT. HE WENT TO MILEPOST 262 BLOCK VALVE TO TAKE PRESSURE READINGS. AT 0230 HOURS, HOUSTON SAID A LEAK HAD BEEN FOUND NEAR MILEPOST 268. BLOCK VALVES AT MILEPOST 262 AND 278 WERE THEN CLOSED. REPLACED 237.5 FEET OF 0.188" WALL PIPE.
2017-09-29 08:50 | YES | NO | 19870212 |  | 10313 | KOCH PIPELINE INC | YES | 1987-09-07 | 1655 | KS | MCPHERSON |  | NO |  | NO | 3 MOLES NORTH AND 2 WEST OF INMAN, KANSAS SW/4 SECTION 30, TOWNSHIP 20 SOUTH RANGE 4 WEST,MCPHERSON COUNTY, KANSAS |  | LINE PIPE | OTHER |  | 1974 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 231414.6669 | 466856.8552 | L. P. G. | 2 | 2553 | 0 | YES | NO | 8 | 0.19 | 42000 | WELDED |  | 1320 | 700 | YES | 24 | 1650 | 1 | 74 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER |  | YES | YES | BILL CAFEY MANAGER OF TECHINAL SERVICES | 4053952377 | WHITE&SONS CONSTRUCTION CO. ARE CONSTRUCTING A 12" PIPELINE FOR KOCH PIPELINES THAT IS TO PARALLEL ANS EXISTING 8" KOCH PIPELINE. WHILE IN SECTION 30, TOWNSHIP20 SOUTH, TANGE 4 WEST, TWO TRACK-HOES OPERATED BY BILL NEWBERRY AND PETE MILTON WERE IN THE PORCESS OF DIGGING THE DITCH FOR A P.I. (POINT OF INTERSECTION) ORBEND IN THE PIPE. THIS P.I. IS USED TO ALLOW THE 12" TO CROSS THE 8" LINE. THE ORGINAL SURVEY CREW MARKED THE 8" LINE BUT THE MARKERS HAD BEEN DESTROYED BY FARMING EQUIPMENT. THE 8" LINE IS SHOWN ON THE CONTRACTOR'S DRAWINGS BUT THE TRACK HOE OPERATORS HAD OVERLOOKED THE EXISTING LINE WHEN THEY BEGAN DIGGING. THE FIRST TRACK-HOE JUST SCRAPED THE 8" PIPE WITHOUT PUNCTURING IT BUT THE SECOND TRACK-HOE DID PUNCTURE THE LINE. AFTER THE LINE WAS PUNCTURED, BOTH OPERATORS JUMPED FROM THEIR TRACK-HOES AND RAN AWAY FROM THE LEAK SITE. ALSO LEAVING THE SITEWERE TWO HELPERS, C.E.NEWBERRY AND LUTHER JONES. WHEN THE MAN WERE APPROXIMATELY 100 YARDS FROM THE LEAK, THE VAPOR CLOUD WAS IGNITED. SOMETHING ON ONE OF THE TRACK-HOES PROBABLY IGNITED THE VAOPRS BECAUSE THE TRACK-HOES' ENGINES WERE STILL RUNNING. BOTH TRACK-HOES AND ONE PICKUP WERE DESTROYED BY THE FIRE. VERL ROBERTS, ONE OF THE KOCH EMPLOYEES IN THE AREA, CALLED THE KOCH OPERATION HEADQUARTERS TO REOPRT THE LEAK AND PROCEEDED TO CLOSE THE VALVES UPSTREAM AND DOWNSTREAM OF THE LEAK.
2017-09-29 08:50 | YES | NO | 19870213 |  | 10012 | KANEB PIPELINE CO | YES | 1987-10-17 | 1551 | NE | STANTON |  | NO |  | NO | 4 MILES OF JCT. OF HWY.92 & HWY.15, ONE-FOURTH MILE EAST, ONE-FOURTH MILE NORTH. |  | LINE PIPE | PIPE |  | 1940 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2776.976 | 5602.2823 | FUEL OIL | 3 | 98 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | NO | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MR. MACK BROWN VICE PRESIDENT OF ENGINEERING & OPERATIONS | 3162621408 | SCRAPER WAS PUCHING A LARGE AMOUNT OF WAX, SEIZED METER-SHEARING METER CASING BOLTS. LIQUID WAS RELEASED THROUGH THE CAPSING BOLT HOLES.E PIPE LINE WERE WITHIN 125' OF THE ACCIDENT SITE.
2017-09-29 08:50 | YES | NO | 19870214 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1987-10-28 | 1820 | CA | RIVERSIDE | BEAUMONT | NO |  | NO | FOUR CORNERS PIPE LINE COMPANY, BEAUMONTPUMP STATION 3 ONE-HALF MILES OF INTERSTATE 10 ON SAN TIMOTEO CANYON ROAD, BEAUMONT, CA. |  | PUMPING STATION | NO DATA | METER #PDM 401 | 1982 | OTHER | FAILURE OF METER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 41654.64 | 84034.2339 | CRUDE OIL | 1 | 50 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.B.KUPREWICZ, VICE PRESIDENT, OPERATIONS | 2134289017 | SCRAPER WAS PUSHING A LARGE AMOUNT OF WAX, WAX SEIZED METER - SHEARING METER CASING BOLTS. LIQUID WAS RELEASED THROUGH THE CASING BOLT HOLES.
2017-09-29 08:50 | YES | NO | 19870215 |  | 26102 | TEXACO INC | NO | 1987-10-14 | 1615 | TX | TRAVIS | AUSTIN | NO |  | NO | INTERSECTION OF E. 1ST STREET AND SHADY LANE IN AUSTIN, TEXAS. APPROXIMATELY 97 DEGREES 41' LONGITUDE AND 30 DEGREES LATITIDE. |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 91000 | 84234.9387 | 169935.8953 | DIESEL FUEL | 3 | 1034 | 0 | NO | NO | 6 | 0.25 | 35000 | WELDED |  | 1050 | 950 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S.MINER, DISTRICT MANAGER | 7134322765 | ON 10-12-87 AT 1800 HOURS THE HEARNE TO SAN ANTONIO 8"/6" LINE WAS SHUTDOWN ACCOUNT OF AN UNEXPLAINABLE HOURLY INTEGRITY SHORTAGE. ON 10-13-87 THE ENTIRE LINEWAS INSPECTED TWICE BY AERIAL OVER FLIGHT. THERE WAS NO VISUAL EVIDENCE OF PRODUCT OUTAGE. ON 10-14-87 IT WAS DETERMINED THAT THE 6" LINE SEGMENT FRON AUSTINTERMINAL TO THE FIRST MAINLINE BLOCK VALVE (1.1 MILES FROM AUSTIN TERMINAL) COULD NOT MAINTAIN STACTIC PRESSURE WHEN IT WAS BLOCKED IN BY ISOLATING VALVES. THELEAK WAS LOCATED IN THE CASTING UNDER EAST 1ST STREET IN AUSTIN, TEXAS. 110' OF LINE WAS REMOVED FROM THE CASING AND REPLACED WITH NEWW PRE-TESTED PIPE. ALL WELDS WERE X-RAYED, REPAIRS SUCCESSFULLY COMPLETED AND THE LINE RE-STARTED AT 2245 HOURS ON 10-17-87.
2017-09-29 08:50 | YES | NO | 19870216 |  | 13131 | CONOCO INC | NO | 1987-10-02 | 920 | CO | ADAMS | COMMERCE | NO |  | NO | 52ND AVENUE AND VASQUEZ BOULEVARD,COMMERCE CITY,CO |  | LINE PIPE | NO DATA |  | 1965 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8225 | 7613.5425 | 15359.5905 | JET FUEL | 3 | 150 | 104 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 440 | 400 | YES | 8 | 550 | 6 | 87 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR | N | Null | NO DATA |  | NO | Null | L.G.HUBBARD,DIRECTOR ENVIRONMENTAL AFFAIRS | 7132932032 | CONTRACTOR DID NOT NOTIFY CONCO PRIOR TO DIGGING AT LEAK SITE ALTHOUGH LINE MARKERS WERE VISABLE ON BOTH SIDES OF LEAK SITE.
2017-09-29 08:50 | YES | NO | 19870217 |  | 4906 | EXXON PIPELINE CO | YES | 1987-09-15 | 200 | TX | UPSHUR |  | NO |  | NO | EPC'S GILMER PUMPING STATION ON THE TALCO - LONGVIEW 8" TRUNKLINE. THE STATION IS LOCATED APPROXIMATELY 12 MILES NORTH OF LONGVIEW,TX IN UPSHUR COUNTY AND JUST |  | NO DATA | TANK |  | 1947 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3876 | 3587.853 | 7238.1487 | CRUDE OIL | 1 | 500 | 500 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P.MURRAY, OPERATIONS MANAGER | 7136565956 | AT APPROXIMATELY 0200 HOURS ON 9-15-87, TANK #1554 AT EPC'S GILMER PUMPING STATION OVERFLOWED LEAVING SOME 500 BBLS. ACCUMULATED IN THE FIREWALL. THE ACCIDENTOCCURRED AS THE RESULT OF THE GAUGE LINE HANGING UP IN THE VAREC GAUGE HEAD, THEREBY RESULTING IN SLACK IN THE LINE INSIDE THE TANK. AS THE TANK LEVEL ROSE, THE SLACK IN THE GAUGE LINE BECAME ENTANGLED IN THE HIGH LEVEL MAGNETROL SWITCH PREVENTING IT FROM WORKING WHEN THE TANK REACHED HIGH LEVEL. EPC'S OTCC CONTROLLER REALIZED THAT AN ERRONEOUS TANK LEVEL WAS BEING TRANSMITTED WHILE BEING PUMPED INTO SO STOPPED FLOW INTO THE TANK. EPC'S FIELD GAUGER DISCOVERED THE OVERFLOW AT 0820 ON 9-15-87 ABD IMMEDIATELY CONTACTED EPC'S OTCC CONTROLLER IN HOUSTON,AND REQUESTED THAT PUMP UNIT #2 BE STARTED UP TO TAKE SUCTION ON THE TANK. EPCPERSONNEL AND CONTRACTED EQUIPMENT AND VACUUM TRUCKS WERE DISPATCHED TO THE SITE AT ABOUT 0830 HOURS TO MAKE REPAIRS AND INITIATED CLEANUP. PERMANENT REPAIRS CONSISTED OF REPAIRING THE VAREC GAUGE HEAD AND RELINGNING GAUGE LINE PULLEYS. CLEANUP OPERATIONS WILL BE COMPLETED ON 9-17-87.
2017-09-29 08:50 | YES | NO | 19870218 |  | 4906 | EXXON PIPELINE CO | YES | 1987-08-05 | 1315 | TX | TRAVIS | AUSTIN | NO |  | NO | LEAK OCCURRED AT STATION 12305 + 41 IN AUSTIN,TEXAS SOME 5.8 MILES SOUTHEAST OF HIGHWAY 290 ON THE PEDERNALES RIVER-WARDA 18" PIPELINE. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 104000 | 96268.5014 | 194212.4518 | CRUDE OIL | 1 | 1150 | 1137 | NO | NO | 18 | 0.31 | 45000 | WELDED |  | 895 | 500 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | G.P.MURRAY,OPERATIONS MANAGER | 7136565956 | AT APPROXIMATELY 1:15 P.M. ON 8-5-87 A ROCK SAW OPERATED BY DON PHILLIPS,INC. FOR UNDER THE SUPERVISION OF THE CITY OF AUSTIN,TX. RUPTURED EXXON PIPELINE COMPANY'S (EPC) 18" CRUDE LINE. PHILLIPS, INC. OBTAINED EPC'S TELEPHONE NUMBER FROM A PIPELINE MARKER IN THE VICINITY OF THE LEAK. THE LEAK WAS REPORTED TO EPC'S OTCC CONTROLLER IN HOUSTON IMMEDIATELY AND THE LINE WAS SHUT DOWN AT 1:30 P.M. ON 8-5-87. EPC WAS NEVER NOTIFIED THAT EXCAVATION OR CONSTRUCTION ACTIVITY WAS ONGOING IN THE VICINITY OF THE 18"PIPELINE. EPC PERSONNEL AND CONTRACTED EQUIPMENT WERE DISPATCHED TO THE SITE. A LOCAL CONTRACTOR (J C EVANS CONSTRUCTION CO,)WAS NOT INVOLVED BUT WORKING IN THE AREA, ASSISTED EPC IN CONTAINMENT OF THE SPILL BY INSTALLING BERMS AND DITCHES AT APPROXIMATELY 2:00 P.M. ON 8-5-87. ALL RELEASED OIL (1150 BBLS.) WAS CONTAINED IN THE MAN MADE BERMS/DITCHES. AT 4:00 P.M. ON 8-5-87 CLEANUP WAS PERFORMED BY RECOVERING ALL BUT 13BBLS. OF THE SPILLEDCRUDE OIL UTILIZING VACUUM TRUCKS. FURTHER CLEANUP INVOLVED REMAVAL OF SOIL AND TURNING OF SOIL. THE GRAVITY FEED LEAK WAS STOPPED BY INSTALLING OF A CLAMP AT APPROXIMATELY 6:30 P.M. ON 8-5-87. PERMANENT REPAIRS WERE MADE BY INSTALLING A NEW 7' SECTION OF 18" PIPE. THE LINE WAS RESTORED TO SERVICE AT 5:25 A.M. ON 8-6-87. AS OF 8-20-87, CLEANUP OPERATIONS CONTINUING, PENDING SOIL ANALYS TESTSAND FINAL APPROVAL FROM TEXAS RAILROAD COMMISSION.
2017-09-29 08:50 | YES | NO | 19870219 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1987-07-31 | 1130 | TX | GRAY |  | NO |  | NO | NW/4,SEC.39, BLK3, I&GN SURVEY, GRAY CO.,TX LINE "BT" - BURNETT JCT.-BORGER -MP 31-48+56 100' SOUTH OF ARCO COMBS WORLEY "C" LEASE WELL #5 |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 14300 | 13236.9189 | 26704.2121 | CRUDE OIL | 1 | 2310 | 1582 | NO | NO | 10 | 0.2 | 42000 | WELDED |  | 1140 | 400 | YES | 24 | 1453 | 7 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.L.THORMAN, MANAGER OF ENGINEERING&TECHNICAL SERVICES | 9186614721 | DOZER STRUCK AND RUPTURED PIPELINE WHILE EXCAVATING FILL FOR A PIT.
2017-09-29 08:50 | YES | NO | 19870220 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1987-09-04 | 300 | TX |  | WHEELER | NO |  | NO | SEC.19, BLK A-4, H&GN SURVEY, WHEELER COTX LINE "BT"-BURNETT JCT.-BORGER-MP 69-25+80 3168'EAST OF MP 69 |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 29622 | 27419.8611 | 55316.9351 | CRUDE OIL | 1 | 1689 | 105 | NO | NO | 10 | 0.2 | 42000 | WELDED |  | 1140 | 495 | NO | 24 | 1365 | 7 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.L.THORMAN, MANAGER OF ENGINEERING&TECHNICAL SERVICES | 9186614721 | COUNTY NAINTAINER RUPTURED LINE WHILE TRYING TO REROUTE WATER THAT RUNS DOWN SANDY CREEK.
2017-09-29 08:50 | YES | NO | 19870221 |  | 5075 | FARMERS UNION CENTRAL EXCHANGE INC - CENEX PIPELIN | YES | 1987-09-29 | 852 | MT | ROSEBUD | ROSEBUD | NO |  | NO | 2 MILES SOUTH OF I-94 AT ROSEBUD, MONTANA ON BUTTE CREEK ROAD, SEC.25, T6N, R42E ROSEBUD COUNTY, MONTANA |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 41654.64 | 84034.2339 | GASOLINE | 1 | 1365 | 0 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1440 | 530 | YES | 24 | 1500 | 5 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | 14DAY AERIAL SURVEY | YES | YES | DAVID CALDWELL | 4062529326 | THE ROSEBUD COUNTY ROAD DEPARTMENT HAD TW0 MOTOR GRADERS GRADING SOIL FROM THE BORROW DITCHES ALONG THE ROAD UP AND INTO THE ROAD CROWN TO RAISE THE ROADWAY ELEVATION PRIOR TO NEW SURFACE GRAVEL APPLICATION. ONE OF THE GRADERS HOOKED THE PIPELINE WITH THE GRADER BLADE, TEARING A GASH APPROXIMATELY 6" LONG BY THREE-FOURTHS WIDE IN THE PIPE. PIPELINE MARKERS ARE LOCATED ON EACH SIDE OF THE R/W ATTHE FENCE LINE STATING "DANGER-HIGH PRESSURE PETROLEUM PIPELINE, ETC,.ETC."ONE SIGN WAS WITHIN 10 FEET OF THE GRADERS. NO LOCATION OR DEPTH WAS REQUESTEDBY THE ROAD DEPARTMENT. THE GRADER OPERATORS WERE ALLEGEDLY TOLD BY THEIR FOREMAN THAT THE LINE WAS "AT LEAST 6 FEET DEEP".
2017-09-29 08:50 | YES | NO | 19870222 |  | 4430 | EMERALD PIPE LINE CORP | YES | 1987-10-05 | 1345 | TX | HANSFORD | TX | NO |  | NO | SEC.56, BLK, P.0, H&GN SURVEY, HANSFORDCOUNTY, TX 10 & ONE-HALF MILES NORTH AND 2 &ONE-EIGHTH MILESEAST OF THE CITY OF GRUVER, TX. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 13600 | 12588.9579 | 25397.0129 | DIESEL FUEL | 3 | 1197 | 888 | NO | NO | 6 | 0.19 | 35000 | WELDED |  | 1420 | 500 | YES | 8 | 1775 | 9 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | GERALD CHILDERS | 8063783583 | AT 13:45 (CENTRAL TIME) 10-5-87, A CABLE PLOW OPERATED BY BIG T CONSTRUCTION COMPANY, STRUCK AND RUPTURED OUR 6 5/8" TURPIN PRODUCTS PIPELINE WHILE LAYING A FIBER-OPTIC TELEPHONE CABLE. 1197 BARRELS OF DIESEL ESCAPED OF WHICH 888 BARRELS WERE RECOVERED, LEAVING A NET LOSS OF 309 BARRELS. THE RUPTURE OCCURRED APPROXIMATELY 900' AND WITHIN SIGHT OF OUR AERIAL MILE MARKER NO. 43. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED.
2017-09-29 08:50 | YES | NO | 19870223 |  | 12628 | MOBIL PIPELINE CO | YES | 1987-10-07 | 1445 | OK | GARVIN |  | NO |  | NO | SEC.13, T4N R3W, 3 MILES WEST OF MAYSVILLE, OK. ADJACENT TO HIGHWAY 19 |  | LINE PIPE | SCRAPER TRAP |  | 1924 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 69424.4001 | 140057.0566 | CRUDE OIL | 1 | 650 | 0 | YES | NO | 8 | 0.32 | 1493 | WELDED |  | 677 | 240 | YES | 8 | 846 | 10 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AERIAL SURVEILLANCE | YES | YES | D.L. DENNARD VICE PRESIDENT, OPERATIONS | 2146582226 | ACACIA PIPE LINE COMPANY WAS WORKING IN A DITCH ON THEIR PIPELINE ADJACENT TOMOBIL'S ABOVEGROUND SCRAPER TRAP. A WELDER ACCIDENTLY IGNITED AN ACCUMUL;ATIONOF OIL THAT HAD LEAKED FROM THEIR LINE WHILE WATER WAS BEING DISPLACED FROM IT. THE FIRE, WHICH WAS NOT EFFECTIVELY CONTROLLED, SPREAD TO OUR FACILITIES. THEPIPELINE WAS SHUT DOWN AND VALVES WERE CLOSED TO ISOLATE THE BURNING SCRAPER TRAP. THE DAMAGED FACILITIES WERE REPLACED WITH NEW MATERIAL.
2017-09-29 08:50 | YES | NO | 19870224 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-09-29 | 1430 | TX | UPTON |  | NO |  | NO | SEC.21 BLK.42 T-5-S RR SVY. |  | LINE PIPE | PIPE |  | 1957 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 277.6976 | 560.2282 | CRUDE OIL | 1 | 800 | 310 | NO | NO | 10 | 0.34 | 700 | WELDED |  | 800 | 700 | YES | 24 | 800 | 7 | 76 | NO DATA | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L.S. ARRINEAU,DIVISION MANAGER | 9156877551 | AT 2:28 P.M. THE PIPE LINE RUPTURED OCCURED. THE PUMP STATION WAS SHUT DOWN AR2:40 P.M. BY PIPE LINE OPERATORS. THE OIL WAS PICKED UP AND CLEANED UP AND BEGAN IMMEDIATELY. THE BAD SECTION OF PIPE WAS REMOVED AND REPLACED.
2017-09-29 08:50 | YES | NO | 19870225 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1987-09-01 | 1000 | OK | CREEK |  | NO |  | NO |  |  | TANK FARM | VALVE |  | 0 | OTHER | BULL PLUG WAS REMOVED. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2000 | 1900 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.R.THOMPSON MAINTENANCE FOREMAN | 9183529442 | BULL PLUG WAS REMOVED FROM GATE VALVE AND VALVE WAS OPENED. (VANDALIZED)
2017-09-29 08:50 | YES | NO | 19870226 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1987-10-12 | 1430 | TX | LAMB |  | NO |  | NO | LINE WA-ODESSA-BORGER CRUDE PIPELINE.MP 179-23+26 APPROXIMATELY 5 MILES NORTH OF OLTON, TX ON HWY.168,THEN APPR.1 1/4 MI. WEST ON DIRT ROAD TO LEAK SITE. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 37000 | 34249.3707 | 69094.8146 | CRUDE OIL | 1 | 3500 | 1879 | NO | NO | 12 | 0.25 | 45000 | WELDED |  | 1270 | 715 | YES | 8 | 1656 | 6 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.L.THORMAN,VICE PRESIDENT | 9186614721 | LAMB COUNTY MAINTAINER PUNCTURED PIPELINE WHILE GRADING DRAINAGE DITCH ALONG-SIDE DIRT ROAD.
2017-09-29 08:50 | YES | NO | 19870227 |  | 30501 | CON - DOR PIPELINE CO | NO | 1987-08-21 | 1448 | TX | COLLIN | WYLIE | NO |  | NO | COLLIN COUNTY,WYLIE QUADRANGLE,FRANCISCODE LA PINA A-688,TRACT-2;200YDS.NO. OF HWY 78, 58FT.SO. OF SANTE FE RAILROAD TRACKS,150YDS.NE,OF NEW WYLIE CITY HALL. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 27850 | 25779.5939 | 52007.8537 | GASOLINE | 3 | 717 | 295 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1440 | 750 | YES | 8 | 1861 | 12 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES T. RAU,DISTRICT SUPERINTENDENT | 3184915855 | PIPELINE PUNCTURED FRIDAY AFTERNOON WITH BACK-HOE DURING EXCAVATION FOR SEWER LINE INSTALLATION. CONOCO OPERATIONS COODINATOR IN HOUSTON NOTED REDUCTION IN PRESSURE ABD SHUT THE LINE DOWN. LOCAL COMPANY PERSONNEL BEGAN SHUTTING BLOCK VALVES AND SEARCHING FOR LEAK SITE. CONTRACTOR TELEPHONED COMPANY AND REPORTED ACCIDENT LOCATION. CLEAN-UP AND REPAIRS WERE INITIATED THE SAME DAY AND ALL WORK WAS COMPLETED BY EARLY SUNDAY MORNING.
2017-09-29 08:50 | YES | NO | 19870228 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-10-26 | 1400 | TX | NAVARRO |  | NO |  | NO | SEE MAP |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4628.2933 | 9337.1371 | GASOLINE | 3 | 300 | 60 | NO | NO | 10 | 0.37 |  | WELDED |  | 675 | 580 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH,DIVISION MANAGER | 4098393100 | DAILY OVER/SHORT METER READINGS REFLECTED SHORTAGE ON SUNDAY MORNING,10/25/87.THE P/L WAS SHUTDOWN AND GATE VALVES WERE BLOCKED, PRESSURE READINGS ON THE SEGMENT BETWEEN DAWSON (M.P. 22) AND GRANDVIEW (M.P.55) GRADUALLY DROPPED MAINTENANCE CREWS WERE CALLED IN TO WALK THE P/L. (UNABLE TO FLY R.O.W. DUE TO FOG)THE P/L COULD NOT BE COMPLETELY WALKED DUE TO NIGHTFALL. MONDAY, AT APP. 2:00P.M. THE LEAK WAS LOCATED AT M.P. 311 AND TEMPORARY REPAIRS MADE BY 5:00P.M.
2017-09-29 08:50 | YES | NO | 19870229 |  | 443 | AMOCO PIPELINE CO | YES | 1987-10-13 | 1200 | WY | FREMONT |  | NO |  | NO | LEAK OCCURRED IN THE NW1/4, SEC 3, T38N, R90W IN FREMONT COUNTY, WYOMING, AT AMOCO PIPELINE'S LOST CABIN STATION. STATION SITE IS ABOUT 4 MILES NORTHEAST OF |  | PUMPING STATION | TANK |  | 1948 | OTHER | EQUIP.MALFUNCTIONED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 991100 | 917420.3054 | 1850807.3167 | CRUDE OIL | 1 | 70 | 60 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.W.WHITE,AREA MANAGER | 3072662119 | THE SPILL WAS REPORTED AT 1200 OCTOBER 13, 1987. THE TANK GAUGE MALFUNCTIONED ON TANK 15 AT LOST CABIN STATION ALLOWING IT TO OVERFILL. ALL SPILLED OIL WAS CONTAINED ON STATION GROUNDS. APPROXIMATELY 60 BARRELS WERE PICKED UP AND PUT BACK INTO THE PIPELINE SYSTEM WITH VACUUM TRUCKS. ABOUT 5 BARRELS COVERED THE TANKAND ANOTHER 5 BARRELS SPRAYED OVER THE STATION YARD. THE TANK WAS CLEANED UP.ALL OILY DIRT WAS PICKED UP AND LAND FARMED INSIDE ONE OF THE STATION'S TANK DIKES. NO OIL REACHED WATER. THE TANK LEVEL GAUGE WAS REPLACED. TO PREVENT THISFROM HAPPENING AGAIN WE PLAN TO INSTALL AN INDEPENDENT HI-LEVEL ALARM.
2017-09-29 08:50 | YES | NO | 19870230 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1987-10-15 | 1154 | WY | UINTA |  | NO |  | NO | S/W 1/4 SECTION 33, TOWNSHIP 16N, RANGE 119W UINTA COUNTY, WYOMING. |  | LINE PIPE | PIPE |  | 1981 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 11099 | 10273.8856 | 20726.5769 | NATURAL GAS LIQUID | 3 | 1043 | 0 | NO | NO | 6 | 0.13 | 2009 | WELDED |  | 1446 | 325 | YES | 24 | 1986 | 1 | 81 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE WARNING SIGNS | NO | NO | S.F.ISAACS, PRESIDENT | 9185811800 | LINE WAS DAMAGED BY THIRD PARTY WHILE EXCAVATING.
2017-09-29 08:50 | YES | NO | 19870232 |  | 2552 | COLONIAL PIPELINE CO | YES | 1987-10-14 | 930 | PA |  | BOOTHWYN | NO |  | NO | BRANDYWINE STATION 1070 KIRK ROAD BOOTHWYN,PA 19061 |  | PUMPING STATION | TANK |  | 1979 | OTHER | IGNITION OF PRODUCT VAPOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9256.5867 | 18674.2742 | OIL AND GASOLINE |  | 0 | 0 | YES | YES | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S.SORROW,REG.,ENVIRON,AFFIRS MANAGER | 4042611470 | AT 0930 HOURS ON 10/14/87 A MAINTENANCE CREW WASS TO REMOVE AN EXTERNAL STORM WATER DOWNSPOUT FROM A 625 BBL. CAPACITY, 15FT. DIA.X 20FT. HIGH CONE ROOF TANK AT BRANDYWINE STATION. THE TANK CONTAINED 105 BBLS. OF TRANSMIX GAS/OIL MIXTURE. PRIOR TO THE START OF WORK, THE TOP RIM OF THE TANK AND SURROUNDING AREAS WERETESTED FOR COMBUSTIBLE VAPORS WITH AN INSTRUMENT AND FOUND TO BE SAFE FOR HOT WORK BY THE STATION OPERATOR. THIS TEST AND COMPLETION OF A HOT WORK PERMIT FORMARE REQUIRED COLONIAL MAINTENANCE PROCEDURE. WHILE REMOVING A SUPPORT BRACKET FOR THE DOWNSPOUT FROM THE TANK SHELL WITH A CUTTING TORCH, VAPORS IGNITED, BLEWTHE TANK ROOF OFF, AND IGNITED THE TRANSMIX PRODUCT IN THE TANK. THE STATION OPERATOR IMMEDIATELY NOTIFIED LOCAL EMERGENCY RESPONSE AGENCIES AND THE COLONIAL PIPELINE CONTROL CENTER IN ATLANTA. THE FIRE DEPARTMERNT ARRIVED AT THE SCENE AT 0950 HOURS AND DECLARED THE FIRE EXTINGUISHED AT 1115 HOURS. TEN BARRELS OF TRANSMIX PRODUCT WERE CONSUMED BY THE FIRE. THE 95 BARRELS OF TRANSMIX PRODUCT REMAINING IN THE TANK WERE EVACUATED, INLET AND OUTLET VALVES REMOVED, AND THE FLANGE CONNECTIONS WERE BLANKED. A TELEPHONIC REPORT OF THE INCIDENT WAS MADE ON 10/14/87 AT 1047 HOURS TO THE NATIONAL RESPONSE CENTER AND RECORDED AS DOT REPORT NO. 13067.
2017-09-29 08:50 | YES | NO | 19870233 |  | 443 | AMOCO PIPELINE CO | YES | 1987-10-17 | 2130 | WY | NATRONA |  | NO |  | NO | ABOUT 50FT. FROM EAST BOUNDARY OF HELL'S HALF ACRE LANDMARK,SOUTH OF U.S.HWY 20/26, IN THE SE1/4 SEC.,36, T36N,R86W,NATRONA COUNTY, WYOMING. |  | LINE PIPE | PIPE |  | 1944 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 16661.856 | 33613.6936 | CRUDE OIL | 1 | 1665 | 1653 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 275 | 188 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | CALL AMOCO PIPELINE | YES | YES | G.W.WHITE,AREA MANAGER | 3072662119 | WE WERE NOTIFIED OF SPILL AT 2130 OCTOBER 17, 1987. A PIPELINE CONTRACTOR'S TRENCHING MACHINE GOUGED THREE HOLES IN OUR PIPELINE. THE CONTRACTOR IMMEDIATELY BUILT A DIRT DAM TO CONTAIN THE SPILLED OIL. 1653 BARRELS OF OIL WERE PICKED UPAND PUT BACK INTO OUR SYSTEM WITH VAC TRUCKS. ABOUT 12 BARRELS SOAKED INTO THEGROUNDD. AS DIRECTED BY WYOMING DEPARTMENT OF ENVIRONMENTAL QUALITY, THE OILY DIRT WAS PICKED UP AND HAULED TO OUR TANK FARM IN CASPER, WYOMING, WHERE IT WAS SPREAD OUT INSIDE A DIKED AREA. THE DAMAGED SECTION OF PIPE WAS REPLACED. SPILL AREA WAS MULCHED AND SEEDED. NO OIL REACHED WATER. TO HELP PREVENT THIS FROMHAPPENING AGAIN WE PLAN TO INCREASE COMMINUCATIONS WITH OTHER COMPANIES AND THEIR EXCAVATION CONTRACTORS.
2017-09-29 08:50 | YES | NO | 19870234 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-09-22 | 1740 | IL | MASSAC | BOAZ | NO |  | NO | NE1/4, NW1/4, SEC.,32, T-14-S, R-3-E, MP-525.5 CAPLINE 40-INCH |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1500 | 1460 | NO | NO | 40 | 0.31 | 52000 | WELDED |  | 585 | 457 | YES | 24 | 760 | 1 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | DAMAGE DONE CONSTRUCTION | NO | NO | J.W.HOLDEN,MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262 | THE LEAK OCCURRED IN A 2-INCH LONG SPLIT OR CRACK IN THE PIPE WHICH WAS CAUSED DURING CONSTRUCTION. A SUPPLEMENTAL REPORT WILL BE FILED AT A LATER DATE.
2017-09-29 08:50 | YES | NO | 19870235 |  | 809 | ARCO PIPE LINE CO | YES | 1987-10-01 | 1315 | IL |  | PEORIA | NO |  | NO | 200'WEST OF PIPELINE AIR MARKET T-2, DIRECTLY SOUTH OF TOWN PF MONICA, ILLINOIS ON SANTA FE RAILROADRIGHT OF WAY ON THE WEST SIDE OF DAILEY ROAD.. |  | LINE PIPE | PIPE |  | 1929 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 11107.904 | 22409.129 | FUEL OIL | 3 | 442 | 161 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 534 | 0 | YES | 24 | 758 | 7 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | N.R.BENNETT, MANAGER | 3163311300 | PIPELINE WAS HIT AND DENTED BY UNKNOWN PERSON OR PERSONS AT A PREVIOUS TIME. DURING REPRESSURING OF PIPELINE, STRESS POINT IN THE DENT CRACKED AND RELEASED THE PRODUCT.
2017-09-29 08:50 | YES | NO | 19870236 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-12-01 | 438 | OK | WASHINGTON CITY |  | NO |  | NO | NE1/4, SE1/4 SECTION 35, T28N, R12E 240'EAST OF CANEY RIVER |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6479.6107 | 13071.9919 | FUEL OIL | 3 | 652 | 65 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1100 | 542 | YES | 8 | 1445 | 7 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA | LINE MARKERS, COMPANY INS | Null | Null | S L COPPER PRESIDENT | 9185883191 | ON DECEMBER 1, 1987 AT 0438 HOURS, DURING A ROUTINE LINE PRESSURIZATION A LEAK OCCURRED AT MILE POST 21+00 ON THE #3-8" BARNSDALL-KANSAS CITY LINE. APPROXIMATELY 1/2 ACRE OF AN ADJACENT WHEAT FIELD WAS AFFECTED BY THE LEAK. VALVES WERE CLOSED ON EITHER SIDE OF THE LEAK AND REPAIRS WERE INITIATED. THE RUPTURE IN THE LINE WAS DISCOVERED TO BE APPROXIMATELY A 10" LONG SPLIT RESULTING FROM PREVIOUS DAMAGE FROM A BACKHOE TOOTH DURING CONSTRUCTION ACTIVITY THAT HAD TAKEN PLACE ON 11-12-87. THE CONTRACTOR APPARENTLY GOUGED THE LINE DURING INSTALLATION OF A NEW8" BELOW GRADE RIVER CROSSING AND WAS EITHER UNAWARE THAT HE HAD DAMAGED THE LINE OR FAILED TO REPORT IT TO WILLIAMS PIPE LINE COMPANY OFFICIALS. THE COMPANY INSPECTOR INVOLVED HAS BEEN SUSPENDED PENDING FURTHER INVESTIGATION. CLEAN UP EFFORTS HAVE BEEN COORDINATED WITH APPROPRIATE STATE OFFICIALS. REPAIRS WERE COMPLETED AND THE NEW CROSSING WAS PLACED INTO SERVICE ON 12-2-87.
2017-09-29 08:50 | YES | NO | 19870237 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-11-18 | 1000 | IL | FRANKLIN PARK |  | NO |  | NO | CHICAGO TERMINAL |  | TANK FARM | TANK |  | 1931 | OTHER | CRACK IN FIBERGLASS TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13884.88 | 28011.4113 | GASOLINE | 3 | 209 | 157 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S L CROPPER PRESIDENT | 9185883191 | TANK #721 AT THE CHICAGO TERMINAL HAD JUST BEEN FIBERGLASSED. THE TANK WAS BEING PARTIALLY FILLED SO AS TO VERIFY THE INTEGRITY OF THE COATING WHEN A LEAK IN THE TANK BOTTOM WAS DISCOVERED. WATER WAS PUMPED INTO THE TAN TO MINIMIZE LOSS OFPRODUCT, WHILE THE REMAINING PRODUCT WAS TRANSFERRED TO ADJACENT TANKS. MAINTENANCE CREWS WERE ABLE TO RECOVER 157 BARRELS. SITE RESTORATION IS BEING COORDINATED WITH THE ILLINOIS EPA. REPAIRS WERE MADE TO THE TANK BOTTOM COATING AND THE TANK HAS SINCE THEN BEEN RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19870238 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-11-25 | 530 | UT | DAVIS |  | NO |  | NO | TOWNSHIP 1-N, RANGE 1-W, SALT LAKE MERIDIAN NEAR INTERSECTION OF 400 WEST AND CUDAHY LANE, SEE ATTACHED SKETCH. |  | LINE PIPE | PIPE |  | 1952 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 92565.8668 | 186742.7421 | GASOLINE | 3 | 2000 | 1700 | NO | NO | 8 | 0.28 | 42000 | WELDED |  | 1880 | 1550 | YES | 8 | 2425 | 9 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PUBLIC EDUCATION | NO | NO | R V SMITH DIVISION MANAGER | 8015367251 | SEE ATTACHED SHEET
2017-09-29 08:50 | YES | NO | 19870239 |  | 443 | AMOCO PIPELINE CO | YES | 1987-11-26 | 1300 | WY | HOT SPRINGS |  | NO |  | Null | SPILL OCCURRED IN THE NE 1/4 OF SECTION 14, T44N, R98W, IN HOT SPRINGS COUNTY WHOMING AT AMOCO PIPELINE'S HAMILTON DOME STATION. |  | PUMPING STATION | GIRTH |  | 1947 | OTHER | TANK TGGAUGING EQUIPMENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1400 | 1295.9221 | 2614.3984 | CRUDE OIL | 1 | 200 | 197 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G W WHITE AREA MANAGER | 3072662119 | THE SPILL WAS REPORTED AT 1300 NOVEMBER 26, 1987. THE TANK GAUGE MALFUNCTIONED ON TANK 6849 AT HAMILTON DOME STATION ALLOWING IT TO OVERFILL. ALL SPILLED OIL WAS CONTAINES INSIDE THE DIKE SURROUNDING THE TANK. APPROXIMATELY 197 BARRELS WERE PICKED UP AN INJECTED BACK INTO THE PIPELINE SYSTEM WITH VAC TRUCKS. THE REMAINING 3 BARRELS OF OIL WERE SUBSEQUENTLY WORKED INTO THE SOIL. NO OIL REACHED WATER. THE TANK LEVEL GAUGE WAS REPAIRED. TO PREVENT THIS FROM HAPPENING AGAIN WE PLAN TO INSTALL AN INDEPENDENT HI-LEVEL ALARM ON THE TANK.
2017-09-29 08:50 | YES | NO | 19870240 |  | 809 | ARCO PIPE LINE CO | YES | 1987-11-24 | 1135 | OH | RICHLAND |  | NO |  | NO | 870' EAST OF OLD BOWMAN ROAD, 2.75 MILES NORTH OF MANSFIELD, OHIO, RICHLAND COUNTY, SECTION 9 T21 NORTH, NORTH, R18 WEST, |  | NO DATA | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 105000 | 97194.1601 | 196079.8792 | FUEL OIL | 2 | 597 | 432 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 1440 | 185 | YES | 0 | 1400 | 0 | 47 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | N R BENNETT MANAGER, NORTHERN AREA OPERATIONS | 3163311300 | LINE WAS STRUCK BY A FRONT END LOADER APPROXIMATELY 597 BARRELS OF #1 FUEL OIL WERE SPILLED WITH APPROXIMATELY 432 RECOVERED.
2017-09-29 08:50 | YES | NO | 19870241 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-12-05 | 1015 | TX | UPTON | RANKIN | NO |  | NO | NW 1/4, SE 1/4, SECTION 53, T-62-N, R-51-E, GC&SF SRUVEY MCCAMEY-KEMPER 10-INCH |  | LINE PIPE | LONGITUDINAL WELD |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5450 | 5044.8397 | 10177.4794 | CRUDE OIL | 1 | 350 | 150 | NO | NO | 10 | 0.25 | 30000 | WELDED |  | 870 | 925 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262 | PIPE SPLIT IN LAP-WELD SEAM DURING PRESSURE TEST
2017-09-29 08:50 | NO | NO | 19870242 |  | 26043 | GOLDEN EAGEL REFINING CO | NO | 1987-12-14 | 915 | CA | LOS ANGELES | WILMINGTON | NO |  | NO | ON THE FAR SIDE OF FRIES AVE ABOUT 150 FT NORTH OF WATER ST. WEST SIDE OF STREET ABOUT 2- T0 3 FT OUT IN RIGHT HAND LANE |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 925.6587 | 1867.4274 | CRUDE OIL | 1 | 25 | 15 | NO | NO | 8 | 0 |  | WELDED |  | 600 | 400 | NO | 0 | 0 | 3 | 85 | EXTERNAL | Null | YES | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | NO | Null | ROBERT D ROBERTSON TERMINAL MANAGER | 2138344495 | AT ABOUT 0915 ON 12-14-87, I GOT A CALL FROM U P R ASKING ABOUT IF WE WERE USING OUR LINE ON FRIES! I WENT TO LOCATION, FOUND APPROXIMATELY 15 TO 25 GALLONS MAX OF CRUDE IN STREET, I SENT SAMPLE TO TERMINAL FOR GRAVITY CHECK. AT ARRIVAL I HAD PIPELING SHUT DOWN. ANYWAY, LINE REPAIRED AND CLEAN UP COMPLETED. AT THE TIME OF INCIDENT WE WERE SHIPPING CRUDE TO FLETCHER OIL LINE PRESSURE 400# I DID NOT GET A NOTIFICATION FROM WHEEL
2017-09-29 08:50 | YES | NO | 19870243 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-12-01 | 1215 | TX | REAGAN | RANKIN | NO |  | NO | SE 1/4, SE 1/4, BLOCK 28 SECTION 28, T-89-S, R-48-E MCCAMEY-KEMPER 10 INCH |  | LINE PIPE | LONGITUDINAL WELD |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 2690 | 2490.0218 | 5023.3798 | CRUDE OIL | 1 | 250 | 170 | NO | NO | 10 | 0.25 | 30000 | WELDED |  | 870 | 800 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870244 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-12-02 | 1000 | TX | REAGAN | BIG LAKE | NO |  | NO | NW 1/4, SE 1/4, SECTION 10, BLOCK 8, T-87-N, R-7-E MCCAMEY-KEMPER 10 INCH |  | LINE PIPE | LONGITUDINAL WELD |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 2070 | 1916.1134 | 3865.5748 | CRUDE OIL | 1 | 100 | 60 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 870 | 900 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870245 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-12-04 | 1015 | TX | UPTON | RANKIN | NO |  | NO | SW 1/4, SE 1/4, SECTION 11, BLOCK 4, UNIVERSITY OF TEXAS SURVEY MCCAMEY-KEMPER 10-INCH |  | LINE PIPE | LONGITUDINAL WELD |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 3440 | 3184.2658 | 6423.9503 | CRUDE OIL | 1 | 250 | 140 | NO | NO | 10 | 0.25 | 30000 | WELDED |  | 870 | 900 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870246 |  | 1845 | BUCKEYE PIPELINE CO LP | YES | 1987-11-30 | 900 | PA | LEHIGH |  | NO |  | NO | SEE ATTACHED SKETCH |  | PUMPING STATION | BOLTED FITTING |  | 1953 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1851.3173 | 3734.8548 | FUEL OIL | 1 | 208 | 203 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R S EASTWOOD MANAGER, SAFETY AND ENVIRONMENTAL | 2158208300 | ABOUT 0900 HOURS (EST) ON NOVEMBER 30, 1987, NO. 2 FUEL OIL WAS OBSERVED SPRAYING FROM A 10-INCH, 600 ANSI FLANGE. THE FLANGE CONNECTED A BYPASS CHECK VALVE TONO. 3 PUMP UNIT MAINFOLD ON BUCKEYE'S MACUNGIE TO PITTSBURGH WESTBOUND PIPELINESYSTEM. THE GASKET SEALING THE FLANGE CONNECTION HAD FAILED AND PERMITTED THE RELEASE OF NO. 2 FUEL OIL. THE PIPELINE SYSTEM WAS IMMEDIATELY SHUT DOWN AND REPAIRS EFFECTED. CONTAINMENT AND RECOVERY OF RELEASED NO. 2 FUEL OIL WAS CONDUCTED AT THE MACUNGIE STATION POND.
2017-09-29 08:50 | YES | NO | 19870247 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1987-11-29 | 1200 | MN | ITASCA |  | NO |  | NO | OPERATOR'S DEER RIVER, MINNESOTA PUMP STATION LOCATED ON U S HIGHWAY NO.2 APPROXIMATELY 1 1/2 MILES EAST OF DEER RIVER, MINNESOTA. |  | PUMPING STATION | TANK |  | 1957 | OTHER | FAILURE OF A 20" GASKET A | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30500 | 28232.5894 | 56956.5363 | CRUDE OIL | 1 | 76 | 65 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J E STAUDOHAR COORDINATOR-OPERATIONS | 7153925631 | A GASKET BETWEEN THE STATION DISCHARGE VALVE AND THE CONNECTION TO THE 26" MAINLINE FAILED RESULTING IN CRUDE OIL MIGRATING TO THE SURFACE OF THE STATION YARD.THE OPERATOR WAS NOTIFIED BY A NEIGHBOR OF THE SMELL OF OIL AND THE LINE WAS SHUT DOWN. ALL OIL WAS CONTAINED ON OPERATOR'S PROPERTY. THE GASKET WAS REPLACED AND FLANGED CONNECTION WAS RETIGHTENE.
2017-09-29 08:50 | YES | NO | 19870248 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-11-27 | 1400 | LA | PLAQUEMINES |  | NO |  | NO | SPILL OCCURRED IN AN UNINHABITED MARSH; SEE ATTACHED FIGURE 1. |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 400 | 310 | NO | NO | 6 | 0.19 | 46000 | WELDED |  | 1144 | 70 | YES | 24 | 1430 | 0 | 64 | EXTERNAL | Null | YES | OTHER |  | NO DATA |  | Null | NO DATA |  | Null | Null | R L DOWNIE DIVISION MANAGER | 5043642496 | THE SIX INCH VENICE TO EMPIRE PIPELINE FAILED AFTERR A SYSTEM STARTUP ON NOVEMBER 27, 1987, RESULTING IN A SPILL OF APPROXIMATELY 400 BARRELS OF CRUDE OIL INTOTHE MARSH IN PLAQUEMINES PARIS, OF WHICH APPROXIMATELY 310 BARRELS WAS RECOVERED. THE PIPE FAILED ADJACENT TO A CIRCUMFERENTIAL WELD ON A WELD NECK FLANGE. THE FAILURE WAS CAUSED BY UNIFORM THINNING OF THE PIPE DUE TO EXTERRNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19870249 |  | 2731 | CHEVRON PIPELINE CO | YES | 1987-11-30 | 800 | NM | SOCORRO |  | NO |  | NO | SAN ANTONIO PUMP STATION (OFF HWY 380, 3 MILES EAST OF SAN ANTONIO N M SECTION 34 TSP4S RIE SURVEY (SEE ATTACHED MAP) |  | PUMPING STATION | PUMP |  | 1955 | OTHER | MECHANICAL SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 15180.8021 | 30625.8097 | GASOLINE | 3 | 50 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R C KINNEAR DIVISION MANAGER | 9156877551 | RELEASE OCCURED WHEN THE INBOARD MECHANICAL SEAL FAILED ON THE #1 PUMP AT SAN ANTONIO STATION. RELEASE WAS CONFINED TO THE STATION PROPERTY. SOCORRO FIRE DEPARTMENT CLOSED HWY 380 FOR APPROX. 40 MINUTES. WE ARE IN THE PROCESS OF INSTALLINGSEAL LEAK DETECTION EQUIPMENT ON ALL PUMPS ON THIS SYSTEM.
2017-09-29 08:50 | YES | NO | 19870250 |  | 18214 | SHAMROCK PIPELINE CORP | NO | 1987-10-29 | 1525 | TX | SWISHER |  | NO |  | NO | SECTION 33, BLOCK K, LS&V SURVEY, SWISHER COUNTY, TEXAS 7 1/2 MILES WEST AND 1 MILE SOUTH OF THE CITY OF KRESS, TEXAS |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 14440.2752 | 29131.8678 | GASOLINE | 3 | 663 | 210 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1480 | 200 | YES | 8 | 1850 | 10 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | GERALD CHILDERS MANAGER PIPELINE SAFETY & REGULATIONS | 8063783583 | AT 15:25 (CENTRAL TIME) OCTOBER 29, 1987, A ROAD GRADER OPERATED BY A SWISHER COUNTY EMPLOYEE, STRUCK AND RUPTURED OUR 6 5/8" ABERNATHY PRODUCTS PIPELINE WHILECLEANING DITCHES ADJACENT TO A COUNTY DIRT ROAD. 663 BARRELS OF PREMIUM UNLEADED GASOLINE ESCAPED OF WHICH 206 BARRELS WERE SUBSEQUENTLY RECOVERED RESULTING INA NET LOSS OF 457 BARRELS. A PIPELINE WARNING SIGN WAS INPLACE AND LOCATED 8 FEET NORTH OF THE RUPTURE SITE. ADDITIONALLY, OUR AERIAL MILE MARKER NO. 116 AND ANOTHER WARNING SIGN WERE IN PLACE 45 FEET TO THE SOUTH AND ACROSS THE ROAD FROM THE DAMAGE SITE. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19870252 |  | 18386 | SOHIO PIPELINE CO | NO | 1987-10-30 | 2320 | OH | WOOD |  | NO |  | NO | 12716 TANK FARM ROAD, CYGNET OHIO 12 FEET EAST OF WAREHOUSE BUILDING |  | TANK FARM | NO DATA | SCREWED 10" PIPE PLUG | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 273 | 272 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC | PIPE IS COATED, BUT SCREW | NO DATA |  | Null | NO DATA |  | Null | Null | G A DEBROCK NORTHERN REGION SUPERINTENDENT | 2163514777 | CURDE OIL WAS BEING PUMPED INTO STORAGE TANK #8 AT THE CYGNET TANK FARM FROM THE MID-VALLEY/MAUMEE 22" PIPELINE. ON A ROUTINE CHECK OF THE TANK GAUGE, THE MID-VALLEY OPERATOR NOTICED A STRONG ODOR OF CRUDE OIL. HE DISCOVERED THE LOCATION OF THE LEAK, NOTIFIED SOHIO PIPE LINE PERSONNEL AND SWITCHED FLOW TO A DIFFERENT TANK. SOHIO AND MID-VALLEY PERSONNEL DETERMINED THE EXTENT OF THE SPILL ON THE SOHIO PROPERTY AND IN A DRAINAGE PIPE AND ROCKY FORD RIVER. THE SPILL WAS CONTAINED AND RECOVERED THAT DAY.
2017-09-29 08:50 | YES | NO | 19870253 |  | 1248 | BELLE FOURCHE PIPELINE CO | NO | 1987-11-11 | 1115 | WY | NIOBRARA |  | NO |  | NO | SECTION 20, TOWNSHIP 34 NORTH, RANGE 66 WEST, NIOBRARA COUNTY, WYOMING |  | LINE PIPE | PIPE |  | 1968 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 4165.464 | 8403.4234 | CRUDE OIL | 1 | 100 | 25 | YES | NO | 12 | 0.22 | 60000 | WELDED |  | 1440 | 1076 | YES | 0 | 0 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H A TRUE III SENIOR VICE-PRESIDENT | 3072379301 | NOVEMBER 11, 1987, BELLE FOURCHE PIPELINE COMPANY'S 12-INCH DONKEY CREEK TO GUERNSEY PIPELINE FAILED, RELEASING ABOUT 100-200 BARRELS OF SWEET CRUDE OIL. CAUSEOF THE FAILURE WAS A SPLIT LONGITUDIAL WELD. THE LINE WAS OPERATING WELL WITHINITS SPECIFIED LIMITS AT THE TIME OF THE FAILURE, AND ALL CONTROLS WORKED PROPERLY, MINIMIZING THE OIL LOST. NO OIL REACHED SURFACE WATER.
2017-09-29 08:50 | YES | NO | 19870254 |  | 12628 | MOBIL PIPELINE CO | NO | 1987-10-24 | 2000 | TX | BEE |  | NO |  | NO | AT MOBIL PIPE LINE COMPANY'S BEEVILLE STATION, WHICH IS NEAR THE WEST CITY LIMITS OF BEEVILLE AND 200 YARDS NORTH OF HIGHWAY 59. |  | PUMPING STATION | NO DATA | 4" GASKET | 1986 | OTHER | 4" GASKET FAILED BETWEEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2776.976 | 5602.2823 | GASOLINE | 3 | 79 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D L DENNARD VICE PRESIDENT OPERATION | 2146582226 | A 4" GASKET FAILED ON THE DISCHARGE OF BEEVILLE PUMPING STATION DURING NORMAL OPERATIONS. THE GASKET WAS ADJACENT TO A CHECK VALVE. A NEW GASKET WAS INSTALLED AND THE STATION WAS RETURNED TO OPERATION.
2017-09-29 08:50 | YES | NO | 19870255 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-11-05 | 1720 | KS | BROWN |  | NO |  | NO | NW1/4 OF SECTION 8, TOWNSHIP 2 SOUTH, RANGE 18 EAST, BROWN COUNTY, KANSAS |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 925.6587 | 1867.4274 | GASOLINE | 3 | 235 | 205 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1100 | 650 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA | C0-REPRESENTATIVES ON SIT | Null | Null | H E JANZEN VICE PRESIDENT-OPERATIONS | 9185883850 | AT APPROXIMATELY 1720 HOURS ON NOVEMBER 5, 1987, A BACKHOE OPERATOR CONTRACTED BY WILLIAMS PIPE LINE COMPANY STRUCK AND PUNCTURED THE KANSAS CITY- IRVINGTON #3-8". THE EQUIPMENT OPERATOR WAS DIGGING A BELL-HOLE IN PREPARATION FOR A TIE-IN OF A NEW SPOOL AT A STREAM CROSSING. WHILE LIFTING THE BUCKET OUT OF THE HOLE, IT STRUCK THE 8" LINE, CREATING A SMALL PUNCTURE. THE LINE WAS IMMEDIATELY SHUT DOWN AND VALVES AT MP 73+21 AND MP 82+47 WERE CLOSED. EQUIPMENT ALREADY ON SITE WAS USED TO CREATE AN EARTHEN DAM TO CONTAIN ALL PRODUCT (REGULAR GASOLINE) AND KEEP IT FROM ENTERING THE CREEK. AT NO TIME DID ANY GASOLINE REACH THE WATER. AFTER A MAJORITY OF THE GASOLINE WAS REMOVED FROM THE DITCH, AND ATTEMPT WAS MADE TO PLUG AND SADDLE THE LINE. THE SADDLE ATTEMPT WAS NOT SUCCESSFUL, AND THE LINE WAS THEN TAPPED AND COMPLETELY DRAINED UP BETWEEN THE TWO (2) VALVES. SINCE A NEW SPOOL HAD ALREADY BEEN PLACED BENEATH THE STREAM BED, THIS NEW BED, THIS NEW SPOOL WAS TIED IN AND THE LINE WAS PLACED INTO SERVICE AT APPROXIMATELY 1810 HOURS ON NOVEMBER 6, 1987.
2017-09-29 08:50 | YES | NO | 19870256 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1987-10-29 | 2400 | TX | RANDALL |  | NO |  | NO | LINE GAINES-BORGER- MP 216-32+71 APPROXIMATELY 3 MILES WEST OF INTERSTATE 87 ON F M 1705 AND 1/4 MILE SOUTH (NORTHWEST OF HAPPY, TEXAS) |  | LINE PIPE | GIRTH |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2025 | 1874.4588 | 3781.5405 | NATURAL GAS LIQUID | 3 | 75 | 0 | NO | NO | 8 | 0.19 | 40000 | WELDED |  | 1180 | 626 | YES | 24 | 1535 | 4 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | B L THORMAN MANAGER OF ENG. AND TECHNICAL SERVICES | 9186614721
2017-09-29 08:50 | YES | NO | 19870257 |  | 13131 | CONOCO INC | YES | 1987-11-01 | 1330 | CO | ADAMS | COMMERCE | NO |  | NO | NW1/4, SW1/4, SEC 12, T3S, R68W 5701 BRIGHTON BLVD. COMMERCE CITY, CO 80022 |  | LINE PIPE | PIPE |  | 1973 | OTHER | HUMAN ERROR, EMPLOYEE CLO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 29621.0774 | 59757.6775 | CRUDE OIL | 3 | 245 | 0 | NO | NO | 12 | 0.38 | 35000 | WELDED |  | 150 | 60 | YES | 8 | 300 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | OTHER | OIL SPILL CONTINGENCY PLA | Null | Null | LARRY G HUBBARD DIRECTOR ENVIRONMENTAL AFFAIRS | 7132932032 | REFINERY PERSONNEL CLOSED VALVE ON TANK #58 AFTER TANK STARTED TO OVERFLOW LOCKED-IN PRESSURE BLEW RUPTURE DISKS, SHUTTING DOWN MAINLINE BUT NOT BEFORE BLOWINGSEVERAL FLANGE GASKETS IN CONOCO PIPLLINE MANIFOLD AND REFINERY RECEIVING LINES. HUMAN ERROR WAS DUE TO OIL MOVEMENTS CORRDINATOR NOT SWITCHING TANKS.
2017-09-29 08:50 | YES | NO | 19870258 |  | 809 | ARCO PIPE LINE CO | YES | 1987-11-03 | 1032 | IL | WILL |  | NO |  | NO | APPROXIMATELY 1-1/2 MILES SOUTH OF MANHATTAN, ILLINOIS UNDER ILLINOIS HIGHWAY 52 |  | LINE PIPE | NO DATA |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2300 | 2129.0149 | 4295.0831 | FUEL OIL | 2 | 159 | 90 | NO | NO | 8 | 0.25 | 24000 | WELDED |  | 685 | 650 | YES | 24 | 780 | 7 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | N B BENNETT MANAGER-NORTH AREA OPERATIONS | 3163311300 | EXTERNAL GALVANIC CORROSION LEAK ON 8" PRODUCT PIPE LINE ESTIMATED 159 BBLS OUT, 90 RECOVERED, NET ESTIMATED LOSS 69 BBLS
2017-09-29 08:50 | YES | NO | 19870259 |  | 443 | AMOCO PIPELINE CO | YES | 1987-10-29 | 1100 | OK | CADDO |  | NO |  | NO | 3 MI, W, WM, N OF COGAR, OK (INTERSECTION OF STATE HWYS 152 + 37 |  | LINE PIPE | NO DATA |  | 1943 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2776.976 | 5602.2823 | CRUDE OIL | 1 | 2500 | 1950 | NO | NO | 16 | 0.28 | 35000 | WELDED |  | 700 | 400 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | J W WILHELM AREA MANAGER OPERATIONS | 9182257271 | THE 16" PIPELINE WAS STRUCK BY CADDO COUNTY, DISTR. #2, ROAD GRADER IN THE DITCH OF A COUNTY ROAD. THE LINE WAS PUNTURED AND CRUDE OIL (APPROX. 2500 BBLS) RAN INTO BUGGY CREEK, CONTAINMENT DAMS WERE INSTALLED AND OIL PICKED UP, HOWEVER HEAVY RAINS WASHED OUT THE DAM BEFORE OIL TRTRIEVAL WAS COMPLETED. SOME OIL WAS LOST DOWNSTREAM. CLEAN UP CREWS ARE CONTINUING WORKING, BURNING OIL IN SMALL POOLS+ PICKING UP WITH SORBENT MATERIALS.
2017-09-29 08:50 | YES | NO | 19870260 |  | 805 | ATLANTIC PIPELINE CORP | YES | 1987-11-11 | 1302 | PA | CHESTER |  | NO |  | NO | SEE ATTACHED. SHIP ROAD IN WEST WHITELAND TWP., CHESTER CO., PA. |  | LINE PIPE | PIPE |  | 1937 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 275000 | 254556.1336 | 513542.5407 | GASOLINE | 3 | 1670 | 380 | NO | NO | 12 | 0.38 | 35000 | WELDED |  | 1000 | 600 | YES | 1 | 500 | 9 | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | HAROLD G HIESTER OPERATIONS MANAGER | 2156788005 | THE INCIDENT CAME TO OUR ATTENTION ON 11/9/87 AT APPROXIMATELY 1210 P.M. WHEN WERE NOTIFIED THAT A HOME OWNER IN WEST WHITELAND TWP., CHESTER CO,. PA. SMELLED GASOLINE FUMES IN HIS BASEMENT. OUR 12" PIPELINE WAS HSUT DOWN AND WE IMMEDIATELY WENT TO THE AREA TO INVESTIGATE THE POSSIBILITY OF A LEAK. WE WALKED OUR LINE THROUGHOUT THE DAY WITHOUT FINDING ANY EVIDENCE OF A LEAK ON THE SURFACE. A PRESSURE CHECK ON THE SEGMENT OF LINE IN THIS AREA REVEALED A PRESSURE LOSS. THE FOLLOWING DAY A PIPELINE LEAK CONSULTANT WAS HIRED TO ASSIST US IN THE SEARCH. BOREHOLES WERE DUG ALONG THE PIPELINE SO THAT A VAPOR ANALYZER COULD DETECT FOR GASES. ON 11/11/87 WE BEGAN EXCAVATING OUR PIPELINE IN SHIP ROAD 250 FT. SOUTH OF THE INTERSECTION WITH HILLCREST WHERE THE GREATEST INDICATION OF VAPORS WAS FOUND. AT 1302 THE LEAK WAS DISCOVERED AT THE FIVE O'CLOCK POSITION OF THE PIPE. BY 1330 THE HOLE WAS CLAMPED.
2017-09-29 08:50 | YES | NO | 19870261 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-11-17 | 1330 | TX | UPTON | RANKIN | NO |  | NO | SE 1/4, SE 1/4, SECTION 54, BLOCK B, GC&SF SURVEY MCCAMEY-KEMPER 10-INCH |  | LINE PIPE | LONGITUDINAL WELD |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 4115 | 3809.0854 | 7684.4638 | CRUDE OIL | 1 | 350 | 200 | NO | NO | 10 | 0.25 | 30000 | WELDED |  | 870 | 750 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19870262 |  | 18273 | SHELL PIPE LINE CORP | YES | 1987-11-24 | 1200 | TX | REAGAN | BIG LAKE | NO |  | NO | SE 1/4, DE 1/4, SECTION 26, T-87-N, R-2-E, BLOCK 1 MCCAMEY-KEMPER 10-INCH APPROXIMATELY 15 MILES EAST OF RANKIN |  | LINE PIPE | LONGITUDINAL WELD |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1250 | 1157.0733 | 2334.2843 | CRUDE OIL | 1 | 50 | 20 | NO | NO | 10 | 0.25 | 30000 | WELDED |  | 870 | 750 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W HOLDEN, MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262 | LINE SPLIT IN LAP-WELD SEAM DURING PRESSURE TEST
2017-09-29 08:50 | YES | NO | 19870263 |  | 30501 | CON - DOR PIPELINE CO | NO | 1987-11-23 | 1030 | TX | HOPKINS | SULPHUR SPRING | NO |  | NO | QUARTER MILE EAST OF TEXAS HIGHWAY 19, 2 MILES SOUTH OF INTERSTATE HIGHWAY 30. NACODOCHES UNIVERSITY SURVEY A-695. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 11107.904 | 22409.129 | GASOLINE | 3 | 207 | 162 | NO | NO | 6 | 0.16 | 42000 | WELDED |  | 1440 | 600 | YES | 8 | 1850 | 12 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES T RAU DISTRICT SUPERINTENDENT | 8174812909 | PIPELINE RUPTURED BY CONTRACTOR DURING EXCAVATION FOR TELEPHONE CABLE INSTALLATION. CONOCO OPERATIONS COORDINATOR IN HOUSTON NOTED REDUCTION IN PRESSURE AND SHUT THE LINE DOWN. CLEAN-UP AND REPAIRS WERE INITIATED THE SAME DAY AND ALL WORK WAS COMPLETE BY EARLY THE FOLLOWING MORNING.
2017-09-29 08:50 | YES | NO | 19870265 |  | 20040 | UNION CARBIDE CORP | NO | 1987-10-31 | 118 | WV | CALHOUN |  | NO |  | NO | ONE MILE NORTH OF ROAD RUN ROAD (TR. 2 4/1) ON UNION CARBIDE RIGHT-OF-WAY |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 3 |  | 0 | YES | NO | 4 | 0.34 | 60000 | WELDED |  | 2040 | 975 | YES | 4 | 2750 | 2 | 52 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM B TROUTMAN PIPELINES GROUP SUPERVISING ENGINEER | 3047472112 | AT 1:18 A.M. OCTOBER 31, 1987, A PHONE MESSAGE WAS RECEIVED BY THE UNION CARBIDE TELEPHONE ATTENDANT FROM THE DISPATCHER AT THE CALHOUN COUNTY JAIL (MR. M. C. CROSKEY THAT THE ARNOLDSBUR, WV, VOLUNTEER FIRE DEPARTMENT HAD REPORTED A FIRE NEAR UNION CARBIDE'S PIPELINE. PUMPING OF ETHAN INTO THE LINE WAS STOPPED AT 1:30A.M. AND TWO CREWS FROM UNION CARBIDE WERE SENT TO THE SITE. THE LINE WAS FURTHER CLOSED IN 3:45 A.M. AND THE FIRE WAS ALLOWED TO BURN OUT. THE SOURCE OF IGNITION IS UNKNOWN BUT WAS BELIEVED TO HAVE BEEN STARTED BY HUNTERS IN THE AREA SINCE IT WAS HUNTERS WHO INITIALLY REPORTED THE FIRE. THE WEST VIRGINIA OFFICE OF PIPELINE SAFETY WAS CONTACTED THE MORNING OF OCTOBER 31. THE SIZE OF THE FIRE ZONEWAS APPROXIMATELY A 5-FOOT SEMI-SPHERE.
2017-09-29 08:50 | NO | NO | 19870266 |  | 3466 | DOME PIPELINE CORP | YES | 1987-10-26 | 1400 | MN | BENSON |  | NO |  | NO | BENSON PUMP STATION, BENSON, MN |  | PUMPING STATION | NO DATA | DIFFERENTIAL PRESSURE GAU | 1978 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 3 | 1 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J L WILLIAMS OPERATION MANAGER | 3193547722 | FAILURE OF A DIFFERENTIAL PRESSURE GAUGE WHICH WAS RATED FOR 2000 PSIG WORKING PRESSURE; HOWEVER FAILURE OCCURRED WHEN REPRESSURING AT APPROXIMATELY 110 PSIG (MAXIMUM WORKING PRESSURE OF DOME SYSTEM IS 1440 PSIG). GAUGE IS OF A MANUFACTURETHAT IS CURRENTLY OBSOLETE AND IS NOT SUPPORTED BY THE MANUFACTURER. WHILE THE CAUSE OF THE FAILURE IS UNKNOWN, WE BELIEVE THAT THE PRESSURIZED BODY OF THIS GAUGE CAME APART WHEN ONE OF THE BOLTS HOLDING THE FRONT AND BACK PLATES TO GETHERFAILED. CURRENTLY, REPLACING ALL THE EXISTING OLD GAUGES WITH THE NEW CURRENT MODEL WITH A WORKING PRESSURE OF 3000 PSIG.
2017-09-29 08:50 | YES | NO | 19870267 |  | 2371 | CINIZA PIPELINE INC | NO | 1986-08-01 | 830 | NM | SANDOVAL |  | NO |  | NO | NE 1/4 OF SE 1/4 SECTION 23 TOWNSHIP 23NRANGE 7W |  | LINE PIPE | PIPE |  | 1952 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2520 | 2384.6835 | 4810.8698 | CRUDE OIL | 1 | 318 | 194 | NO | NO | 4 | 0.16 | 1700 | WELDED |  | 650 | 400 | YES | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PIPE LINE MARKERS | NO | NO | ROBERT ULLO GENERAL MANGER OF PIPE LINE OPERATIONS | 5056328006 | LYBROOK-HOSPAH 4" LINE WAS HIT BY BCO ROAD GRAGER. REPAIRS MADE BY REPLACING 12' OF PIPE.
2017-09-29 08:50 | YES | NO | 19870268 |  | 2371 | CINIZA PIPELINE INC | NO | 1986-10-12 | 2400 | NM | RIO ARRIBA |  | NO |  | NO | CINIZA PIPE LINE INC. - APACHE STATION SE 1/4 OF SE 1/4 OF SECTION 33 TOWNSHIP 25N RANGE 6W |  | PUMPING STATION | NO DATA | 1/4" NEW NIPPLE ON SAMPLE | 1986 | OTHER | DEFECTIVE MATERIAL - 1/4" | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 141.9454 | 286.3613 | CRUDE OIL | 1 | 170 | 160 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT ULLO GENERAL MANAGER OF PIPE LINE OPERATIONS | 5056328006 | A NEW 1/4" NIPPLE ON SAMPLER LOOP OF NEW ACT UNIT BROKE. A NEW HEAVY DUTY 1/4" NIPPLE WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19870269 |  | 2371 | CINIZA PIPELINE INC | NO | 1986-11-20 | 1215 | NM | MCKINLEY |  | NO |  | NO | MOLERES RANCH. NW 1/4 OF NW 1/4 SECTION 17 TOWNSHIP 18N RANGE 8W |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 1064.5908 | 2147.7097 | CRUDE OIL | 1 | 75 | 0 | NO | NO | 4 | 0.25 | 1700 | WELDED |  | 650 | 320 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT ULLO GENERAL MANAGER OF PIPE LINE OPERATIONS | 5056328006 | LEAK WAS CAUSED BY EXTERNAL CORROSION. REPAIRS WERE MADE WITH PATCH AND U-BOLT CLAMPS.
2017-09-29 08:50 | YES | NO | 19870270 |  | 2371 | CINIZA PIPELINE INC | NO | 1986-12-22 | 2400 | NM | SANDOVAL |  | NO |  | Null | STAR LAKE BOOSTER STATION - NE 1/4 OF SE /4 SECTION 18 TOWNSHIP 21 RANGE 7W |  | PUMPING STATION | NO DATA | 1/2" HIGH PRESSURE NIPPLE | 1985 | OTHER | LAKE WAS CAUSED BY A BROK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2300 | 2176.4968 | 4390.8732 | CRUDE OIL | 1 | 150 | 35 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT ULLO GENERAL MANAGER OF PIPE LINE OPERATIONS | 5056328006 | LEAK WAS CAUSED BY A BORKEN 1/2" PRESSURE NIPPLE. REPAIRS WERE MADE BY REMOVINGBROKEN NIPPLE AND REPLACING WITH FLEX HOSE.
2017-09-29 08:50 | YES | NO | 19870271 |  | 2371 | CINIZA PIPELINE INC | NO | 1987-05-31 | 1300 | NM | RIO ARRIBA |  | NO |  | NO | SE1/4 SW1/4 SECTION 17 TOWNSHIP 24N RANGE 6W 7.2 MILES NORTH OF LYBROOK, NEW MEXICO |  | LINE PIPE | PIPE |  | 1953 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 472.0859 | 952.388 | CRUDE OIL | 1 | 90 | 65 | NO | NO | 4 | 0.25 | 2330 | WELDED |  | 920 | 800 | YES | 8 | 1310 | 3 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PIPE LINE MARKERS | NO | NO | ROBERT ULLO GENERAL MANAGER OF PIPE LINE OPRATIONS | 5056328006 | EL PASO NATURAL GAS CO. WAS GRADING ROAD AND CUTTING DIVERSION DITCHES FROM ROAD OUT INTO THE PASTURE. WHILE GRADING DITCH THE GRADER BLADE KNOCKED A HOLE IN OUR LINE.
2017-09-29 08:50 | YES | NO | 19870272 |  | 2371 | CINIZA PIPELINE INC | YES | 1987-06-26 | 1030 | NM | RIO ARRIBA |  | NO |  | NO | SW1/4 SE1/4 SECTION 13 TOWNSHIP 25N RANGE 3W SEVEN MILES NORTHWEST OF LINDRITH, NEW MEXICO |  | LINE PIPE | PIPE |  | 1984 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1900 | 1758.7515 | 3548.1121 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 4 | 0.16 | 1640 | WELDED |  | 1000 | 350 | YES | 8 | 1200 | 0 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA | PIPE LINE MARKERS | NO | NO | ROBERT ULLO GENERAL MANAGER OF PIPE LINE OPERATIONS. | 5056328006 | FOUR-FOUR CONSTRUCTION COMPANY WAS DIGGING A DITCH FOR A PIPELINE ACROSS OUR LINE AND RUPTURE THE LINE WITH THEIR BACKHOE.
2017-09-29 08:50 | YES | NO | 19870273 |  | 2371 | CINIZA PIPELINE INC | NO | 1986-03-04 | 800 | NM | RIO ARRIBA |  | NO |  | NO | NE1/4 OF NE1/4 OF SECTION 32 TOWNSHIP 25N RANGE 4W |  | PUMPING STATION | NO DATA | 1/2" HIGH PRESSURE NIPPLE | 1985 | OTHER | HIGH PRESSURE NIPPLE BROK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1419.4545 | 2863.613 | CRUDE OIL | 1 | 75 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT ULLO | 5056328006 | A HIGH PRESSURE 1/2" NIPPLE ON PUMP DISCHARGE LINE TO AIR BLEED VALVE BROKE. VALVE AND NIPPLE WERE REMOVED FROM LINE. A 1/2" PLUG WAS INSTALL IN WELD-O-LET.
2017-09-29 08:50 | YES | NO | 19870274 |  | 3505 | DOUGLAS OIL PURCHASING CO INC | NO | 1987-02-19 | 230 | AL | MOBILE | CITRONELLE | NO |  | NO |  |  | PUMPING STATION | SCRAPER TRAP |  | 1957 | OTHER | PACKING NUT BACKED OFF ON | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 50 | 40 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | NO DATA | PUMPING STATION | Null | NO DATA |  | Null | Null | TRAVIS LEUIS | 2058665503 | PACKING NUT BACKED OFF ON GARDEN DENVER PUMP, CAUSING LEAK AT PUMPING STATION
2017-09-29 08:50 | YES | NO | 19880001 |  | 4906 | EXXON PIPELINE CO | NO | 1987-12-01 | 1205 | TX | MCLENNAN |  | NO |  | NO | LEAK OCCURRED AT STATION 340+99 (NEAR TEHUACANA CREEK) SOME 3 MILES SOUTH OF WACO STATION ON THE WACO-HEARNE 8-INCH PIPELINE. |  | LINE PIPE | OTHER | STOPPLE FITTING (0-RING) | 1978 | OTHER | O-RING STOPPLE FITTING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 5553.952 | 11204.5645 | GASOLINE | 3 | 200 | 75 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1881 | 200 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT 1205 HOURS ON DECEMBER 1, 1987, A PRODUCTS LEAK WAS REPORTED BY TEXACO PIPELINE TO EPC HEADQUARTERS IN LONGVIEW, TX. THE WACO, TX GAUGING SUPERVISOR WAS IMMEDIATELY NOTIFIED AND EPC PERSONNEL WERE DISPATCHED TO THE LEAK SITE TO INVESTIGATE THE REPORT. AT 1310 HOURS THE GAUGING SUPERVISOR ARRIVED AND REQUESTED A BACKHOE TO EXCAVATE THE SITE. PRODUCTS WERE SEEPING OUT OF THE GROUND AND HAD RAN INTO A NEARBY ROCK QUARRY, WHERE IT WAS CONTAINED. AFTER EXCAVATION, AT 1405 HOURS, IT WAS CONFIRMED THAT THE LEAK BELONGED TO EPC, SO THE LINE WAS SHUT DOWNAND BLOCK VALVES CLOSED TO ISOLATE THE LEAK SITE. ADDITIONAL EPC PERSONNEL ALONG WITH CONTRACTED EQUIPMENT AND VACUUM TRUCKS WERE DISPATCHED TOTHE LEAK SITE AT ABOUT 1610 HURS. THE PRODUCT WAS FOUND TO BE COMING FROM A STOPPLE FITTING WHICH WAS PLACED ON THE LINE IN 1978 TO INSTALL A CREEK CROSSING. THE LINE HAD TOBE DRAINED DOWN AND PERMANENT REPAIRS MADE BY INSTALLING A NEW O-RING, ALONG WITH A NEW BLIND FLANGE AND FLEXTAULIC GASKETS. THE LINE WAS RESTORED TO SERVICE AT 1330 HOURS ON 12-3-87.CLEAN UP OPERATIONS HAVE BEEN COORDINATED ALONG WITH THE TWC AND HAVE CONSISTEDOF VACUUMING UP THE EXCESS PRODUCTS AND DIGGING SEVERAL PITS TO ALLOW THE PRODUCTS TO SEEP OUT OF THE GROUND. CLEANUP IS STILL IN PROGRESS WHILE SOIL AND WATERSAMPLES HAVE BEEN TAKEN TO DETERMINE THE EXTENT OF CONTAMINATION.
2017-09-29 08:50 | YES | NO | 19880002 |  | 443 | AMOCO PIPELINE CO | Null | 1988-01-06 | 900 | TX | BRAZORIA | ALVIN | NO |  | NO | SURVEY A.C.H. & B A-416 RRC LEASE # 05624. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 448.3824 | 904.5684 | CRUDE OIL | 1 | 775 | 770 | NO | NO | 6 |  |  | WELDED |  | 50 | 40 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL P. CLANCY | 7133322476
2017-09-29 08:50 | YES | NO | 19880003 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1988-01-11 | 2038 | WI |  | SUPERIOR | NO |  | NO | OPERATOR'S SUPERIOR, WISCONSIN TERMINAL LOCATED WITHIN THE CITY OF SUPERIOR, WISCONSIN, 2800 EAST 21ST STREET. |  | TANK FARM | PIPE |  | 1950 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4483.8238 | 9045.6836 | CRUDE OIL | 1 | 174 | 169 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.E. STAUDOHAR | 7153925631 | A VALVE GAVE AN INDICATION IT HAD OPENED DURING A TANK SWING WHEN, IN FACT, IT HAD NOT. THE RESULTING BUILDUP OF PRESSURE CAUSED AN 18" O.D. SECTION OF LINE TO FAIL. ALL OIL SPILLED WAS CONFINED TO OPERATOR'S TERMINAL SITE THE 18" LINE HAS BEEN REMOVED FROM SERVICE AND WILL NOT BE REPLACED.
2017-09-29 08:50 | YES | NO | 19880004 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-12-21 | 745 | NE |  | OMAHA | NO |  | NO | OMAHA TERMINAL |  | TANK FARM | TANK |  | 1950 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13884.88 | 28011.4113 | GASOLINE | 3 | 80 | 16 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD JANZEN, VICE PRESIDNET - OPERATIONS | 9185883850 | ON DECEMBER 21, 1987, A LEAK WAS DISCOVERED IN TANK #1410 AT OUR OMAHA TERMINAL. LOCATION PERSONNEL NOTICED UNLEADED GASOLINE COLLECTING AT THE BASE OF THE TANK. THE TANK'S CONTENTS WERE IMMEDIATELY TRANSFERRED AND RECOVERY OPERATIONS WERE INITIATED. A TOTAL OF 80 BARRELS WAS RELEASED, OF WHICH 16 WERE RECOVERED.THE LEAK APPEARS TO HAVE RESULTED FROM AN INTERNAL CORROSION PIT IN THE TANK BOTTOM. THE TANK HAS BEEN TAKEN OUT OF SERVICE UNTIL REPAIRS CAN BE COMPLETED. THE CLEAN UP IS BEING CONDUCTED IN FULL COOPERATION WITH THE NEBRASKA DEPARTMENT OF ENVIRONMENTAL CONTROL.
2017-09-29 08:50 | YES | NO | 19880005 |  | 2327 | CHEVRON USA INC | NO | 1987-12-23 | 1530 | CA | KERN | LOST HILLS | NO |  | NO | N/W 1/4 SEC 9, T27S, 1 MILE EAST OF BROWN MATERIAL RD 1 MILE SOUTH OF HWY 46 |  | LINE PIPE | PIPE |  | 1935 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL |  | 60 | 50 | NO | NO | 3 | 0.26 | 4320 | THREADED |  | 1100 | 550 | YES | 0 | 1180 | 12 | 80 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. BAILEY , DISTRICT SUPERVISOR | 8057632202 | AN EXTERNAL CORROSION PIT RESULTED IN A 60 BBL. LEAK. TEMPORARY REPAIRS WERE COMPLETED 12/23/87. REPLACEMENT OF 200' OF PIPE WAS COMPLETED 12/31/87.
2017-09-29 08:50 | YES | NO | 19880006 |  | 2327 | CHEVRON USA INC | NO | 1987-12-16 | 800 | CA | KERN | TAFT | NO |  | NO | SEC 24, T32S, R23E, 100'S OF WOOD ST CROSS ST HWY 33 TAFT, CA. |  | LINE PIPE | PIPE |  | 1920 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL |  | 60 | 50 | NO | NO | 0 |  |  | NO DATA |  | 800 | 400 | YES | 0 | 1050 | 10 | 81 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. BAILEY, DISTRICT SUPERVISOR | 8057632202 | AN EXTERNAL CORROSION PIT RESULTED IN A 60 BBL LEAK. TEMPORARY REPAIRS WERE COMPLETED AND PERMANENT REPAIRS IS SCHEDULED FOR THE 1ST QUARTER OF 1988.
2017-09-29 08:50 | YES | NO | 19880008 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1987-12-18 | 1415 | KS | BUTLER |  | NO |  | NO | 12" BLUE LINE-BORGER-E. CHICAGO. MP 291-14+43 4 1/4 MILES NORTH OF TOWN OF TOWANTA. (SEC. 21, T25S, R4E). |  | LINE PIPE | GIRTH |  | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2314.1467 | 4668.5686 | L. P. G. | 2 | 100 | 0 | NO | NO | 12 | 0.25 | 40000 | WELDED |  | 960 | 633 | YES | 24 | 1549 | 8 | 77 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECH. SERVICES | 9186614721 | PROPERTY OWNER REPORTED A PROPANE LEAK IN HIS PASTURE LAND. BLUE LINE WAS SHUTDOWN AND BLOCKED. LEAK WAS IN A FAILED GIRTH WELD. LINE WAS STOPPLED ON BOTH SIDES OF THE LEAK AND 46' OF PIPE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19880009 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1987-12-14 | 110 | CO | ADAMS | COMMERCE CITY | NO |  | NO | PIPING MANIFOLD AT DENVER TERMINAL, LOCATED AT 3960 E. 56TH AVENUE, COMMERCE CITY, CO 80022. |  | TANK FARM | OTHER | PIPELINE FILTER COVER. | 1972 | OTHER | 0-RING SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 435.0596 | 877.6909 | TURBINE FUEL | 3 | 96 | 85 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L.THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | O-RING ON FILTER VESSEL LID BLEW OUT SPRAYING PRODUCT ONTO SURROUNDING AREA.
2017-09-29 08:50 | YES | NO | 19880010 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1987-12-10 | 642 | SD |  | CANTON | NO |  | NO | CANTON TERMINAL |  | TANK FARM | PUMP |  | 1984 | OTHER | MECHANICAL SEAL FAILURE. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 100 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E.JANZEN, VICE PRESIDENT-OPERATIONS | 9185883850 | ON DECEMBER 10, 1987 AT APPROXIMATELY 0640 HOURS, THE NORTH TANK PUMP AT THE CANTON LPG TERMINAL EXPERIENCED A MECHANICAL SEAL FAILURE. THE SAFETY CONTROL EQUIPMENT (HAZARDOUS GAS DETECTOR) WAS TRIGGERED BY THE RELEASE, AND SHUT DOWN THE TERMINAL OPERATIONS, AND ALARMED THE DISPATCHING CONTROL CENTER IN TULSA. LOCAL FIRE DEPARTMENT PERSONNEL WERE NOTIFIED AND SUMMONED TO HELP ISOLATE THE AREA AND SERVE AS STAND BY UNTIL THE CLOUD OF GAS DISPERSED. LOCATION RECORDS INDICATE100 BARRELS OF LPG WERE RELEASED.
2017-09-29 08:50 | YES | NO | 19880011 |  | 18718 | SUN PIPELINE CO | Null | 1988-01-03 | 607 | TX | RUSK |  | NO |  | NO | ONE (1) MILE WEST ON HWY 13 FROM INTERSECTION OF HWY 13 AND HWY 42 AT PRICE, TEXAS. ONE (1) MILE SOUTH ON BIG SPRING CEMETARY ROAD. |  | PUMPING STATION | BOLTED FITTING |  | 1931 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 236 | 226 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E.F. MCKINLEY, JR., AREA MANAGER, COMPLIANCE |  | AT 6:07 A.M. IN JAN. 3, 1988, THE STATION DISCHARGE PRESSURE DROPPED AND THE FLOW RATE INCREASED ACTIVATING THE ALARM SYSTEM. THE STATION WAS CRASHED AND BY THE TIME OUR ATTENDENT LOCATED THE SOURCE OF THE LEAK AND CLOSED THE APPROPRIATE VALVE, APPROXIMATELY 236 BBLS OF CRUDE HAD LEAKED FROM OUR SYSTEM AND SPREAD OVER APPROXIMATELY ONE ACRE OF S.P.L.'S UNUSED LAND ADJACENT THE TANK FARM. THE ENTIRE SPILL WAS CONTAINED ON SPL PROPERTY. THE LEAK OCCURED FROM A RUPTURED 10" SERIES 600 FLANGE GASKET. THE PRESSURE PRIOR TO LEAK WAS APPROXIMATELY 890 PSIG. CLEANUP CREWS ARRIVED BY 9:00 AM (SAME DAY) AND COMMENCED THE CLEANING PROCESS. CLEAN-UP WAS COMPLETED JANUARY 11, 1988. OTHER AGENCIES NOTIFIED ARE THE TEXAS R.R. COMMISSION, NATIONAL RESPONSE CENTER, TEXAS PARK AND WILDLIFE AND THE TEXAS ATER CONTROL BOARD. THE FLANGE GASKET WAS REPLACED AND THE SYSTEM TESTED. OPERATIONS RESUMED AT 6:30 PM SUNDAY EVENING WITH NO LEAKAGE FROM THE GASKET AREA.
2017-09-29 08:50 | YES | NO | 19880012 |  | 443 | AMOCO PIPELINE CO | YES | 1987-12-14 | 1355 | IL | GRUNDY | 2-1/2 MI.EAST OF MAZON. | NO |  | Null | MAZON TOWNSHIP, T32N - R7E S1/2 OF NE 1/4 OF SECTION 13. |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 4500 | 4300 | NO | NO | 22 | 0.34 | 35000 | WELDED |  | 788 | 250 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | J.W. CARICO, AREA MANAGER | 8154784007 | A CONTRACTOR, AGRI-TILE SYSTEMS, INC. WAS INSTALLING DRAIN TILES IN A CORNFIELDAT THE LOCATION DESCRIBED ABOVE. THE TILE PLOW WAS STOPPED SHORT OF THE MARKERS INDICATING THE PIPELINE LOCATION. AS THE MACHINE WAS ADVANCE A FEW FEET TO CAP THE INSTALLED TILE, THE PIPELINE WAS STRUCK. THE RESULT WAS A LONGITUDINAL TEAR IN THE PIPE WALL, 6" IN LENGTH AT THE 9 O'CLOCK POSITION, AT THE BOTTOM OF A 9" DIAMETER, 1-1/2" DEEP DENT. THE PIPELINE WAS SHUT DOWN, AND BLOCK VALVES CLOSED IMMEDIATELY. AGRI-TILE BUILT AN EARTHEN DIKE TO CONTAIN THE SPILLED OIL. RECOVERY OPERATIONS COMMENCED APPROXIMATELY 1800 12/14. TEMPORARY REPAIRS WERE ACCOMPLISHED BY 1700 12/16. PERMANENT REPAIRS, WELDED FULL ENCIRCLEMENT SLEEVE WAS COMPLETED AT 1800 12/17. EXCAVATION AND REMOVAL OF CONTAMINATED EARTH CONTINU
2017-09-29 08:50 | YES | NO | 19880013 |  | 26141 | SHELL OIL CO | YES | 1987-12-02 | 920 | CA | KERN | BAKERSFIELD | NO |  | NO | SECTION 35, T-28S, R-27-E, MDB&M SURVEY 100 FEET WEST OF AIRPORT DRIVE, ROUND MOUNTAIN 12-INCH. |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 46.2829 | 93.3714 | CRUDE OIL | 1 | 450 | 450 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 1440 | 1000 | YES | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER REGULATIONS & MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19880014 |  | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1987-12-17 | 1300 | CA | MERCED |  | NO |  | NO | SE4/SE4 SECTION 17,, T10S, R9E, M.D.B.M., MERCED COUNTY. |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 18513.1734 | 37348.5484 | CRUDE OIL | 1 | 6500 | 6000 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 936 | 0 | NO | 0 | 0 | 0 | 86 | EXTERNAL | Null | YES | OTHER | INTERFERENCE RELATED | NO DATA |  | Null | NO DATA |  | Null | Null | RODNEY W. PENNER, DISTRICT MANAGER | 8053270110 | DURING A ROUTINE STATION OUTAGE WHILE THE PIPELINE HYDRAULICS WERE STABILIZING WE EXPERIENCED A SUDDEN LOSS OF DISCHARGE PRESSURE FROM OUR LOS BANOS STATION (UPSTREAM). SUBSEQUENT LOAD SUCTION PRESSURE DOWNSTREAM INDICATED A PIPELINE LEAKAND THE PIPELINE WAS IMMEDIATELY SHUTDOWN AND BLOCKED IN. INVESTIGATION REVEALED A LINE BREAK ORIGINATING FROM A 4" CLUSTER OF CORROSION PIT AT A LOCATION WHERE OUR LINE CROSSES ANOTHER MAJOR OIL LINE.
2017-09-29 08:50 | YES | NO | 19880015 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1987-12-02 | 0 | TX |  |  | NO |  | NO | 1074 & 893 COUNTY HIWAY CROSS ROAD 30' INTO FIELD ON NORTH SIDE. |  | LINE PIPE | PIPE |  | 1968 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 5 | 0 | NO | NO | 10 | 0.19 |  | WELDED |  | 700 | 550 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | ISOLATED PIT | NO DATA |  | Null | NO DATA |  | Null | Null | LYNN D. NEAL | 5122894831
2017-09-29 08:50 | YES | NO | 19880016 |  | 2731 | CHEVRON PIPELINE CO | NO | 1987-12-16 | 1015 | TX | CHAMBERS | WINNIE | NO |  | NO | SEE DRAWING. |  | PUMPING STATION | PUMP |  | 1952 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 46282.9334 | 93371.371 | L. P. G. | 2 | 3 | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E.SMITH DIVISON MANAGER | 4098393128 | PUMPS FAILURE TO SHUT-DOWN BURING A REMOTE COMMAND SHUT-DOWN. EXTREME INTERNALPUMP TEMPERATURES CAUSED THE E-P TO VAPOR AND IGNITE. THE VAPORS CONFINED WITHIN THE PUMP SELF-EXTINGUISHED. IT APPEARS THAT THE SUCTION AND DISCHARGE GATES CLOSED AND THE MOTOR AND PUMP CONTINUED TO OPERATE.
2017-09-29 08:50 | YES | NO | 19880017 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1987-11-12 | 1315 | TX | HIDALGO |  | NO |  | NO | 1/2 MILE SOUTH OF SHELL MCALLEN STATION 18 MILES WEST OF HWY 281. 1/2 MILE SOUTH OF HWY 1017. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6479.6107 | 13071.9919 | GASOLINE | 1 | 284 | 20 | NO | NO | 4 | 0.16 | 2912 | WELDED |  | 1000 | 800 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COASTAL | YES | YES | D.C. HUNT JR. AREA SUPERVISOR | 5122894818 | PIPELINE WAS HIT BY J.Y. CHAPA CONSTRUCTION CO. WHO WAS LAYING A FLOW LINE FOR SHELL OIL CO.
2017-09-29 08:50 | YES | NO | 19880018 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | NO | 1987-12-12 | 1302 | CA | ALAMEDA | HAYWARD | NO |  | NO | ON CANAL ROAD, PARALLELLING CABOT ROAD ACROSS STREET FROM DEPOT ROAD IN THE CITY OF HAYWARD. |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TURBINE FUEL | 3 | 80 | 60 | NO | NO | 8 | 0.2 | 52000 | WELDED |  | 1440 | 176 | YES | 8 | 1815 | 11 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BARRY R. PEARL, VICE PRESIDENT-OPERATIONS | 2134867860 | AT 1302, 12-12-87, OUR FIELD PERSONNEL AT SAN JOSE TERMINAL REPORTED A PRESSUREDROP ON THIS PIPELINE. LINE WAS ON A SCHEDULED SHUTDOWN AT THAT TIME. FIELD PERSONNEL WERE IMMEDIATELY DISPATCHED TO CHECK ON REASON FOR PRESSURE DROP. APPROXIMATELY 1555, 12-12-87, THE HAYWARD FIRE DEPARTMENT CALLED IN ON OUR EMERGENCYPHONE NUMBER AND ADVISED OF A PIPELINE LEAK IN THE CITY OF HAYWARD. MAINLINE BLOCK VALVES WERE CLOSED ON BOTH SIDES OF THE LEAK. A SMALL AMOUNT OF PRODUCE MIGRATED INTO A NEARBY FLOOD CANAL AND CLEAN-UP WORK WAS IMMEDIATELY STARTED. LINE RUPTURE WAS CAUSED BY AN OUTSIDE CONTRACTOR (D-8 CATERPILLAR). APPROXIMATELY 40 FEET OF PIPE REPLACED.
2017-09-29 08:50 | YES | NO | 19880019 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1987-12-29 | 1400 | OH | ALLEN | LIMA | NO |  | NO | PLUG VALVE ON MARATHON FILL LINE TO TANK #91. WIHTIN CONFINES OF DYKE AREA. 250' FROM DIXIE HIGHWAY. |  | TANK FARM | VALVE |  | 0 | OTHER | FAILED FORGED FITTING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9256.5867 | 18674.2742 | CRUDE OIL | 1 | 250 | 245 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DENNIS L. MOENIG AREA FOREMEN | 4196553313 | AT 1400 ON 12-29-87 A CONTRACT HAND THEIFING TANKS AT OUR LIMA STATION NOTICED A VALVE LEAKING OIL AT TANK #91. HE IMMEDIATELY NOTIFIED MR. G.G.FLETCHER THE TERMINAL FOREMAN. UPON INVESTIGATION MR. FLETCHER FOUND THE MARATHON FILL VALVE TO TANK #91 WAS CRACKED AND LEAKING.AT 1410 MR. FLETCHER CLOSED THE MARATHON HEAD GATE EAST (BLOCK VALVE) TO ISOLATE THE VALVE FROM THE MARATHON FILL LINE. MR. FLETCHER NOTIFIED D.L. MOENING AT 1430. CONTRACTORS WERE CONTACTED TO MAKE REPAIRS AND PICK UP THE OIL WITHIN THEDYKE AREA.AT 1630 WE STARTED DRAINING THE SECTION OF LINE IN ORDER TO REMOVE THE VALVE FROM SERVICE. AT 1920 THE VALVE WAS REMOVED FROM SERVICE AND BLIND FLANGES WERE INSTALLED N EITHER SIDE OF THE LINE. ON 12-30-87 THE BLIND FLANGES WERE REMOVED AND A SPOOL (PIECES OF PIPE WITH WELD NECK FLANGES ON BOTH ENDS) WAS INSTALLED IN LIEU OF REPLACING THE VALVE. THE LINE PREVIOUSLY HAD TWO (2) VALES GOING TO TANK#91 SO NO VALVE WILL BE INSTALLED IN IT'S PLACE.UPON INSPECTION OF THE VALVE IT WAS FOUND THAT THE VALVE BODY HAD CRACKED APPROXIMATELY 24" ACROSS THE TOP OF THE VALVE RUNNING PARALLED TO THE FLANGED PART.
2017-09-29 08:50 | YES | NO | 19880020 |  | 18718 | SUN PIPELINE CO | YES | 1988-01-09 | 1100 | OK | PONTOTOC | ALLEN | NO |  | Null | NE/4 SECTION 26-T5N-R8E; 1/4 MILE WEST OF ALEN, OKLAHOMA. |  | TANK FARM | OTHER | 4" BULL PLUG BOT.DRAIN VA | 1954 | OTHER | EXTENDED LOW TEMP. NEAR 0 | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.9676 | 18.0914 | GASOLINE | 1 | 280 | 100 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DONALD G. MEARS, AREA MAN. ENVIR. SAFETY & HEALTH. | 9185866942 | TULSA DISPATCHER NOTICED THAT PRODUCT LEVEL IN TANK 801 WAS DECREASING ON REMOTEGAUGE, ALTHOUGH THERE WAS NO ACTIVITY ON THE TANK. NOTIFIED OFF DUTY TERMINALMAN WHO INVESTIGATED AD FOUND BULL PLUG WAS CRACKED. HE CLOSED THE WATER DRAW VALVE WHICH STOPPED THE DISCHARGE. ALL PRODUCT WAS CONTAINED IN THE TANK DIKE. AVACUUM TRUCK WAS USED TO RECOVER THE SPILLED PRODUCT. THE 80,000 BARREL TANK HAD DECREASED APPROXIMATELY 2' DUE TO THE SPILL. TIS EQUATES TO APPROXIMATELY 280 BARRELS TOTAL FLUID DECREASE-INCLUDING WATER AND GASOLINE. ABOUT 180 BARRELS WAS RECOVERED.INITIAL DATE AND TIME OF DISCOVERY- JANUARY 9, 1988 - 1100ALL STANDING PRODUCT RECOVERED - JANUARY 9, 1988 - 1800FINAL CLEANUP COMPLETED - JANUARY 11, 1988- 1300
2017-09-29 08:50 | NO | NO | 19880021 |  | 26360 | HOUSTON LIGHTING & POWER CO | NO | 1988-01-01 | 1400 | TX | HARRIS | BAYTOWN | NO |  | NO | ACCIDENT OCCURRED AT MAINLINE VALVE STATION NO. BNXNO1 WHICH IS APPROXIMATELY 182 FEET SOUTH OF BAYWAY DRIVE AND 246 FEET NORTH OF HOUSTON SHIP CHANNEL. |  | LINE PIPE | VALVE |  | 1976 | OTHER | LIQUID RELEASED FROM VENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 26000 | 23315.8836 | 47037.5549 | FUEL OIL | 3 | 3 | 3 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MR. R.S. RAY, PIPELINE SUPERVISOR | 7134817786 | JANUARY 1, 1988-AT APPROXIMATELY 1400, THE COAST GUARD ADVISED EXXON OF A OIL SPILL IN EXXON'S PIPELINE CORRIDOR AT THE PREVIOUS SPECIFIED LOCATION. EXXON INVESTIGATED LOCATION AND DETERMINED THE APPARENT SOURCE OF THE LIQUID RELEASE WAS FROM HL&P'S PIPELINE FACILITIES. 1500-EXXON NOTIFIED HL&P'S DISPATCHING DEPARTMENT OF AN APPARENT OIL SPILL FROM HL&P'S PIPELINE FACILITIES AT THE PREVIOUS SPECIFIED LOCATION. THE PIPELINE OPERATIONS DEPARTMENT CONCURRED WITH DISPATCHING THAT THE SUSPECT LINE SEGMENT (BERTRON TO CEDAR BAYOU 12" LINE) WAS NOT IN SERVICE BUT SOMEONE WOULD BE DISPATCHED IMMEDIATELY TO THE SITE TO INVESTIGATE. 1550-PIPELINE OPERATIONS INDIVIDUAL INVESTIGATED LOCATION AND DETERMINED THAT LIQUIDRELEASE WAS FROM HL&P'S PIPELINE FACILITIES. RELEASE WAS COMING FROM THE MAINLINE VALVE BODY VENT FITTING. THE PIPELINE OPERATIONS INDIVIDUAL WAS ABLE TO STOP THE FLOW OF LIQUID BY FURTHER TIGHTENING ON THE PLUG ON THE VENT FITTING. 1600-PIPELINE OPERATIONS PERSONNEL CONTACTED A THIRD PARTY SPILL CLEANUP CONTRACTOR TO BRING EQUIPMENT AND PERSONNEL TO BEGIN CLEANUP. 1640-PIPELINE OPERATIONS PERSONNEL INSTALLED AN OIL SPILL BOOM ACROSS THE DITCH LEADING TO THE HOUSTON SHIP CHANNEL. 1700-PIPELINE OPERATIONS PERSONNEL CONSTRUCTED AN EARTHEN DAM ACROSS THE DITCH. 1715-THIRD PARTY SPILL CLEANUP CONTRACTOR ARRIVED ON SITE AND COMMERCED CLEANUP. JANUARY 2, 1988 - 1430-THIRD PARTY SPILL CLEANUP CONTRACTOR COMPLETED CLEANUP.
2017-09-29 08:50 | YES | NO | 19880022 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1988-01-01 | 1800 | NC | GUILFORD |  | NO |  | NO | APPROXIMATELY 0.4 MILES NORTH OF OLD BATTLEGROUND ROAD (NC 2340) IN AN AREA UNDER DEVELOPMENT KNOWN AS GUILFORD GREENE SUBDIVISION IN GUILFORD CO., NC. |  | LINE PIPE | PIPE |  | 1964 | OTHER | MANUFACTURING DEFECT PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 116579.418 | 235187.7743 | OIL AND GASOLINE |  |  | 0 | NO | NO | 8 | 0.19 |  | WELDED |  | 1450 | 950 | YES | 24 | 1903 | 10 | 64 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.M. CROOK, VICE PRESIDENT-OPERATIONS | 4043655880 | AT APPROXIMATELY 6:00 P.M. EST ON JANUARY 1, 1988, A LEAK WAS LOCATED ON PLANTATION'S 8-INCH,.188 WALL THICKNESS, GRADE X-52, SEAMLESS PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN GREENSBORO, NC AND ROANOKE, VA. THE LEAK OCCURRED INAN AREA BEING DEVELOPED NEAR GREENSBORO, NC KNOWN AS GUILFORD GREENE SUBDIVISION. THE SEAMLESS LINE PIPE HAD A ONE INCH LONG CRACK IN THE SEVEN O'CLOCK POSITIONLOOKING DOWNSTREAM APPROXIMATELY NINE FEET FROM THE NEAREST WELD. THERE WERE NO OPERATIONAL UPSETS AND THE PIPELINE WAS OPERATING WITHIN DESIGN CRITERIA. A TEMPORARY REPAIR WAS MADE USING A FULL ENCIRCLEMENT SLEEVE. THE FAILED LENGTH OF PIPE WILL BE REMOVED FROM THE OPERATING PIPELINE TO ALLOW FOR A FULL ANALYSIS OFTHE CAUSE OF THE FAILURE.
2017-09-29 08:50 | YES | NO | 19880023 |  | 2387 | CITGO PIPELINE CO | YES | 1988-01-02 | 1445 | LA | CADDO | SHREVEPORT | NO |  | NO | APPROXIMATELY 1750' EAST OF HEARNE AVENUE. |  | LINE PIPE | PIPE |  | 1932 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5858 | 5253.2479 | 10597.9229 | CRUDE OIL | 1 | 355 | 0 | NO | NO | 8 | 0.24 | 30000 | WELDED |  | 1192 | 300 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | JOHN C. PRINCE - DISTRICT MANAGER | 2147592522 | PIPELINE CONTROLER DETERMINED THAT THERE WAS A SHORTAGE OF OIL IN LINE. LINE WAS SHUTDOWN AND AERIAL PATROL WAS CALLED OUT TO INSPECT AND LOOK FOR LEAK. LEAKWAS LOCATED AND AREA OF LINE WAS ISOLATED BY CLOSING VALVES. CAUSE OF LEAK HASNOT BEEN DETERMINED DUE TO HIGH WATER.
2017-09-29 08:50 | YES | NO | 19880024 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1988-01-02 | 745 | CA | KERN |  | NO |  | NO | 1000' + S.E. OF HWY. 166 NEAR THE INTERSECTION OF OLD RIVER RD. |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 22500 | 20177.207 | 40705.5763 | CRUDE OIL | 1 | 700 | 430 | NO | NO | 10 | 0.38 | 1752 | WELDED |  | 456 | 150 | YES | 8 | 570 | 7 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE SURVEYED & STAKED | NO | YES | R.B. KUPREWICZ - V.P. OPERATIONS | 2134289017 | FARM EQUIPMENT OPERATOR PUNCTURED LINE 1 WITH A RIPPER BEING PULLED BY A CAT. THE AREA OVER THE PIPELINE HAD BEEN MARKED.
2017-09-29 08:50 | YES | NO | 19880025 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1987-11-27 | 1707 | TX | UPTON |  | NO |  | NO | LINE 80-1-6 LOOP- SPRABERRY-BENEDUM-MP 68-06+07. EAST OF MIDKIFF, TEXAS ON FARM ROAD 2401 APPROXIMATELY 2 MILES, THEN SOUTH ON DIRT ROAD APPROXIMATELY 1 1/2 MI |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60057 | 55592.2826 | 112152.0886 | NATURAL GAS LIQUID | 2 | 6139 | 0 | NO | NO | 8 | 0.19 | 35000 | WELDED |  | 1100 | 595 | YES | 24 | 1395 | 9 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.L.THORMAN, MANAGER OF ENG. & TECH. SERVICES | 9186614721 | FARMER PUNCTURED LINE WITH PLOW.
2017-09-29 08:50 | YES | NO | 19880026 |  | 2327 | CHEVRON USA INC | NO | 1987-10-16 | 1030 | CA | FRESNO |  | NO |  | NO | PIPELINE STA. NO. MP11+1649 SECTION 11, T-21-S, R-17-E, FRESNO CO. CA. OR APPR.2 1/8 MI. N. OF THE INTERSECTION OF INTERSTATE 5 AND ST. HWY 269. |  | LINE PIPE | PIPE |  | 1947 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8500 | 7868.0987 | 15873.1331 | CRUDE OIL | 1 | 1661 | 1051 | NO | NO | 18 | 0.25 | 1444 | WELDED |  | 1040 | 950 | YES | 5 | 1300 | 5 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | M.K. CANNON , DISTRICT SUPERVISOR | 8057722611 | THE AERIAL PATROL PILOT REPORTED ON 10/15/87 THAT RIPPING WAS IN PROGRESS NEAR OUR PIPELINE. OUR COMPANY REPRESENTATIVE RESPONDED TO THE SCENE THE FOLLOWING MORNING AT APPROXIMATELY 0800 HOURS AND ADVISED THE TRACTOR OPERATOR THAT A PIPELINE WAS PRESENT AND SPOTTED IT'S LOCATION. THE TRACTOR STRUCK THE PIPELINE AT APPROXIMATELY 1030 HOURS. THE RUPTURE WAS DETECTED BY THE LEAK DETECTION SYSTEM AND THE PIPELINE WAS IMMEDIATELY SHUTDOWN. THE LINE WAS REPAIRED WITH FULL ENCIRCLEMENT SLEEVES AND THE PIPELINE WAS PLACED BACK IN SERVICE BY 2300 HOURS ON 10/16/87.
2017-09-29 08:50 | NO | NO | 19880027 |  | 13131 | CONOCO INC | YES | 1987-12-16 | 800 | OK | CARTER |  | NO |  | NO | NE/4, SECTION 7, T1S, R3W CARTER COUNTY, OKLAHOMA. |  | PUMPING STATION | OTHER | 1/4IN. STEEL,80 PIPE USED | 1987 | OTHER | BREAK IN STEEL PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 9256.5867 | 18674.2742 | CRUDE OIL | 1 | 35 | 25 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY F. CLYNCH, DIVISION MANAGER | 4057676352 | ON DECEMBER 16, 1987 AT 0800 HOURS, A SPILL WAS DISCOVERED AT THE CONOCO PIPE LINE COMPANY'S TUSSY, OKLAHOMA PUMP STATION. THE SOURCE WAS A 1/4 INCH SCHEDULE 80 STEEL PIPE NIPPLE ON A FLEX-FLOW CONTROL VALVE WHICH BROKE DUE TO VIBRATION FATIGUE CAUSING THE RELEASE OF APPROXIMATELY 35 BBLS OF CRUDE OIL INTO AN UNNAMEDCREEK. THE OIL WAS CONTAINED ON THE CREEK AND REMOVED WITH SORBENT BOOMS, PADSAND VACUUM TRUCKS. REFERENCE NRC REPORT 15695.
2017-09-29 08:50 | YES | NO | 19880028 |  | 13131 | CONOCO INC | YES | 1987-11-30 | 930 | MO | NEWTON |  | NO |  | NO | CONOCO PIPE LINE COMPANY'S #1 LINE AS IT CROSSES COUNTY ROAD IN NEWTON COUNTY. |  | LINE PIPE | PIPE |  | 1931 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 27769.76 | 56022.8226 | GASOLINE | 1 | 150 | 100 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 900 | 765 | YES | 8 | 1076 | 8 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | L.G. HUBBARD - DIRECTOR ENVIRONMENTAL AFFAIRS | 7132932032 | NEWTON COUNTY ROAD GRADER WAS DEEPENING CHANNEL IN BAR DITCH WHEN HE STRUCK OUR
2017-09-29 08:50 | YES | NO | 19880030 |  | 2327 | CHEVRON USA INC | NO | 1988-01-13 | 1700 | HI |  | HAWAII | NO |  | NO | LEAK OCCURED UNDERGROUND ALONG NIMITZ HWY AND IN FRONT OF HAWAIIAN ELECTRIC COMPANY'S IWILEI TANK FARM. MP 22.5. |  | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 26902.9426 | 54274.1018 | DIESEL FUEL | 3 | 250 | 200 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 205 | 25 | YES | 8 | 425 | 9 | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.KAPPEL, AREA SUPERVISOR | 8086825711
2017-09-29 08:50 | YES | NO | 19880031 |  | 443 | AMOCO PIPELINE CO | YES | 1988-01-03 | 340 | OK | LINCOLN |  | NO |  | NO | NW 1/4 9 T13N - R5E. |  | LINE PIPE | PIPE |  | 1919 | FAILED PIPE | SUBSIDENCE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3587.059 | 7236.5469 | CRUDE OIL | 1 | 350 | 200 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 860 | 200 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | SUBSIDENCE |  | Null | NO DATA |  | Null | Null | J.W. WILHELM, AREA MANAGER | 9182257271 | (200 BBLS) WAS PICKED UP BY VACUUM TRUCKS AND RETURNED TO THE PIPELINE. THE REMAINING OIL WAS BURNED.
2017-09-29 08:50 | YES | NO | 19880032 |  | 12628 | MOBIL PIPELINE CO | Null | 1988-01-11 | 30 | TX | COMANCHE | 5 MI. N. OF DELEON | NO |  | NO | 0.8 MILES EAST OF STATE HIGHWAY 16 IN JAMES P. STEPHENSON SURVEY A-833. |  | LINE PIPE | PIPE |  | 1955 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 72000 | 64567.0623 | 130257.8443 | CRUDE OIL | 1 | 3920 | 2511 | NO | NO | 16 | 0.25 | 1438 | WELDED |  | 1033 | 970 | YES | 2 | 1145 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226
2017-09-29 08:50 | YES | NO | 19880033 |  | 2552 | COLONIAL PIPELINE CO | YES | 1988-01-05 | 704 | NJ | GLOUCESTER | DEPTFORD TOWNSHIP | NO |  | NO | SEE ATTACHED MAP. |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 403544.1392 | 814111.5266 | FUEL OIL | 3 | 2375 | 2295 | NO | NO | 30 | 0.28 | 52000 | WELDED |  | 701 | 738 | YES | 24 | 860 | 1 | 64 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. SORROW-REGULATORY & ENVIRONMENTAL AFFAIRS MAN. | 4042611470 | AN OPERATIONAL CHANGE WAS MADE ON THE 30" DIAMETER PIPELINE BETWEEN THE PUMPINGSTATIONS AT WOODBURY, NEW JERSEY AND ALLENTOWN, NEW JERSEY AT 0702 HOURS ON JANUARY 5, 1988. THIS CHANGE CAUSED THE LOSS OF PUMPING UNITS AT ALLENTOWN DUE TO THE HIGH CASE PRESSURE PROTECTIVE SWITCH SHUTTING DOWN THE UITS (CASE PRESSURE IS MEASURED BETWEEN THE PUMP UNITS AND THE STATION CONTROL VALVE). THE PUMPING UNITS AT WOODBURY WERE IN TURN LOST DUE TO THE HIGH STATION DISCHARGE PRESSURE PROTECTIVE SWITCH ACTIVATING AT A PRESSURE OF 714 PSI AT 0703 HOURS. THE FAILURE IN THE PIPELINE OCCURRRED AT A LOCATION 3.9 MILES DOWNSTREAM FROM WOODBURY WHERETHE LINE RUNS PARALLEL TO THE NEW JERSEY TURNPIKE AND BETWEEN POPLAR AND VERMONT STREETS AT 0704 HOURS. ALTHOUGH THE 738 PSI PRESSURE WAS ABOVE THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF 701 PSI IT WAS A MONENTARY EVENT AND WAS STILL BELOW THE 10% ALLOWABLE FOR SUCH EVENTS OF 771 PSI PRESSURE. AN ESTIMATED 2,375 BARRELS OF NO. 2 FUEL OIL WERE LOST FROM THE PIPELINE THROUGH A 40" LONG RUPTURE INTHE PIPE AT THE 6 O'CLOCK POSITION. THE LONGITUDINAL SEAM OF THE PIPE WAS LOCATED AT THE 12O'CLOCK POSITION. AN AREA ON THE SURFACE OF THE PIPE FROM THE 6O'CLOCK TO THE 9O'CLOCK POSITION AND ABOUT 54" LONG WAS CORRODED, AND HAD CAUSED THINNING OF THE PIPE WALL SUFFICIENT TO RESULT IN TH FAILURE. A 9'-10" LONG PIECE OF 30" O.D. Z .312" WT., 5L-X52 HYDROSTATICALLY TESTED PIPE WAS WELDED INTO THE P
2017-09-29 08:50 | YES | NO | 19880034 |  | 4805 | EXPLORER PIPELINE CO | YES | 1988-02-16 | 1010 | TX | DALLAS | DALLAS | NO |  | NO | ON NORTH SIDE OF ST. LOUIS SOUTHWESTERN RAILROAD APPROXIMATELY 2000 FEET SOUTHWEST OF PRESTON ROAD AT EXPLORER'S MILEPOST 36.7. |  | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 26902.9426 | 54274.1018 | GASOLINE | 3 | 819 | 538 | NO | NO | 12 | 0.22 | 52000 | WELDED |  | 1286 | 515 | YES | 24 | 1628 | 11 | 71 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | R.E SANDS, VICE PRESIDENT OF OPERATIONS | 9184935106 | ON FEBRUARY 16, 1988, AT APPROXIMATELY 10:10, A CONTRACTOR INSTALLING A FIBER OPTICS CABLE FOR U.S. SPRINT STRUCK EXPLORER'S 12" PIPELINE AT M.P. 36.7, RESULTING IN A PUNCTURE AND EXCAPE OF 819 BARRELS OF UNLEADED GASOLINE.THE PIPELINE WAS SHUT DOWN AT 10:12 AND THE UPSTREAM BLOCK VALVE AT M.P. 35.6 WAS CONFIRMED CLOSED AT 10:35. THE DOWNSTREAM BLOCK VALVE AT M.P. 39.5 WAS CLOSED AT 11:34, AFTER ALLOWING AS MUCH PRODUCT AS POSSIBLE TO GRAVITY DRAIN FROM THELEAK SITE. EARTHEN DAMS WERE BUILT TO CONTAIN THE SMALL AMOUNT OF PRODUCT NOT CONTAINED IN THE DITCH OPENED BY THE SPRINT CONTRACTOR. NO PRODUCT ESCAPED INTO THE NEARBY CREEK.APPROXIMATELY 538 BARRELS OF GASOLINE WAS RECOVERED FROM THE SITE WITH VACUUM TRUCKS AND HAULED TO EXPLORER'S TANK FARM AT GREENVILLE, TEXAS. AT THE REQUEST OFTHE TEXAS WATER QUALITY BOARD, APPROXIMATELY 200 CUBIC YARDS OF SOIL WAS HAULEDTO A SANITARY LANDFILL AFTER LABORATORY SOIL ANALYSIS AND APPROVAL OF ENVIRONMENTAL AUTHORITIES.THE DAMAGED SECTION OF PIPE WAS REMOVED AND REPLACED WITH A 12 FOOT PRE-HYDROSTATICALLY TESTED PIECE OF 12" PIPE USING WELD+ENDS. REPAIRS WERE COMPLETED AND THE LINE PUT BACK INTO OPERATION AT 05:36 ON FEBRUARY 17, 1988.
2017-09-29 08:50 | YES | NO | 19880035 |  | 18718 | SUN PIPELINE CO | YES | 1988-02-01 | 845 | TX | RUSK |  | NO |  | NO | ONE (1) MILE EAST ON HWY 13 FROM INTERSECTION OF HWY 13 AND HWY 42 AT PRICE, TEXAS. ENTER ELLEN TILLL LEASE ROAD, NORTH OF HWY 13. NORTH 100 FEET. LEAK AREA IN |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 70 | 68 | NO | NO | 4 | 0.19 | 35000 | THREADED |  | 200 | 200 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | E.F. MCKINLEY, JR. AREA MANAGER, COMPL.SAFETY & HEALTH | 2147570220 | AT 8:05 AM, PRODUCER NOTIFIED SUN PIPE LINE PERSONNEL OF LEAK IN AREA OF THE 36-4"-A SYSTEM. INVESTIGATION REVEALED A PITTED AREA THAT HAD A SMALL HOLE CAUSING LOSS OF OIL. THE OIL WAS CONTAINED IN A SMALL DEPRESSION OF 40'X60' AREA.CLEAN UP ACTIVITIES ARE IN PROGRESS.THE HOLE WAS CLAMPED WITH A 2-BOLT SKINNER CLAMP UNTIL A REPLACEMENT SEGMENT CAN BE INSTALLED.
2017-09-29 08:50 | YES | NO | 19880036 |  | 19536 | TOTAL PIPELINE CORP | YES | 1988-01-29 | 700 | TX | WICHITA |  | NO |  | NO | 7 MILES WEST, 1/2 MILE SOUTH, 1/4 MILE WEST FROM INTERSECTION OF HIGHWAYS 369 & 240 AT BURKBURNETT, TEXAS. |  | PUMPING STATION | PUMP |  | 1987 | OTHER | SPRING IN PUMP BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 10761.177 | 21709.6407 | CRUDE OIL | 1 | 602 | 85 | NO | NO | 1 |  |  | THREADED |  | 480 | 75 | YES | 8 | 900 | 7 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | NO | NO | MICHAEL J. COOPER, CORROSION ENGINEER | 4052291638 | TOTAL PIPELINE GAUGER REPORTED LEAK AT 7:00 A.M. ON 1/29/88. LEAK RESPONSE CREW WAS IMMEDIATELY DISPATCHED TO LEAK SITE AND CLEANUP WAS INITIATED. LEAK WAS CAUSED WHEN A 3/4" THREADED NIPPLE BROKE OFF OF THE METERING LOOP WHEN THE POSITIVE DISPLACEMENT PUMP BROKE SPRINGS ON THE DISCHARGE SIDE CAUSING EXTREME VIBRATION. PRESSURE AND OIL WAS PUMPED FROM THE BOOSTER PUMP UNTIL THE GAUGER SHUT IT DOWN AT 7:00 A.M. ON 1/19/88. OVER AND SHORT CALCULATIONS DETERMINED THAT 602 BARRELS WAS LOST AND 85 BARRELS WAS RECOVERED WITH VACUUM TRUCKS.APPROXIMATELY 2 1/2 ACRES OF PASTURE LAND WAS OIL SPRAYED DURING THE LEAK. LANDOWNERS WERE CONTACTED AND TOTAL IS MAKING FINAL CLEANUP AT THIS TIME.
2017-09-29 08:50 | NO | NO | 19880037 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-01-07 | 1045 | IL | COOK | CHICAGO | NO |  | NO | CHICAGO TERMINAL |  | TANK FARM | OTHER | OIL/WATER SEPARATOR | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2690.2943 | 5427.4102 | FUEL OIL | 3 | 2 | 2 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | HOWARD JANSEN , VICE PRESIDENT-OPERATIONS | 9185883850 | AT 10:45 HOURS ON JANUARY 7, 1988, A LEAK WAS DISCOVERED IN A SMALL CREEK LOCATED ADJACENT TO OUR CHICAGO TERMINAL. THE LEAK RESULTED FROM THE FAILURE OF AN OUTFALL SEPARATOR WHICH (UNDER STATE PERMIT) DISCHARGES RUNOFF WATER INTO THE CREEK. DAMAGE FROM INTERNAL ICE FORMATION CAUSED THE SEPARATOR TO UPSET AND RELEASED 2 BARRELS OF PETROLEUM PRODUCT INTO THE CREEK. BOOMS WERE PLACED IN THE CREEK TO CONTAIN THE SPILL. MAINTENANCE PERSONNEL WERE ABLE TO RECOVER THE ENTIRERELEASED VOLUME. STATE EPA OFFICIALS HAVE INVRSTIGATED THE SITE AND HAVE APPROVED OF OUR CLEAN_UP EFFORTS.
2017-09-29 08:50 | YES | NO | 19880039 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1988-01-17 | 1700 | LA | BOSSIER | BOSSIER | NO |  | NO | VICINITY MAP, TPA-V-4 ATTACHED. |  | TANK FARM | TANK |  | 1968 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3138.6766 | 6331.9785 | FUEL OIL | 3 | 1150 | 1140 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM M. OLLER - EXECUTIVE VICE PRESIDENT | 7137593605 | UPON ROUTINE CHECK OF TANKS AND FIREWALLS, OPERATOR NOTICED PRODUCT BUBBLING OUT FROM THE BOTTOM OF TANK NO. 3309. PRODUCT WAS TRANSFERRED FROM LEAKING TANK TO ANOTHER WHILE PRODUCT INSIDE FIREWALL WAS RECOVERED. PROBLEM WAS TRACED TO A CRACKED WELD ON THE BOTTOM OF THE TANK NEAR THE FILL NOZZLE. WELD WAS REPAIRED AND TANK PUT BACK IN SERVICE. ALL PRODUCT WAS CONFINED TO COMPANY PROPERTY.
2017-09-29 08:50 | YES | NO | 19880040 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1987-12-23 | 707 | TX | WHARTON |  | NO |  | NO | 3/4 MILE SOUTHWEST OF COASTAL'S BAY CITYSTATION. STATION IS LOCATED 1 MILE SOUTHEAST OF MAGNET, TEXAS ONSTATE HIGHWAY 60. |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13884.88 | 28011.4113 | GASOLINE | 3 | 220 | 217 | NO | NO | 12 | 0.2 | 1465 | WELDED |  | 1050 | 923 | YES | 24 | 1315 | 1 | 65 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RON MCGRAY - MAINTENANCE SUPERVISOR | 7138776896 | ON THE MORNING OF 12-23-87, THE DISPATCHER RECEIVED AND INDICATION FROM DAMON OF A LOSS OF PRESSURE. HE IMMEDIATELY SHUT DOWN THE LINE. HE THEN NOTIFIED OPERATING PESONNEL AT DAMON TO INVESTIGATE LOSS OF PRESSURE. I WAS NOTIFIED AT APPROX. 07:45 OF WHAT WAS GOING ON. I IMMEDIATELY NOTIFIED PETE TURNER OF POSSIBLE LEAK. AT ABOUT 08:15 PETE CALLED ME BACK AND SAID TO GET A HELICOPTER AND FLY THE P/L FROM DAMON TO DANNEVANG. HELICOPTER PICKED ME UP IN ALVIN AT 11:00 AND WEFLEW TO DAMON, THEN TO BAY CITY. ABOUT 11:45 I SPOTTED PRODUCT ON TOP OF WATERIN A CANAL APPROX.3/4 OF A MILE SOUTH OF BAY CITY STATION. WE LANDED AT BAY CITY STATION WHERE I HAD A VEHICLE STANDING BY AND DROVE DOWN TO INVESTIGATE THE SITE. UPON VISUAL INSPECTION I DISCOVERED THE PIPELINE CROSSING AT THE LOWER COLORADO RIVER AUTHORITY CANAL WAS IN CASING AND HAD APPARENTLY BLOWN OUT. I NOTIFIED PETE TURNER OF LOCATING THE LEAK SITE, THEN CALLED IN MAINTENANCE PERSONNELTO START REPAIRS AND CLEAN UP. FAILURE DETERMINED TO BE CAUSED BY LOCALIZED CORROSION ON THE OUTSIDE SURFACE OF TH PIPE IN THE AREA OF CONTACT WITH CASING SPACERS.
2017-09-29 08:50 | YES | NO | 19880041 |  | 720 | ASHLAND OIL & TRANSPORTATION CO | YES | 1988-01-28 | 1500 | WV | KANAWHA | ST. ALBANS | NO |  | NO | OPAL STREET OFF KANAWHA TERRACE. |  | PUMPING STATION | PUMP |  | 1978 | OTHER | SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 896.7648 | 1809.1367 | NATURAL GAS LIQUID | 2 | 7 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LOUIS B. MORGAN - ENGINEERING SUPERVISOR | 5026832485 | WE RECEIVED A REPORT OF A LEAK AT ST. ALBANS AT 3:00 P.M. INVESTIGATION REVEALED A LEAKING PUMP SEAL AT ST. ALBANS STATION AND A VAPOR CLOUD ALONG THE RAILROADDITCH FOR ABOUT 100 FEET. THE STATION WAS SHUT DOWN AND ISOLATED AND THE VAPORDISSIPATED BY 3:30P.M.
2017-09-29 08:50 | YES | NO | 19880042 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1988-01-22 | 1000 | TX | CARSON |  | NO |  | NO | GAINES-BORGER - LINE "80" - MP 264-20+63SECTION 66, BLK. T, ADAMS, BEATY, & MOULTON SURVEY APPROXIMATELY 1/4 MILE NORTH OF F.M. 293. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 9050 | 8115.721 | 16372.6874 | NATURAL GAS LIQUID | 2 | 800 | 0 | NO | NO | 8 | 0.19 | 40000 | WELDED |  | 1150 | 345 | YES | 24 | 1500 | 6 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | CONSTRUCTION COMPANY LAYING CABLE PUNCTURED PIPELINE.
2017-09-29 08:50 | YES | NO | 19880043 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1988-02-11 | 1530 | VA | HANOVER |  | NO |  | NO | ON R.F.&P. RAILROAD PROPERTY APPROXIMATELY 1100 FEET SOUTH OF VIRGINIA HIGHWAY 688 AND 756 FEET SOUTH OF THE C&O RAILROAD LINE NEAR DOSWELL, VIRGINIA. |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 91400 | 81964.2985 | 165355.0967 | GASOLINE | 3 | 200 | 0 | NO | NO | 12 | 0.2 | 1655 | WELDED |  | 1133 | 670 | YES | 26 | 1309 | 6 | 64 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.M.CROOK, VICE PRESIDENT-OPERATIONS | 4043645880 | AT APPROXIMATELY 3:30 P.M. EST ON FRBRUARY 11, 1988, A LEAK WAS LOCATED ON PLANTATION'S 12-INCH, .203 WALL THICKNESS, GRADE X--52, ERW PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN GREENSBORO, NC AND WASHINGTON, D.C. THE LEAK OCCURRED ON R.F.&P. RAILROAD RIGHT OF WAY NEAR DOSWELL, VIRGINIA WHEREIN THE PIPELINE LAYS BY PERMIT. THE PIPELINE WAS RESTING ON TWO ROCKS WHICH HAD BROKEN THE COATING AND CREATED AN AREA OF GALVANIC CORROSION. PRODUCT ESCAPED THROUGH A PINHOLE LOCATED IN A ONE-INCH DIAMETER CORROSION PIT LOCATED IN AN AREA OF VARIOUS SMALLER NON-LEAKING PITS AT THE SIX O'CLOCK POSITION ON THE PIPE.THERE WERE NO OPERATIONAL UPSETS AND THE PIPELINE WAS OPERATIG WITHIN DESIGN CRITERIA. THE PIPELINE WAS REPAIRED WITH A TWO-FOOT-LONG FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19880044 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1988-02-15 | 1700 | OK | STEPHENS | VELMA | NO |  | NO | 1/4 MILE WEST OF TEXACO GAS PLANT, 1/4 MILE NORTH AND EAST INTO SITE. |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 672.5736 | 1356.8525 | CRUDE OIL | 1 | 95 | 86 | NO | NO | 4 | 0.24 | 100 | NO DATA |  | 500 | 80 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.A. WILLIAMSON, GENERAL FOREMAN | 4058675810 | SOURCE OF LEAK WAS EXTERNAL CORROSION AT A JOINT WELD ON THIS 4" GATHERING LINE. OUR GAUGER HAD ONE PUMP UNIT INJECTING INTO SYSTEM AT RATE OF 45 BBLS. PER HOUR FOR 4 1/2 HOURS UPSTREAM OF LEAK SITE ABOUT 4 MILES. THIS PUMPED OUT AT APPROX. 2:30 P.M., ABOUT THE TIME THE TEXACO EMPLOYEE DISCOVERED THE LEAK. OIL HAD RAN FROM LEAK SITE, IN WHEAT FIELD, INTO A SMALL DRAINAGE DITCH FOR APPROX. 100 YDS., THEN INTO SMALL RUNNING STREAM FOR 1/2 MILE, CONFINED BY A COFFER DAM. RECOVERY AND CREEK CLEANUP IS COMPLETED.
2017-09-29 08:50 | YES | NO | 19880045 |  | 13131 | CONOCO INC | YES | 1988-01-21 | 1126 | MT | GLACIER |  | NO |  | NO | T33N, R5W, SEC. 18, 100 YARDS SOUTHEAST OF PIPELINE AERIAL MARKER 366. SKETCH ATTACHED. |  | LINE PIPE | LONGITUDINAL WELD |  | 1961 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4483.8238 | 9045.6836 | CRUDE OIL | 1 | 494 | 30 | NO | NO | 8 | 0.22 | 52000 | WELDED |  | 2050 | 1541 | NO | 0 | 2560 | 12 | 61 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.G.HUBBARD, DIRECTOR, ENVIRONMENTAL AFFAIRS | 7132932032 | CONOCO PIPE LINE COMPANY'S OIL MOVEMENTS GROUP IN HOUSTON, TX, SUSPECTED A LEAKHAD OCCURRED WHEN THE CUT BANK, MT, STATION PUMPS SHUT DOWN DUE TO LOW SUCTION PRESSURE AT 11:26 A.M., FRIDAY, JANUARY 21, 1988. THE LINE WAS IMMEDIATELY SHUTDOWN AND ALLOWED TO DRAIN INTO THE ROUNDUP,MT, STATION. WHEN THE LINE WAS SHUT DOWN, THE CUT BANK STATION DISCHARGE PRESSURE DROPPED TO ZERO AND THE CONRAD,MT, STATION SUCTION PRESSURE DROPPED TO 161 PSIG, INDICATING THE LEAK WAS IN THE PROXIMITY OF CUT BANK.OIL MOVEMENTS IMMEDIATELY NOTIFIED COMPANY FIELD PESONNEL OF THE SUSPECTED LEAK. THE CUT BANK STATION WAS ISOLATED AND CONTRACT PERRSONNEL WERE DISPATCHED BY HELICOPTER TO LOCATED TH LEAK. THE LEAK WAS SPOTTED AT 12:20 P.M. THE LANDOWNER WAS NOTIFIED OF THE LEAK AND APPROVAL WAS OBTAINED FOR SUBSEQUENT LINE REPAIRSAND CLEANUP. APPROXIMATELY 494BBLS. OF SUNDRE LIGHT CANADIAN CRUDE WERE SPILLED AND CONTAINED WITHIN A 200-YARD SECTION OF A HARVESTED WHEAT FIELD. APPROXIMATELY 30 BBLS. OF THE SPILLED OIL WERE RECOVERED.A 48-FOOT SECTION OF PIPE CONTAINING THE 23-INCH SEAM SPLIT WAS REMOVED AND REPLACED WITH A PRETESTED SECTION OF .250 WALL SEAMLESS Z-52 LINE PIPE. AFTER OBTAINING APPROVAL FROM THE LANDOWNER, THE LOCAL POLICE DEPARTMENT AND THE STATE OF MONTANA, THE OIL-SOAKED AREA WAS BURNED OFF. THE LINE WAS RETURNED TO SERVICE AT10:22PM ON JANUARY 21, 1988.
2017-09-29 08:50 | YES | NO | 19880046 |  | 13131 | CONOCO INC | NO | 1988-02-01 | 2100 | OK | GRANT |  | NO |  | NO | CONOCO PIPE LINE COMPANY'S 4" PBC LINE I GRANT COUNTY, OKLAHOMA (SEE ATTACHED MAP) T27N-R5W, SW/4 OF NE/4 OF SECTION 36. |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 448.3824 | 904.5684 | NATURAL GAS LIQUID | 2 | 35 | 0 | NO | NO | 4 | 0.13 | 42000 | WELDED |  | 1150 | 260 | YES | 8 | 1440 | 8 | 82 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.G.HUBBARD DIRECTOR, ENVIRONMENTAL AFFAIRS | 7132932032 | LINE WAS IN NORMAL OPERATION WHEN LOSS OF PRESSURE INDICATED A LEAK. LINE WAS SHUT IN AND REPRESSURED TO FIND EXACT LOCATION OF LEAK. AT APPROXIMATELY 2100 ON2-1-88, LEAK WAS FOUND TO BE CORROSION CAUSED AND TEMPORARY REPAIRS WERE MADE PENDING LINE REPLACEMENT OF CORRODED AREA.
2017-09-29 08:50 | YES | YES | 19880047 |  | 4906 | EXXON PIPELINE CO | NO | 1988-02-09 | 1830 | TX | HARRIS |  | NO |  | NO | INCIDENT OCCURRED NEAR THE 17,500 BLOCK OF STUEBNER AIRLINE DRIVE (NORTHWEST HARRIS COUNTY) AT PIPELINE STATION NUMBER 833+07 (TOMBALL LPG JUNCTION) SOME 13 MIL |  | LINE PIPE | OTHER | TEMPORARY FLARE | 1988 | OTHER | SUDDEN UNEXPEC. PRESSURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 50 | 44.8382 | 90.4568 | L. P. G. | 2 | 1 | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | A FLASH FIRE OCCURRED DURING THE PROCESS OF RESTORING A SECTION OF LPG PIPELINETO SERVICE AFTER COMPLETION OF HYDROSTATIC TESTS. AS A RESULT OF THE FLASH FIRE, WHICH LASTED ONLY A FEW SECONDS, AN EMPLOYEE WAS BURNED ON THE FACE, HANDS AND WRISTS. BURNS ON THE FACE WERE FIRST DEGREE, WHILE BURNS ON THE EMPLOYEE'S HANDS AND WRISTS WERE FIRST AND SECOND DEGREE.SOME OF THE GRASS ON THE RIGHT-OF-WAY CAUGHT FIRE AS A RESULT OF THE FLASH FIRE. HOWEVER, THESE VERY SMALL AREA FIRES WERE EXTINGUISHED WITHIN A FEW MINUTES. THERE WAS NO SIGNIFICANT PROPERTY DAMAGE.AS THE HYDROSTATIC TEST WATER WAS BEING DISPLACED FORM THE LINE WITH A PIG FOLLOWED BY PRODUCT(LPG), THE WATER WAS BEING ROUTED INTO A VACUUM TRUNK; AND AS LPGVAPORS ARRIVED INTERMITTENTLY, THEY WERE ROUTED TO A TEMPORARY FLARE. AT ONE POINT, A MIXTURE OF LPG AND WATER SURGED THROUGH THE FLARE. THIS CREATED A FIRE BAL WHICH DROPPED TO THE GROUND AND IGNITED A SMALL QUANTITY OF LPG VAPORS, WHICH HAD SETTLED UNOBSERVED IN THE AREA AND LEFT A VACUUM TRUCK. WITHIN A VERY SHORT PERIOD OF TIME, PROBABLY LESS THAN 5 SECONDS, THE FIRE REACHED THE VACUUM TRUCK VIA THE VAPOR TRAIL. AT THAT TIME, THE EMPLOYEE, WHO HAD POSITIONED HIMSELF OVER THE HATCH TO WATCH FOR LPG VAPORS, WAS BURNED.THE LINE, A SEGMENT OF WHCH HAD BEEN HYDROSTATICALLY TESTED TO MEET DOT 195 REQU
2017-09-29 08:50 | YES | NO | 19880048 |  | 3445 | DIXIE PIPELINE | NO | 1988-02-15 | 809 | AL | AUTAUGA |  | NO |  | NO | PRATTVILLE PUMP STATION, NW/4 SECTION 1, 518N, R15E. AUTAUGA COUNTY, ALABAMA. |  | PUMPING STATION | NO DATA |  | 1972 | OTHER | SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 20 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.A. HILLEASTERN DISTRICT MANAGER | 4042962994 | AT 0809 ON FEBRUARY 15, 1988 THE #2 UNIT AT PRATTVILLE STATION SHUT DOWN ON SEAL FAILURE. AT 0825 THE DISPATCH CENTER WAS NOTIFIED BY TELEPHONE FROM A LOCAL RESIDENT THAT IT APPEARED PROPANE VAPOR WAS LEAKING FROM THE STATION AND APPROACHING THE HIGHWAY. AT 0826 THE STATION SUCTION VALVE WAS CLOSED AND THE PIPE LINESHUT DOWN. AT 0929 THE SHERIFF WAS NOTIFIED AND THE SHERIFF ADVISED THE HIGHWAYWOULD BE BLOCKED BY 08:30. AT 10:33 A DIXIE SUPERVISOR ARRIVED. NO GAS WAS LEAKING WHEN HE ARRIVED. THE SHERIFF AND THE FIRE TRUCKS THE SHERIFF HAD DISPATCHED WERE RELEASED.THE SEAL IN THE NUMBER 2 UNIT BLEW OUT RESULTING IN THE DISCHARGE OF THE GAS INTH PUMP AND ASSOCIATED LINE. THE DISCHARGE CHECK VALVE MAY NOT HAVE SEALED 100% ALLOWING ADDITIONAL GAS THAN NORMAL TO BE DISCHARGE. THE CHECK VALVE WAS REPLACED AS A PRECAUTION.
2017-09-29 08:50 | YES | YES | 19880049 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1988-01-29 | 45 | IL | WILL | MONEE | NO |  | NO | VICINITY MAP TPA-V-76 ATTACHED. |  | PUMPING STATION | OTHER | FLOW SWITCH-LINE PRESSURE | 1971 | OTHER | FLOW SWITCH FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 2 | 0 | 160000 | 143482.3606 | 289461.8761 | NATURAL GAS LIQUID |  |  | 0 | YES | YES | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM M. OLLEREXECUTIVE VICE PRESIDENT | 7137593605 | APPARRENTLY A FLOW SWITCH'S METAL BELLOWS CRACKED, PERMITTING NORMAL BURANE TO PRESSURIZE AN ELECTRICAL CONDUIT. THE BUTANE PENETRATED TWO ELECTRICAL CONDUIT SEALS AND MIGRATED INTO THE PUMP STATION CONTROL ROOM AT APPROXIMATELY 0045 HRS. ON JANUARY 29, 1988. THE BUTANE WAS ACCIDENTLY IGNITED IN THE CONTROL ROOM, NEAR THE CONTROL PANEL AREA, CAUSING AN EXPLOSION AND FIRE IN THE PROXIMITY OF THE STATION CONTROL PANEL. MOST OF THE CONTROL PANEL INSTRUMENTATION, AS WELL AS THE S.C.A.D.A. TERMINALS, COMPUTER TERMINAL AND COMMUNICATIONS EQUIPMENT WERE HEAVILY DAMAGED EITHER BY THE FIRE OR FIRE DEPARTMENT EFFORTS. MOST OF THE CONTROL CABLE AND POWER WIRING WAS ALSO HEAVILY DAMAGED.OF THE TWO OPERATORS BURNED IN THE FLASH FIRE, MR. GRIFFING SPENT THREE DAYS INI.C.U., HAD SKIN GRAFT SURGERY, AND WAS RELEASED FROM THE HOSPITAL ON FEBRUARY 12, 1988. MR. HALL SPENT FIVE DAYS IN I.C.U., HAD SKIN GRAFT SUREGERY AND WAS RELEASED FROM THE HOSPITAL ON FEBRUARY 19, 1988.
2017-09-29 08:50 | YES | NO | 19880050 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-01-27 | 1500 | KS | KANSAS |  | NO |  | NO | FAIRFAX WEST TERMINAL. |  | TANK FARM | VALVE |  | 0 | OTHER | WATER FROZE & CR. HOUSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 896.7648 | 1809.1367 | CONDENSATE - WATER | 3 | 1045 | 985 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E.JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | AT 1500 HOURS ON JANUARY 27, 1988, A SPILL WAS DISCOVERED NEAR THE FILTER PRESSOPERATIONS LOCATED AT OUR FAIRFAX WEST TERMINAL IN KANSAS CITY. THE RELEASE ORIGINATED FROM A 3" TANK LINE VALVE FOR TANK #546. TANK BOTTOM SLUDGE WAS BEING STORED IN TANK #546 IN PREPARATION FOR PROCESSING THROUGH OUR FILTER PRESS. WATER APPARENTLY COLLECTED AND FROZE IN THE BOTTOM OF TH VALVE CAUSING THE VALVE BODY TO CRACK. 1045 BARRELS OF TANK BOTTOM SLUDGE AND WATER WAS RELEASED WITH 985BARRELS RECOVERED. CLEAN UP MEASURES ARE BEING CORRDINATED WITH APPROPRIATE GOVERNMENT OFFICIALS.
2017-09-29 08:50 | YES | NO | 19880051 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1988-01-23 | 915 | CA | LOS ANGELES | LONG BEACH | NO |  | NO | 9TH AND CANAL AT RAIL ROAD RIGHT-OF-WAY, LONG BEACH. |  | LINE PIPE | OTHER | INSULATING KIT FLANGES | 1988 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 15245.0008 | 30755.3243 | FUEL OIL | 3 | 150 | 130 | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 720 | 200 | NO | 8 | 911 | 9 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | R.B. KUPREWICZ, VICE PRESIDENT - OPERATIONS | 2134289017 | LEAK WAS FROM A SET OF VALVE FLANGES THAT WERE NOT PROPERLY TIGHTENED.THIS IS A NEW CONNECTION INSTALLED BY GOLDEN WEST TO FCPL'S LINE 79.AH&S CONTRACTORS DID THE CONNECTION WORK.
2017-09-29 08:50 | YES | NO | 19880053 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-02-19 | 1700 | TX | REEVES |  | NO |  | NO | BLOCK 56, TWP. 2, SECTION 36, T&P RAIL ROAD COMPANY SURVEY. |  | PUMPING STATION | PUMP |  | 1964 | OTHER | VIBRA.ON PUMP BROKE LINE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1740 | 1560.3707 | 3147.8979 | CRUDE OIL | 1 | 190 | 170 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | OTHER | VIBRA. CHECK PERIOD | Null | Null | R.C. KINNEAR, DIVISION MANAGER | 9156877551 | 1/2" COOLING LINE ON #1 PUMP BROKE FROM VIBRATION.
2017-09-29 08:50 | YES | NO | 19880054 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1988-03-01 | 1030 | OK | STEPHENS |  | NO |  | NO | ONE MILE WEST OF COUNTY LINE, 2 MILES NORTH , 1 1/2 MILES WEST, 1/2 MILE NORTH. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 448.3824 | 904.5684 | CRUDE OIL | 1 | 384 | 226 | NO | NO | 6 | 0.25 | 2640 | WELDED |  | 960 | 85 | YES | 24 | 1200 | 5 | 81 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | HERBERT MCCONNELL, MAINTENANCE FOREMAN | 4058674822 | MOBIL OIL COMPANY'S ELECTRICIAN WAS DIGGING AN ANCHOR FOR A DEADMAN WHEN THEY HIT MID-CONTINENT PIPELINE'S 6" MAIN LINE FROM VELMA, OK TO EOLA STATION. MOBIL DID NOT "CALL OKIE" NOR WAS MID-CONTINENT NOTIFIED. MID-CONTINENT PIPE LINE MARKERS WERE ON A LEASE ROAD APPROXIMATELY TWENTY(20) YARDS FROM LINE DAMAGE.
2017-09-29 08:50 | YES | NO | 19880055 |  | 4906 | EXXON PIPELINE CO | YES | 1988-02-17 | 1530 | TX | SAN PATRICIO |  | NO |  | NO | LEAK OCCURRED AT STATION 36+21, SOME 131 FEET OUTSIDE WEST PROERTY FENCE LINE OF EXXON PIPELINE COMPNA'S INGLESIDE STATIO ALONG THE INGLESIDE TO VANDERBILT 16" |  | LINE PIPE | PIPE |  | 1966 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 16141.7656 | 32564.4611 | CRUDE OIL | 1 | 1300 | 1295 | NO | NO | 16 | 0.22 | 56000 | WELDED |  | 1104 | 1020 | YES | 24 | 1380 | 12 | 66 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT APPROXIMATELY 3:30 P.M. ON FEB. 17, 1988, EXXON PIPELINE COMPANY'S (EPC) OILTRAFFIC CONTROL CENTER (OTCC) CONTROLLER NOTIFIED THE STATION OPERATOR AT EPC'SINGLESIDE STATION. OTCC HAD NOTICED A SUDDEN RATE OF CHANGE IN FLOW RATE. THESTATION OPERATOR VERIFIED OTCC'S REMOTE READINGS OF FLOW AND ALSO PRESSURE. THE STATION OPERATOR THEN INSTRUCTED OTCC TO SHUT THE LINE DOWN. THE LINE WAS SHUTDOWN AT 3:35 P.M.THE LINE FLYER WAS CONTACTED AND AERIAL SURVEILLANCE WAS MADE AT 5:40 P.M. TO IDENTIFY LEAK LOCATION. AT THIS TIME, TOTAL BARRELS OF CRUDE OIL RELEASED WERE ESTIMATED TO BE 75 BBLS. (ACTUAL AMOUNT WAS 150 BBLS).EPC PERSONNEL AND CONTRACT EQUIPMENT (INCLUDING VACUUM TRUCKS) WERE DISPATCHED TO THE SITE AT 5:45 P.M. THE LINE WAS DRAINED (1150 BBLS) AND PERMANENT REPAIRSWERE MADE BY INSTALLING A NEW 5-1/2' SECTION OF PIPE.THE LINE WAS RESTORED TO SERVICE AT 7:00 A.M. ON FRB. 19, 1988. CLEAN-UP OPERATIONS ARE CURRENTLY IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19880056 |  | 4906 | EXXON PIPELINE CO | NO | 1988-02-06 | 725 | TX | WALLER |  | NO |  | NO | IN WALLER COUNTY APROXIMATELY 1 MILE WEST OF FM 359, 2 1/2 MILES MORTH OF FM 529 AND 2 MILES EAST OF FM 1887. LEAK WAS ON THE RACOON BEND-SATSUMA 8" PIPELINE. |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13451.4713 | 27137.0509 | CRUDE OIL | 1 | 4150 | 3500 | NO | NO | 9 | 0.32 | 25000 | COUPLED |  | 400 | 170 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER |  | LEAK WAS REPORTED TO EXXON PIPELINE COMPNAY DISPATCHER BY TENANT (MR. HARTMAN) ON 2-6-88 AT APPROXIMATELY 7:20 P.M. EXXON PIPELINE COMPANY'S AREA FOREMAN WAS NOTIFIED AT APPROXIMATELY 7:25 P.M.THE FLOW WAS SHUTDOWWN REMOTELY BY THE EXXON PIPELINE DISPATCHER AND A GANG FOREMAN AND GANG WERE SENT TO THE LEAK SITE. TEMPORARY REPAIRS (PATCH & CLAMP) WERE COMPLETED AT APPROXIMATELY 7:30 A.M. ON 2-7-88 AND CLEAN-UP OPERATIONS WERE STARTED. PERMANENT REPAIRS (NEW PIPE) WERE COMPLETED ON 2-16-88.THE LEAK WAS CAUSED BY EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19880057 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1988-02-15 | 700 | KS | KINGMAN |  | NO |  | NO | BORGER-E. CHICAGO LINE - RAGO TERMINAL -MP 225 , 1 MILE SOUTH OF RAGO, KS, ON HWY. 14. |  | NO DATA | PIPE |  | 1987 | OTHER | TUBE STRING FAILURE. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2241.9119 | 4522.8418 | L. P. G. | 2 | 1 | 0 | YES | YES | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | POSSIBLE BRINE TUBING FAILURE IN CAVERN #8 ALLOWED PROPANE TO LEAK BACK TO TERMINAL WATER HEADER. FROM THERE VAPORS LEAKED BACK TO NORTH FRESH WATER WELL. VAPORS LEAKED INTO PUMP BUILDING, REACHED AN IGNITION SOURCE, AND MINOR EXPLOSION AND FIRE FOLLOWED.
2017-09-29 08:50 | YES | NO | 19880058 |  | 443 | AMOCO PIPELINE CO | NO | 1988-02-08 | 845 | TX |  |  | YES | LAT 28 48' LONG 94 34' | YES | APPROXIMATELY 31 MILES SOUTHEAST OF GALVESTON, TEXAS. |  | LINE PIPE | PIPE |  | 1978 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 237000 | 212533.2466 | 428765.404 | CRUDE OIL | 1 | 15000 | 0 | NO | NO | 14 | 0.38 | 42000 | WELDED |  | 1620 | 750 | YES | 24 | 2025 | 9 | 78 | NO DATA | Null | YES | NO DATA |  | SHIP ANCHOR |  | Null | NO DATA |  | Null | Null | HOWARD B. SPALDING - SUPERVISOR - OPERATIONS | 4099483407 | AT APPROXIMATELY 8:15 AM ON 2/8/88, THE HIPS CONTROL CENTER COMPLETED CALCULATIONS INDICATING A SHORTAGE IN THE OIL MEASURED INTO TEXAS CITY OPERATONS CONTROL CENTER. INITIALLY, IT WAS BELIEVED THAT THE SHORTAGE WAS DUE TO A MEASUREMENT ERROR. AT THE SAME TIME A RE-CHECK WAS BEING MADE ON THE MEASUREMENT CALCULATIONS, OUR HELICOPTER WAS DISPATCHED TO MAKE AN AERIAL PATROL OF THE OFFSHORE PIPELINE. AN OIL SLICK APPROXIMATELY 1 - 3 MILES WIDE X 15 - 20 MILES LONG WAS LOCATED ABOUT 21 MILES SOUTHEAST OF GALVESTON.A DIVE BOAT WAS MOBILIZED ON 2/11/88. THE 14" LINE HAD BEEN PULLED OUT OF THE TRENCH AND ABOUT 110 FT. OF THE PIPE WAS SUSPENDED 6' - 8' ABOVE THE MUDLINE. REPAIRS WERE MADE USING ON PIPE JOINT (43' _+) OF NEW PIPE AND A SET OF "GRIPPER"REPAIR TOOLS. THE DAMAGE WAS THE RESULT OF A SHIP ANCHOR.
2017-09-29 08:50 | NO | NO | 19880059 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-02-07 | 1330 | IL | MENARD |  | NO |  | NO | MENARD TERMINAL |  | TANK FARM | VALVE |  | 1984 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 34000 | 30490.0016 | 61510.6487 | FUEL OIL | 3 | 40 | 34 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H. E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | ON FEBRUARY 7, 1988, A 40 BARREL FUEL OIL LEAK WAS DISCOVERED AT OUR MENARD, ILLINOIS TERMINAL. PARTICULATE MATTER LODGED IN A TANK PUMP THERMAL RELIEF VALVE AND CAUSED IT TO STICK OPEN. THE OPEN VALVE THEN RELIEVED PRODUCT INTO THE SUMPSEPARATOR SYSTEM, UPSET THE OIL/WATER SEAL, AND RESULTED IN THE DISCHARGE OF PRODUCT INTO A NEARBY TANK DIKE. THE RELEASE WAS CONTAINED ON OUR PROPERTY, WITHIN THE DIKED AREA. THE AREA WAS FLOODED WITH WATER TO MINIMIZE PRODUCT CONTACT WITH THE SOIL, AND TO AID IN PRODUCT RECOVERY. CLEANUP OPERATIONS ARE IN PROGRESS. THE THERMAL RELIEF DEVICES WERE RELOCATED ON THE PUMP PIPING TO MINIMIZE THE POSSIBILITY OF A REOCCURENCE.
2017-09-29 08:50 | YES | NO | 19880060 |  | 19213 | TEXACO CHEMICAL CO - A DIV OF TEXACO INC | NO | 1988-02-03 | 830 | TX | JEFFERSON |  | NO |  | NO | ON PLANT PROPERTY OF DUPONT DE NEMOURS E I & CO., ALONG HIGHWAY 347, APPROXIMATELY 5 MILES SOUTH OF BEAUMONT, TEXAS. |  | NO DATA | OTHER | METERING STATION | 1977 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 50 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MAX E. SEARS, PLANT MANAGER | 4099896501 | OPERATOR'S CONTRACTOR, IN PREPARATION FOR CALIBRATING METER, MADE IMPROPER VALVE ALIGNMENT THAT ALLOWED APPROXIMATELY 50 BARRELS OF PROPYLENE TO BE RELEASED THROUGH THE VENT STACK TO THE ATMOSPHERE.
2017-09-29 08:50 | YES | NO | 19880062 |  | 443 | AMOCO PIPELINE CO | YES | 1988-02-09 | 1500 | OK | JEFFERSON |  | NO |  | NO | NE 1/4 SECTION 4 T6S-R4W. 7 MI. SOUTH AND S1 1/2 MI. WEST OF RINGLING, OK. |  | LINE PIPE | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 448.3824 | 904.5684 | CRUDE OIL | 1 | 880 | 860 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 0 | 150 | YES | 24 | 917 | 6 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | J.W. WILHELM | 9182257271 | THE COUNTY ROAD GRADER WAS GRADING THE ROAD AND STRUCK THE PIPELINE IN THE DITCH BOTTOM. MARKER SIGNS WERE LOCATED AT THE ROAD CROSSING. AN 8 ROOT SECTION OF 8" PIPE WAS CUT OUT AND REPLACED.ADDITIONAL GRAVEL COVER IS TO BE PLACED OVER THE PIPELINE AT THIS POINT TO PROTECT IT FROM FUTURE PROBLEMS.
2017-09-29 08:50 | NO | NO | 19880064 |  | 2327 | CHEVRON USA INC | NO | 1988-02-19 | 1130 | TX | HARDIN |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3587.059 | 7236.5469 | GASOLINE | 1 | 20 | 15 | NO | NO | 12 | 0.38 |  | WELDED |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. E. SMITH, DIVISION MANAGER | 4098393130 | EXTERNAL PIT ON PIPELINE, RELEASED DISCOVERED BY AERIAL PATROL PLANE. ALL NECESSARY AGENCIES WERE NOTIFIED. CLEAN UP WAS NOMINAL. TWO VISITS BY THE BIG THICKET NATIONAL PRESERVE RANGERS AND OUR RESPONSE AND CLEANUP WAS ADEQUATE AND TIMELY.PLIDCO REPAIR SLEEVE TO BE WELDED 2/22/88, SORBENT PADS WERE DESPOSED AT AUTHORIZED DISPOSAL SITE.PLIDCO SLEEVE WAS WELDED, DOPED, WRAPPED, ANODES INSTALLED AND BACKFILLED.
2017-09-29 08:50 | YES | NO | 19880065 |  | 18718 | SUN PIPELINE CO | NO | 1988-03-24 | 600 | TX | COKE |  | NO |  | NO | SECTION 315, BLOCK 1A, H&TC RR CO. SURVEY APPROXIMATELY 2 MILES SOUTH OF SIVER, TEXAS AT OUR JAMESON TRUNK STATION. |  | PUMPING STATION | PUMP |  | 1975 | OTHER | PACKING GLAND BLOT BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 1097.6401 | 2214.3834 | CRUDE OIL | 1 | 70 | 56 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E. F. MCKINLEY, JR. | 2147570220 | PACKING SEIZED THE ROD SAUSING BOLTS TO BREAK THAT HOLDS GLAND NUT - THIS ALLOWED PACKING TO COME OUT CAUSING SPILL.REPAIRS TO PUMP BEGAIN IMMEDIATELY, PACKING INSTALLED. ROD WAS REPLACED. BACK ON LINE, PUMP WORKING SATISFACTORILY.56 BARRELS WERE RECOVERED AND PUMPED BACK INTO SYSTEM - 14 BARRELS SOAKED IN GROUND AND COVERED WITH FRESH DIRT.
2017-09-29 08:50 | YES | NO | 19880066 |  | 4906 | EXXON PIPELINE CO | NO | 1988-01-15 | 657 | MA | MEDFORD |  | NO |  | NO | ROUTE #16@ MALDEN RIVER BRIDGE, MEDFORD, MASSACHUSETTS. |  | LINE PIPE | PIPE |  | 1944 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 1500 | 500 | NO | NO | 7 | 0.45 |  | WELDED |  | 1273 | 540 | YES | 0 | 1400 | 2 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | KENNETH P. GABRIEL - TERMINAL SUPT. | 6173812847 | ON JANUARY 15,1988 @ 06:57 DURING A TRANSFER OF GASOLINE FROM EVERETT, MASS. TOWALTHAM, MASS. A PIPELINE LEAK OCCURRED IN MEDFORD,MASSACHUSETTS. LOOSE CONTACTS ON A PUMP RELAY CAUSED PUMPS TO COME ON AND OFF CAUSING SHOCK WAVES INSIDE THE PIPELINE. THIS COUPLED WITH LOAD PRESSURE ON THE PIPELINE RESULTED IN A LINE FAILURE.
2017-09-29 08:50 | YES | NO | 19880067 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1988-02-26 | 1600 | TX | WHARTON | DANEVANG | NO |  | NO | OFF FM 3986 APPROXIMATELY 3/4 MILES NORTH AND/OR 1/4 MILE SOUTH OF COASTAL'S DANEVANG PUMPING STATION. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 16141.7656 | 32564.4611 | L. P. G. | 2 | 997 | 0 | NO | NO | 8 | 0.32 | 2614 | WELDED |  | 750 | 410 | YES | 24 | 1050 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PUBLIC EDUCATION | NO | Null | KENNETH P. RATLIFF- AREA SUPERVISOR | 5128971721 | PIPELINE STRUCK BY MAINTAINER (ROAD GRADER) CUTTING DRAINAGE DITCH FOR IRRIGATION CANAL. BLADE PUNCTURED LINE AND OPERATOR BACKED MAINTAINER OFF OF PIPELINE.
2017-09-29 08:50 | YES | NO | 19880068 |  | 19226 | TEXACO PIPELINE INC | NO | 1988-03-14 | 2300 | TX | HARRIS | HOUSTON | NO |  | NO |  |  | LINE PIPE | VALVE |  | 1965 | OTHER | RELIEF LINE REMOVED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 89.6765 | 180.9137 | CRUDE OIL | 1 | 200 | 199 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. MINER | 7134322765 | ON 11/12/87 ARCO PIPELINE CO. DISCONNECTED OUR 16" PIPELINE HEADER AND THEIR 20"LINE AT LANE ST. JCT. IN PREPARATION TO HYDROTEST THEIR LINE. TO DISCONNECT AND REMOVE HEADER, LOCATED BETWEEN OUR LINES, ARCO REQUESTED TPLI TO REMOVE THE 1"RELIEF LINE BETWEEN THE HEADER AND THE TPLI LINE (SEE SKETCH). THE RELIEF VALVE WAS SET @ 50# TO RELEIVE SUN PRESSURE ON BARREL WHEN LINE IS DOWN. WE VERBALLY INSTRUCTED ARCO TO ADVISE US AS TO WHEN THEIR LINE WOULD BE READY FOR SERVICE AND WE SOULD AT THAT TIME RE-INSTALL THE RELIEF LINE. ON 3/14/88 AT ABOUT 11:30P.M. TPLI WAS CALLED AND NOTIFIED THAT ARCO HAD A LEAK AT LANE ST. JCT. ARCO HAD RE-INSTALLED THE HEADER AND PUT THEIR LINE BACK IN SERVICE BUT FAILED TO NOTIFY TPLI. ARCO SAID THEYHAD LEFT THEIR MAINLINE VALVE OPENED TO HEADER WHICH SHOULD HAVE BEEN CLOSED, PLUS HAD FAILED TO NOTIFY US AS TO RE-INSTALLING THE HEADER.
2017-09-29 08:50 | NO | NO | 19880069 |  | 12628 | MOBIL PIPELINE CO | NO | 1988-03-12 | 1215 | TX | WILSON |  | NO |  | NO | IN THE LOUIS MANCHACA II LEAGUE GRANT SURVEY. |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 3300.0943 | 6657.6232 | GASOLINE | 3 | 35 | 0 | NO | NO | 4 | 0.24 | 35000 | WELDED |  | 1270 | 900 | YES | 2 | 1357 | 9 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D. L. DENNARD , VICE PRESIDENT, OPERATIONS | 2146582226 | A SECTION OF THE 4" CORPUS CHRISTI TO SAN ANTONIO REFINED PRODUCTS PIPELINE WASISOLATED AND PRESSURIZED WITH WATER TO DETERMINE THE LOCATION OF A LEAK. THE LEAK WAS THE RESULT OF EXTERNAL CORROSION PENETRATING THE WALL OF THE PIPE. THE JOINT OF 4" PIPE WAS REMOVED AND REPLAED WITH NEW PRETESTED 4" PIPE.
2017-09-29 08:50 | YES | NO | 19880070 |  | 443 | AMOCO PIPELINE CO | YES | 1988-03-17 | 1100 | IL | WILL | MONEE | NO |  | NO | 130 FEET WEST OF STEGER-MONEE ROAD, 1/16MILE SOUTH OF DRALLE, 1/16 MOLE NORTH OF HAMILTON. |  | LINE PIPE | BOLTED FITTING |  | 1934 | OTHER | FIBER GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 22419.1188 | 45228.4181 | GASOLINE | 3 | 100 | 75 | NO | NO | 14 | 0.38 | 35000 | WELDED |  | 720 | 500 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. A. STAHL - AREA MANAGER | 2197382384 | ON THE MORNING OF MARCH 17, 1988, A PIPELINE MAINTENANCE CREW BROKE SOME FIELD TILES WHILE EXCAVATING AN ADJACENT PIPELINE. THE FIELD TILES CONTAINED UNLEADEDGASOLINE. FURTHER INVESTIGATION REVEALED THAT A FLANGED SPOOL PIECE WAS LEAKING ON THE 14" PIPELINE. IT APPEARS THAT THE FIBER GASKETS ON THE FLANGED SPOOL PIECE HAD DETERIORATED WITH AGE AND ALLOWED TH GASOLINE TO LEAK FROM THE PIPELINE
2017-09-29 08:50 | YES | NO | 19880071 |  | 19212 | TESORO PIPELINE CO | NO | 1988-03-24 | 1200 | TX | DIMMIT | CARRIZO SPRINGS | NO |  | NO | 3 MILES WEST OF CARRIZO SPRINGS, TEXAS ON TEXAS 277, TO TESORO PIPELINE CROSSING. NORTH ON RIGHTAWAY ABOUT 2/10 MILES. |  | LINE PIPE | NO DATA |  | 1973 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1345.1471 | 2713.7051 | CRUDE OIL | 1 | 80 | 0 | NO | NO | 4 | 0.13 | 1944 | WELDED |  | 360 | 50 | YES | 0 | 0 | 0 | 73 | INTERNAL | Null | YES | NO DATA | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | FORREST FINLEY, SAFETY COORDINATOR, TESORO CRUDE OIL CO. | 5123335634 | THE PENA CREEK GATHERING SYSTEM DEVELOPED LEAKS IN TWO SEPERATE LOCATIONS. THELEAKS WERE 2/10 MILE APART. THE MOUNT OF CRUDE OIL LOSS WAS APPROXIMATELY 50-80BARRELS. THE LEAKS WERE EXPOSED, CLAMPED, COATED AND WRAPPED, COMPLETELY STOPPING THE LEAKS.
2017-09-29 08:50 | NO | NO | 19880072 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1988-03-16 | 800 | CA | CONTRA COSTA | CONCORD | NO |  | NO | 1551 SOLANO WAY - JUST ACROSS STREET ROM OUR CONCORD PUMP STATION. |  | LINE PIPE | PIPE |  | 1967 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 |  | 244 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 1099 | YES | 24 | 1450 | 0 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | BARRY R. PEARL, VICE PRESIDENT-OPERATIONS | 2134867860 | OUR FIELD PERSONNEL FOUNE A STAIN ON GROUND OUTSIDE CONCORD PUMP STATION. PRESSURE WAS BLED OFF THE LLINE. THE PIPE AT POINT OF LEAK WAS FOUND TO HAVE BEEN DAMAGED SOMETIME IN THE PAST. PIPE WAS ALSO FOUND TO BE LAMINATED AT THIS LOCATION AND A SECTION OF PIPE WAS REPLACED.MR. DAVID DONALDSON-ROOM 8417INFORMATION RESOURCES MANAGERDEPARTMENT OF TREANSPORTATION-DPS-10400 SEVENTH STREET, S.W.WASHINGTON, D.C. 205902-CCMR. JAMES F. MCMULLENSTATE FIRE MARSHAL7171 BOWLING DRIVE, SUITE 600SACRAMENTO, CALIFORNIA 95823
2017-09-29 08:50 | YES | NO | 19880073 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-03-12 | 1330 | TX | WARD | MONAHANS | NO |  | NO | SW 1/4, NW 1/4, SECTION 6, BLOCK 19THREE MILES EAST OF MONAHANS, HENDRICK-B ARNSLEY NO. 2 - 6-INCH. |  | LINE PIPE | PIPE |  | 1920 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2097 | 1880.5157 | 3793.7597 | CRUDE OIL | 1 | 510 | 455 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 800 | 150 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. W. HOLDEN, MANAGER REGULATIONS AND MAINTENANCE STANDARDS | 7132416262
2017-09-29 08:50 | YES | NO | 19880074 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-03-01 | 1920 | KS | ALLEN |  | NO |  | NO | LINE SECTION 006, SW1/4 SECTION 20, T24S R20E. |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2241.9119 | 4522.8418 | FUEL OIL | 3 | 443 | 200 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1050 | 930 | YES | 8 | 1554 | 7 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS | NO | NO | H. E. JANZEN, VICE-PRESIDENT- OPERATIONS | 9185883850 | ON MARCH 1, 1988, A LOCAL FARMER CONDUCTING MAINTENANCE WORK ON A LAND TERRACE STRUCK OUR #3-8" BARNSDALL-DANSAS CITY PIPELINE WITH A MOLD BOARD PLOW. THE LINE WAS SHALLOW, HOWEVER, THIS AREA HAD BEEN UNDER CULTIVATION FOR 30 YEARS WITHOUT ANY PREVIOUS PROBLEMS. THE SHALLOW LINE IN THE VICINITY OF THE LEAK SITE WILLBE LOWERED TO APPROPRIATE DEPTHS. CLEANUP EFFORTS ARE UNDERWAY IN COOPERATION WITH TH STATE.
2017-09-29 08:50 | YES | NO | 19880075 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-02-26 | 2335 | NE | LANCASTER |  | NO |  | NO | LINCOLN TERMINAL |  | TANK FARM | PUMP |  | 1940 | OTHER | VIBRATION/WEAR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 80708.8278 | 162822.3053 | GASOLINE | 3 | 60 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H. E. JANZEN, VICE - PRESIDENT - OPERATIONS | 9185883850 | AT 2330 HOURS ON FRBRUARY 26, 1988, A GASOLINE LEAK WAS DISCOVERED AT OUR LINCOLN, NEBRASKA TERMINAL. THE RELEASE ORIGIANATED FROM TANK #731'S PUMP. VIBRATION APPARENTLY CAUSED THE METAL SEATING SURFACE ON THE PUMP CASE TO WEAR, RESULTING IN LEAKAGE AROUND THE CASE BOLT HOLES. THE PUMP WAS NOT RUNNING AT THE TIME THE RELEASE WAS DISCOVERED. CONTAMINATED SOIL HAS BEEN EXCAVATED AND CLEANUP OPERATIONS ARE CONTINUING IN FULL COOPERATION WITH THE STATE.
2017-09-29 08:50 | YES | NO | 19880076 |  | 4906 | EXXON PIPELINE CO | NO | 1988-02-20 | 300 | TX | BRAZORIA |  | NO |  | NO | APPROXIMATELY 100 FEET EAST OF F.M. 517 NEAR ALVIN, TEXAS. LEAK OCCURRED AT STATION NUMBER 1792+19 ON THE BOLING-WEBSTER 8-INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 896.7648 | 1809.1367 | CRUDE OIL | 1 | 600 | 585 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 600 | 100 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | SALT WATER | NO DATA |  | Null | NO DATA |  | Null | Null | G. P. MURRAY, OPERATIONS MANAGER | 7136565956 | DURING NORMAL OPERATION, A LEAK OCCURRED IN THE BODY OF THE PIPE. THERE WERE NO UNUSUALY ACTIVITIES ASSOCIATED WITH THIS LEAK. THE LEAK WAS STOPPED BY INSTALLING A "PLIDCO" SLEEVE.
2017-09-29 08:50 | YES | NO | 19880077 |  | 4906 | EXXON PIPELINE CO | NO | 1988-02-21 | 1200 | TX | BRAZORIA |  | NO |  | NO | APPROXIMATELY 50 FEET EAST OF F.M. 1762 NEAR ALVIN, TEXAS. LEAK OCCURRED AT STATION NUMBER 1591+880 ON THE BOLING - WEBSTER 8-INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1700 | 1524.5001 | 3075.5324 | CRUDE OIL | 1 | 1500 | 1465 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 600 | 100 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | SALT WATER | NO DATA |  | Null | NO DATA |  | Null | Null | G. P. MURRAY, OPERATIONS MANAGER | 7136565956 | DURING NORMAL OPERATIONS, A LEAK OCCURRED INTHE BODY OF THE PIPE. THERE WERE NO UNUSUAL ACTIVITIES ASSOCIATED WITH THIS LEAK. A CLAMP WAS INSTALLED TO STOP THE LEAK. PERMANENT REPAIRS WERE COMPLETED LATER AN CONSISTED OF "FULL WRAPPING"THE PIPE. THE PIPELINE WAS TAKEN OUT OF SERVICE AND HYDROSTATICALLY TESTED.
2017-09-29 08:50 | YES | NO | 19880078 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-03-09 | 1245 | TX | WARD | MONAHANS | NO |  | NO | SW 1/4, SW 1/4, SECTION 6, BLOCK 19 THREE MILES EAST OF MONAHANS HENDRICK-BARNSLEY NO. 2 - 6 INCH. |  | LINE PIPE | PIPE |  | 1920 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2536 | 2274.1954 | 4587.9707 | CRUDE OIL | 1 | 850 | 780 | NO | NO | 6 | 0.28 |  | WELDED |  | 800 | 100 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. W. HOLDEN, MANAGER REGULATIONS AND MAINTENANCE STANDARDS. | 7132416262
2017-09-29 08:50 | NO | NO | 19880079 |  | 443 | AMOCO PIPELINE CO | Null | 1988-01-07 | 1500 | LA | CAMERON | HACKBERRY | NO |  | NO | LEAK OCCURRED ON PATRICK PUMP STR. 4" DISCHARGE LINE 200 FT. EAST OF PUMP; 2 CRUDE GATHERING LINE SECTION 28 T-125, R-10W. |  | NO DATA | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 224.1912 | 452.2842 | CRUDE OIL | 1 | 20 | 20 | NO | NO | 4 | 0.24 |  | WELDED |  | 150 | 100 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | OXIDATION | NO DATA |  | Null | NO DATA |  | Null | Null | J. E. BRASFIELD- FIELD SUPT. | 4098355381 | LINE CORROSION DUE TO COATING FAILURE 10 BBLS. OF OIL WAS RECOVERED AND THE REMAINING 10 BBLS. WAS DISPOSED OF REPAIR WAS MAKE BY REPLACING 42 ST. OF LINE WITHNEW PIPE.
2017-09-29 08:50 | YES | YES | 19880081 |  | 18718 | SUN PIPELINE CO | YES | 1988-02-17 | 1607 | OH | SENECA | PLEASANT TOWNSHIP | NO |  | NO | PLEASANT TOWNSHIP, SENECA COUNTY, OHIO N 1/2 OF THE W 1/2 OF THE SE 1/4 OF SECTION 26-T3N-R15E. 1020' EAST OF A POINT IN THE CENTERLINE OF CO. RT. 37 WHICH IS |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 6 | 3 | 3 | 0 | 0 | 0 | TOLUENE | 3 | 4191 | 643 | NO | NO | 9 | 0.28 | 35000 | WELDED |  | 1200 | 1095 | YES | 54 | 1500 | 11 | 52 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE PATROL | NO | NO | CHARLES W. DUNN, MANAGER OF COMPLIANCE | 9185866231 | AT APPROXIMATELY 1607 HRS., FEBRUARY 17, 1988, SUN PIPE LINE ("SPL") DETERMINEDTHAT A LEAK HAD OCCURRED ON ITS EASTERN AREA PRODUCTS PIPELINE BETWEEN ITS FOSTORIA, OHIO AND LOWELL, OHIO PUMPING STATIONS. TOLUENE WAS BEING TRANSPORTED THROUGH THIS SEGMENT OF THE PIPELINE AT THE TIME. PUMPING OPERATIONS WERE CEASED AT 1608 HRS. AND SPL PERSONNEL DISPATCHED TO DETERMINE THE LEAK LOCATION. AT APPROXIMATELY 1830 HRS. THE LEAK WA FOUND AT SPL MILE POST 89/2384 IN PLEASANT TOWNSHIP, SENECA COUNTY, OHIO (NEAR TIFFIN, OH).TOLUENE FROM THE RUPTURE TRAVELED INTO AND THROUGH SUGAR CREEK ULTIMATELY REACHING THE SANDUSKY RIVER. THIS RIVER FLOWS NORTH TO LAKE ERIE. HOMES AND BUSINESSES ALONG THE WATER WERE EVACUATED. SPILL BOOMS AND SIPHON DAMS WERE INSTALLED ACROSS THE CREEK AND RIVER TO CONTAIN THE TOLUENE. VACUUM TRUCKS WERE UTILIZED TO REMOVE THE PRODUCT FROM THE SURFACE OF THE WATER.A LONGITUDINAL RUPTURE APPROXIMATELY 14.5 INCHES IN LENGTH AND 7/8 INCHES AT THE WIDEST POINT WAS FOUND UPON UNCOVERING THE LINE. A PIECE OF PLASTIC CORRUGATED PIPE, USED FOR AGRICULTURAL DRAINAGE, WAS FOUND RESTING ON THE PIPELINE AT THEPOINT OF FAILURE. THE FAILED SECTION OF FPIPE WAS REMOVED AND TAKEN TO THE BATTELLE INSTITUTE, COLUMBUS, OHIO FOR FURTHER STUDY. THE FAILED SECTION WAS REPLACED WITH NEW PRETESTED PIPE BUTT WELDED INTO PLACE.AT 0825 HRS, 2/21/88 THE LINE WAS PLACED IN OPERATION AT 80% NORMAL OPERATING PRESSURE AS A SAFETY PRECAUTION PENDING A PRELIMINARY ANALYSIS OF FAILURE. THE LINE WAS RETURNED TO FULL SERVICE (100% NORMAL OPERATING PRESSURE) ON THE AFTERNOONOF 2/23/88 AFTER BATTELLE REPRESENTATIVES, SPL ENGINEERS AND A DOT REPRESENTATIVE COMPLETED THEIR PRELIMINARY ANALYSIS. THIS ANALYSIS INDICATED THAT THIRD PARTYDAMAGE WAS THE CAUSE OF FAQILURE. NO SERIOUS INJURIES OR DEATHS HAVE BEEN REPORTED AS A RESULT OF THIS LEAK.
2017-09-29 08:50 | YES | YES | 19880082 |  | 18718 | SUN PIPELINE CO | YES | 1988-02-17 | 1307 | OH | SENECA | ADAMS TOWNSHIP | NO |  | NO | STATE ROUTE 19, REPUBLIC, OHIO, S.W. 1/4 SECTION 28, ADAMS TOWNSHIP, SENECA COUNTY, OHIO. |  | PUMPING STATION | OTHER | NIPPLE FROM STRAINER BAR. | 1980 | OTHER | STRAINER NIPPLE FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 2 | 0 | 5 | 4.4838 | 9.0457 | TOLUENE | 3 | 1 | 1 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DUNN, MANAGER OF COMPLIANCE | 9185866231 | THIS INCIDENT IS NOT A REPORTABLE ACCIDENT UNDER DOT PART 195 REGULATIONS, HOWEVER, SUN PIPE LINE COMPANY WISHES T ADVISE YOU OF THIS RELEASE BECAUSE OF OUR NOTIFICATION TO THE NRC.AT APPROXIMATELY 1307 HRS., FEBRUARY 17, 1988, WHILE PERFORMING PREVENTIVE MAINTENANCE ON A STRAINER DRAIN AT LOWELL PUMP STATION A NIPPLE BROKE OFF AN RELEASED APPROXIMATELY 20 GALLONS OF TOLUENE OF WHICH APPROXIMATELY 10 GALLONS WERE RECOVERED. A NEW NIPPLE AND VALVE HAS BEEN INSTALLED.
2017-09-29 08:50 | YES | NO | 19880085 |  | 15851 | PRIDE REFINING INC | NO | 1988-04-04 | 1135 | TX | JONES |  | NO |  | NO | STA 277 + 25 M. MILLARD SUREVEY SECTION 243. APPROXIMATELY 1.75 MILES NORTH OF PRIDE REFINERY. APPROXIMATELY 40 FEET EAST FO BURLINGTON RAILROAD. |  | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 130 | 105 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 470 | 90 | YES | 8 | 750 | 0 | 74 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | TERRY PRITCHARD, MANAGER OF ENGINEERING | 9156748473 | OUR PIPELINE PATROL PILOT REPORTED TO THE REFINERY AN OIL SPOT ONTHE PIPELINE RIGHTAWAY AT THE TIME AND LOCATION RECORDED ABOVE. REFINERY MAINTENANCE PERSONNEL WERE DISPATCHED TO THE SITE. CLEAN UP OPERATIONS BEGAN, AND THE BURIED LINE WAS UNCOVERED REVEALING 3 SMALL PIN HOLES WITHIN 8" OF EACH OTHER. A PIPE CLAMP WAS INSTALLED. REPLACEMET OF THIS SECTION IS PLANNED.,
2017-09-29 08:50 | YES | NO | 19880086 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1988-03-19 | 125 | OK | CUSTER |  | NO |  | NO | BUXTON-BORGER LINE "O" - MP 155-05+831038' SOUTH AND 53' WEST OFTHE NE CORNER OF SEC. 19, T13N, R13W. |  | LINE PIPE | GIRTH |  | 1951 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 21093 | 18915.4589 | 38160.121 | CRUDE OIL | 1 | 1903 | 928 | NO | NO | 11 | 0.2 | 42000 | WELDED |  | 1140 | 760 | YES | 24 | 1380 | 2 | 78 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B. L. THORMAN, MANAGER OF ENGINEERING & TECH. SERVICES | 9186614721 | WHEN THE PIPELINE CONTROLLER DISCOVERED A PRESSURE LOSS AT CLINTON PUMP STATION(DOWNSTREAM FROM LEAK) AND AN INCREASE IN FLOW AT BUXTON STATION, HE SHUT THE LINE DOWN AND BLOCKED IT IN. THE LEAK WAS CAUSED BY A 6" CRACK IN THE GIRTH WELD.
2017-09-29 08:50 | YES | NO | 19880087 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1988-03-19 | 1930 | MO | CASS |  | NO |  | NO | BORGER - E. CHICAGO "BLUE"LINE - MP 448-05+06 2 1/2 MILESNORTH OF CITY OF HARRISONVILLE, MO ON EAST SIDE OF HARRISONVILLE CITY LAKE. |  | LINE PIPE | PIPE |  | 1972 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 103.1279 | 208.0507 | L. P. G. | 2 | 5 | 0 | NO | NO | 11 | 0.22 | 52000 | WELDED |  | 1080 | 460 | YES | 24 | 1677 | 11 | 72 | NO DATA | Null | Null | NO DATA |  | OTHER | THIRD PARTY (BULLET) | Null | ONE CALL |  | Null | Null | B. L. THORMAN, MANAGER OF ENGINEERING & TECH. SERVICES | 9186614721 | CASS COUNTY SHERIFF NOTIFIED AREA OFICE THAT THERE WAS PRODUCT SPRAYING INTO THE AIR AT OUR VALVE SITE ON THE EAST SIDE OF HARRISONVILLE LAKE.LINE WAS SHUT DOWN AND BLOCKED. MANUAL BLOCK VALVES WERE CLOSED, THEREBY ISOLATING A 1000' SECTION OF PIPE TOMAKE THE REPAIR. THE CAUSE OF THE LEAK WAS A BULLET HOLE IN THE PIPE.
2017-09-29 08:50 | NO | NO | 19880088 |  | 443 | AMOCO PIPELINE CO | YES | 1988-03-23 | 1045 | MO | CASS | FREEMAN | NO |  | NO | SE/4 SECTION 7, T44N, R32W, CASS CO., MISSOURI (SEE ATTACHED SKETCH) |  | TANK FARM | VALVE |  | 1930 | OTHER | SUBSIDENCE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 12 |  |  | FLANGED |  | 400 | 10 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | SUBSIDENCE |  | Null | NO DATA |  | Null | Null | MITCHELL B. WEISS, AREA MANAGER, AMOCO PIPELINE | 8169685387 | A THIN, CIRCUMFERENTIAL CRACK APPROXIMATELY 18-INCHES LONG BETWEEN THE BODY ANDFLANGE OF A CRANE 400 WOG GATE VALVE UNDER ABOUTH 10 PSI OF TANK HEAD RELEASED SOME CRUDE OIL ONTO THE GROUND WITHIN OUR FREEMAN TANK FARM FACILITY. BEFORE RECOVERY WASCOMPLETE, WITHOUT OUR KNOWLEDGE, A SMALL AMOUNT ENTERED THE STORM WATER FRAINAGE SYSTEM AND WAS SUBSEQUENTLY DISCHARGED INTO THE GRAND RIVER. ON OUR SCHEDULED SURVEILLANCE THE DISCHARGE WAS DISCOVERED, BOOMS ( 2 HARD AND 3 ABSORBANT) WERE PUT ACROSS THE RIVER, AND THE EXCAPING OIL (APPX. 25 GALLONS) WAS CONTAINED WITHIN 1000FT. OF OUR OUTFALL AND SUBSEQUENTLY RECOVERED.
2017-09-29 08:50 | YES | NO | 19880089 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-03-20 | 1015 | MO | DE KALB |  | NO |  | NO | NW 1/4, SW1/4, SECTION 13, T57N, R31W DEKALB COUNTY, MISSOURI. OSBORN PUMP STATION. |  | PUMPING STATION | PUMP |  | 0 | OTHER | ROTATE ELEM.OF PUMP SEIZE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 35870.5901 | 72365.469 | GASOLINE | 3 | 0 | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD JANZEN , VICE PRESIDENT - OPERATIONS | 9185884850 | THE ROTATING ELEMENT OF THE #4 PUMP UNIT AT OSBORN SEIZED DUE TO A WEAR RING PROBLEM. THE HEAT WHICH RESULTED, OVERHEATED THE MECHANICAL SEAL, AND CAUSED THE SEALMATERIAL TO FAIL. GASOLINE VAPORS THEN ESCAPED THROUGH THE SEAL AND IGNITED. THE FIRE WAS EXTINGUISHED BY WILLIAMS PIPE LINE PERSONNEL, WITH NO EVIDENCE OF LIQUID PRODUCT HAVING LEAKED FROM THE PUMPING UNIT. REPAIRS TO THE PUMP ARE IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19880090 |  | 13131 | CONOCO INC | YES | 1988-03-15 | 1015 | WY | BIG HORN |  | NO |  | NO | T56N, R97W, SECTION 14, 200 YARDS SOUTH OF MILE POST 2. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17935.2951 | 36182.7345 | CRUDE OIL | 1 | 351 | 170 | NO | NO | 8 | 0.16 | 52000 | WELDED |  | 1460 | 820 | YES | 0 | 0 | 0 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS | NO | NO | L. G. HILL, DIRECTOR, ENVIRONMENTAL AFFAIRS | 7132932032 | APPROXIMATELY ONE WEEK PRIOR TO THE INCIDENT, PACIFIC POWER AND LIGHT DRILLED AHOLE WITH AN AUGER DIRECTLY OVER CONOCO PIPE LINE COMPANY'S BYRON-FRANNIE 8-INCHPIPELINE WHILE ATTEMPTING TO INSTALL AN ELECTRIC POWER POLE. THE AUGER STRUCK THE PIPELINE, WHICH WAS NOT IN OPERATON AT THE TIME. CONOCO PIPE LINE COMPANY WAS NOT NOTIFIED OF THE INCIDENT AND THE DAMAGED PIPELINE WAS COVERED UP BY THE POWER COMPANY.AT 7:09 A.M. ON MARCH 15, 1988, PLATTE PIPE LINE COMPANY BEGAN PUMPING CRUDE OIL OT FRANNIE FROM BYRON VIA THE 8-INCH PIPELINE.THE PIPELINE RUPTURED AT 10:15 A.M. AND WAS SHUT DOWN DUE TO LOW DISCHARGE PRESSURE. THE LEAK SITE WAS DISCOVERED AT 1:35 P.M. BY A LINE FLYER SENT OUT BY CONOCO PIPE LINE. APPROXIMATELY 351 BBLS OF OREGON BASIN ASPHALT CRUDE WERE SPILLED IN A 2- ACRE SWAMPY PASTURE AREA. APPROXIMATELY 170 BBLS OF THE OIL WRE RECOVEA 12-FOOT SECTION OF THE PIPELINE WAS REMOVED AND REPLACED WITH A PRETESTED SECTION OF .219 WALL, X-52, FUSION BONDED EPOXY COATED LINE PIPE ONMARCH 16, 1988. AN ON-SITE INSPECTION OF THE LEAK SITE WAS CONDUCTED BY THE WYOMNG DEPARTMENT OFENVIRONMENTAL QUALITY. APPROVAL WAS OBTAINED FOR THE CLEANUP EFFORTS WHICH INCLUDED BURNING OF THE AREA AND REMOVING THE TOP LAYER OF SOIL FOR DISPOSAL.
2017-09-29 08:50 | NO | NO | 19880091 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1988-04-15 | 1640 | MN | PENNINGTON |  | NO |  | NO | NE1/4 SECTIO 13, TOWNSHIP 153 NORTH RANGE 44 WEST, PENNINGTON COUNTY, MINNESOTA. APPROXIMATELY 1700FEET UPSTREAM (NORTH) OF COUNTY ROAD 16. |  | LINE PIPE | GIRTH |  | 1967 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 17500 | 15693.3832 | 31659.8927 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 605 | 300 | YES | 8 | 756 | 8 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. E. STAUDOHAR | 7153925631 | THE FARMER WORKING HIS FIELD NOTED AN ODOR OF OIL AND CALLED OPERATOR. AN INVESTIGATION DISCOVERED A 3/8" LONG DEFECT AT THE UPSTREAM EDGE OF THE CIRCUMFERENTIAL BUTT WELD. A 30" X 34" PLIDCO REPAIRE SLEEVE WAS INSTALLED AND WELDED OVER THE DEFECT.
2017-09-29 08:50 | YES | NO | 19880092 |  | 809 | ARCO PIPE LINE CO | YES | 1988-04-17 | 630 | MO | JACKSON | KANSAS CITY | NO |  | NO | NE 1/4 SEC. 22 - T48N-R32W, JACKSON COUNTY, MISSOURI. IN THE MEDIAN OF MISSOURI STATE HIWAY 350 APPROXIMATELY 1/2 MILE WEST OF NOLAND ROAD (ROUTE V). |  | LINE PIPE | NO DATA |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 8100 | 7263.7945 | 14654.0075 | FUEL OIL | 3 | 103 | 74 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 600 | 137 | YES | 0 | 1000 | 0 | 48 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | N. R. BENNETT - MANAGER NORTHERN AREA OPERATIONS | 3163311300 | EXTERNAL GALVANIC CORROSION LEAK.
2017-09-29 08:50 | YES | NO | 19880093 |  | 12127 | MARATHON PIPE LINE CO | YES | 1988-04-08 | 830 | IN | CLAY |  | NO |  | NO | SECTION 15, T12N R7W, CLAY COUNTY, POSEY TWP., INDIANA. |  | LINE PIPE | NO DATA |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 96560 | 86591.6046 | 174690.2422 | OIL AND GASOLINE | 3 |  | 1091 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1000 | 450 | YES | 24 | 1250 | 9 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H. E. MILLER, VICE PRESIDENT | 4194223009 | ON FRIDAY, APRIL 8, 1988, MARATHON PIPE LINE COMPANY EASTERN DIVISION WAS NOTIFIED BY THEIR OPERATIONS CENTER OF THE POSSIBLITY OF A LEAK ON SATURDAY, APRIL 9,1988. THE LINE WAS SHUT DOWN, REPAIRS WERE MADE, AND CLEANUP WAS INITIATED. REPLACEMENT OF DAMAGED PIPE WITH A NEW SECTION OF PIPE WAS COMPLETED ON APRIL 25,1988. DUE TO THE SIZE OF THE LEAK, IT IS IMPOSSIBLE TO DETERMINE THE EXACT AMOUNT OF REFINED PETROLEUM PRODUCTS INVOLVED IN THIS ACCIDENT. CLEANUP ACTIVITIES ARE STILL IN PROGRESS. TO DATE, 1091 BBLS. OF PRODUCT HAVE BEEN RECOVERED USINGVACUUM TRUCKS.
2017-09-29 08:50 | YES | NO | 19880094 |  | 2371 | CINIZA PIPELINE INC | YES | 1988-04-13 | 1145 | NM | MCKINLEY | BORREGO PASS | NO |  | NO | NW 1/4, NW1/4 SECTION 4 TOWNSHIP 15N RANGE 11W ONE MILE NORTH OF BORREGO PASS TRADING POST. |  | LINE PIPE | PIPE |  | 1973 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 11546 | 10354.0458 | 20888.2926 | CRUDE OIL | 1 | 434 | 50 | NO | NO | 6 | 0.19 | 2210 | NO DATA |  | 1400 | 550 | YES | 24 | 1760 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE MARKERS | NO | NO | ROBERT ULLO, GENERAL MANAGER OF PIPELINE OPERATIONS | 5056328006 | THE BUREAU OF INDIAN AFFAIRS ROAD DEPARTMENT WAS GRADING A ROAD NEAR BORREGO PASS WHEN THE BLADE HIT THE HOSPAH 6" PIPELINE AND PUNCHED A HOLE IN IT NEAR MILE POST 20.
2017-09-29 08:50 | YES | NO | 19880095 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1988-04-02 | 1230 | CO | CROWLEY |  | NO |  | NO | MCCULLOCH-BORGER-MP 243-10+23. FROM ORDWAY, CO, 16.5.5 MILES NORTH ON HWY. 71,2 MILES WEST ON DIRT,3 MILES NORTH ON DIRT. |  | LINE PIPE | LONGITUDINAL WELD |  | 1951 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 18310 | 16419.7626 | 33125.2934 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 7 | 0.19 | 42000 | WELDED |  | 1440 | 860 | YES | 8 | 1825 | 10 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B. L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICE | 9186614721 | FOLLOWING NOTIFICATION BY LANDOWNER OF YELLOW LIQUID BUBBLING IN THE SNOW NEAR AN 8" VALVE AT MP 243, THE LINE WAS SHUT DWON AND BLOCKED IN AT MP 2390 AND 254. THE AUSE OF THE LEAK WAS A VERY SMALL PINHOLE LEAK IN THE SEAM.
2017-09-29 08:50 | YES | NO | 19880096 |  | 19335 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1988-04-08 | 1045 | TX | DAWSON |  | NO |  | NO | SECTION 103, BLOCK 3, D.L. CUNNINGHAM SURVEY. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10300 | 9236.677 | 18634.1083 | CRUDE OIL | 1 | 150 | 25 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 800 | 20 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | CO. LINE MARKERS | NO | NO | EDWIN H. GRIPP, DISTRICT MANAGER | 9159497019 | AT APPROXIMATELY 10:30 A.M. ON APRIL 8, 1988, A DAWSON COUNTY ROADGRADER STRUCKOUR 10" SUNDOWN-MIDLAND MAIN LINE APPROXIMATELY 1 1/2 MILES NORTH OF SANDS STATION. THE LEAK WAS REPORTED TO TEXAS-NEW MEXICO PIPE LINE COMPANY BY HE GRADER OPERATOR, VERNON FLENNIKAN, AT 10:45 A.M. COMPANY PERSONNEL ARRIVED AT TEH SITE AT 11:00 A.M. WITH CREW AND BACKHOE. VACUUM TRUCKS ARRIVED AT 11:30 A.M. THE LEAKWAS SUCCESSFULLY CLAMPED OFF AT 11:45 A.M. OIL WAS CONTAINED IN A DITCH ALONG THE ROADWAY AND RECOVERY OF OIL WASCOMPLETED AT 5:00 P.M. TEMPORARY REPAIRS WERE COMPLETED ON APRIL 9, 1988, BY INSTALLING 2' OF 10" HALF WRAP. PERMANENT REPAIRS TO BE MADE AT A LATER DATE.
2017-09-29 08:50 | YES | NO | 19880097 |  | 4495 | ENTERPRISE PIPELINE CO | YES | 1988-03-11 | 1805 | TX | ORANGE | ORANGE | NO |  | NO | HIGHWAY #1006 2.8 MILES EAST OFS INTERSECTION WITH HIGHWAY #87 ORANGE, TEXAS. |  | PUMPING STATION | NO DATA |  | 1984 | OTHER | TANDEM PUMP SEAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8967.6475 | 18091.3673 | NATURAL GAS LIQUID | 2 | 3 | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DANALD R. SCOTT , PIPELINE SUPERINTENDENT | 3184777640 | TANDEM PUMP SEAL FAILED CAUSING FIRE.
2017-09-29 08:50 | YES | YES | 19880098 |  | 1996 | CABOT GAS PROCESSING CORP | NO | 1988-05-06 | 830 | TX |  |  | NO |  | NO |  |  | NO DATA | SCRAPER TRAP | PIG RECEIVER WAS OPEN. | 1981 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 2 | 1 | 1 | 30000 | 26902.9426 | 54274.1018 | NATURAL GAS LIQUID | 2 | 0 | 0 | YES | NO | 4 | 0.19 | 2924 | WELDED |  | 1754 | 11 | YES | 24 | 1478 | 1 | 81 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVE BUSTOS NDT EXMINER | 8063736042 | A CONTRACTED VACUUM TRTUCK WAS PULLING LIQUID DRAINED INTO HALF DRUM FROM LINE 1729-100 AT THE PIG RECEIVER. THIS LINE WAS OUT OF SERVICE AND THE LINE PRESSURE AT THIS LOCATION WAS II PSIG. LIQUID VAPORS WERE PRESENT, SOURCE OF IGNITION IS UNKNOWN AT THIS TIME.THIS WAS NOT A PIPELINE FAILURE IT WAS A FLASH FIRE AT THE PIG RECEIVER.
2017-09-29 08:50 | YES | NO | 19880099 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-05-19 | 1500 | NM | LEA | JAL | NO |  | NO | SE 1/4, NE 1/4, SECTION 26, T-23-S, R-36-E, 9.75 MILES NORTH OF JAL LEA-WINK 8-INCH. |  | LINE PIPE | PIPE |  | 1936 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 1165.7942 | 2351.8777 | CRUDE OIL | 1 | 200 | 150 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 600 | 540 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19880100 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-05-01 | 1100 | NM | LEA | JAL | NO |  | NO | SW 1/4, NW1/4, SECTION 9, T-24-S, R-37-E, 9.25 MILES NORTH OF JAL HOBBS-HENDRICK 10-INCH. |  | LINE PIPE | PIPE |  | 1935 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1950 | 1748.6913 | 3527.8166 | CRUDE OIL | 1 | 155 | 105 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 900 | 450 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19880101 |  | 10012 | KANEB PIPELINE CO | YES | 1988-04-26 | 1500 | IA | DICKINSON |  | NO |  | NO | TANK FARM FACILITY OWNED AND OPERATED BY KANEB PIPE LINE CO. |  | TANK FARM | TANK |  | 1967 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 156933.8319 | 316598.927 | GASOLINE | 3 | 536 | 44 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARK BROWN, V.P. - ENG. & OPERATOR | 3162621408 | EMPLOYEE MISCALCULATED FLOW RATE WHEN TRANSFERRING GASOLINE BETWEEN TANKS WHICHRESULTED IN THE TANK OVERFILL CREATING THE SPILL WHICH RESULTED IN THE LOST PRODUCT.
2017-09-29 08:50 | YES | NO | 19880102 |  | 18718 | SUN PIPELINE CO | Null | 1988-04-15 | 2300 | AR | CRITTENDEN | WEST MEMPHIS | NO |  | NO | TANK FARM, DIKE 107 & 805, SUN PIPE LINE TERMINAL, WEST MEMPHIS, ARKANSAS. |  | TANK FARM | TANK |  | 0 | OTHER | HIGH LEVEL SHUT DOWN SWIT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | JET FUEL | 1 | 700 | 370 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RACHMAN | 5017351610 | TRANSFER THE A FROM STOWAGIE TANK TO TARANSFER TANK AND A HIGH LEVEL SHUT SWITCHFAILED.
2017-09-29 08:50 | YES | NO | 19880103 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1988-05-03 | 1300 | MO | ST LOUIS |  | NO |  | NO | BORGER-E CHICAGO "BLUE" LINE - MP 655-40+00 APPROXIMATELY 1000' WEST OF THE MERAMEC RIVER AT TIMES BEACH AND APPROXIMATELY 1/8 MILE SOUTH OF I-44. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 22419.1188 | 45228.4181 | L. P. G. | 2 | 2179 | 0 | NO | NO | 9 | 0.19 | 40000 | WELDED |  | 1080 | 240 | YES | 24 | 1410 | 6 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | B. L. THORMAN, MANAGER FO ENGINEERING & TECHNICAL SERVICES | 9186614721 | THE FARMER (TENANT) WAS PLOWING HIS FIELD WHEN HE HIT THE LINE WITH THE PLOW AROUND 1:00 P.M. THE EUREKA FIRE DEPARTMENT WAS CALLED IMMEDIATELY, AND THEIR DESPATCHER NOTIFIED THE BARTLESVILLE PIPELINE CONTROLLER. THE LINE HAD BEEN DOWN THAT THE TIME OF THE ACCIDENT AND THE REMOTE OPERATED VALVES HAD BEEN BLOCKED. THE NEAREST BLOCK VALVES WERE THEN CLOSED BY THE MAINTENANCE CREW AROUND 2:30 P.M., AND THE PRESSURE WAS OFF THE LINE BY APPROXIMATELY 4:30 P.M. THE LINE WAS REPAIRED BY 1:00 PM. THE NEXT DAY.
2017-09-29 08:50 | YES | NO | 19880104 |  | 2386 | OXY CITIES SERVICE NGL INC | YES | 1988-05-16 | 1500 | OK | KAY |  | YES | SEC. 19, TOWNSHIP 28N. | NO | APPROXIMATELY 1 MILE EAST OF HIGHWAY I35 IN A WHEAT FIELD JUST NORTH OF THE CHICKASKIA RIVER. |  | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 15245.0008 | 30755.3243 | L. P. G. | 2 | 588 | 0 | NO | NO | 4 | 0.24 | 3687 | WELDED |  | 960 | 900 | YES | 24 | 1487 | 12 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | WILLIAM C. BOYER - PLANT MANAGER - HUTCHINSON | 3166626691 | THE AMBROSE PLANT CHIEF OPERATOR ON DUTY, JIM LIVELY, NOTED THE 4" HUTCHINSON PIPELINE PRESSURE DROPPED SUDDENLY FROM 900 PSIG TO ABOUT 450 PSIG. MR. LIVELY INFORMED THE ACTING FIELD SUPT., MR. LENNIE DEBOARD, THAT HE HAD LOST PRESSURE ON THE 4" HUTCHINSON LINE AND HAD SHUT DOWN HIS PIPELINE PUMP. LIVELY THEN CALLED THE ASSISTANT OPERATOR, MR. DARRELL SCOTT, TO LOOK OVER THE PIPING AND VALVES ATTHE PUMP AREA AND CLOSE THE BLOCK VALVES AT THE PUMPS.
2017-09-29 08:50 | YES | NO | 19880105 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-05-16 | 1700 | TX | MARTIN |  | NO |  | NO | SEC. 3, BLOCK 39 T-2-N G& MMB A SURVEY: MILE POLE 67.9 SNYDER-WINK 10" CRUDE LINE: ON MABEE RANCH 1.5 MILES WEST OF HWY (FAP) 349 AND 6.5 MILES S. OF HWY (FAS) |  | LINE PIPE | PIPE |  | 1984 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 269.0294 | 542.741 | CRUDE OIL | 1 | 795 | 720 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1205 | 1170 | YES | 8 | 1483 | 4 | 81 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R. C. KINNEAR, DIVISION MANAGER | 9156877551 | RANCHER WHILE GRADING ROAD AND CLEARING BAR DITCH STRUCK PIPE LINE WITH MAINTAINER. LINE MARKERS LOCATED 10 FT. AND 350 FT. FROM INCIDENT LOCATION.
2017-09-29 08:50 | YES | NO | 19880106 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-05-25 | 1015 | TX | WARD |  | NO |  | NO | 3 MILES S. OF WICKET, TX. OFF WHY 1219 SECTION 3 BLOCK 16 UNIVERSITY SURVEY. |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 10 | 0 | NO | NO | 5 | 0.16 | 35000 | WELDED |  | 600 | 600 | YES | 8 | 1800 | 0 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. C. KINNEAR, DIVISION MANAGER | 9156877551 | LEAK WAS DISCOVERED BY SAM WELCH CABET ESTES PLANT EMPLOYEE.EFFECTED SECTION OF LINE WAS BLEED OFF, AND REPLACED 78 FEET OF 4 1/2" PIPE.
2017-09-29 08:50 | YES | NO | 19880107 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-06-04 | 1000 | TX | WARD | MONAHANS | NO |  | NO | MONAHANS PUMP STATION 1/2 MILE WEST OF TX HIGHWAY 18, SEC. 78,BLK A, G&MMB&A SURVEY. |  | TANK FARM | OTHER | ROOT DRAIN LINE | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1370 | 240 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. C. KINNEAR, DIVISION MANAGER | 9156877551 | LEAK DUE TO MECHANICAL FAILURE OF ROOF DRAIN LINE. OIL CONTAINER IN TANK BERMEDAREA. INATTENTION (LACK OF IMMEDIATE RESPONSE) BY OPERATOR CONTRIBUTED TO THE AMOUNT OF OIL LOSSED.
2017-09-29 08:50 | YES | NO | 19880108 |  | 13131 | CONOCO INC | YES | 1988-04-14 | 1730 | TX | WICHITA |  | NO |  | NO | T. E. HUBBARD SURVEY, ABSTRACT 325. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3587.059 | 7236.5469 | CRUDE OIL | 1 | 400 | 300 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | L. G. HUBBARD, DIRECTOR, ENVIROMENTAL AFFAIRS | 7132932032 | AT APPROXIMATELY 17:30 HOURS A FARMER, USING A CHISEL, STRUCK CONOCO PIPE LINE COMPANY'S LINE. SOMETIME BETWEEN 17:30 HRS. AND 18:30 HRS. THE FARMER CONTACTED THE TEXAS RAILROAD COMMISSION. AT 18:20 HRS. THE TEXAS RAILROAD COMMISSION CONTACTED CONOCO PIPE LINE COMPANY ABOUT THE PIPELINE LEAK. CONOCO EMPLOYEES ARRIVED ON SITE AT 18:30 HRS. EMPLOYEES WERE DISPATECHED TO SHUT DOWN INJECTIONS AN REPAIR CONTRACTORS WERE ON SITE TO BEGIN CONTAINMENT AT 19:30 HRS. THE LINE WAS CLOSED IN AT 20:00 HRS. PIPELINE WAS CLAMPED OFF AT 20:15 HRS. THE OIL WAS CONTAINED AND PICKED UP WITH TRANSPORT TRUCKS. THE PIPELINE WAS REPLACED AD LOWERED APRIL 15, 1988.
2017-09-29 08:50 | NO | NO | 19880109 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1988-05-23 | 1225 | MI | MACKINAC |  | NO |  | NO | APPROXIMATELY 3 MILES EAST OF GOULD CITY, MICHIGAN AND 1/2 MILE NORTH OF U.S. HIGHWAY NO. 2. |  | LINE PIPE | LONGITUDINAL WELD |  | 1953 | OTHER | WEEPER IN LONG. SEAM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 26000 | 23315.8836 | 47037.5549 | CRUDE OIL | 1 | 40 | 35 | NO | NO | 30 | 0.34 | 52000 | WELDED |  | 613 | 543 | YES | 4 | 853 | 11 | 64 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. E. STAUDOHAR | 7153925631 | A 3/4" CRACK WAS FOUND IN A LONGITUDINAL SEAM OF THE OPERATORS 30" O.D. PIPELINE. IT APPEARS THE AREA HAD BEEN REPAIRED (WELDED OVER) DURING CONSTRUCTION. A PLIDCO SLEEVE WAS WELDED OVER THE CRACK.
2017-09-29 08:50 | YES | NO | 19880110 |  | 19226 | TEXACO PIPELINE INC | NO | 1988-03-30 | 1555 | TX | ELLIS | MAYPEARL | NO |  | NO | NEAR AN UNNUMBERER COUNTY ROAD, BETWEEN MAYPEARL AND WAXAHACHIE, 1 MILE NORTH OF COUNTY ROAD 1446, ELLIS COUNTY , TEXAS. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 8830 | 7918.4328 | 15974.6773 | GASOLINE | 3 | 474 | 193 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1170 | 300 | YES | 24 | 1000 | 0 | 48 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | P. NOTIFICATION SIGN | YES | YES | R. D. GUIDRY - ASST. DISTRICT MANAGER | 7139534262
2017-09-29 08:50 | NO | NO | 19880111 |  | 443 | AMOCO PIPELINE CO | NO | 1988-04-09 | 1505 | TX |  |  | YES | LOG 28-5-14 LAT 93-54-53 | YES | LOCATION IS @ A340 -PENNZOIL HIGH ISLAND (OFFSHORE) LONGITUDE 28-05-14. LATITUDE 93-54-53. |  | NO DATA | VALVE |  | 1978 | OTHER | BROKEN GLAND BOLT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | HOWARD B. SPALDING- SUPERVISOR-OPERATIONS | 4099483407 | SLICK WAS REPORTED BY A-340 PERSONNEL @ 15:05 4/9/88. @ 16"32 OUR HELICOPTER WAS OVER SITE REPORTING BLOSSOMS AT ONE (1) PER SECOND. A-340 PLATFORM PRESSURE WS1645 PSI. SEGMENT III PRESSURE WAS 1330 PSI AN FLOW RATE @ TCY WAS 3400 BHP. A-340 WAS NOT PUMPING AT THIS TIME. AT 12:34 ON 4/10/88 CAL - DIVE'S BOAT WAS ONLOCATIN, AND DIVER DOWN. CONFIRMED CHECK VALVE STEM GALND "O" RING WAS LEAKING.
2017-09-29 08:50 | YES | NO | 19880112 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-04-19 | 800 | ND | FARGO |  | NO |  | NO | FARGO TERMINAL #218. |  | TANK FARM | VALVE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 192 | 192 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD E. JANZEN | 9185884850 | ON APRIL 19TH, OPERATING PERSONNEL AT OUR FARGO TERMINAL DISCOVERED THAT GASOLINE HAD ENTERED THE FACILITY WATER RETENTION POND, WHICH IS FED FROM THE OIL/WATER SEPARATOR SYSTEM. A 1/2 INCH DRAIN VALVE IN THE PUMP CHANGE ROOM HAD BEEN OPENED TO DRAIN A LINE FOLLOWING THE PREVIOUS PUMP OPERATION.WHEN THE NEW PUMP OPERATION WAS LINED UP, THIS DRAIN VALVE (LOCATED IN A RELATIVELY OBSCURE POSITION) WAS INADVERTENTLY LEFT OPEN. PRODUCT CONSEQUENTLY DRAINED INTO THE SUMP SYSTEM, OVERLOADED THE SEPARATOR, THEN GRAVITATED INTO THE WATERACCUMULATOR HERE IT WAS AUTOMATICALLY PUMPED INTO THE RETENTION POND. ALL PRODUCT WAS CONTAINED IN THE POND AND WAS COMPLETELY RECOVERED.
2017-09-29 08:50 | NO | NO | 19880113 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-04-11 | 1700 | OK | OKLAHOMA |  | NO |  | NO | SW1/4, SE1/4 SECTION 29 T12N R2W (EAST OF SOONER ROAD, NORTH OF NE 10TH STREET). |  | LINE PIPE | PIPE |  | 1986 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8967.6475 | 18091.3673 | FUEL OIL | 3 | 2 | 1 | NO | NO | 8 | 0.19 | 42 | WELDED |  | 275 | 0 | YES | 8 | 500 | 12 | 86 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H. E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | ON APRIL 11, 1988 WPL PERSONNEL WERE NOTIFIED OF A SUSPECTED LEAK ON THE 8" SPUR LINE BETWEEN OUR SOONER ROAD FACILITY AND THE TEXACO TERMINAL IN OKLAHOMA CITY. THE LINE WAS ISOLATED AND THE SUBSEQUENT LOSS IN PRESSURE CONFIRMED THE PRESENCE OF A LEAK. EXCAVATION AT THE LEAK SITE REVEALED A SINGLE EXTERNAL CORROSIONPIT NEAR THE BOTTOM SIDE OF THE PIPE. PIPE-TO-SOIL READINGS TAKEN NEAR THE SITE INDICATED POTENTIALS OF AT LEAST - 1.0 VOLTS, HOWEVER, THERE WAS SOME EVIDENCEOF DISBONDED COATING. THE FAILED JOINT OF PIPE WAS REMOVED FOR FULL METALLURGICAL ANALYSIS. FURTHER IVESTIGATION IS STILL IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19880114 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-05-11 | 1605 | NE | LANCASTER |  | NO |  | NO | SE1/4, NE1/4, SECTION 28, T10N, R6E. |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13451.4713 | 27137.0509 | FUEL OIL | 3 | 50 | 3 | NO | NO | 6 | 0.22 |  | WELDED |  | 1200 | 50 | YES | 8 | 1500 | 0 | 71 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD E. JANZEN, VICE PRESIDENT, OPERATIONS | 9185884850 | ON MAY 11, 1988 A LEAK WAS DISCOVERED ON OUR 6" BURLINGTON NORTHERN (BN) DILIVERY PIPELINE BY A BN EMPLOYEE AN REPORTED TO OUR DISPATCHING CENTER IN TULSA. THE LINE WAS IDLE AT THE TIME OF THE DISCOVERY. MAINTENANCE CREWS WERE DISPATCHEDTO REPAIR THE LEAK AND INITIATE CLEAN -UP PROCEDURES. EXTERNAL CORROSION WAS DETERMINED AS THE CAUSE OF THE LEAK. SUBSEQUENT INVESTIGATION ALSO INDICATED THE PIPE COATING HAD BEEN DAMAGED AND THAT HAS BEEN REPAIRED AND THE INTERFERENCE ELIMINATED.
2017-09-29 08:50 | YES | NO | 19880115 |  | 443 | AMOCO PIPELINE CO | YES | 1988-04-09 | 2132 | IL | PEORIA | EDELSTEIN | NO |  | NO | WEST SIDE OF TIMBER LAKE ROAD ABOUT 500 FEET NORTH OF LAKE SHORE DRIVE IN WOODLAND HEIGHTS SUBDIVISION. SE 1/4 SECTION 21 T11N R8E. |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1345147.1305 | 2713705.0886 | CRUDE OIL | 1 | 5000 | 4975 | NO | NO | 20 | 0.34 | 25200 | WELDED |  | 867 | 800 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | JOHN W. CARICO | 8154784007 | PIPELINE RUPTURED AT THE 1-2 O'CLOCK POSITION RESULTING IN A CONGITUDINAL OPENING, 18" LONG AND 4" WIDE AT THE WIDES PART AT A DRAINAGE DITCH ALONGSIDE A RESIDENTIAL STREEET. LINE SHUTDOWN PROCEDURES WERE COMMENCED WITHIN 1 MINUTES AND BLOCK VALVES WERE CLOSED WITHIN ONE HOUR. ESCAPING OIL SPRAYED TWO HOMES, SEVERALLAWNS AND NUMEROUS TREES. THE MATERIAL FLOWED THROUGH DRAINAGE AND CREEKS TO TWO LAKES WHERE IT WAS CONTAINED AND COLLECTED. AREA RESIDENTS WERE IMPACTED BY ABJECTIONAL VAPORS. PIPELINE REPAIRE WAS COMPLETED ON APRIL 13, 1988, BY INSTALLATION OF A PIECE OF .375 WALL 5LX42 PIPE BETWEEN WELD PLUS ENDS. CLEAN-UP EFFORTS CONTINUE.PART D - CAUSE OF ACCIDENT : FAILURE OF THE 20 IN. CRUDE OIL LINE NEAR CHILLICOTHE, IL. WAS THE RESULT OF SEVERE MECHANICAL DAMAGE. EXTERNAL GOUGING OF THE PIPEAT SOME PREVIOUS TIME INITIATED CRACKS IN THE PIPE BODY WHICH PROPAGATED PART WAY THROUGH THE WALL BY A FATIGUE MECHANISM DURING SERVICE. FAILURE OCCURED WHEN THE REMAINING WALL THICKNESS COULD NO LONGER SUPPORT THE PRESSURE STRESS. NO EVIDDENCE OF OTHER PIPE DEGRADATION MECHANISMS, SUCH AS CORROSION, HYDROGEN CRACKING, OR STRESS CORROSION CRACKING, WERE FOUND. THE MECHANICAL PROPERTIES OF THE FAILED PIPE EXCEEDED THE REQUIREMENTS OF API 5L GRADE B.
2017-09-29 08:50 | YES | NO | 19880116 |  | 443 | AMOCO PIPELINE CO | YES | 1988-05-27 | 1030 | TX | ANDREWS |  | NO |  | NO | SE 1/4, SEC 16, BLOCK A-48, ANDREWS COUNTY , TX. |  | NO DATA | OTHER | CHECK VALVES FAILED | 1946 | OTHER | CHECK VALVES FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 313.8677 | 633.1979 | CRUDE OIL | 1 | 50 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES L. HORNER | 5053962817 | * CHECK VALVES FAILED WITH TANK ON LINE, LETTING TANK BACKOVER. REPLACED 1-2"SCREW CHECK VALVE & 1 3" ASA150 CHECK VALVE.
2017-09-29 08:50 | YES | NO | 19880117 |  | 443 | AMOCO PIPELINE CO | YES | 1987-06-11 | 100 | MI | ST JOSEPH | CONSTANTINE | NO |  | NO | 63636 CONSTANTINE ROAD CONSTANTINE, MICHIGAN FLORENCE TOWNSHIP, ST. JOSEPH COUNTY, MICHIGAN. |  | LINE PIPE | BOLTED FITTING |  | 1953 | OTHER | LEAK AT FLANGE ON MAINLIN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4628.2933 | 9337.1371 | GASOLINE | 3 | 24000 | 600 | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 900 | 900 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. A. STAHL - AREA MANAGER | 2197382384 | IN JUNE OF 1987, A LOCAL LANDOWNER COMPLAINED OF A DEAD OAK TREE AND SOME STUNTED CROPS. UPON INVESTIGATION, IT WAS IDSCOVERED THAT A MAINLINE BLOCK VALVE FLANGE WAS LEAKING. BASED ON THE AREA OF STUNTED CROPS, IT WAS DECIDED TAT AN INVESTIGATION WAS WARRANTED. A SERIES OF OBSERVATION WELLS REVEALED A CONSIDERABLE VOLUME OF PRODUCT ON THE WATER TABLE. FROM THAT POINT TO PRESENT, WE HAVE BEEN WOEKING WITH THE MICHIGAN DEPARTMENT OF NATURAL RESOURCES TO RECOVER THE PRODUCT AND REMEDIATE THE SITE.
2017-09-29 08:50 | YES | NO | 19880118 |  | 443 | AMOCO PIPELINE CO | YES | 1988-04-12 | 1930 | MO | ST CHARLES | ORCHARD FARM | NO |  | NO | SE 1/4, SECTION 32, TOWNSHIP 48 NORTH, RANGE 5 EAST, IN ST. CHARLES COUNTY MISSOURI NEAR ORCHARD FARM, MO. |  | LINE PIPE | WELDING FITTING |  | 1940 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 59 | 10 | NO | NO | 12 | 0.28 | 1111 | WELDED |  | 720 | 564 | YES | 4 | 900 | 0 | 82 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | MITCHELL B. WEISS, AREA MANAGER | 8169685387 | A 1 1/2- INCH, CAPPED AIR VENT PROJECTING 8-9 INCHES ABOVE A 12-INCH PIPELINE WAS STRUCK BY MR. HERBERT BOERDING WHILE PLOWING HIS FIELD. THOUGH THE PIPELINE WAS ADEQUATELY BELOW NORMAL PLOW DEPTH, THE UPWARD PROJECTING FITTING WAS STRUCKAND DAMAGE BY MR. BOERDING'S PLOW CAUSING PRODUCT TO BE RELEASED THROUGH A HARILINE CRACK IN THE CIRCUMFERENCE OF THE BRANCH WELD. MUCH OF THE PRODUCT WAS VAPORIZED AS IT PASSED UNDER PRESSURE THROUGHT THE NARROW CRACK. THE MOST HEAFILY SATURATED SOIL WAS MOVED TO A STATE APPROVED LANDFILL FOR FURTHER TREATMENT. THE BALANCE OF THE EFFECTED SOIL IS BEING AERATED TO PERMIT RELEASE OF ANY RESIDUAL HYDROCARBON VAPORS. FOUR DOMESTIC WATER WELLS IN THE GENERAL VICINITY ARE BEING TESTED ON A FRGULAR BASIS. SEEN GROUND WATER OBSEVATI0ON WELLS HAE BEEN DRILLED AND AN ENVIRONMENTAL CONSULTANT HAS BEEN ENGAGED TO OVERSEE THE MONITORING AND REMEDIATION EFFORTS.
2017-09-29 08:50 | YES | NO | 19880119 |  | 809 | ARCO PIPE LINE CO | NO | 1988-06-15 | 1000 | TX | GUADALUPE |  | NO |  | NO | IN A FIELD ALONG HIGHWAY 775 APPROX. ONE MILE SOUTH OF INTERSTATE HIGHWAY 10 IN GUADALUPE COUNTY TEXAS. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6520 | 5846.9062 | 11795.5715 | GASOLINE | 3 | 303 | 27 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 600 | 80 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | V.P. DRISKI, OPERATIONS MANAGER-SOUTHERN AREA | 3163311300 | MAINTAINER WORKING FOR TENANT HIT PIPELINE WHILE MAKING TERRACES IN FIELD.
2017-09-29 08:50 | YES | NO | 19880120 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1988-06-16 | 1450 | MI | MACOMB |  | NO |  | NO | SECTION 13, T5N, R12 E ADJACENT TO BROWN ROAD, APPROXIMATELY FOUR MILES NORTH OF ROMEO, MICHIGAN. |  | LINE PIPE | PIPE |  | 1976 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 3200000 | 2869647.2118 | 5789237.5224 | CRUDE OIL | 1 | 8800 | 7300 | YES | NO | 30 | 0.25 | 52000 | WELDED |  | 682 | 200 | YES | 24 | 869 | 6 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.E. STAUDOHAR | 7153925631 | A CROSSOVER BETWEEN THE OPERATORS 30" PIPELINE AND A 30" PARALLEL LOOP RUPTUREDAPPARENTLY AS A RESULT OF THE THERMAL EXPANSION OF THE IDLE 30" LOOP. A CLOSEDVALVE ON THE MAIN LINE SIDE OF THE CORSSOVER PREVENTED THE ESCAPE OF OIL FROM THE MAIN LINE ( THE MAIN LINE WAS ACTUALLY SHUT DOWN AT THE TIME OF THE INCIDENT FOR AN UPSTREAM DILIVERY.) THE OIL REACHED THE NORHT BRANCH OF THE CLINTON RIVERAND TRAVELED APPROXIMATELY 3 RIVER MILES BEFORE IT WAS FULLY CONTAINED. A FIRESTARTED WHEN EXCAVATING EQUIPMENT SRUCK A ROCK CAUSING A SPARK.
2017-09-29 08:50 | YES | NO | 19880121 |  | 4906 | EXXON PIPELINE CO | NO | 1988-06-06 | 1200 | LA | PLAQUEMINES |  | NO |  | NO | LEAK OCCURRED AT STATIN NO. 313+00 ON THE LAKE WASH. TO MANILA JCT. 12" PIPELINE. THIS POINT IS APPR. 10 MILES NE OF GRAND ISLE, LA. |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 165300 | 148235.2138 | 299050.3008 | CRUDE OIL | 1 | 12 | 10 | NO | NO | 12 | 0.31 | 52000 | WELDED |  | 1200 | 300 | YES | 12 | 1500 | 12 | 55 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT 1000 HOURS ON 6/6/88, EPC WAS NOTIFIED OF A CRUDE OIL SPILL IN THE VICIITY OF OUR PIPELINE SYSTEM IN BARATARIA BAY OF PLAQUEMINES PARISH, LA. ALL INJECTIONS INTO THIS SYSTE WERE IMMEDIATELY SHUT DOWN AND AN AERIAL SURVEILLANCE INSPECTION OF THE SPILL SITE CONDUCTED. AT 1200 HOURS THE SPILLAGE (12 BBLS.) WAS VERIFIED TO BE ORIGINATING FROM OUR LAKE WASHINGTON-MANILA JCT. 12" PIPELINE. AT 1430 HOURS THE PIPELINE SYSTEM WAS ISOLATED WHEN APPROPRIATE BLOCK VALVES WERE CLOSED. CLEANUP AND REPAIR PERSONNEL AND EQUIPMENT WERE DISPATCHED TO THE SITEAT 1500 HOURS. THE MAJORITY OF THE SPILLAGE HAD DRIFTED WESTERLY AND WAS ULTIMATELYCONTAINED BY BOOMS IN MARSHLAND POT HOLES. APPR. 10 BBLS. WERE RECOVERED. CLEANUP WAS ACCOMPLISHED BY USING SORBENTS AND SKIMMING AND WAS FINALIZED ON 6/21/88. THE DAMAGED PIPELINE WHICH HAD 8' OF WATER AND 2 1/2' OF MUD COVER OVER IT WAS REPAIRED ON 6/8/88 BY CHANGING OUT 42' OF 12" PIPE. DAMAGE COSISTED OF 8 DIAGONAL DENTS IN THE LINE EXTENDING FROM THE 11 TO THE 1 O'CLOCK POSITION AND WAS APPARENTLY CAUSED BY DEEP-DRAFT, MARINE EQUIPMENT STRIKING THE LINE. ONE DENT, SLIGHTLY DEEPER THAN THE OTHERS, PENETRATED THE PIPE ALLOWING THE OIL TO ESCAPE THROUGH A CRACK ABOUT 1/32" WIDE AND 8" LONG.
2017-09-29 08:50 | YES | YES | 19880122 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-06-02 | 1135 | NE | LANCASTER |  | NO |  | NO | LINCOLN TERMINAL #336. |  | TANK FARM | PUMP |  | 1984 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 1 | 1 | 0 | 500 | 448.3824 | 904.5684 | GASOLINE | 3 |  | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | ON JUNE E, 1988 A PORTABLE TRANSFER PUMP CAUGHT FIRE DURING A TANK WATER DRAW OPERATION AT OUR LINCOLN TERMINAL, RESULTING IN BURN INJURIES TO A COMPANY EMPLOYEE. WATER WAS BEING TRANSFERRED FROM THE WATER DRAW TO A TRANSPORT TRUCK VIA ANENGINE DRIVEN PORTABLE CENTRIFIGAL PUMP. SHORTLY AFTER THE PUMP HAD BEEN STOPPED, THE ATTENDING EMPLOYEE ATTEMPTED TO UNSCREW THE PRIMING PLUG FROM THE PUMP CASE. GASOLINE, WHICH HAD UNEXPECTEDLY BEEN SUCKED INTO THE PUMP, SPRAYED OUT THE OPENING AND IGNITED. THE EMPLOYEE SUSTAINED PRIMARILY SECOND DEGREE BURNS. THE HOT ENGINE MUFFLER APPEARS THE MOST LIKELY CAUSE OF THE IGNITION. OTHER PERSONNEL ON THE PROPERTY PUT OUT THE FIRE WITH A PORTABLE WHEELED EXTINGUISHER. APPROPRIATE PRECAUTIONALRY PROCEDURES HAVE BEEN REAFFIRMED TO PREVENT A REOCCURRENCE.
2017-09-29 08:50 | YES | NO | 19880123 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-06-10 | 600 | LA | PLAQUEMINES | BURAS | NO |  | NO | CHEVRON PIPE LINE CO.-EMPIRE/OSTRICA TERMINAL LOCATED ONTEH LEFT DESCENDING BANK OF THE MISSISSIPPI RIVER, RMP 26.7 A.H.P. ACROSS RIVER FROM BURAS, LA. |  | TANK FARM | TANK |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 4035.4414 | 8141.1153 | CRUDE OIL | 1 | 1108 | 1098 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L. DOWNIE, DIVISION MANAGER | 5043642496 | THE RELIEF TERMINAL SUPERVISOR DISCOVERED OSTRICA TANK 2049 OVERFLOWING WHILE MAKING HSI MORNING CHECK. 1108 BBLS. OF CRUDE OIL HAD SPILLED ONTO THE GROUND AND WAS CONTAINED WITHIN THE TANK FIREWALLS. THE SPILL WAS CAUSED BY AUTOMATIC TANK GAUGE (ATG) AND HIGH LEVEL ALARM (HLA) MALFUNCTIONS. BOTH SYSTEMS HAVE BEENREPAIRED AND CALIBRATED.
2017-09-29 08:50 | YES | NO | 19880124 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-06-21 | 1315 | LA | PLAQUEMINES | BURAS | NO |  | NO | ACCIDENT OCCURRED AT SOUTH PASS 49 ONSHORE FACILITY (SOUTH PASS 27 TANK BATTERY) (LATITUDE 2902.4 - LONGITUDE 8919.2). |  | PUMPING STATION | VALVE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 95 | 90 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L. DOWNIE-DIVISIO MANAGER | 5043642496 | MAINTENANCE PERSONNEL LEFT A 1" DRAIN VALVE OPEN AFTER CLEANING STRAINERS ON S/P 49 LACT UNIT. CRUDE OVERFLOWED ONTO THE FACILITY PLATFORM DECK AND ONTO SURROUNDING SURFACE WATER. THE OIL HAS BEEN CONTAINED WITH BOOMS AND IS BEING CLEANED UP USING WATER SPRAY, SKIMMER BARGE AND SORBENT PADS. RECOVERED OIL WAS PUMPED BACK INTO FACILITY TANKS. OPERATING AND MAINTENANCE PROCEDURES HAVE BEEN REVIEWED BY 0 & M PERSONNEL.
2017-09-29 08:50 | YES | NO | 19880125 |  | 19226 | TEXACO PIPELINE INC | NO | 1988-06-23 | 730 | TX | FALLS |  | NO |  | NO | APPROXIMATELY 1550 FEET SOUTH OF PIPELINE CROSSING OF FM 2307. THIS PIPELINE CROSSES FM 2307 0.7 MILES EAST OF STATE HIGHWAY #6. |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 4000 | 300 | NO | NO | 10 | 0.25 | 1628 | WELDED |  | 1025 | 1080 | YES | 0 | 1000 | 12 | 48 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. MINER, DISTRICT MANAGER | 7139534260 | DOWNSTREAM BOOSTER STATION WENT DOWN DUE TO ELECTRIC POWER OUTRAGE. UPSTREAM BOOSTER SHUTS DOWN ON PRESSURE BUILDUP TO 1100 PSIG. SEAM SPLIT AT 1080 PSIG. OPERATOR SHUT SYSTEM DOWN. SPLIT PIPE LOCATION BETWEEN THESE TWO BOOSTER STATIONS,ABOUT 4 MILES DOWNSTREAM OF UPSTREAM BOOSTER.
2017-09-29 08:50 | YES | NO | 19880126 |  | 22430 | WEST SHORE PIPE LINE CO | YES | 1988-06-04 | 7 | WI | MILWAUKEE | WAUWATOSA | NO |  | NO | 500 FEET SOUTH OF BLUE MOUND RD. AN 124 TH ST. |  | LINE PIPE | PIPE |  | 1961 | OTHER | SCRATCH DEVELOPED CRACK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 3 | 2738 | 2000 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1170 | 1000 | YES | 24 | 1460 | 12 | 61 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH C. ANDREEN, AREA MANAGER | 3122573740 | PRIOR TO 23:54 ON JUNE 3, 1988 THE PIPELINE SEGMENT HAD BEEN SHUTDOWN IN THE NORMAL COURSE OF OPERATIONS. AT THE ABOVE TIME, THE PIPELIE SEGMENT WAS RE-STARTED AT THE ORIGIN. NORMAL OPERATIONS REQUIRE THE OPERATOR TO OPEN THE TERMINAL BLOCK VALVE WHEN THE PRESSURE AT THE TERMINAL INCREASES. THAT VLVE WAS OPENED AT00:07 ON JUNE 4. THE OPERATOR NOTED INADEQUATE FLOW INTO THE TERMINAL AND SHUTTHE LINE DOWN AT 00:09. WEST SHORE PERSONNEL WERE DISPATCHED TO CHECK THE LINEFOR LEAKS. THE WAUWATOSA FIRE DEPARTMENT CALLED US AND ADVISED US OF THE LEAK LOCATION AT 01:45. CLEANUP AND REPAIR PROCEDED AT THAT TIME. A PIECE OF PIPE 15 FEET LONG WAS REMOVED. THE PIPE SPLIT WAS 26 INCHES LONG AND APPROXIMATELY 3 INCHES WIDE. THE PIPELINE SEGMENT WAS PUT BACK INTO OPERATION AT 02:30 ON JUNE 5, 1988.
2017-09-29 08:50 | YES | NO | 19880127 |  | 320 | ALLEGHENY PIPELINE CO | YES | 1988-05-03 | 1435 | PA | HUNTINGDON | MOUNT UNION | NO |  | NO | A REMOTE AREA. U.S. GEOLOGICAL SURVEY MAP ENTITLED "HARRISBURG" IS ATTACHED SHOWING ACCIDENT LOCATION AT MILE POST 161.8. |  | LINE PIPE | OTHER | 1" CONN. ATTACHED TO PIPE | 1962 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7700 | 6905.0886 | 13930.3528 | L. P. G. | 2 | 50 | 103 | NO | NO | 6 | 0.28 | 30000 | WELDED |  | 1440 | 444 | YES | 12 | 2184 | 8 | 81 | NO DATA | Null | Null | NO DATA |  | OTHER | LARGE STONE | Null | ONE CALL |  | YES | YES | WILLIAM M. OLLER | 7137593605 | A COMPANY CREW WAS EXCAVATING LINE FOR ROUTINE MAINTENANCE WORK, WHEN A LARGE STONE ROLLED FROM TEH DITCH BANK INTO THE EXCAVATED SITE AT 1435 HRS. C.D.T. ON MAY 3, 1988, STRIKING AND FRACTURING A ONE (1) INCH CONNECTION ATTACHED TO THE PIPELINE. MAIN LINE BLOCK VALVE WERE CLOSED ON EACH SIDE OF TEH ACCIDENT SITE TO ISOLATE TEH ACCIDENT SITE. APPROXIMATELY 50 BARRELS OF PROPANE, IN THE VAPOR SATE, ESCAPED FROM TEH PIPELINE, PRIOR TO THE VAPORS BEING INTENTIONALLY INGNITED AT 1805 HRS. C.D.T. ON MAY 3, 1988. WHILE THE FLARING WAS TAKING PLACE IN A CONTROLLED CONDITION IN THIS REMOTE AREA, 103 BARRELS OF PROPANE WERE REMOVED FROM THE ISOLATED PIPELINE SECTION TO TANK TRUCKS. AFTER THE FLARING WAS COMPLETED, ASECTION OF PIPE WAS REPLACED AND THE PIPELINE PLACED BACK INTO SERVICE AT 0132 HRS. C.D.T. ON MAY 5, 1988. AT 1620 HRS. C.D.T. ON MAY 5, 1988, IT WAS DETERMINABLE TAT TEH ESTIMATED VOLUME OF PROPANE LOST PLACED THE ESTIMATED TOTAL PROPERTYDAMAGE OVER $5,OOO AND THAT A TELEPHONIC NOTICE OF THE ACCIDENT WOULD BE REQUIRED. THE TELEPHONIC NOTICE WAS GIVEN AT 1628 HRS. C.D.T. ON MAY 5, 1988. THE ACTUAL VOLUM OF PROPANE LOST WAS DETERMINED AT 1710 HRS. D.C.T. ON MAY 6, 1988, UPON COMPLETION OF THE DELIVERY OF THE PROPANE BATCH TO A SHIPPER AT SCHAEFFERSTWOM, PA. A SECOND TELEPHONIC NOTICE WAS GIVEN AT 1714 HRS. C.D.T. ON MAY 6, 1988,AMENDING THE VOLUME OF PROPANE LOST.
2017-09-29 08:50 | YES | YES | 19880128 |  | 3115 | CSX NGL CORP | NO | 1987-07-24 | 1545 | LA | PLAQUEMINES | BURAS | NO |  | NO | BASTIAN BAY MARSH AREA - WEST OF EMPIRE CANAL. |  | NO DATA | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 2 | 0 | 2 | 1 | 0 | 1 | 500000 | 462829.3338 | 933713.7104 | NATURAL GAS LIQUID | 2 | 6330 | 0 | YES | NO | 8 | 0.5 |  | WELDED |  | 0 | 700 | YES | 8 | 2000 | 5 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER |  | Null | Null | THEODORE TALLORNEY | 7138534700 | 165 FOOT FISHING VESSEL OPERATING IN SHALLOW WATERS, DISREGARDING PIPELINE MARKERS, RAMMED INTO PIPELINE CAUSING RUPTURE IN LINE AND PRODUCT ESCAPED. THERE WAS AN EXPLOSION AND FIRE ON THE VESSEL.
2017-09-29 08:50 | YES | NO | 19880129 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-05-24 | 1315 | NE | LANCASTER |  | NO |  | NO | LINCOLN TERMINAL #336. |  | TANK FARM | TANK |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6277.3533 | 12663.9571 | GASOLINE | 3 | 294 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | ON MAY 24, 1988 A LEAK WAS DISCOVERED IN TANK #793 DURING A STATIC LEAK TEST. FURTHER INVESTIGATION ATTRIBUTED THE RELEASE TO SEVERAL INTERNAL CORROSION PITS IN THE TANK FLOOR. THE TANK HAS BEEN CLEANED AND REPAIRS HAVE BEEN INITIATED.
2017-09-29 08:50 | NO | NO | 19880130 |  | 26148 | WITCO CHEMICAL CORP | NO | 1988-06-06 | 800 | CA | KERN | OILDALE | NO |  | NO | 7" CRUDE OIL LINE ON SOUTH SIDE OF CHINA GRADE LOOP APPROXIMATELY. 40' EAST OF HARRISON DR. |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2 | 0 | NO | NO | 7 | 0.33 | 2400 | WELDED |  | 340 | 140 | YES | 4 | 425 | 9 | 85 | EXTERNAL | Null | YES | OTHER | CATHODIC INTERFERENCE | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES LANKFORD, SUPERINTENDENT TRANSPORTATION | 8053937110
2017-09-29 08:50 | YES | NO | 19880131 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-05-19 | 550 | OK |  | TULSA | NO |  | NO | TULSA TERMINAL #295 |  | TANK FARM | VALVE |  | 1931 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 448.3824 | 904.5684 | GASOLINE | 3 | 70 | 60 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD JANZEN | 9185884850 | ON 5/19/88, 70 BBLS. OF GASOLINE WAS ACCIDENTLY RELEASED THROUGH THE WATER DRAWVALVE ON TANK #605. THE RELEASE WAS THE RESULT OF OPERATOR ERROR. TANK #605 HAD BEEN TEMPORARILY OUT OF SERVICE FOR CLEANING AND BOTTOM REPAIR. AN ADJACENT TANK, #604, WAS BEING UTILIZED AS A GASOLINE RACK TANK IN THE INTERIM. DURING AN ANORMAL TRANSFER OPERATION INTO TANK #604, PRODUCT ALSO FLOWED (UNBEKNOWNST TOTHE OPERATOR AT THE TIME) THROUGH A COMMON LINE (SHARED BETWEEN 604 AND 605) INTO TANK #605 HAD BEEN CHAINED CLOSED (STANDARD PROCEDURE DURING TANK MAINTENANCE), HOWEVER IT WAS UNLOCKED AND OPENED EARLIER IN THE DAY FOR A PLANNED RECEIVE OPERATION THAT WAS LATER CANCELLED. THE OPERATOR ON DUTY NOTICED A DISCREPANCY IN HIS TANK GAUGE READINGS AND, UPON INVESTIGATING, DISCOVERED THE RELEASE. ACTIONS TAKEN BY PERSONNEL INVOLVED WITH THIS INCIDENT HAVE BEEN REVIEWED AND APPROPRIATE INSTRUCTIONS HAVE BEEN GIVEN TO PREVENT A FUTURE REOCCURRENCE.
2017-09-29 08:50 | YES | NO | 19880132 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1988-06-18 | 1124 | KS | COWLEY | ATLANTA | NO |  | NO | 1 1/2 MILES WEST, 4 MILES SOUTH OF ATLANTA, KANSAS, (COWLEY COUNTY) SECTION 4, TOWNSHIP 31 SOUTH, RANGE 6 EAST. |  | LINE PIPE | PIPE |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 14041 | 12591.4739 | 25402.0888 | NATURAL GAS LIQUID | 3 | 850 | 0 | NO | NO | 6 | 0.13 | 2264 | WELDED |  | 1630 | 113 | YES | 24 | 2220 | 8 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE WARNING SIGNS | NO | NO | S.F. ISAACS, PRESIDENT | 9185811800 | ACCIDENT OCCURRED WHEN A THIRD PARTY WAS GATHERING GRAVEL FROM A CREEK BOTTOM.THE LINE WAS PUNCTURED WHEN THE BUCKET OF THE FRONT-END LOADER STRUCK THE LINE.
2017-09-29 08:50 | YES | NO | 19880133 |  | 26125 | CALNEV PIPELINE CO | YES | 1988-06-14 | 1315 | CA | SAN BERNARDINO |  | NO |  | NO | 3.9 MILES SOUTH OF PHELAN RD. ON BALDY MESA RD. (MIDWAY BETWEEN PHELAN, CA AD HESPERIA, CA). |  | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 44838.2377 | 90456.8363 | JET FUEL | 3 | 85 | 18 | NO | NO | 8 | 0.22 | 2140 | WELDED |  | 500 | 300 | YES | 24 | 2100 | 8 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | PAUL B. STRENGELL, MANAGER OF ENGINEERING | 7148887771 | CONTRACTOR WAS INSTALLING CONDUIT FOR FIBER OPTIC CABLE IN ROADWAY OF BALDY MESA RD. AND STRUCK 8" PIPELINE WITH TRENCHING MACHINE CAUSING ABOUT 3/4" HOLE. THE PIPELINE WAS NOT OPERATING AT THE TIME. THE CONTRACTOR NOTIFIED SAN BERNARDINO OFFICE IMMEDIATELY AND AN INTERMEDIATE BOOSTER STATION DOWNSTREAM WAS STARTED UP AND THE LINE WAS DRAINED DOWN THEREBY MINIMIZING PRODUCT LOSS.
2017-09-29 08:50 | YES | NO | 19880134 |  | 300 | ALL AMERICAN PIPELINE CO | NO | 1988-07-01 | 930 | CA | KERN |  | NO |  | NO | 0.1 MILES EAST OF PENTLAND ROAD, 0.5 MILES SOUTH OF STATE HIGHWAY 166 (MARICOPA ROAD), MARICOPA FIELD, SECTION 9, WELL 9K #6, KERN COUNTY, CALIFORNIA. |  | LINE PIPE | PIPE |  | 1987 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 262410 | 235320.039 | 474735.5682 | CRUDE OIL | 1 | 3384 | 1750 | NO | NO | 16 | 0.25 | 65000 | WELDED |  | 1440 | 420 | YES | 24 | 1902 | 5 | 26 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | H.D. HORTON, MANAGER, REGULATORY COMPLIANCE | 8053985300 | MAJOR COMENTING COMPANY, INC., (WORKING FOR CHEVRON USA, INC.) WAS CLEANING UP AROUND AN OLD WELL LOCATION OWNED BY CHEVRON WITH A MICHIGAN 275B FRONT-END LOADER. THE OERATOR WAS WORKING DIRECTLY OVER A 30" CRUDE OIL LINE OWNED BY ALL AMERICAN PIPELINE COMPANY AND A 16" CRUDE OIL LINE OWNED BY CELERON GATHERING CORPORATION AND OPERATED BY ALL AMERICAN PIPELINE COMPANY UNDER AN OPERATING AN MAINTENANCE AGREMENT. THE 30" AND 16" LINES ARE PARALLEL LINES, APPROXIMATELY 15 FEET APART. WHEN THE FRONT-END LOADER HIT THE 16" LINE WITH THE LOADER BUCKET IT CAUSED A 6" TO 12" RUPTURE IN THE LINE. WHEN THE EQUIPMENT HIT THE 16" LINE, THEBACK WHEELS WEE RESTING ON TOP OF THE 30" LINE, CAUSING DAMAGE TO THE COATING.THE EQUIPMENT OPERATOR TURNED OFF THE ENGINE AND LEFT THE FRONT-END LOADER IN PLACE. A PIPELIE WARNING MARKER WAS WITHIN 30 FEET EAST OF TEH ACCIDENT, ANOTHERPIPELINE WARNING MARKER WAS APPROXIMATELY 0.1 MILES WEST OF THE ACCIDENT. THE OIL SPILL WAS QUICKLY CONTAINED, LIMITING THE CONTAMINATED AREA TO APPROXIMATELYONE ACRE.
2017-09-29 08:50 | YES | NO | 19880135 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1988-07-26 | 400 | OH | ALLEN | LIMA | NO |  | NO | TANK 97 ON MID-VALLEY TANK FARM . |  | TANK FARM | TANK |  | 1945 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL |  | 206 | 205 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DENNIS L. MOENING, AREA SUPERINTENDENT | 4196553313 | AT 0401 C.S.T. ONE OF OUR LIMA STATION TERMINAL OPERATORS REALIZED THAT HE WASSUPPOSE TO MAKE A TANK CHANGE AT 0330 C.S.T. A STATEMENT FROM OUR OPERATOR SAIDHE KNEW HE HAD A TANK CHANGE AT 0330 C.S.T. BUT FORGOT TO MAKE THE CHANGE. OURTANKS ARE EQUIPPED WITH A HIGH SOUNDS THE HORN WHEN THE FLOATING ROOF MAKES CONTACT WITH A MECHANICAL SWITCH. THE OPERATOR ON DUTY STATES THAT HE NEVER RECEIVED ANY ALARMS. UPON INVESTIGATION WE HAVE DETERMINED THE HORN AND THE ALARM SYSTEM ON TANK 97 WAS OPERABLE APPROXIMATELY TWO WEEKS BEFORE THE INCIDENT, AS WITNESSED BY AN ELECTRICAL TECHNICIAN. THE SYSTEM WAS ALSO CHECKED IMMEDIATELY FOLLOWING THE INCIDENT AND FOUND TO BE WORKING. WE KNOW OF NO REASON WHY THE ALARMSYSTEM DIDN'T WORK AT THE TIME OF THE OVERFILL.OUR PROGRAMMABLE CONTROLLERS ARE OPERATED IN A "FAIL SAFE", IN THAT, IN THE EVENT A WIRE WOULD COME LOOSE, IT WOULD AUTOMATICALLY SOUND AN ALARM. AT 0401 C.S.T. OUR OPERATOR OPENED INTO ANOTHER TANK AND CLOSED OUR OF TANK 97, HOWEVERE 296BARRELS HAD ESCAPED FROM THE TOP OF THE TANK BY THIS TIME. WE TRANSFERRED OIL FOM TANK 97 (BY GRAVITY) TO OUR TANK 90 TO ALLOW THE ROOF TO COME BACK DOWN TO NORMAL SAFE FILL LEVEL. ALL ALARMS, GAUGING SYSTEM, AND THE ROOF ITSELF HAVE BEEN CHECKED AND ARE OPEATIONAL. AT 1600 C.S.T. ON JULY 27, 1988 WE PLACED THE TANK BACK IN SERVICE. AN ENVIRONMENTAL SPECIALIST CONTRACTOR WAS CALLED IN TO PICKUP THE OIL AND WASH DOWN THE TANK WITH A HIGH PRESSURE WASHER UTILIZING BIO-DEGRADABLE DETERGENT AND WATER. ALL OIL WAS CONTAINED IN THE DIKE AREA. BY 1600 CSTON JULY 27, 1988 THE EXTERIOR OF THE TANK WAS CLEANED AND THE OIL WAS RECOVERED.THE OHIO EPA WAS ON THE SCENE AT 1400 CST ON JULY 26, 1988, THEY WERE SATISFIEDWITH THE CLEANUP EFFORTS AND LEFT AT 1430 CST.
2017-09-29 08:50 | YES | NO | 19880136 |  | 13162 | NAVAJO REFINING CO | YES | 1988-08-02 | 500 | TX | HUDSPETH |  | NO |  | NO | MILE POST 119.5 |  | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 35646 | 31966.0764 | 64488.4877 | DIESEL FUEL | 3 | 1896 | 263 | NO | NO | 7 | 0.16 | 42 | WELDED |  | 1260 | 430 | YES | 27 | 900 | 6 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | CONTRACTOR-PUBLIC AWARE | NO | NO | JIMMY LILES - PIPELINE | 5057481311 | AT APPROXIMATELY 0500 HOURS, 2 AUGUST 1988, WHILE BALANCING PIPELINE INTEGRITY REPORT OPERATORS IN EL PASO, TEXAS AND TRTESIA, NEW MEXICO NOTED DISCREPANCY IN VOLUMES. LINE WAS SHUT DOWN AND PERSONNEL WERE CALLED IMMEDIATELY TO LOCATE PROBLEM. AT 0615 HOURS AIRPATROL BEGAN FLYING PIPELINE, AT 1030 HURS AIRPATROL OBSERVED AND REPORTED BY RADIO LEAK LOCATION. CREW OF MAINTENANCE PERSONNEL WERE THEN DISPATCHED TO REPAIR LEAK. LEAK/SPLIT WAS REPAIRED COMPLETELY AT 2200 HOURS, 2 AUGUST 1988.
2017-09-29 08:50 | YES | NO | 19880137 |  | 443 | AMOCO PIPELINE CO | YES | 1988-07-31 | 2130 | OK | PAYNE |  | NO |  | NO | NW 1/4, SECTION 12, TOWNSHIP 17N, RANGE 5E. |  | TANK FARM | NO DATA |  | 1920 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 4000 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. CARICO, AREA MANAGER-CUSHING OPERATIONS | 9182257271 | OIL WAS BEING TRANSFERRED TO TANK 1391 WITH CUSHING UNTI #5. THIS OPERATION WAS TO CEASE AT 19:00 HOURS. A NOTE TO THAT EFFECT WAS LEFT BY THE CONTROLLER WHOSE SHIFT ENDED AT 18:30 FOR THE CONTROLLER THAT RELIEVED HIM. THE LATTER MISINTERPRETED THE NOTE TO MEAN THAT THE UNIT HAD ALREADY BEEN SHUT DOWN, AND STOPPED WATCHING HIS TANK GAUGES. A HIGH TANK ALARM RECEIVED AT 20:10 WAS THOUGHT TO BEINVALID. AT ABOUT 22:45, A FIELD OPERATOR HAPPENED TO PASS BY FOR ANOTHER REASON, NOTICED THE OVER RUN AND SHUT THE TRANSFER DOWN. OIL WAS CONTAINED WITHIN TEH TANK DIKE FROM WHERE IT IS BEING RECOVERED.
2017-09-29 08:50 | YES | YES | 19880138 |  | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1988-06-15 | 1330 | IA | POLK | PLEASANT HILL | NO |  | NO | 4401 VANDALIA ROAD, DES MOINES, IOWA 50317. |  | TANK FARM | VALVE |  | 1963 | OTHER | FIRE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 1 | 0 | YES | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.W. KINDER, VICE PRESIDENT, OPERATIONS | 7138535599 | ARC WELDING NUTS TO STUD BOLTS ARE OUTLET VALVE OF WATER KNOCK OUT TANK, FOR THE NORMAL BUTANE DEHY. A WELDING SPARK IGNITED PRODUCT VAPOR AND STARTED A FIRE. THE FIRE WATCH EMPLOYEE EXTINGUISHED THE FIRE IN APPROXIMATELY 5 SECONDS. ONEEMPLOYEE (THE WELDER) RECEIVED A BURN ON HIS ARM AT HIS ELBOW, 3"X5" (2ND DEGREE).
2017-09-29 08:50 | YES | NO | 19880139 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-06-17 | 925 | KS | CRAWFORD |  | NO |  | NO | NE 1/4, NW 1/4, S28, T29S, R25E. |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 26902.9426 | 54274.1018 | GASOLINE | 3 | 507 | 0 | NO | NO | 8 | 0.17 | 52000 | WELDED |  | 1400 | 723 | YES | 8 | 1830 | 0 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS | NO | NO | ROBERT G. VAN HOLEHE | 9185884850 | ON 6/17/88 AN EMPLOYEE OF CRAWFORD COUNTY STRUCK OUR 8" HUMBOLDT-SPRINGFIELD PIPELINE WITH A D-7 DOZER WHILE GRADING IN AN ABANDONED LANDFILL AREA. THE LINE WAS ACTUALLY STRUCK TWICE WITHOUT PUNCTURE, HOWEVER, THINKING HE HAD HIT A LARGE ROCK, THE DOZER OPERATOR STRUCK THE LINE A THIRD TIME, AND PUNCTURED IT. GASOLINE SPRAYED THE DOZER AD THE OPERATOR BUT NO IGNITION OCCURRED. THE OPERATOR REPORTED THE INCIDENT TO THE CRAWFORD COUNTY HIGHWAY DEPARTMENT. THE RESPONDING AMBULANCE CREW WASHED THE DOZER OPERATOR DOWN WITH WATER AND SENT HIM TO A LOCAL HOSPITAL WHERE HE RECEIVED A CHECK-UP AND WAS THEN RELEASED. CONVERSATIONS WITH THE OPERATOR INDICATED THAT HE WAS AWARE OF THE PIPELINES LOCATION (LINE MARKER WAS PRESENT), BUT HE DID NOT REALIZE THAT HE WAS GRADING DEEP ENOUGH TO HIT THE LINE. CLEANUP EFFORTS ARE BEING COORDINATED WITH APPROPRIATE STATE AGENCIES.
2017-09-29 08:50 | YES | NO | 19880140 |  | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1988-07-03 | 1000 | CA | KERN |  | NO |  | NO | SECTION 34, TOWNSHIP 27 SOUTH, RANGE 29 EAST, APPROXIMATELY .3 MILE SOUTH BROW MATERIAL ROAD AND 1.9 MILES WEST HIGHWAY 33. |  | PUMPING STATION | VALVE |  | 1985 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 44838.2377 | 90456.8363 | CRUDE OIL | 1 | 3000 | 2600 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. E. KELLEY, CENTRAL DISTRICT MANAGER | 8053270110 | A DANIEL DANFLOR PRESSURE RELIEF/SURGE RELIEF VALVE IN MAINLINE SURGE RELIEF SYSTEM LOST ENOUGH CHARGE TO ALLOW THIS VALVE TO OPEN AND ALLOW CRUDE TO ENTER SURGE RELIEF TANK (3000 BBLS. CAPACITY); AS THE CRUDE FILLED THIS TANK THE HIGH LEVEL SHUTDOWN FAILED TO CLOSE MOTORIZED VALVE AND TANK OVERFLOW.
2017-09-29 08:50 | YES | NO | 19880141 |  | 13131 | CONOCO INC | YES | 1988-07-16 | 1230 | WY | NIOBRARA |  | NO |  | NO | SE 1/4, NE 1/4 SECTION 13, 36 NORTH, 64 WEST. |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 448.3824 | 904.5684 | CRUDE OIL | 1 | 2000 | 500 | NO | NO | 6 | 0.22 | 2310 | WELDED |  | 250 | 225 | YES | 0 | 300 | 0 | 79 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.G. HUBBARD, DIRECTOR, ENVIRONMENTAL AFFAIRS | 7132932032 | THE SPILL WAS THE RESULT OF A LEAK CAUSED BY CORROSION ON THE BOTTOM OF THE PIPE. BECAUSE OF EXTREMELY DRY CONDITIONS, THE CRUDE OIL DID NOT SURFACE IMMEDIATELY. ONCE THE LEAK WAS DISCOVERED, THE LINE WAS ISOLATED BY CLOSING A BLOCK VALVE
2017-09-29 08:50 | YES | NO | 19880142 |  | 809 | ARCO PIPE LINE CO | YES | 1988-07-07 | 945 | KS | MIAMI |  | NO |  | NO | APPROXIMATELY 350' N OF K-68, 1/2 MILE WEST OF U.S. 169 E/2 SE/4 SE/4 SEC. 27, T16S, R23E, MIAMI COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1929 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 44838.2377 | 90456.8363 | FUEL OIL | 3 | 1266 | 298 | NO | NO | 8 | 0.25 | 24000 | NO DATA |  | 595 | 550 | YES | 0 | 1050 | 0 | 48 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | O.D. HARRIS - NORTHERN AREA MANAGER | 3163311300 | DAMAGE CAUSED WHEN AN TRACK DRIVEN FRONT LOAKER STRUCK AND DAMAGED OUR LINE. TOTAL BBLS OUR 1266, 298 RECOVRED FOR NET LOSS OF 968 BBLS.
2017-09-29 08:50 | YES | NO | 19880143 |  | 26141 | SHELL OIL CO | NO | 1988-07-14 | 1600 | CA | KERN | WASCO | NO |  | NO | SECTION 6, 7-28S, R-24-3, DMB&M SURVEY BAKESFIELD TANK FARM. |  | TANK FARM | OTHER | EXPANSION JOINT | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 6725.7357 | 13568.5254 | CRUDE OIL | 1 | 150 | 135 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | VALVE OPENED ALLOWING PRESSUE TO BUILD UP CAUSING EXPANSIN JOINT TO BLOW OUT.
2017-09-29 08:50 | YES | NO | 19880144 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-07-12 | 945 | NM | LEA | JAL | NO |  | NO | SW 1/4, SW 1/4, SECTION 16, T-15-S, R-37-E TWO MILES EAST OF JAL, HOBBS-HENDRICK 10-INCH. |  | LINE PIPE | PIPE |  | 1935 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 627.7353 | 1266.3957 | CRUDE OIL | 1 | 65 | 50 | NO | NO | 10 | 0.28 | 25000 | WELDED |  | 900 | 200 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY&ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19880145 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-07-05 | 1000 | TX | UPTON | RANKIN | NO |  | NO | SW 1/4, SW 1/4/, SECTION 8, BLOCK 4, UNIVERSITY OF TEXAS SURVEY FIVE MILES EAST OF RANKIN ON HIGHWAY 67 MCCAMEY-KEMPER 10-INCH. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1323 | 1186.4198 | 2393.4879 | CRUDE OIL | 1 | 250 | 215 | NO | NO | 10 | 0.37 | 30000 | WELDED |  | 1010 | 852 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | YES | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | UPTON COUNTY ROAD DEPARTMENT MAINTENANCE HIT LINE.
2017-09-29 08:50 | YES | NO | 19880147 |  | 2552 | COLONIAL PIPELINE CO | YES | 1988-06-18 | 130 | NC | MECKLENBURG | PAW CREEK | NO |  | NO | COLONIAL PIPELINE COMPANY DELIVERY FACILITY. |  | TANK FARM | TANK |  | 1963 | OTHER | FAILURE OF TANK ROOF | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 10761.177 | 21709.6407 | GASOLINE | 3 | 919 | 558 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. SORROW - REGUALTORY AND ENVIRONMENTAL MANAGER | 4042611470 | A DELIVERY FROM THE MAIN PIPELINE OF 5,000 BARRELS OF GASOLINE WAS COMPLETED INTO BREAKOUT TANK NO. 716 AT 2025 HOURS ON JUNE 17, 1988. THE 23,000 BARREL CAPACITY TANK WAS EMPTY WITH THE EXTERNAL FLOATING ROOF RESTIG ON THE ROOF LEGS PRIOR TO THE DELIVERY. AFTER THE DELIVERY THE HEIGHT OF PRODUCT INTHE TANK WAS 10.60FEET. AT 2108 HOURS ON JUNE 17, 1988, THE STATION OIPERATOR MADE AN INSPECTIONOF TEH FACILITY AND FOUND NOTHING UNUSUAL. AT 0130 HOURS ON JUNE 18, 1988, THESTATION OPERATOR INSPECTED THE FACILITY AND FOUND GASOLINE RUNNING FROM THE ROOF DRAIN LINE ON TANK NO. 716 ITO THE TANK DIKE. THE DIKE DRAIN VALVE WAS IN THECLOSED POSITION AND ALL SPILLED PRODUCT WAS CONTAINED IN THE DIKE. THE OPERATOR CLOSED THE TANK ROOF DRAIN VALVE AND CALLED THE SUPERVISOR. THE TANK GAUGE INDICATED THAT 919 BARRELS OF PRODUCT HAD BEEN LOST FROM THE TANK. THE FACILITY FIRE FIGHTING SYSTEM WAS ACTIVATED AND WATER FROM THE HYDRANT SYSTEM WAS INTRODUCED INTO THE TANK DIKE TO FORM A BARRIER BENEATH THE PRODUCT TO REDUCE THE AMOUNTOF PRODUCT SOAKING INTO THE SOIL. ABOUT 558 BARRELS OF TEH SPILLED PRODUCT WERE RECOVERED LEAVING A NET LOSS OF 361 BARRELS OF GASOLINE. LATER THE TANK WAS CLEANED AND VAPOR FREED FOR ENTRY. IT WAS FOUND THAT THE INTERNAL FLOATING ROOF DRAIN LINE HAD RUSTED WHERE IT WAS ATTACHED TO THE ROOF DRAIN SUMP AND A DETERIORATED THREADED JOINT HAD FAILED. THE ROOF DRAIN LINE WAS REPLACED.
2017-09-29 08:50 | NO | NO | 19880148 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-07-01 | 1530 | MO | JASPER |  | NO |  | NO | CARTHAGE TERMINAL #227. |  | TANK FARM | OTHER | PRODUCT ESCAPE (WATER) | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1076.1177 | 2170.9641 | FUEL OIL | 3 | 5 | 5 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | ON THE EVENING OF JULY 1, 1988 OPERATING PERSONNEL AT OUR CARTHAGE, MISSOURI THERMINAL DISCOVERED WHAT APPEARS TO HAVE BEEN FUEL OIL IN A SMALL NATURAL DRAINAGE AREA ADJACENT T THE TERMINAL PROPERTY. CREWS WERE ABLE TO CONTAIN THE PRODUCT BY BUILDIG COFFER DAMS AND THUS PREVENTED ANY PRODUCT FROM MIGRATING FURTHE DOWN THE GRADIENT INTO A NEARBY CREEK. WATER PREVIOUSLY HAD BEEN DRAWN OF THE BOTTOM OF A 500 BBL. RELIEF TANK INTO THE DIKED AREA SURROUNDING THE TANKS. SUBSEQUENT WATER ACCUMMULATION IN THE DIKED AREA FROM A HEAVY RAIN FALL, NECESSITATED THAT OPERATORS RELEASE TEH CONTAINED WATER OFF THE PROPERTY INTO THE ADJACENT DRAINAGE FIELD. IT IS SPECULATED THAT SOME PRODUCT WAS ACCIDENTALLY RELEASED ALONG WITH THE BOTTOM WATER DURING THE TANK WATER DRAW OPERATION. ALL RELEASED PRODUCT WAS RECOVERED.
2017-09-29 08:50 | YES | NO | 19880149 |  | 4906 | EXXON PIPELINE CO | YES | 1988-07-08 | 1005 | TX | TITUS |  | NO |  | NO | LEAK OCCURRED AT STATION 3290+10 (NEAR WHITE OAK CREEK) SOME 2 MILES SOUTH OF TALCO STATION ON THE 8-INCH TALCO - LONGVIEW TRUNK LINE. |  | LINE PIPE | PIPE |  | 1936 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3480 | 3120.7413 | 6295.7958 | CRUDE OIL | 1 | 550 | 545 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 741 | 260 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AERIAL PATROL | NO | NO | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT 1005 HOURS ON JULY 8, 1988 A BULLDOZER CONTRACTEDBY THE LANDOWNER WAS CLEARING A WOODED BOTTOM AREA WHEN HE GOT ON EPC'S ROW AND CAME IN CONTACT WITH OUR PIPELINE GOUGING A ONE FOOT LONG SLIT IN THE BODY OF THE PIPE. THE DOZER OERATOR OTIFIED THE LANDOWNER WHO IN TURN CALLED THE LONGVIEW DISTRICT HEADQUARTERS AND REPORTED THE INCIDENT. THE TALCO GAUGER WAS AT ONE OF THE ON LINE PUMPING STATIONS WHEN TEH STATION WENT DOWN DO TO LOW PRESSURE. HE CONTACTED THE OTCC CONTROLLER IN HOUSTON WHO BY THAT TIME HAD BEEN NOTIFIED OF THE INCIDENT SO THE LINE WAS LEFT DOWN. MEANWHILE, THE DOZER OPERATOR DAMMED A SMALL AREA TO CONTAIN THE OIL. EPC PERSONNEL AND CONTRACTED EQUIPMENT AD VACUUM TRUCKS WERE DISPATCHED TOTHE SITE AT ABOUT 1030 HOURS. THE LINE WAS PERMANENTLY REPAIRED BY REPLACING A16.5 FOOT SECTION OF PIPING. THE LINE WAS RESTORED TO SEVICE AT 2100 HOURS ON 7/8/88. CLEANUP OPERATIONS WERE COMPLETED JULY 11, 1988.
2017-09-29 08:50 | YES | NO | 19880150 |  | 12127 | MARATHON PIPE LINE CO | YES | 1988-07-13 | 1600 | IL | MADISON |  | NO |  | NO | SECTION 34, T3N, R9W, WOOD RIVER TWP. MADISON COUNTY, ILLIMOIS (AMOCO REFINERY PROPERTY). |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 125547.0655 | 253279.1416 | OIL AND GASOLINE | 3 | 2979 | 2401 | NO | NO | 8 | 0.32 |  | WELDED |  | 1200 | 860 | YES | 24 | 1802 | 0 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE PRESIDENT | 4194223009 | ON WEDNESDAY, JULY 13, 1988, MARATHON PIPE LINE COMPANY EASTERN DIVISION DISCOVERED THE POSSIBILITY OF A LEAK ON THE 8" EAST ST. LOUIS TO WOOD RIVER LINE. THELINE WAS SHUT DOWN. THE LEAK, CAUSED BY EXTERAL CORROSION PITTING, WAS DISCOVERED IN FILL AREA OF VERY POROUS SOIL. REPAIR OF THE LEAK WAS COMPLETED WITH A PLIDCO CLAMP AND CLEAN UP PROCEDURES WERE INITIATED. CLEAN UP ACTIVITIES CONTINUE WITH VACUUM TRUCKS. TO DATE 2302 BBLS OF PRODUCT HAVE BEEN RECOVERED.AS OF THIS DATE (11/7/88) 2401 BARRELS OF PRODUCT HAVE BEEN RECOVERED OUT OF ANESTIMATED 2979 BARRELS RELEASED. MOST, IF NOT ALL, OF THE BALANCE WAS LOST TO EVAPORATION. THE SITE HAS BEEN RETURNED TO ITS PRE-RELEASE CONDITION.
2017-09-29 08:50 | YES | NO | 19880151 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1988-07-22 | 1138 | TN | MONTGOMERY | CLARSVILLE | NO |  | NO | ONE MILE NORTH OF NEEDMORE ROAD & WHITFIELD INTERSECTION IN ST. BETHLEHEM COMMUNITY, 5 MILES NORTH OF CLARKSVILLE, TN. |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 224191.1884 | 452284.1814 | CRUDE OIL | 1 | 8517 | 1200 | NO | NO | 22 | 0.28 | 52000 | WELDED |  | 960 | 353 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.B. NEWMAN, MANAGER OF PIPELINE OPERATIONS | 2147570207 | ON JULY 22, 1988 KEAY CONSTRUCTION CO. WAS BUILDING A SUBDIVISION ROAD FOR MELTON CONSTRUCTION CO. (DEVELOPER) AND BARNETT INSTRUMENT CO. (LANDOWNER) WHEN A DOZER BLADE RUPTURED THE 22" CRUDE OIL PIPELINE. THE PIPELINE WS WELL MARKED IN THE AREA AD HAD APPROXIMATELY 36" COVER AT THE LEAK POINT BEFORE THE CONTRACTOR BEGAN EXCAVATON. MID-VALLEY WAS NOT ADVISED BY THE CONTRACTOR (SEE ATTACHED WARNING SIGN WHICH HAS OUR 24 HR. PHONE NUMBER) OR THE "ONE-CALL" SYSTEM FOR THE STAE OF TENNESSEE. THE LEAK IN THE PIPE WAS TEMPORARILY REPAIRED UTILIZING A "PLIDCO" SPLIT SLEEVE. THE PERMANENT REPAIR IS SCHEDULED FOR THE WEEK OF AUGUST 22, 1988, WHEN WE WILL IMPLEMENT A "DOUBLE-STOPPLE" PROCEDURE TO CUT-OUT AND REPLACE THE DAMAGED PIPE. THE AMOUNT OF OIL NOT RECOVERED HAS BEEN DETERMINED TO BE 7317 BBLS. THE CLEAN-UP HAS MET THE APPROVAL OF THE TN DIVISION OF SOLID WASTE MANAGEMENT AND THE TN DIVISION OF WATER POLLUTION CONTROL. IN AN EFFORT TO LOCATE AND MITIGATE THE ENVIRONMENT EFFECTS OF THE SEVERAL THOUSAND BBLS. OF OIL SUSPECTED TO STILL BE IN THE GROUND, MID-VALLEY HAS ENGAGED THE SERVICES OF DR. D.M.S. BHATIA (GEOLOGIST, GEOCHEMIST, AND PROFESSOR OF GEOLOGY AT AUSTIN PEAY UNIVERSITY I CLARKSVILLE) TO ACT AS CONSULTANT AND THEREBY MAKE RECOMMENDATIONS AS TO WHAT ACTIONS ARE IN TEH BEST INTEREST OF THE PUBLIC. HIS RECOMMENDATIONS TO DATE INCLUDE MONITORING WATER SAMPLES I THE VICINITY FOR A PERIOD NOT TO EXCEED TWO YEARS. THAT PROGRAM HAS BEEN IMPLEMENTED. IN ADDITION TO DR BAHTIA, PETREX CORP (LAKEWOOD, CO) HAS ALSO BEEN ENGAGED TO PERFORM SUBSURFACE TESTS TO DETERMINETHE DIRECTION OF ANY SUBSTRARE MIGRATION OF THE CRUDE OIL.
2017-09-29 08:50 | YES | NO | 19880152 |  | 12628 | MOBIL PIPELINE CO | NO | 1988-07-18 | 1315 | TX | HILL |  | NO |  | NO | 8-1/2 MILES NW OF WHITNEY, TX - 5.5 MILES WEST OF STATE HIGHWAY 933. |  | NO DATA | VALVE |  | 1957 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 313.8677 | 633.1979 | NATURAL GAS LIQUID | 2 | 25 | 0 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582381 | A COMPANY MAINTENANCE CREW WAS EXPOSING A 12" GATE VALVE ON THE BADEN TO CORSICANA, TX 12" NGL PIPELINE WHEN THE BACKHOE STRUCK AND KNOCKED OFF A SMALL THERMALRELIEF VALVE ON THE BODY OF THE GATE VALVE. THE PIPELINE WAS SHUT DOWN AND THEVALVE ISOLATED. REPAIRS WERE MADE BY REPLACING THE RELEIF VALVE.
2017-09-29 08:50 | YES | NO | 19880153 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-07-18 | 1300 | TX | HASKELL | HASKELL | NO |  | NO | SE 1/4, SW 1/4, SECTION 47, BLOCK 1, W.F. BACHELOR SURVEY FIVE MILES WEST AND ONE MILE EAST OF HASKELL MCCAMEY-CUSHING 10-INCH. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1793.5295 | 3618.2735 | CRUDE OIL | 1 | 50 | 33 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 900 | 200 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19880154 |  | 443 | AMOCO PIPELINE CO | Null | 1988-07-28 | 1200 | IL | COOK | SAUK VILLAGE | NO |  | NO | 1/2 MILE NORTH OF THE INTERSECTION OF SAUK TRAIL AND U.S. ROUTE 30. |  | LINE PIPE | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 26902.9426 | 54274.1018 | GASOLINE | 3 | 1900 | 0 | NO | NO | 10 | 0.34 | 35000 | WELDED |  | 720 | 450 | YES | 10 | 500 | 7 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.A. STAHL - AREA MANAGER | 2197382384 | THE TWO HOUR SYSTEM BALANCES STARTED TO TREND HIGHER THAN NORMAL. THE PIPELINEWAS SHUT DOWN AND PRESSURE TESTED TO DETERMINE IF THERE WAS A LEAK PRESENT. A TEN MILE SECTION OF PIPELINE WAS ISOLATED AND SEGMENTED UNTIL TEH LEAK WAS LOCATED. THE LINE WAS THEN REPAIRED AND RETESTED AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19880155 |  | 26135 | PACIFIC GAS & ELECTRIC CO | NO | 1988-07-23 | 1100 | CA | CONTRA COSTA |  | NO |  | NO | APPROXIMATELY 115 FTR. DUE WEST OF HASTINGS SLOUGH ADJACENT TO SOUTHER PACIFIC RAILROAD TRACKS. |  | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 448382.3768 | 904568.3629 | DIESEL FUEL | 1 | 67 | 27 | NO | NO | 16 | 0.34 |  | WELDED |  | 480 | 12 | YES | 4 | 600 | 3 | 88 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ERNEST W. SIMPSON, PLANT MANAGER | 4156827400 | ON WEDNESDAY, JULY 20, 1988, AT 2010 HOURS, A CITIZEN CALLED PG&E'S PITTSBURG POWER PLANT AND REPORTED AN OIL SPILL BETWEEN PORT CHICAGO AND SOLANO WAY. THE OPERATING FOREMAN FROM THE PLANT DISPATCHED PG&E PERSONNEL TO INVESTIGATE THE SITUATION. PG&E HAS A FUEL OIL PIPELINE LOCATED IN TEH AREA, AD THE PG&E REPRESENTATIVES WENT TO THAT AREA BUT WERE UNABLE TO FIND ANY SIGN OF A LEAK IN TEH PIPELINE. AS A PRECAUTIONARY MEASURE, THE ISOLATION STOP VALVES AT PACHECO CREEK ANDPORT CHICAGO WEE CLOSED. THIS PIPELINE HAS NOT BEEN IN OPERTION FOR SEVERAL YEARS, AND CONTAINED DISPLACEMENT OIL. ON THURSDAY, JULY 21, 1988, AT APPROXIMATELY 0630 HOURS, PG&E PERSONNEL AGAIN CHECKED THE AREA BUT WERE UNABLE TO FIND ANYSIGN OF A LEAK IN THE PIPELINE. PG&E REPRESENTATIVES THEN WENT TO THE POWER PLANT TO REVIEW AERIAL MAPS OF THE AREA AND TO DEVELOP A PLAN TO WALK ALONG THE PIPELINE BETWEEN PORT CHICAGO AND SOLANO WAY. A PG&E EMPLOYEE WAS DIRECTED TO WALDALONG THE PIPELINE AND OBTAIN A SAMPLE OF ANY OIL FOUND. NO OIL WAS FOUND DURING THIS INVESTIGATION, BUT THE EMPLOYEE RETURNED WITH A SAMPLE OF BLACK-COLORED ALGAE. AT THT TIME PG&E PLANT PERSONNEL BELIEVED THAT THE CALL PLACED ON WEDNESDAY EVENING WAS MADE BY SOMEONE WHO HAD MISTAKEN THE BLACK-COLORED ALGAE FOR OIL. PG&E PERSONNEL THEN OPENED THE PIPELINE ISOLATION STOP VALVES ON THE PIPELINE AT PORT CHICAGO AND PACHECO CREEK.
2017-09-29 08:50 | NO | NO | 19880157 |  | 2731 | CHEVRON PIPELINE CO | NO | 1988-07-20 | 1515 | TX | LIBERTY |  | NO |  | NO | SOUR LAKE TO RAYWOOD PIPELINE RIGHT OF WAY M.P 14.1. |  | LINE PIPE | NO DATA |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 89.6765 | 180.9137 | GASOLINE | 1 | 4 | 2 | NO | NO | 6 | 0.22 | 42000 | WELDED |  | 617 | 17 | YES | 8 | 772 | 0 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | A.E. SMITH DIVISION MANAGER | 4098393130 | R.O.W. MOWER HIT PIPELINE WITH BUSH HOG AND WAS THEN REPORTED TO MOWING INSPECTOR. PRODUCT (HYDROGENATED PYROLYSIS GASOLINE) CONFINED BY BOOMS ON SURFACE WATER. AFFECTED AREA 25' WIDE BY 75' LONG. PRODUCT WAS PICKED UP WITH ADSORBENT PADS PLACED INTO DRUMS FOR DISPOSAL. PLIDCO SLEEVE INSTALLED UNTIL DAMAGE PIPE CAN BE REPLACED.
2017-09-29 08:50 | NO | NO | 19880158 |  | 2552 | COLONIAL PIPELINE CO | YES | 1988-07-29 | 1338 | GA | COBB |  | NO |  | NO |  |  | TANK FARM | TANK |  | 1962 | OTHER | LIGHTNING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 22419.1188 | 45228.4181 | GASOLINE |  |  | 0 | Null | Null | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX - TECHNICAL AND REGUALATORY MANAGER | 4048412296 | AT APPROXIMATELY 1:38 PM ON JULY 29, 1988, AT ATLANTA JUNCTION TANK FARM, TANKSNO. 313 AND NO. 330 WERE STRUCK BY LIGHTNING AND WERE DISCOVERED BURNING IN THESECONDARY SEAL AREA AROUND THEIR FLOATING ROOFS. COLONIAL'S FIRE FORM SYSTEM, AND FOAM TRUCKS FROM COBB COUNTY FIRE DEPARTMENT AND DOBBINS AIRE BASE EXTINGUISHED THE FIRE AT APPROXIMATELY 3:00 PM.
2017-09-29 08:50 | NO | NO | 19880159 |  | 2731 | CHEVRON PIPELINE CO | NO | 1988-08-12 | 1930 | TX | LIBERTY |  | NO |  | NO |  |  | LINE PIPE | NO DATA |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 896.7648 | 1809.1367 | CRUDE OIL | 2 | 1 | 1 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 580 | 0 | YES | 8 | 0 | 0 | 87 | EXTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  | 4098393100 | LEAK FOUND DURING PIPELINE INSPECTION BY COMPANY AND CONTRACT PERSONNEL WALKINGPIPELINE RIGHT-OF-WAY. TEMPORARY REPAIRS MADE WITH PIEPLINE CLAMP - CORRODED SECTION WILL BE REPLACED WITH NEW PIPE.
2017-09-29 08:50 | NO | NO | 19880160 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-08-22 | 1127 | TX | NOLAN |  | NO |  | NO | SECTION 56 BLOCK 22 T&P RAILROAD SURVEY MP 108.20 ON 1# 10" COAHOMA TO RANGER LPG LINE. |  | LINE PIPE | NO DATA |  | 1945 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 582.8971 | 1175.9389 | L. P. G. | 2 | 4 | 0 | NO | NO | 11 | 0.37 | 35000 | WELDED |  | 880 | 860 | YES | 30 | 1442 | 0 | 72 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. KINNEAR, DIVISION MANAGER | 9156877551 | LEAK OCCURRED DUE TO EXTERNAL CORROSION. WILL REPLACE APPROX. 250 FT. OF 10" PI
2017-09-29 08:50 | YES | NO | 19880161 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1988-07-22 | 1927 | KS | SHAWNEE | TOPEKA | NO |  | NO | TOWNSHIP 13 SOUTH RANGE 15 EAST SECTION 24 1.5 MILES SOUTH OF FORBES AIR FORCE BASE ON HIGHWAY 75. |  | LINE PIPE | NO DATA |  | 1960 | CORROSION | WAITING FOR REPORT | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 25795 | 23132.0468 | 46666.6818 | L. P. G. | 2 | 4000 | 0 | YES | NO | 8 | 0.22 | 2641 | WELDED |  | 1650 | 1468 | YES | 24 | 2198 | 6 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185821800
2017-09-29 08:50 | YES | NO | 19880162 |  | 11101 | LAKE CHARLES PIPELINE CO | YES | 1988-08-23 | 805 | LA | CALCASIEU |  | NO |  | NO | LAKE CHARLES PIPE LINE COMPANY TANK FARM, 1/4/MILE EAST OF THE INTERSECTION OF LA ROAD 1133 AND CLIFTON RIDGE ROAD, CALCASIEU PARISH, LOUISIANA. |  | TANK FARM | NO DATA |  | 1965 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 13451.4713 | 27137.0509 | GASOLINE | 3 | 273 | 173 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN P. HARTMAN, DISTRICT SUPERINTENDENT | 3184915092 | OPERATOR ATTEMPTED TO ACCEPT UNLEADED GASOLINE FLOW INT TANK #11 BUT FAILED TO OPEN VALVE INDENTIFIED AS #1. PUMP CAN (1) RUPTURED ALLOWING LEAK OF APPROXIMATELY 273 BARRELS. PUMP CAN #2 WAS OUT OF SERVICE AND BLINDED OFF AS SHOWN.
2017-09-29 08:50 | YES | NO | 19880163 |  | 13131 | CONOCO INC | YES | 1988-08-28 | 128 | MT | YELLOWSTONE |  | NO |  | NO | T1S, R33E, SECTION 2. MONTANA POWER COMPANY'S COAL-FIRED POWER PLANT. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1345.1471 | 2713.7051 | GASOLINE | 3 | 390 | 380 | NO | NO | 8 | 0.22 | 52000 | WELDED |  | 1900 | 1613 | YES | 0 | 0 | 0 | 62 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | LINE MARKERS | YES | YES | L.G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | APPROXIMATELY TWO DAYS BEFORE THE INCIDENT, A BACKHOE BEING USED BY A CONOCO CONTRACTOR TO DIG AROUND THE PIPE, UNINTENTIONALLY HIT THE LINE. THE LINE WAS DENTED AND SCRAPED. A HALF-SOLE WITH PIPE CLAMP WAS INSTALLED FOR SUPPORT SO THAT THE LINE COULD BE PUT BACK INTO SEVICE REPLACEMENT THE FOLLOWING WEEK. AT 1:20 AM. ON AUGUST 28, 1988, THE LINE WAS SHUT DOWN DUE TO LWO DISCHARGE PRESSURE AT THE BILLINGS STATION. THE LEAK SITE WAS DISCOVERED AT 2:40 AM. BY CONOCO FIELD PERSONNEL. 390 BARRELS OF LEADED GASOLINE WERE SPILLED INTO THE CONSTRUCTION DITCH SURROUNDING THE PIPE. ALL PRODUCT WAS CONTAINED IN THE TRENCH. 380 BARRELSWERE RECOVERED. TEMPORARY REPAIRS WERE MADE ON AUGUST 28, 1988 WITH A PRETESTED 6 FOOT SECTION OF X-52, 0.219-WALL LINE PIPE AD WELD + ENDS. THE LINE WAS PUTBACK IN SERVICE AT 4:30 PM. THE SAME DAY AT REDUCED PRESSURE. THE PIPELINE WASSHUT DOWN ON AUGUST 30, 1988 AT WHICH TIME PERMANENT REPAIRS WERE MADE.
2017-09-29 08:50 | YES | NO | 19880164 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-07-28 | 1744 | KS | BUTLER |  | NO |  | NO | ELDORADO PUMP STATION. |  | PUMPING STATION | VALVE |  | 0 | OTHER | ERROR BY CONTRACTOR PERS. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 986.4412 | 1990.0504 | GASOLINE | 3 | 225 | 225 | NO | NO | 0 |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | ON JULY 28 A 225 BARREL PRODUCT RELEASE OCCURRED AT OUR ELDORADO PUMP STATION.THE RELEASE RESULTED WHEN AN OPERATOR ON DUTY ATTEMPTED TO OPEN A MOTOR OPERATED MANIFOLD VALVE BUT, DUE TO A WIRING ERROR, ANOTHER VALVE OPENED INSTEAD. THE INCORRECT WIRING HAD ALSO DISABLED THE VALVE CLOSE CIRCUITRY SO THE VALVE HAD TOBE MANUALLY CLOSED. DUE TO THE GEAR RATIO IN THE MANUAL OVERRIDE ON THE MOTOR OPERTOR, SEVERAL HUNDRED TURNS (REQUIRING SEVERAL MINUTES) WERER NECESSARY TO COMPLETELY CLOSE THE VALVE. FURTHER INVESTIGATION REVEALED THAT AN ELECTRICAL CONTRCTOR, SUBCONTRACTING ON A MANIFOLD UPGRADE PROJECT HAD INAPPROPRIATELY CONNECTED THE VALVE CIRCUITRY DURING THE PREVIOUS WEEK. MEASURES HAVE BEEN TAKEN TO REAFFIRM APPLICABLE SAFETY POLICIES BOTH FOR CONTRACTORS AND COMPANY PERSONNEL. THE ENTIRE RELEASE WAS CONTAINED ON SITE AND HAS BEEN FULLY RECOVERED.
2017-09-29 08:50 | YES | NO | 19880165 |  | 18095 | SAN JUAN PIPELINE | NO | 1988-07-25 | 0 | NM | SAN JUAN |  | NO |  | YES | 5 1/2 MILES SOUTH OF BLOOMFIELD, NM AND 1 MILE WEST OF HIGHWAY 44. |  | LINE PIPE | NO DATA |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8967.6475 | 18091.3673 | CRUDE OIL | 3 | 651 | 11 | NO | NO | 6 | 0.19 | 1490 | WELDED |  | 1440 | 200 | YES | 24 | 1000 | 0 | 78 | EXTERNAL | Null | YES | OTHER | SOIL CORROSION | NO DATA |  | Null | OTHER | RT-OF-WAY MARKERS | NO | NO | ROBERT E. MCCOY, OPERATOR | 5053276205 | NO REMARKS GIVEN.
2017-09-29 08:50 | YES | NO | 19880167 |  | 443 | AMOCO PIPELINE CO | YES | 1988-08-27 | 1900 | TN | GILES | PULASKI | NO |  | NO | THREE MILES SOUTH OF PULASKI, TENNESSEE ON HWY 11. |  | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 44838.2377 | 90456.8363 | XYLENE | 3 | 740 | 719 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1440 | 390 | YES | 24 | 1970 | 0 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R.A. STAHL - AREA MANAGER | 2197382384 | LANDOWNER HAD HIRED CONTRACTOR TO STRAIGHTEN OUT A CROOK IN THE CREEK AND WHILETHERE, DIG A LOW SPOT TO HOLD DRINKING WATER FOR THE LANDOWNERS CATTLE. CONTRACTOR BEGAN WORK WITHOUT NOTIFYING AMOCO AND WITHIN MINUTES HAD RUPTURED THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19880168 |  | 18273 | SHELL PIPE LINE CORP | NO | 1988-08-22 | 1300 | TX | UPTON | MCCAMEY | NO |  | NO | NE 1/4, NE 1/4, SECTION 12, BLOCK 6, TEN MILES NORTH OF MCCAMEY HENDRICK-BARNSLEY 10". |  | LINE PIPE | PIPE |  | 1936 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1345.1471 | 2713.7051 | CRUDE OIL | 1 | 150 | 95 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 900 | 200 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19880169 |  | 3012 | D - S PIPELINE CORP | NO | 1988-08-19 | 1700 | TX | KING |  | NO |  | NO | SECTION 2, GC&SF RR CO. SURVEY, KING COUNTY, TX 13 MILES WEST ON US 82/STATE 114 AND 5 MILES NORTH OF THE CITY OF BENJAMIN, TX. |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 34000 | 30490.0016 | 61510.6487 | CRUDE OIL | 1 | 2000 | 0 | NO | NO | 10.5 | 0.37 | 25000 | WELDED |  | 800 | 450 | YES | 24 | 1000 | 6 | 73 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS, MANAGER, PIPELINE SAFETY & REGULATIONS | 8063783583 | AT APPROXIMATELY 1700 HOURS ON AUGUST 19, 1988, OUR TEXAS PLAINS 10" PIPELINE DEVELOPED A CORROSION LEAK ALLOWING 2000 BARRELS OF CRUDE OIL TO ESCAPE. THE LEAK OCCURRED 5 MILES NORTH OF OUR BENJAMIN STATION IN A REMOTE AREA. THE SPILLED CRUDE OIL DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19880171 |  | 809 | ARCO PIPE LINE CO | YES | 1988-08-17 | 945 | TX | TARRANT |  | NO |  | NO | IN CITY LIMITS OF ARLINGTON, TEXAS BETWEEN GREEN OAKS AND THE TRINITY RIVER. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 156933.8319 | 316598.927 | GASOLINE | 3 | 1455 | 34 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 450 | 50 | YES | 0 | 1155 | 1 | 56 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | V.P. DRISKI - MANAGER - SOUTHERN AREA OPERTIONS | 3163311300 | LINE WAS STRUCK BY A CONTRACTOR OPERATING A MOTOR GRADER TOTAL OF 1455 BARRELS WERE OUT - 34 RECOVERED.
2017-09-29 08:50 | YES | NO | 19880172 |  | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1988-09-04 | 1150 | CA | MERCED |  | NO |  | Null | SEC. 19, 511S, R10E, MDB&M, SALT CREEK AREA, APPROX. 2 MILES WEST OF INTERSTATE 5. |  | LINE PIPE | NO DATA |  | 1967 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17935.2951 | 36182.7345 | CRUDE OIL | 1 | 4000 | 3700 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 936 | 1000 | Null | 0 | 0 | 3 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. W. PENNE , DISTRICT MANAGER | 8053270110 | THE LEAK OCCURRED IN A PERIOD OF TRANSITION FROM ONE UNIT PER STATION OPERATIONTO TWO UNITS PER STATION.A UNIT AT GUSTINE HAD A MECHANICAL FAILURE APPROXIMATELY 9:48 AND A MECHANIC WAS SERVICING THE LUBE OIL PUMP TO BRING THE UNIT BACK ONLINE. WITH TWO UNITS RUNNING AT LOS BANOS AND WESTLY STATIONS,SECOND UNITS WERESTARTED AT TRACY AND GUSTINE AT APPROXIMATELY 11:24. THE GUSTINE UNIT FAILED TO STAY ON LINE AND SUBSEQUENTLY TRIPPED WESTLY STATION OFF-LINE ON LOW SUCTION PRESSURE FOLLOWED BY BOTH UNITS AT TRACY STATION. THE COMPOUNDED REVERSE FLOW SURGE MET THE HIGH DISCHARGE PRESSURE AT LOS BANOS STATION AND RUPTURED THE PIPELINE AT A WEAKEND PIPE WALL LOCATION.
2017-09-29 08:50 | YES | NO | 19880173 |  | 14295 | OLYMPIC PIPE LINE CO | YES | 1988-08-30 | 2330 | WA | SKAGIT |  | NO |  | NO | IMMEDIATELY NORTH OF STATE HWY. 20, 5 MILES EAST OF ANOCORTES & 3.5 MILES WEST OF BURLINGTON AT ALLEN PIPELINE PUMP STATION YARD. |  | LINE PIPE | PIPE |  | 1965 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 162000 | 145275.8901 | 293080.1496 | DIESEL FUEL | 3 | 3250 | 1200 | NO | NO | 16 | 0.31 | 2028 | WELDED |  | 1440 | 1440 | YES | 24 | 1825 | 0 | 65 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C. MORRIS, JR., VICE PRESIDENT | 2146582215 | 16" MAIN LINE PIPE RUPTURE OCCURRED IN PUMP STATION YARD APPROXIMATELY 30 FT. DOWNSTREAM OF SCRAPER TRAP ON DISCHARGE SIDE OF MAIN LINE PUMPS. PRESSURE ON DISCHARGE WAS RECORDED AT 1440 PSI AND HAD BEEN STEADY. NO UPSETTING CONDITIONS ARE KNOWN. STATION WAS UNMANNED AT THE TIME. RUPTURE WAS ON TOP OF PIPE AND CONSISTED OF A LATERAL TEAR APPROXIMATELY 40" LONG AND 4-5" WIDE. DIESEL FUEL SATURATED 1 ACRE IN STATION YARD, INCLUDING CONTROL BUILDING AND ELECTRICAL SUBSTATION. ADJACENT FARM PROPERTIES WERE DAMAGED WITH FUEL ENCROACHMENT WHICH MAY BE APPROXIMATELY ONE ACRE. MAJORITY OF SPILLED DIESEL WAS CONTAINED IN DITCHED AREA ADJACENT TO PUMP STATION.PIPELINE STATION SHUTDOWN AUTOMATICALLY ON LOW SUCTION PRESSURE, MINIMIZING PRODUCT LOSS. THE DAMAGED PIPE WAS REMOVED FROM THE PIPELINEAND REPLACED WITH A NEW SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19880174 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-09-13 | 1125 | TX | ECTOR | PENWELL | NO |  | Null | SEC.-1, BLK. 44, T&P - GO WEST ON *-20 TO PENWELL TAKE SERVICE RD. WEST TO TEXACO FIELD OFFICE TURN SOUTH AT OFFICE GO TO CHEVRON PIPE LINE STATION LEAK IN FIRE |  | LINE PIPE | NO DATA |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 403.5441 | 814.1115 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 4 | 0.24 | 35000 | WELDED |  | 600 | 8 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. KINNEAR, DIVISION MANAGER | 9156877551 | LEAK ON THE 4" DISCHARGE LINE FROM THE KINNEY PUMP. EXTERNAL CORROSION WAS THE C AUSE OF TEH LEAK. THE OIL WAS RECOVERED WITH VACUUM TRUCK.
2017-09-29 08:50 | YES | NO | 19880175 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-09-23 | 1500 | TX | WARD |  | NO |  | NO | APPROXMATELY MP 214 ONYATES TO WINK CRUDE T/L, SECTION 6, BLOCK 0, G&MMB&A SURVEY, APPROX. 2 MILES SOUTH OF I-2 SOUTH OF WICKETT, TX . |  | LINE PIPE | NO DATA |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1345.1471 | 2713.7051 | CRUDE OIL | 1 | 2768 | 2660 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1120 | 400 | YES | 24 | 1465 | 8 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | R.C. KINNEAR , DIVISION MANAGER | 9156877551 | CHEVRON'S 10" YATES TO WINK CRUDE TRUNK LINE WAS HIT BY CHEVRON'S USA PRODUCTION CONTRACTOR DITCHING MACHINE. SPILLED OIL WAS HAULED TO MONAHANS STATION.
2017-09-29 08:50 | YES | NO | 19880176 |  | 443 | AMOCO PIPELINE CO | NO | 1988-09-09 | 1021 | TX | BRAZORIA | ANGLETON | NO |  | NO | NW OF INTERSECTION OF HENDERSON RD. AND HWY 35. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 717.4118 | 1447.3094 | NATURAL GAS LIQUID | 2 | 285 | 0 | NO | NO | 4 | 0.3 |  | WELDED |  | 400 | 200 | YES | 24 | 1260 | 11 | 86 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MICHAEL P. CLANG, PIPELINE MAINTENANCE FOREMAN | 7133322476 | LINE WAS IN OPEN FIELD. A BRUSH HOG WAS IN OPERATION MOWING WEEDS. BRUSH HOG HIT EXPOSED LINE CAUSING RUPTURE. OPERATOR WAS ABLE TO MOVE EQUIPMENT TO SAFE LOCATION WITHOUT ISO-BUTANE VAPOR IGNITING.
2017-09-29 08:50 | YES | NO | 19880177 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-08-23 | 1445 | MN | HENNEPIN |  | NO |  | NO | MP 12+33 - NEAR FORT SNELLING STATE PARK T28N-R23W-SEC. 32. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | FROSTHEAVE | NATURAL FORCE DAMAGE | TEMPERATURE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 89676.4754 | 180913.6726 | JET FUEL | 3 | 136 | 80 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 850 | 0 | YES | 8 | 2125 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | FROSTHEAVE |  | Null | OTHER | LINE MARKERS | Null | Null | H.E. JANZEN , VICE PRESIDENT - OPERATIONS | 9185884850 | ON AUGUST 23, A LEAK WAS DISCOVERED ON OUR #7-8" ROSEMOUNT TO MINNEAPOLIS AIRPORT PIPELINE. THE LEAK OCCURRED AT MP 12+33 NEAR FORT SNELLING STATE PARK. FURTHER INVESTIGATION REVEALED THAT THE LINE, WHICH WAS 12-15' DEEP, HAD BEEN DENTEDAND CREASED BY A LARGE PIECE OF CONCRETE RUBBLE. IT IS THOUGHT THAT THE AIRPORT HAD DUMPED MISCELLANEOUS FILL MATERIAL IN THE AREA BACK IN THE 1970'S. THE EXACT CAUSE AND TIME OF THE LEAK IS STILL UNKNOWN AS OF THIS DATE. SINCE THE AREAIS RELATIVELY MARSHY, IT IS SPECULATED THAT SOIL MOVEMENT FROM REPETITIVE FROST ACTION COULD HAVE PUSHED THE PIPELINE AGAINST THE CONCRETE RUBBLE,THEREBY CAUSING THE DAMAGE. CONVERSATIONS WITH OTHER LOCAL UTILITIES (WATER, SEWER) WHO HAVE LINE IN THE AREA LEND SUPPORT TO THIS THEORY. APPROXIMATELY 20' OF NEW LINE WAS INSTALLED AND BACKFILLED WITH SAND. CLEANUP OPERATIONS ARE BEING COORDINATEDWITH STATE OFFICIALS.
2017-09-29 08:50 | YES | NO | 19880178 |  | 26134 | MOBIL OIL CORP - WEST COAST PIPELINES | NO | 1988-09-10 | 408 | CA | LOS ANGELES | ENCINO | NO |  | NO | M-70 PIPELINE, WOODLEY AVENUE AND VENTRUA BLVD. IN ENCINO. CALIFORNIA. ST 3211+53 4A-633. |  | LINE PIPE | PIPE |  | 1977 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1345147.1305 | 2713705.0886 | CRUDE OIL | 1 | 3155 | 2861 | NO | NO | 12 | 0.25 | 2039 | WELDED |  | 1440 | 1043 | YES | 8 | 1830 | 10 | 81 | EXTERNAL | Null | YES | OTHER | COATING DAMAGE SHIELDING | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. ROLLINS | 2133282550 | AN ANOMALY WAS FIRST OBSERVED BY THE TORRANCE CONTROL CENTER AT 4:08 AM. WHEN ALARMS FROM SATICOY PUMP STATION REGISTERED ON THE CONTROL CONSOLE. THE CONTROL CENTER OPERATOR IMMEDIATELY SHUT DOWN THIS SECTION OF THE PIPELINE AND VERIFIED THE CONSOLE READINGS WITH THE SATICOY STATION OPERATOR. BASED ON THE INITIAL ALARMS INDICATING A POTENTIAL PROBLEM BETWEEN NEWHALL AND SATICOY STATIONS, THE CONTROL CENTER OPERATOR DIVERTED THE STREAM INTO STATION, DOWNSTREAM OF THE LEAK SITE, IN AN ATTEMPT TO MINIMIZE THE AMOUNT OF OIL LEAVING THE PIPELINE. AFTER CONFIRMATION,THE STATION OPERATOR WAS DISPATCHED NORTH TO PATROL THE PIPE RIGHT-OF-WAY IN SEARCH OF THE LEAK. SATICOY SHUT DOWN ON LOW SUCTION PRESSURE AT 4:24 AM. AT APPROXIMATELY 5:00 AM, THE STATION OPERATOR HEARD OF A MAJOR LEAK AT THE INTERSECTION OF WOODLEY AVENUE AND VENTURA BLVD. ON THE RADIO AND RESPONDED IMMEDIATELY. REPAIR AND CLEANUP CREWS WERE DISPATCHED AT THE SAME TIME. INSPECTION OF THE LEAK SITE REVEALED THAT THE 12" PIPELINE WAS IN CONTACT WITH A 30" STEEL WATER LINE. THE CONTACT WITH THE WATER LINE CAUSED LOCALIZED CORROSION ON THE 12" PIPELINE. THE AFFECTED AREA WAS 4" X 20" WITH A 5" LONG BREAK LOCATED IN THE CENTER. THE LEAK WAS REPAIRED BY REPLACING THE SECTION OF THE PIPE WITH NEW LINE PIPE. TO PREVENT CONTACT WITH THE WATER LINE, OFFSETS WERE INSTALLED IN THE NEW SECTION OF LINE PIPE. APPROXIMATELY 400 BARRELS OF CRUDE OIL, WHICH LEAKED FROM THE PIPELINE, FLOWED INTO STORM DRAINS AND SUBSEQUENTLY INTO THE LOS ANGELES RIVER. SPILL BOOMS WERE PLACED IN THE RIVER AT 8 LOCATIONS FROM LOS FELIZ BLVD TOWILLOW ST IN LONG BEACH. THE CRUDE IN THE RIVER WAS FULLY CONTAINED AND NONE REACHED THE LONG BEACH HARBOR CHANNEL. THE REMAINING CRUDE OIL WAS PICKED UP WITH VACUUM TRUCKS.
2017-09-29 08:50 | YES | NO | 19880179 |  | 12628 | MOBIL PIPELINE CO | NO | 1988-09-03 | 930 | TX | NUECES |  | NO |  | NO | F.Z. BISHOP SUBDIVISION OF THE WEIL RANCH, SECTION 152 (APPROXIMATELY 1/2 MILE NE FM RD. 70). |  | LINE PIPE | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3200 | 2869.6472 | 5789.2375 | GASOLINE | 3 | 112 | 0 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 780 | 150 | YES | 2 | 858 | 9 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | THE LEAK DEVELOPED FROM AN ISOLATED CORROSION PIT WHICH PENETRATED THE WALL OF THE PIPE. THE PIT WAS IN A PLACE WHERE THE COATING HAD BEEN DAMAGED DURING INSTALLATION OF A 2" FLOW LINE CROSSING OUR PIPELINE FROM A NEARBY WELL. MPLCO. WASNOT NOTIFIED THAT THE CROSSING WAS BEING MADE. THE LEAK WAS REPAIRED BY WELDING TWO FULL ENCIRCLEMENT WRAPS TO THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19880180 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1988-09-16 | 45 | TX | EL PASO | EL PASO | NO |  | NO | SOUTHERN PACIFIC PIPE LINES' EL PASO STATION IN EL PASO, TEXAS. |  | PUMPING STATION | VALVE |  | 1966 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TURBINE FUEL | 3 | 131 | 9 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BARRY R. PEARL, VICE PRESIDENT-OPERATIONS | 2134867860 | PIECES OF ROCK FOUND IN THE FULL-FLOW RELEIF VALVE CAUSED THE SURGE TANK TO OVERFLOW. A VALVE UPSTREAM OF THE RELIEF VALVE WAS CLOSED AND PIPELINE WAS SHUT DOWN. CLEANUP WAS IMMEDIATELY STARTED.
2017-09-29 08:50 | NO | NO | 19880181 |  | 18718 | SUN PIPELINE CO | YES | 1988-09-29 | 1045 | OK | PITTSBURG | RURAL | NO |  | YES | SOUTHWEST 1/4/SECTION 29, TOWNSHIP 7 NORTH, RANGE 16 EAST, PITTSBURG COUNTY, OK. LEAK LOCATED UNDER THE WATERS OF LAKE EUFAULA. |  | LINE PIPE | PIPE |  | 1954 | OTHER | DAMAGE TO PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 44838.2377 | 90456.8363 | DIESEL FUEL | 1 | 3 | 3 | NO | NO | 12 | 0.38 |  | WELDED |  | 1200 | 280 | YES | 24 | 1500 | 0 | 54 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | DONALD G. MEARS, AREA MANAGER, ENVIRONMENTAL, SAFETY&HEALTH | 9185866942 | AT 1045 HOURS SEPTEMBER 29, 1988, CONTRACT AIR PATROL REPORTED A SHEEN ON THE WATER OF LAKE EUFAULA DIRECTLY OVER SUN PIPE LINE'S LINE. CENTRAL CONTROL IN TULSA SHUT THE LINE DOWN AND PERSONNEL WERE DISPATCHED TO CHECK THE PROBLEM. THE UPSTREAM VALVE WAS CLOSED BY RESPONSE PERSONNEL ON THE WAY TO THE SITE. A VALVE AND CHECK VALVE ARE LOCATED APPROXIMATELY ONE HALF MILE EAST OF THE LEAK SITE. THIS VALVE WAS ALSO CLOSED. IT WAS DETERMINED THAT THERE WAS AN APPARENT PINHOLELEAK LOCATED APPROXIMATELY 75' OFFSHORE IN A SMALL COVE. WATER DEPTH WAS 8'.SPILL BOOMS ALONG WITH ABSORBENT BOOMS WERE PLACED ACROSS THE MOUTH OF THE COVETO CONTAIN ANY LEAKAGE UNTIL THE LINE COULD BE REPAIRED. EXCAVATION USING DIVERS AND WATER JETTING WAS UNSUCCESSFUL IN REMOVING OVERBURDEN FROM THE LINE. A DRAG LINE WAS USED TO REMOVE COVER DOWN TO THE LINE AND THEN THE DIVERS WERE ABLE TO REMOVE THE REST BY WATER JET. THE PINHOLE LEAK WAS STOPPED INITIALLY BY USING A SHARPENED WOOD STICK, THEN A PLIDCO SPLIT SLEEVE WAS INSTALLED OVER THE LEAK AND SECURED BY USING AIR WRENCHES. LINE PRESSURE BETWEEN THE NEAREST VALVES WAS INCREASED TO 400 PSI. TO CHECK FOR LEAKAGE USING WATER INJECTED AT A TAP PLACED ON THE LINE ONSHORE DOWNSTREAM OF THE LEAK SITE. WHEN THERE WAS NO EVIDENCE OF LEAKAGE, ALL VALVES WERE REOPENED AND THE LINE PRESSURED FROM ALLEN, OKLAHOMATO FT. SMITH, ARKANSAS. WHEN ALL INDICATORS APPEARED NORMAL, PUMPING WAS RESUMED AT NORMAL PRESSURES AND RATES. A PRESSURE GAUGE INSTALLED AT THE TAP INDICATED 280 PSI AT THE LEAK SITE. TEMPORARY REPAIRS WERE COMPLETED ON OCTOBER 4. CLEANUP AND REMOVAL OF SPILL BOOMS CONTINUED UNTIL OCTOBER 6. PERMENANT REPAIR PLANS ARE INCOMPLETE. CONTAINMENT AND CLEANUP COSTS WERE HIGHER THAN NORMAL DUE TO THENECESSITY TO PROTECT THE LAKE WATERS AND PREVENT FUEL FROM ENTERING POTABLE WATER INTAKES ON PRIVATE WATER SYSTEMS NEAR THE SITE. EXTENSIVE TESTING OF WATER ATTHESE INTAKES AND OUTTAKES AT THE TREATMENT SYSTEMS INDICATED NO ABNORMAL LEVELSOF HYDROCARBONS OR OTHER CHEMICALS WHICH WOULD HAVE BEEN ATTRIBUTED TO THE SPILL
2017-09-29 08:50 | YES | NO | 19880182 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-09-30 | 1145 | IA | HARDIN |  | NO |  | NO | ALDEN STATION (#651). |  | PUMPING STATION | VALVE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6277.3533 | 12663.9571 | FUEL OIL | 3 | 275 | 266 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT-OPERATIONS | 9185884850 | THE LOCAL MAINTENANCE CREW WAS IN THE PROCESS OF REPLACING THE VALVE BOX FOR THE BELOW GRADE FIRE VALVE AT THE ALDEN PUMP STATION. WHILE LIFTING THE OLD VALVEBOX OUT OF THE GROUND ONE OF THE SMALL (2") DRAIN VALVES LOCATED ON THE PIPE ADJACENT TO THE FIRE VALVE WAS ACCIDENTLY STRUCK BY THE BACKHOE. THE RESULTING IMPACT BROKE THE THREADED NIPPLE AND CONSEQUENTLY CAUSED THE PRODUCTS RELEASE. THE LINE WAS NOT RUNNING AT THE TIME BUT WAS PRESSURED TO APPROXIMATELY 30 PSI. THE VALVE WAS REPLACED AND THE NEW VALVE BOX WAS INSTALLED. CLEANUP EFFORTS HAVE BEEN COORDINATED WITH THE IOWA DWNR.
2017-09-29 08:50 | YES | NO | 19880183 |  | 300 | ALL AMERICAN PIPELINE CO | YES | 1988-09-29 | 1322 | AZ | COCHISE |  | NO |  | NO | ALL AMERICAN PIPELINE'S HOT SPRINGS STATION, SECTION 3, TOWNSHIP 13-S, RANGE 21-E IN COCHISE COUNTY, ARIZOA. |  | PUMPING STATION | SCRAPER TRAP |  | 1987 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 2750 | 2466.1031 | 4975.126 | CRUDE OIL | 1 | 100 | 0 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H. D. HORTON, MANAGER, REGULATORY COMPLIANCE | 8053985330 | A TECHNICIAN REQUESTED THAT THE LAUNCHER VALVES BE CYCLED REMOTELY BY THE OPERATOR FOR A ROUTINE CHECK. THE LAUNCHER BARREL HAD BEEN LEFT DE-PRESSURIZED AND THE 4" DRAIN VALVE ON THE BARREL HAD BEEN LEFT PARTIALLY OPEN. IT TOOK SEVEN MINUTES AND TWELVE SECONDS FOR THE VALVES TO COMPLETELY CYCLE OPEN AND BACK CLOSED,ALLOWING APPROXIMATELY 100 BARRELS OF CRUDE OIL TO ESCAPE THROUGH THE 4" DRAIN VALVE.
2017-09-29 08:50 | YES | YES | 19880184 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-10-11 | 945 | TX | MARTIN |  | NO |  | NO | APPROX. 4 1/2 MI. S.E. OF STANTON, TX APPROX. 2 MI. S. OF I-20 & 4 MI. EAST OF STATE ROAD 137. (SEE ATTACHMENT "A" MAP) SEC. 28, BLOCK 35, T-1-S, T&0 RAILROAD S |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 1 | 1 | 0 | 0 | 0 | 0 | 46500 | 41699.561 | 84124.8577 | L. P. G. | 2 | 1824 | 0 | YES | YES | 10 | 0.25 | 42000 | WELDED |  | 1097 | 933 | YES | 24 | 1372 | 11 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. KINNEAR - DIVISION MANAGER | 9156877551 | ON OCTOBER 11, 1988, AT 9:45 HRS., A LANDOWNER, MR. PAUL HOPPER CALLED THE CHEVRON PIPE LINE (CPL) COMPANY HOUSTON DISTRIBUTION CENTER (HDC) TO REPORT AN APPARENT LPG LEAK IN THE AREA OF CPL'S RIGHT-OF-WAY. HDC NOTIFIED THE OPERATIONS SUPERVISOR FOR THE AREA. PIPE LINE PRESSURES WERE REDUCED ( THERE ARE TWO 10 INCH LPG LINES IN THAT RIGHT-OF-WAY) AND THE MAINTENANCE SUPERVISOR WAS CONTACTED. THE LEAK WAS INVESTIGATED AND CONFIRMED AT APPROXIMATELY 11:40 HRS. TO BE ON THE # 1-10 " LPG LINE, MIDLAND TO COAHOMA, TX SEGMENT (38.58 MILES) AT MILE POST(MP) 186.157; APPROXIMATELY 4.5 MILES SOUTHEAST OF STANTON,TX (SEE ATTACHMENT "A"). THE LINE WAS SHUTDOWN.INITIAL EXCAVATION OF A BELL HOLE WAS STARTED TO ASSESS WHETHER A TEMPORARY REPAIR COULD BE MADE OR PERMAENT REPAIRS WOULD BE REQUIRED. IT WAS DETERMINED THAT A TEMPORARY REPAIR COULD NOT BE MADE. THE PLAN WASTO PURGE THE PIPELINE WITH NITROGEN INJECTED BEHIND A 4 CUP SWAB AT MP 193.634 AND DISPLACE TO THE BLOCK VALVE AT MP 182.570 ( APPROXIMATELY A 10-MILE SECTION). THE PLAN WAS IMPLEMENTED,NITROGEN ORDERED AND PREPARATIONS OF THE LINE WERE STARTED FOR THE DISPLACEMENT. THE BACKHOE OPERTOR WAS TO EXCAVATE AND EXPOSE THE LINE EASTERLY AND WESTERLY TO A POINT WHERE THE NEW PIPE COULD BE WELDED INTO THE EXISTING PIPELINE. THE BACKHOE OPERATOR STARTED, APPROXIMATELY 26 FEET EASTOF THE LEAK, DOUBLE DITCHING ALONG THE LINE EXPOSING 55 FEET OF PIPE. THE OPERATOR THEN MOVED THE BACKHOE TO A POINT APPROXIMATELY 33 FEET WEST OF THE LEAK TO DUPLICATE THE PIPELINE EXPOSURE AND STRIPPING. SHORTLY AFTER COMMENCING WORK (2 TO 3 BUCKETS FULL) THE OPERATORLIFTED THE BUCKET AND OUTRIGGER PADS SUFFICIENTLYENOUGH TO MOVE AND PROCEEDED TO A POINT APPROXIMATELY 132 FEET WEST OF THE LEAK.IT WAS AT THIS TIM, APPROX. 15:55, A WITNESS REPORTED TO HEAR THE ENGINE OF THEBACKHOE BEGIN TO "REV", WHICH THE WITNESS BELIEVED TO BE THE SOUND OF NORMAL ACCELERATION AND NOT OF T\AN ENGINE BEGINNING TO RUN AWAY. WITNESSES THEN REPORTEDTHAT THERE WAS AN EXPLOSION AND FIRE. THE OPERATOR, BACKHOEAND THE AREAS SURROUNDING THE LEAK WERE ENGULFED IN FLAMES. SHORTLY AFTER IGNITION, THE FIRE WAS LIMITED TO THE LEAK AREA APPROX. 30 FEET IN DIAMETER. THE FIRE WAS MONITORED AND ALLOWED TO BURN AND WHEN THE SWAB AND NITROGEN WHICH HAD BEEN INJECTED PASED THE LEAK SITE, THE FIRE IMMEDIATELY SUBSIDED. THE LPG SATURATED SOIL WAS ALLOWED TO BURN SEVERAL HOURS TO ENSURE ELIMINATION OF ALL LPG VAPORS IN THE AREA AND THE POTENTIAL OF A FLASHBACK. WATER FURNISHED BY VACUUM TRUCKS AND WITH THE ASSISTANCEOF THE LOCAL VOLUNTEER FIRE DEPT. THE REMAINING GROUND FIRES WERE EXTINGUISHED AAND THE ENTIRE AREA SATURATED WITH WATER. THE OPERATOR PASSED AWAY AT 22:10, 10/12/88, FROM COMPLICATIONS RESULTING FROM BURNS RECEIVED.
2017-09-29 08:50 | YES | NO | 19880185 |  | 13131 | CONOCO INC | YES | 1988-10-05 | 1438 | OK | COTTON |  | NO |  | NO | CONOCO PIPE LINE CO. 8" PETROLEUM PIPELINE IN COTTON COUNTY, OK (SEE ATTACHED MAP) T2S R9W WEST BOUNDARY OF SECTION 4. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8967.6475 | 18091.3673 | GASOLINE | 1 | 500 | 300 | NO | NO | 8 | 0.16 | 52000 | WELDED |  | 1354 | 190 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | L.G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | COTTON COUNTY ROAD GRADER WAS DEEPENING THE CHANNEL IN THE BAR DITCH WHEN HA STRUCK AND RUPTURED OUR PIPELINE.
2017-09-29 08:50 | YES | NO | 19880186 |  | 13131 | CONOCO INC | Null | 1988-11-01 | 1915 | CO | WELD |  | NO |  | NO |  |  | PUMPING STATION | NO DATA |  | 1980 | OTHER | 1" LINE ON PUMP BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2690.2943 | 5427.4102 | CRUDE OIL | 1 | 200 | 155 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | AT APPROXIMATELY 1915 HOURS ON 11/1/88, OIL MOVEMENTS IN HOUSTON RECEIVED A DEVIATION (INCREASE) IN PUMPING RATE WHICH ALERTED THE OPERATIONS COORDINATOR OF A PROBLEM. HE IMMEDIATELY SHUT THE PUMP STATION DOWN. FIELD PERSONNEL WERE CALLED OUT AND CLEAN UP PROCEDURES WERE IMPLEMENTED.
2017-09-29 08:50 | YES | NO | 19880187 |  | 809 | ARCO PIPE LINE CO | YES | 1988-10-13 | 730 | KS | MONTGOMERY |  | NO |  | NO | 1/2 MILE NORTH OF U.S. HWY 166 - 1 MILE E OF INTERSECTION WITH U.S. 75. |  | TANK FARM | VALVE |  | 0 | OTHER | TANK VALVE CRACKED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6277.3533 | 12663.9571 | CRUDE OIL | 1 | 3300 | 3000 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.D. HARRIS, MANAGER-NORTHERN AAREA OPERATIONS | 3163311300 | TANK VALVE SPLIT ON TANK LEASED TO KOCH OIL.OIL DRAINED FROM TANK INTO TANK DIKEAND WAS CONTAINED THERE. ESTIMATED 3300 BARRELS OUT, 3000 RECOVERED BY TANK TRUCK.
2017-09-29 08:50 | YES | NO | 19880188 |  | 2552 | COLONIAL PIPELINE CO | YES | 1988-10-13 | 2049 | GA | COBB | POWDER SPRINGS | NO |  | NO | 4458 SHILOH TRAIL, LOST MOUNTAIN ESTATES SUBDIVISION POWDER SPRINGS, GA. (SEE ATTACHED MAP). |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 224191.1884 | 452284.1814 | DIESEL FUEL | 1 | 644 | 288 | NO | NO | 12 | 0.22 | 52000 | WELDED |  | 1286 | 1120 | YES | 24 | 1440 | 0 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES A. COX - TECHNICAL AND REGULATORY MANAGER | 4048412296 | AN ESTIMATED 644 BARRELS OF DIESEL FUEL ESCAPED FROM COLONIAL'S LINE NO. 19 WHEN THE PIPELINE RUPTURED AT 8:49 PM. EDT, OCTOBER 13, 1988. THE ACCIDENT OCCURRED IN 12-3/4" OD, . 219" W.T., GRADE X52 LINE PIPE APPROXIMATELY SIX MILES DOWNSTREAM OF ATLANTA JUNCTION AT 4458 SHILOH TRAIL IN THE LOST MOUNTAIN ESTATES SUBDIVISION IN POWDER SPRINGS, GEORGIA. AN ADJACENT LANDOWNER CALLED COLONIAL'S CONTROL CENTER, AND SIMULTANEOUSLY THE ATLANTA JUNCTION ORIGINATING PUMPS WERE AUTOMATICALLY SHUTTING DOWN ON LOW SUCTION. COBB COUNTY FIRE AND POLICE PERSONNEL,AND COLONIAL RESPONSE AND MAINTENANCE PERSONNEL RESPONDED. RESIDENTS WERE EVACUATED FROM HOMES IN A THREE-BLOCK AREA AROUND THE LEAK SITE.AT APPROX. 12:30,EDT,ON OCT. 14, THE LINE AT THE LEAK SITE WAS EXCAVATED AND FOUND TO CONTAIN A RUPTURE 31 INCHES LONG AND 2-1/2 INCHES WIDE AT THE MAXIMUM OPENING. THE FRACTURE APPEARED TO HAVE ORIGINATED IN ONE OF SEVERAL GOUGES WHICH WERE THE RESULT OF THIRD PARTY,HEAVY EQUIPMENT DAMAGE. THIS DAMAGE, IN ADDITION TO THE GOUGES, APPEARED TO HAVE SEVERELY FLATTENED THE PIPE AND REMOVED APPROXIMATELY 8 FEET OF COATING. EIGHTEEN FEET OF PIPE CONTAINING THE RUPTURE AND THIRD-PARTY DAMAGE WERE REMOVED FROM THE PIPELINE AND REPLACED WITH 12-3/4" OD, .250" W.T., GRADE X52, HYDROSTATICALLY TESTED PIPE. THE TIE-IN WELDS WERE REDIOGRAPHED. SERVICE WAS RESTORED ON THE LINE AT 3:16 PM. EDT, ON OCTOBER 14. ENVIRONMANTAL RESTORATION WORK IS STILL IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19880189 |  | 2731 | CHEVRON PIPELINE CO | NO | 1988-10-17 | 1010 | TX | EASTLAND |  | NO |  | NO | EASTLAND CO MAP ATTACHED. |  | LINE PIPE | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4483.8238 | 9045.6836 | DIESEL FUEL | 1 | 300 | 281 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 450 | 0 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | ONE CALL |  | YES | YES | A.E. SMITH , DIVISION MANAGER | 4098393130 | WHILE DISPLACING THE RANGER TO EASTLAND LINE WITH NITROGEN TO ALLOW FOR SAFE CUT OUTS ON THIS SEGMENT. A CORROSION LEAK OCCURRED AT M.P. 11.17 ON OUR RIGHT OF WAY. A CONTRACT INPECTOR WORKING CHEVRON PIPELINE CO. WAS CHECKING CUT OUT LOCATIONS THAT HAD ALREADY BEEN EXCAVATED AND SAW THE LEAK WITHIN 5 MIN. OF OCCURANCE. WE NOTICED A DECREASE INFLOW ALSO AND WERE PREPARING THE SHUT DOWN THE DISPLACEMENT PRODECURE WHEN WE RECEIVED NOTIFICATION OF THE LEAK. CUT OUTS ON THE ENTIRE SEGMENT WERE ALREADY PLANNED AND WILL BE COMPLETED BY 10-21-88. A TEMPORARY PATCH WAS INSTALLED UNTIL PERMANENT REPAIRS ARE MADE. THE RECOVERED PRODUCTHAS BEEN RETURN TO STORAGE.
2017-09-29 08:50 | YES | NO | 19880190 |  | 18194 | SEMINOLE PIPELINE CO | NO | 1988-09-19 | 56 | TX | BRAZOS |  | NO |  | NO | THOMAS YATES SURVEY A-247. |  | NO DATA | WELDING FITTING |  | 1985 | OTHER | HYDROGEN STRESS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6824 | 6119.5227 | 12345.549 | NATURAL GAS LIQUID | 2 | 214 | 0 | YES | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | WHILE EXCAVATING AROUND A BURIED VALVE TO REPAIRE A PREVIOUSLY DISOVERED PINHOLE LEAK, THE BACKHOE STRUCK AN OBJECT, PROBABLY A ROCK, CAUSING A SPARK WHICH IGNITED THE PRODUCT THAT SATURATED THE SURROUNDING DIRT.
2017-09-29 08:50 | YES | NO | 19880191 |  | 443 | AMOCO PIPELINE CO | YES | 1988-10-21 | 530 | WY | GOSHEN | FT. LARAMIE | NO |  | NO | AMOCO PIPELINE COMPANY FT. LARAMIE STATION S/E 1/5 OF SECTION 23; T-26N; R-64W; GOSHEN COUNTY, WYOMING. |  | PUMPING STATION | OTHER | THREADED INSTR. ON PIPE. | 1986 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 125 | 120 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.P. FOLEY , AREA MANAGER | 3032866411 | AT APPROXIMATELY 0530 ON OCTOBER 21, 1988 WHILE RECEIVING A CRUDE OIL DELIVERYFROM CONOCO PIPELINE A 1/2" THREADED INSTRUMENT CONNECTION FOR A PRESSURE SWITCH FAILED AND APPROXIMATELY 125 BARRELS OF CRUDE OIL WAS RELEASED ONTO THE GROUND.THE PIPELINE WAS SHUTDOWN AND THE OIL WAS VACUUMED UP AND RETURNED TO TANKAGE.
2017-09-29 08:50 | YES | NO | 19880192 |  | 809 | ARCO PIPE LINE CO | Null | 1988-10-24 | 2100 | TX | HARRIS | HOUSTON | NO |  | NO | ONE MILE EAST AND .3 MILE SOUTH OF INTERSECTION OF HWY. #59 AND EAST BELT. |  | NO DATA | VALVE |  | 1988 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 190 | 140 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, SOUTHERN AREA MANAGER | 3163311300 | UHKNOWN PARTIES REMOVED PACKING NUTS FROM 2" VALVE RESULTING IN LOSS OF PRODUCT.
2017-09-29 08:50 | YES | NO | 19880193 |  | 13131 | CONOCO INC | YES | 1988-10-09 | 2000 | CO | WELD |  | NO |  | NO | NW1/4, NW1/4, SECTION 20, TOWNSHIP 2N, RANGE 66 WEST. |  | PUMPING STATION | OTHER | NOT SPECIFIED | 1980 | OTHER | PUMP COOLING LINE SEP. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.9676 | 18.0914 | COMM: CRUDE OIL; CLASS: 1; LOSS: 190; RECOV: 185; FIRE: NO; EXP: NO; PRTST: NO; FACTD: Null; FACAT: Null; PREVT: Null; EXCAL: Null; TMPMK: Null; PNAME: L.G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS; PHONE: 7132932032 | SPILL WAS THE RESULT OF A HIGH PRESSURE COMPRESSION FITTING SEPARATING ON BEARING COOLING LINE. K.L. MALMBORG NOTIFIED: DOLORADO HEALTH DEPT. ANSWERING SERVICE THEN RETURNED CALL @ 10:30 AM ON OCT. 10, 1988. STAN MAY (303) 377-6326. ENVIRONMENTAL PROTECTION AGENCY FLOYD NICHOLS @ 10:15 AM, OCT 10, 1988,(303) 293-1788.
2017-09-29 08:50 | YES | NO | 19880194 |  | 13131 | CONOCO INC | YES | 1988-09-30 | 1100 | WY | CONVERSE |  | NO |  | NO | SE1/4, SW1/4 SEC. 22, T33N, R76W, SOUTHWEST OF GLENROCK, WYOMING. |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1793.5295 | 3618.2735 | CRUDE OIL | 1 | 917 | 0 | NO | NO | 4 | 0.24 |  | WELDED |  | 150 | 0 | NO | [5 empty] | Null | Null |  |  | DAMAGE BY OTHERS |  | Null |  |  | NO | NO | L.G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | THE SPILL WAS A RESULT OF OUTSIDE FORCE DAMAGE. ROSA PETROLEUM (ROSA), OPERATOR OF THE PRODUCTION LEASE, ASSUMED THE PIPELINE BELONGED TO HIM AND WAS NOT IN USE. ROSA INSTRUCTED HIS CONTRACTOR TO REMOVE 115 FEET OF PIPE TO BE USED ELSEWHERE. THIS WAS DONE AT A TIME THE PIPELINE WAS NOT OPERATING WITHOUTINCIDENT. WHEN THE PIPELINE WAS STARTED UP TO SHIP PRODUCER OIL, 917 BARRELS OF CRUDE OIL WAS DISCHARGED ONTO THE GROUND DUE TO VOID IN THE PIPELINE.
2017-09-29 08:50 | YES | YES | 19880195 |  | 22907 | WYCO PIPE LINE CO | YES | 1988-08-04 | 1005 | CO | ADAMS | AURORA | NO |  | YES | NORTH SIDE OF 56TH AVENUE AND PEORIA, ARMY CORE OF ENGINEERS. INSIDE ARSENAL GROUNDS. |  | LINE PIPE | OTHER | NOT SPECIFIED | 1966 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 0 | 2 | 15000 | 13451.4713 | 27137.0509 | GASOLINE | 1 | 98 | 15 | NO | NO | 6 | 0.22 | 42000 | WELDED |  | 1440 | 0 | YES | 24 | 2000 | 9 | 66 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | R.D. SEALOCK, FIELD SUPERVISOR WYCO PIPE LINE CO. | 3032866400 | CONTRACTOR WORKING WITH FRONT END LOADER OVER THE PIPELINE WITHOUT PERMISSION. THE LINE HAD BEEN MARKED AND CONTRACTOR WAS TOLD NOT TO REMOVE DIRT OVERLINE. A FEW DAYS LATER HE WENT AHEAD WITH DIRT REMOVAL AND HIT THE LINE.
2017-09-29 08:50 | YES | NO | 19880196 |  | 24003 | YELLOWSTONE PIPELINE CO | YES | 1988-10-09 | 1611 | MT | POWELL |  | NO |  | NO | TOP CENTER OF SECTION 18, TOWNSHIP 9N, NEAR GARRISON, MONTANA SEE ATTACHED SKETCH. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 188000 | 168591.7737 | 340117.7044 | GASOLINE | 3 | 6263 | 0 | NO | NO | 10.75 | 0.28 | 46000 | WELDED |  | 1719 | 1087 | YES |  |  | 1 | 54 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | OTHER | MARKERS, INSPECTORS | NO | YES | STAN B. BELL, DISTRICT MANAGER | 3036494080 | APPROXIMATELY 2 WEEKS PRIOR TO THE LEAK, YELLOWSTONE PIPE LINE COMPANY'S (YPL) 10-INCH PRODUCTS PIPELINE WAS STRUCK BY A CONTRACTOR WHO WAS INSTALLING A FIBER OPTICS CABLE. THE PIPELINE APPARENTLY DID NOT RUPTURE AT THAT TIME. YPL WAS NOT NOTIFIED OF THE INCIDENT. AT 1848 MDT ON SUNDAY, OCTOBER 9, 1988,CONOCO'S OIL MOVEMENTS CONTROL CENTER WAS NOTIFIED OF THE LEAK BY THE PROPERTY OWNER. THE LINE WAS SHUT DOWN AT 1853 MDT. THE MISSOULA PUMP UNIT WAS LEFT IN OPERATION TO PULL PRODUCT FROM THE LEAK SITE. FIELD PERSONNEL ARRIVED AT THE LEAK SITE APPROXIMATELY 40 MINUTES LATER, CLOSED THE NEAREST BLOCK VALVE AND BEGAN CLEANUP EFFORTS. SEVERAL SECTIONS OF THE PIPELINE WERE DAMAGED BY THE CONTRACTOR. A TOTAL OF 244 FEET OF PIPE WERE REMOVED AND REPLACED WITH PRETESTED SECTIONS OF 0.322 WALL X-46, 0.365 WALL X-52, AND O.307 WALL X-52LINE PIPE. ALL WELDS WERE 100% X-RATED. THE LINE WAS PUT BACK INTO SERVICEAT 630 MDT ON OCTOBER 13. YPL IS CONTINUING CLEANUP EFFORTS WITH THE ASSISTANCE OF AN OUTSIDE CONSULTING FIRM AND IN CLOSE COOPERATION WITH STATE AUTHORITIES. A REVIEW OF PRESSURE LOGS INDICATES THAT THE LEAK PROBABLY OCCURRED AT1611 MDT. THE LINE WAS EXPERIENCING PRESSURE FLUCTUATIONS DUE TO A PLANNEDUNIT SHUTDOWN AT THOMPSON FALLS. THEREFORE, THE PRESSURE DROP THAT OCCURREDAT 1611 MDT AT DRUMMOND STATION WAS NOT INTERPRETED AT THE TIME AS A POTENTIAL LEAK.
2017-09-29 08:50 | YES | NO | 19880197 |  | 24003 | YELLOWSTONE PIPELINE CO | YES | 1988-09-27 | 1341 | MT | POWELL |  | NO |  | NO | SE 1/4, SECTION 2, T9N, R9W, APPROXIMATELY 30 MILES WEST OF HELENA, MONTANA. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 56000 | 50218.8262 | 101311.6566 | GASOLINE | 3 | 1906 | 0 | NO | NO | 10.75 | 0.28 | 46000 | WELDED |  | 1719 | 1198 | YES |  |  | 1 | 54 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | OTHER | MARKER AND INSPECTOR | YES | YES | L.G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | ON THE DAY THE INCIDENT OCCURRED, YELLOWSTONE PIPE LINE COMPANY'S (YPL) 10-INCH PRODUCTS PIPELINE WAS STRUCK BY EQUIPMENT BEING USED BY A CONTRACTOR FOR AT&TTO INSTALL FIBAR OPTIC TELEPHONE CABLE. AT 13:41 MDT CONOCO'S OIL MOVEMENTS GROUP NOTICED A SUDDEN PRESSURE DROP AT THE DRUMMOND PUMP STATION WHICH WAS BEING BYPASSED. THE PIPELINE WAS IMMEDIATELY SHUT DOWN. THE EQUIPMENT OPERATORS FOR AT&T NOTICED LIQUID LEAKING FROM THE PIPELINE AND NOTIFIED YPL BY TELEPHONE. THE EQUIPMENT OPERATORS WERE INSTRUCTED TO CLOSE A BLOCK VALVE WHICH WAS NEAR THE LEAK SITE. YPL PERSONNEL ARRIVED AT THE LEAK SITE APPROXIMATELY ONE HOUR LATER AND BEGAN CLEANUP EFFORTS. TWO SECTIONS OF THE PIPELINE WERE DAMAGED BY THE AT&T EQUIPMENT. A 14-FOOT SECTION AND A 39-FOOT SECTION OF THE PIPELINE WERE REMOVED AND REPLACED WITH PRETESTED SECTIONS OF 0.279-WALL, X-46 LINE PIPE. THE PIPELINE WAS PUT BACK INTO SERVICE AT APPROXIMATELY 20:00 MDT ON SEPTEMBER 28, 1988. YPL IS CONTINUING CLEANUP EFFORTS IN CLOSE COOPERATION WITH STATE AUTHORITIES.
2017-09-29 08:50 | YES | NO | 19880198 |  | 13131 | CONOCO INC | YES | 1988-11-10 | 2045 | MT | PONDERA |  | NO |  | NO | NW 1/4, SECTION 28, TOWNSHIP 31N, RANGE 4W, NEAR MILE POST 348. |  | LINE PIPE | LONGITUDINAL WELD |  | 1962 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 15245.0008 | 30755.3243 | CRUDE OIL | 1 | 610 | 25 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 1632 | 1421 | YES |  |  | 1 | 62 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | L.G. HUBBARD, MANAGER, SUPPLY AND TRANSPORTATION | 7132932032 | AT 20:46MST, NOVEMBER 10, SUCTION AND DISCHARGE PRESSURE ALARMS AT CONRAD ANDA DISCHARGE PRESSURE ALARM AT CUT BANK WERE RECEIVED BY CONOCO PIPE LINE COMPANY'S OIL MOVEMENTS GROUP IN HOUSTON. THE PIPELINE WAS IMMEDIATELY SHUT DOWNAND COMPANY FIELD PERSONNEL WERE NOTIFIED OF A POSSIBLE LEAK BETWEEN THE CUTBANK AND CONRAD PUMP STATIONS. FIELD PERSONNEL PROCEEDED TO THE MARIAS RIVER TO CLOSE THE MANUAL BLOCK VALVES. THEY THEN BEGAN LOOKING FOR THE LEAK SITE WITH THE AID OF CONTRACT PERSONNEL AND A HELICOPTER. THE LEAK SITE WAS LOCATED AT 09:00 MST ON NOVEMBER 11. REPAIR AND CLEANUP EFFORTS WERE STARTED SHORTLY THEREAFTER. A 47-FOOT SECTION OF PIPE CONTAINING THE 52-INCH SEAM SPLIT WAS REMOVED AND REPLACED WITH A PRE-TESTED SECTION OF 0.250 WALL SEAMLESS X-52 LINE PIPE. FOLLOWING THE INITIAL CLEANUP EFFORTS, APPROVAL WAS RECEIVEDFROM THE LANDOWNERS AND THE PROPER AUTHORITIES AND THE OIL-SOAKED AREA WAS BURNED OFF. THE LINE WAS PUT BACK INTO SERVICE AT 18:45 MST, NOVEMBER 11.
2017-09-29 08:50 | YES | NO | 19880199 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-10-24 | 1045 | MO | ST CHARLES |  | NO |  | NO | COUNTRY POINT ESTATES, HIGHWAY Z, SOUTH OF WENTZVILLE, MISSOURI. |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3587.059 | 7236.5469 | CRUDE OIL | 3 | 223 | 128 | NO | NO | 8 | 0.19 | 5200 | WELDED |  | 1250 | 401 | YES | 8 | 1790 | 1 | 66 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | THE ACCIDENT OCCURRED WHEN A TRENCHER OWNED AND OPERATED BY PURLER, CANNON AND SHUTLE CONTRUCTION CO. OF O'FALLON, MISSOURI, STRUCK THE #2-8" LINE. THE RESULTING LINE PUNCTURE ALLOWED APPROXIMATELY 233 BBLS. OF X-GRADE PRODUCT TO ESCAPE FROM THE LINE AND FLOW APPROXIMATELY 400' DOWN A ROAD DITCH. THE PRODUCT WAS CONTAINED AND APPROXIMATELY 128 BBLS. WERE RECOVERED. THE LINE WAS NOT OPERATING WHEN THE ACCIDENT OCCURRED. THE LINE WAS MARKED ON EITHER SIDE OF THE DAMAGED AREA, 20 FT. AND 40 FT. RESPECTIVELY. WPL IS A MEMBER OF THE MISSOURI ONE CALL SYSTEM; HOWEVER, THE CONTRACTOR DID NOT CALL. THE LINEWAS REPAIRED ON 10/24/88 BY INSTALLING A 2' SPOOL OF PIPE TO REPLACE THE DAMAGED SECTION OF PIPE. THE OIL SOAKED SOIL WAS EXCAVATED AND HAULED TO A SANITARY LANDFILL. ALL CLEAN-UP WAS COORDINATED WITH THE MISSOURI DEPARTMENT OF NATURAL RESOURCES.
2017-09-29 08:50 | YES | NO | 19880200 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-11-08 | 2345 | IL | KANKAKEE | LIMESTONE | NO |  | NO | NE 1/4, NE1/4, SECTION 3, T-31-N, R-11-E ONE-HALF MILE NORTH OF ROUTE 17 NORTH LINE 14-INCH PRODUCTS LINE. |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 160000 | 143482.3606 | 289461.8761 | GASOLINE | 3 | 380 | 105 | NO | NO | 14 | 0.31 | 48000 | WELDED |  | 1180 | 1176 | YES | 24 | 1100 | 1 | 53 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | LEAK OCCURRED IN LOCALIZED CORROSION PIT WHEN PIPELINE WAS INADVERTENTLYBLOCKED IN DURING A VALVE SWITCH. PRESSURES DID NOT EXCEED 110% OF MOPDURING THE ABNORMAL CONDITION. LEAK WAS DISCOVERED AT 2245 HOURS ON NOVEMBER9, 1988. SUPPLEMENTAL REPORT 4/12/94 INDICATES A CORRECTION IN PART G, #3:BARRELS SPILLED FROM 2431 TO 380, FILED BY J.W. HOLDEN, MANAGER HEALTH,SAFETY AND ENVIRONMENT ON 12/5/88. REPORTS CONTINUES: DURING RECENTINVESTIGATION INTO THIS SPILL, WE DISCOVERED A DISCREPANCY IN THE VOLUMEAMOUNT WHICH WAS REPORTED TO THE ILLINOIS EPA VERSUS THAT WHICH WASORIGINALLY REPORTED TO DOT-OPS. WE FILED THE ORIGINAL DOT-7000-1 REPORT ON12/5/88, SHOWING AN ESTIMATED SPILL AMOUNT OF 2431 BBLS. DURING REMEDIATIONWORK CONDUCTED FOLLOWING THE SPILL, WE CONDUCTED SUBSEQUENT ANALYSIS OF THERELEASE VOLUME AND SUBMITTED A VOLUME RANGE OF 300-500 BBLS TO THE ILLINOISEPA ON 2/13/89. (THIS VOLUME RANGE WAS LATER SIMPLIFIED TO 380 BBLS FORDISCUSSION AND REPORTING PURPOSES.) THE MORE CURRENT VOLUME AMOUNT IS BASEDON HYDRAULIC AND GEOMETRIC CALCULATIONS USING AN "ORIFICE" MODEL. FOLLOWINGTHIS CORRECTION IN OUR ORIGINALLY ESTIMATED VOLUME, WE FAILED TO SUBMIT ATIMELY REVISED DOT-7000-1 WHICH INCLUDED THE NEW SPILL VOLUME.
2017-09-29 08:50 | YES | NO | 19880201 |  | 2731 | CHEVRON PIPELINE CO | Null | 1988-11-19 | 730 | TX | CRANE |  | NO |  | NO | CRANE PIPELINE STATION SECTION 202, BLOCK F, CCS-D&RGNG SURVEY APPROX. 4 MILES NE OF CRANE, TX. |  | TANK FARM | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 538.0589 | 1085.482 | CRUDE OIL | 1 | 83 | 80 | NO | NO | 12 | 0.38 | 35000 | WELDED |  | 50 | 0 | NO |  |  |  |  | EXTERNAL | Null | NO | GALVANIC |  |  |  | Null |  |  | Null | Null | R.C. KINNEAR, DIVISION MANAGER | 9156877551 | LEAK WAS DISCOVERED BY CHEVRON PIPELINE EMPLOYEE AT 7:30 ON NOVEMBER 19,1988. LEAK WAS CAUSED BY EXTERNAL CORROSION ON THE 12 INCH SUCTION LINE FROM TANK 1995 AT CRANE PIPE LINE STATION. 80 BARRELS OF THE 83 BARRELS LEAKED WERE RECOVERED. TEH LINE WAS CLAMPED AND SITE CLEANED UP.
2017-09-29 08:50 | YES | NO | 19880202 |  | 10313 | KOCH PIPELINE INC | NO | 1988-11-29 | 1130 | OK | GRANT |  | NO |  | NO | NE/4 , NW/4, SEC. 505Z6N R5W. |  | LINE PIPE | PIPE |  | 1977 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 500 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1440 | 1373 | YES | 26 | 1800 | 10 | 88 | EXTERNAL | Null | YES | OTHER | CONCENTRATION CELL | NO DATA |  | Null | NO DATA |  | Null | Null | MARC S. DEVARENNES, DIVISION ENGINEER | 4053952377 | LEAK WAS SPOTTED AT APPROXIMATELY 11:30 HRS. ON 11/29/88. ACTION WAS TAKEN TO STOP TRAFFIC NORTH AND SOUTH OF LEAK ON U.S. HIGHWAY 81. THE LINE PUMP WAS SHUTDOWN AT 11:39 HRS. THE LEAK WAS MONITORED UNTIL 09:30 HRS. ON 11/30/88 WHEN TRAFFIC WAS ALLOWED TO RESUME. THE LEAK WS REPAIRED AND THE LINE OPERATIONAL AT 20:30 HRS. ON 12/1/88.
2017-09-29 08:50 | NO | NO | 19880203 |  | 18718 | SUN PIPELINE CO | YES | 1988-11-04 | 1100 | MI | WAYNE | REDFORD | NO |  | NO | ON THE SUN PIPE LINE CO. 6" HAMTRAMCK SPUR LINE NEAR THE VICINITY OF 8 MILE RD. AND KINLOCK RD. PLEASE REFERENCE THE ATTACHMENT FOR MORE PRECISE LOCATION. |  | LINE PIPE | PIPE |  | 1933 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15500 | 13899.8537 | 28041.6192 | TOLUENE | 2 | 0 | 3 | NO | NO | 6 | 0.28 | 2750 | WELDED |  | 1000 | 1285 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT, MANAGER OF COMPLIANCE | 9185866231 | WHILE HYDROSTATIC TESTING THIS LINE WITH WATER, A FAILURE TOOK PLACE AT THIS LOCATION. UPON INSPECTION, A CORROSION PIT WAS FOUND TO BE THE CAUSE. IT SEEMS THAT A VERY SMALL LEAK WAS ENLARGED DURING THE INCREASE IN LINE PRESSURE. GERAGHTY & MILLER HYDROGEOLIGISTS WERE RETAINED TO DETERMINE THE EXTENT OF SOIL AND/OR GROUND WATER CONTAMINATION. BASED ON CURRENT RESULTS IT SEEMS THAT THE PIPE HADNOT BEEN LEAKING MUCH OR LONG AS THE BORING SAMPLES SHOWED HYDROCARBONS ONLY INTHE IMMEDIATE VICINITY OF THE LEAK AND THAT GROUNDWATER ENCOUNTERED AT 7-8' INDICATED NO HYDROCARBONS. CLEAN UP IS CONTINUING AND SPL WILL CONTINUE TO WORK WITH THE STATE DEPARTMENT OF NATURAL RESOURCES UNTIL PROPER CLOSURE IS ATTAINED ATTHIS SITE.
2017-09-29 08:50 | NO | NO | 19880204 |  | 12628 | MOBIL PIPELINE CO | YES | 1988-11-25 | 1215 | NY | ONTARIO | PHELPS | NO |  | NO | WEST ON COUNTY ROAD #6 (PRE-EMPTION ROAD) OF TOWN OF PHELPS. NY. |  | LINE PIPE | GIRTH |  | 1941 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 40354.4139 | 81411.1527 | GASOLINE | 3 | 35 | 30 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 1440 | 900 | YES | 8 | 1857 | 9 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | THE SPILL WAS CAUSED BY A SMALL PINHOLE LEAK IN A WELD. THE LEAK WAS TEMPORARILY REPAIRED BY INSTALLING A PLEDCO CLAMP. PERMANENT REPAIR WAS MADE BY REPLACING ASECTION OF PIPE INCLUDING THE WELD WITH 6 FEET OF NEW PIPE. THE SPILLED GASOLINEWAS PICKED UP WITH A VACUUM TRUCK AND ABSORBENT PADS. TRENCHES WERE CUT TO TRAPAND TO RECOVER ANY PRODUCT MIGRATING IN THE SOIL.
2017-09-29 08:50 | YES | NO | 19880205 |  | 2731 | CHEVRON PIPELINE CO | YES | 1988-12-26 | 1330 | TX | WINKLER |  | NO |  | NO | SEC. 32 BLOCK 5 PSL LAND SURVEY. WINK (WEST) PIPE LINE STATION TANK FARM (TANK-3) LOCATED 1 MILE NORTH WINK, TX. |  | TANK FARM | OTHER | TANK-3 AT WINK TANK FARM | 1930 | OTHER | TANK BOTTOMS SEAL LEAK. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 134.5147 | 271.3705 | CRUDE OIL | 1 | 110 | 95 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. KENNEAR, DIVISION MANAGER | 9156877551 | LEAK WAS CAUSED BY LEAKING TANK BOTTOMS SEAL (TANK-3) SPILL WAS CONFINED WITH IN TANK FIRE WALL BASIN. CRUDE OIL WAS PICKED UP BY CONTRACTOR ( P&N TRUCKING CO., 271 W. HWY. 302 KERMIT, TX. 79745) VACUUM TRUCK. TANK-3 WAS EMPTIED TO PREVENT ANY MORE LOSS. TANK SEAL WILL BE REPAIRED.
2017-09-29 08:50 | YES | YES | 19880206 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1988-11-16 | 1618 | TX | GLASSCOCK |  | NO |  | NO | GLASSCOCK COUNTY SECTION 194 2 MILES EAST OF U.S. HIGHWAY 87. |  | LINE PIPE | NO DATA |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 1 | 0 | 1 | 0 | 0 | 0 | 19006 | 17043.9109 | 34384.4526 | NATURAL GAS LIQUID | 2 | 2400 | 0 | YES | NO | 5 | 0.14 | 2650 | WELDED |  | 1631 | 441 | YES | 24 | 2162 | 1 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE WARN. SIGNS | NO | NO | S.F. ISAACS, PRESIDENT | 9185811800
2017-09-29 08:50 | NO | NO | 19880207 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | NO | 1988-11-02 | 800 | CA | CONTRA COSTA | RODEO | NO |  | NO | APPROX. 20 FT. FROM PACIFIC REFINERY'S BACK FENCE. APPROX. 50 FT. FROM RAILROAD TRACKS. APPROX. 300 FEET FROM A PRIVATE HOUSE. |  | LINE PIPE | OTHER | INSULATING FLANGE | 0 | OTHER | INSUL. FLANGE GASK. FAIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OIL AND GASOLINE | 3 | 10 | 0 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BARRY R. PEARL, VICE PRESIDENT-OPERATIONS | 2134867860 | INSULATING FLANGE BEGAN TO LEAK. THERE WAS A STEADY DRIP THAT ALLOWED APPROXIMATELY 10 BARRELS OF PRODUCT TO ESCAPE. A SMALL PRODUCT SHEEN APPEARED ON SAN PABLO BAY- ALL THE SHEEN WAS CONTAINED BY BOOMS. REPAIR WAS ACCOMPLISHED BY REPLACING GASKET.
2017-09-29 08:50 | YES | NO | 19880208 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1988-09-21 | 1038 | CA | RIVERSIDE |  | NO |  | NO | LEAK LOCATED BETYWEEN SOUTHERN PACIFIC RAILROAD AND WENDY ROAD AT RRMP 581 (PLMP 45.3). |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 3622 | 318 | NO | NO | 12 | 0.28 | 46000 | WELDED |  | 1368 | 554 | YES | 24 | 1710 | 0 | 55 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | YES | BARRY R. PEARL, VICE PRESIDENT-OPERATIONS | 2134867860 | A CONTRACTOR WORKING FOR OUR COMPANY HIT THE COLTON TO PHOENIX PIPELINE. THE INPUT STATION WAS IMMEDIATELY SHUT DOWN, THE UPSTREAM BLOCK VALVE WAS CLOSED, AND BOOSTER STATIONS DOWNSTREAM WERE KEPT ON LINE UNTIL PIPE AT LEAK SITE WAS DRAINED. APPROXIMATELY 23 FEET OF PIPE REPLACED.
2017-09-29 08:50 | YES | NO | 19880209 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1988-11-18 | 1100 | CA | LOS ANGELES |  | NO |  | NO | T7N, R18W, SEC 36 - LOS ANGELES COUNTY, CALIFORNIA. |  | LINE PIPE | OTHER | PIPLN. CLAMP COVER WELD | 1925 | OTHER | FAIL PIPLN CLAMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 40354.4139 | 81411.1527 | CRUDE OIL | 1 | 60 | 50 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 500 | 240 | YES | 8 | 623 | 10 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD B. KUPREWICZ - VICE PRESIDENTS, OPERATIONS | 2134289017 | THE LEAK OCCURRED WHEN A PIPELINE CLAMP, POSITIONED AT THE SITE OF AN ACETYLENEWELDED JOINT, FAILED. THE LINE PIPE HAD BEEN HYDROTESTED IN 1984. NO RECORDSEXIST OF THE CLAMP'S INSTALLATION. INFORMATION AVAILABLE INDICATES THE CLAMP WAS INSTALLED PRIOR TO 1952.
2017-09-29 08:50 | YES | NO | 19880210 |  | 12628 | MOBIL PIPELINE CO | YES | 1988-11-10 | 1500 | TX | TAYLOR | ABILENE | NO |  | NO | PASTURE IN BLOCK 13 OF THE WILLIAM B. HARDIN SURVEY SOUTHWEST OF THE CITY OF ABILENE AND ONE MILE WEST OF FM 707. |  | LINE PIPE | PIPE |  | 1944 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 51000 | 45735.0024 | 92265.973 | CRUDE OIL | 1 | 3200 | 250 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 825 | 550 | YES | 2 | 908 | 4 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE MARKERS | NO | NO | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | DOZER PUNCTURED THE PIPELINE WITH A DEEP ROOT PLOW. DAMAGED 34 FT. SECTION WASREPLACED WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 19880211 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1988-12-04 | 920 | TX | HARRIS | HOUSTON | NO |  | NO | ISLAND ON NORH SIDE OF HOUSTON SHIP CHANNEL NORTH AND EAST OF SAN JACINTO MONUMENT - 16" LINE P64; M.P. 11.01. |  | LINE PIPE | VALVE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 89.6765 | 180.9137 | L. P. G. | 2 | 5 | 0 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM M. OLLER, EXECUTIVE VICE PRESIDENT | 7137593605 | RECEIVED NOTIFICATION FROM OPERATOR OF DREDGE BARGE WORKING ON HOUSTON SHIP CHANNEL THAT THERE WAS AN AREA OF FROST ON AN ISLAND ON NORTH SIDE OF CHANNEL. THE OPERATOR WAS CONFIDENT THAT TEPPL PIPELINES CROSSED THE ISLAND, AND HE STATED THAT THE FROST WAS DUE TO AN LPG LEAK. ON INVESTIGATION BY TEPPL PEOPLE, THE LEAKWAS FOUND TO BE DUE TO CORROSION AND FROM A HALF-INCH BODY DRAIN PIPE AT THE SURFACE ON A VALVE OF AN AUXILLIARY LINE CROSSING OF THE CHANNEL.
2017-09-29 08:50 | YES | NO | 19880212 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1988-12-01 | 930 | IL | COOK | FORREST VIEW | NO |  | NO | 14' LINE P37 - M.P. 4.70; ALIGNMENT DRAWING NO. TPE-P37-3 ATTACHED. |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 71741.1803 | 144730.9381 | JET FUEL | 3 | 60 | 40 | NO | NO | 14 | 0.25 | 52000 | WELDED |  | 1304 | 56 | YES | 22 | 1630 | 1 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | WILLIAM M. OLLER | 7137593605 | A FRONT-END LOADER, OPERATED BY OTHERS, STRUCK AND RUPTURED THE 14" PIPELINE WHILE LOADING CRUSHED CONCRETE FROM A PILE NEAR THE PIPELINE. A SECTION OF PIPE WAS REPLACED WITH PRETESTED PIPE, AND THE AREA WAS CLEANED UP.
2017-09-29 08:50 | YES | NO | 19890001 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1988-12-14 | 1200 | TX | GAINES |  | NO |  | NO | SECTION 381 CCSD & RGNG R.R. BLOCK G. |  | LINE PIPE | PIPE |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 28147 | 25241.2375 | 50921.7714 | NATURAL GAS LIQUID | 2 | 2610 | 0 | NO | NO | 10 | 0.19 | 1819 | WELDED |  | 1310 | 695 | YES | 24 | 1743 | 3 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | P/L WARNING SIGNS | NO | NO | S.F. ISAACS | 9185811800 | THIRD PARTY RUPTURED LINE WHILE EXCAVATING.
2017-09-29 08:50 | YES | NO | 19890002 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1988-12-06 | 830 | KS | JOHNSON |  | NO |  | NO | 115TH AND PFLUM, IN HOMESTEAD CREE SUBDIVISION NE 1/4, N3 1/4 S16, T13S, R24E OF HOHNSON COUNTY , KANSAS. |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17935.2951 | 36182.7345 | GASOLINE | 3 | 60 | 5 | NO | NO | 8.63 | 0.2 | 35000 | WELDED |  | 1150 | 300 | YES | 8 | 1430 | 0 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | NO | H.E. JANZEN,VICE PRESIDENT- OPERATIONS | 9185883850 | EQUITY CONSTRUCTION WAS HIRED BY JONES INTERCABLE TO LAY TV CABLE. EQUITY CONTACTED KANSAS ONE-CALL NOVEMBER 16,1988, REGARDING THE PROJECT. HOWEVER, IN THE ONE CALL-REPORT, EQUITY STATED THAT THEY WOULD DELIVER PRINTS TO THE UTILITIES REGARDING THE EXACT LOCATION OF THE WORK SO THAT LINES COULD BE APPROPRIATELY MARKED. THAT FOLLOW-UP CONTACT TO THE UTILITIES WAS NEVER MADE. WPL PERSONNEL ATTEMPTED TO CONTACT EQUITY CONSTRUCTION TO INQUIRE ABOUT THE ANTICIPATED PRINTS, HOWEVER, THEY WERE UNABLE TO REACH THEM BECAUSE THE LISTED PHONE NUMBER ON THE ONE-CALL REPORT WAS A NON WORKING NUMBER. LEONARD BROWN, WITH EQUITY CONSTRUCTION, PROCEEDED TO PLOW A TRENCH FOR TV CABLE, AT WHICH TIME HE STRUCK AND PUNCTUREDTHE 8" WPL BARNSDALL TO KANSAS CITY PIPELINE. CLEANUP EFFORTS HAVE BEEN COORDINATED WITH THE STATE.
2017-09-29 08:50 | YES | YES | 19890003 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1988-11-28 | 1355 | TX | GALVESTON | FRIENDSWOOD | NO |  | NO | 8" PROPANE LINE - CLEMENS-PASADENA, MAP NO. RT. Z-13, MP 45Z-46+58 GALVESTON CO. WATER AUTHORITY CANAL CROSSING NEAR FM RD #528 WITHIN CITY LIMITS OF FRENDSWOR |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 2 | 2 | 0 | 116053 | 104072.24 | 209955.7444 | L. P. G. | 2 | 4836 | 0 | YES | YES | 8.63 | 0.19 | 46000 | WELDED |  | 1440 | 367 | YES | 8 | 1819 | 3 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | EMPLOYEES OF GALVESTON COUNTY WATER AUTHORITY WERE MOWING THE IRRIGATION CANAL DIKES WHEN A MOWER HIT THE ABOVE GROUND PROPANE PIPELINE CANAL CROSSING. THE MOWER CAUSED A THREE INCH HOLE IN THE SIDE OF THE PIPELINE. THIS ALLOWED THE PROPANE TO ESCAPE AND SUBSEQUENTLY IGNITE.
2017-09-29 08:50 | NO | NO | 19890005 |  | 15975 | QUANAH PIPELINE CORP | NO | 1988-09-07 | 915 | TX | SUTTON |  | NO |  | NO | 9 1/2 MILES NW. OF SONORA, TX SURVEY GC & SF RR CO., BLK. D SECTION 72 1/2. |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 26902.9426 | 54274.1018 | L. P. G. | 2 | 3 | 0 | NO | NO | 6.63 | 0.19 | 52000 | WELDED |  | 1440 | 1100 | YES | 24 | 2000 | 0 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | JAMES H. ELMORE, DIVISION MANAGER | 9156947700 | 9/7/88 RONNIE PAXTON (GAUGER) RECIEVED CALL AT SONORA OFFICE AT 9:15AM THAT THEQUANAH PIPELINE HAD BEEN HIT AND WAS LEAKING. CAUSE OF THE ACCIDENT WAS DETERMINED THAT CONTRACTOR - SUTTON SPECIALTY ELECTRIC, INC., WHILE DOING WORK FOR ENRON OIL & GAS COMPANY, HAD STRUCK QUANAH PIPELINE WITH AN AUGER WHILE DRILLING FENCE POST. THE PLANTS WERE NOTIFIED TO SHUT DOWN WHILE MR. PAXTON AND MR. BOB BUCK (GAUGER) CLOSED BLOCK VALVES ON BOTH SIDES OF THE LEAK. BLOCK VALVES CLOSED AT APPROXIMATELY 10:30 AM. REPAIR CREWS WERE DISPATCHED, THE LINE WAS BLOWN DOWN, REPLACED 10' OF PIPE AND INSTALLED TWO WELD PLUS ENDS. REPAIRS WERE COMPLETE 9/8/88.
2017-09-29 08:50 | YES | NO | 19890006 |  | 10012 | KANEB PIPELINE CO | YES | 1988-12-09 | 834 | NE | DIXON |  | NO |  | NO | SE 1/4, SECTION 32, T-30-N, R-6-E. |  | LINE PIPE | PIPE |  | 1988 | OTHER | SEE PART K | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 80708.8278 | 162822.3053 | FUEL OIL | 3 | 438 | 166 | NO | NO | 6 | 0.22 | 42000 | WELDED |  | 1440 | 580 | YES | 4 | 1848 | 10 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L. LEROY ANDERSON, MANAGER OF REGULATORY AFFAIRS. | 3162621408 | THIS ACCIDENT OCCURRED IN NEW LINE PIPE THAT HAD BEEN INSTALLED UNDERGROUND TO REPLACE AN OVERHEAD PIPE LINE CROSSING OF SOUTH CREEK, NEAR PONCA, NEBRASKA; APPROXIMATELY SIXTY DAYS AFTER IS WAS PLACED IN OPERATION. OUR INVESTIGATION SHOWTHAT THE PIPE HAD BEEN WELDED TOGETHER, X-RAYED, PLACED INTO THE TRENCH, AND ONLY THE BANKS OF THE CREEK BACKFILLED TO PREVENT WATER FROM ENTERING INTO THE TRENCH. A RAINSTORM DEVELOPED, WHICH CAUSED SOME OF THE REMAINING TRENCH SIDEWALLSTO CAVE-IN, WHICH RESULTED IN THE PIPE SHIFTING TO AN UNDERSIRABLE POSITION. IN AN ATTEMPT TO RECTIFY THE PROBLEM, THE PIPING WAS LIFTED AND MOVED TO ONE SIDESO THAT THE CAVED-IN SOIL COULD BE REMOVED TO RETURN THE PIPE TO ITS ORIGINAL POSITION. DURING THIS OPERATION, A WRINKE WAS PLACED IN THE PIPE THAT WAS NOT DETECTED. THE TRENCH WAS BACKFILLED, THE PIPING WAS THEN PRESSURE TESTED, AND TIED INTO THE ORIGINAL MAIN LINE. THE WRINKLED AREA FAILED ON DECEMBER 9TH, RESULTING IN THE RELEASE OF NO.2 FUEL OIL DISTILLATE.
2017-09-29 08:50 | YES | NO | 19890007 |  | 809 | ARCO PIPE LINE CO | YES | 1988-12-30 | 2200 | TX | COOKE |  | NO |  | NO | 5 MILES NORTHWEST OF MUENSTER, TEXAS, PIPE LINE STATION 2028 + 10. |  | LINE PIPE | OTHER | THREADED COLLAR | 1917 | OTHER | COLLAR SEPARATED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 19000 | 17038.5303 | 34373.5978 | CRUDE OIL | 1 | 1197 | 432 | NO | NO | 8 | 0.32 | 35000 | NO DATA |  | 750 | 150 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.D. HARRIS , MANAGER, NORTHER AREA OPERATIONS. | 3163311300 | LEAK WAS CAUSED BY COLLAR SEPARATION. 1197 BBLS OUT, 432 RECOVERED FOR A NET LOSS OF 765 BBLS.
2017-09-29 08:50 | NO | NO | 19890008 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1988-12-16 | 2145 | MS | LEFLORE |  | NO |  | NO | 2 MILES SOUTH OF SUNNYSIDE, MS - 1/4 MILES WEST OF MS. HWY 49E - SW QUARTER OF SE QUARTER OF SEC 21, R1S-T21N. |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17935.2951 | 36182.7345 | CRUDE OIL | 1 | 10 | 5 | NO | NO | 22 | 0.28 | 52000 | WELDED |  | 960 | 375 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | I.B. NEWMAN, MGR. OF PIPELINE OPERATIONS | 2147570207 | AT 9:45 PM ON 12/16/88, A TRACTOR/SUB-SOILER ON THE PROPERTY OF J.P. COLE(MID-VALLEY MILEPOST 297 - SEE ATTACHED) STRUCK AND RUPTURED THE 22" CRUDE OIL PIPELINE IN TWO (2) PLACES APPROXIMATELY 15 FT. APART RESULTING IN TWO (2) CRACKS IN THEPIPE - EACH CIRCUMFERENTIALLY ORIENTED AND APPROXIMATELY 1/2 INCHES LONG. TEN(10) BBLS OF CRUDE OIL WAS SPILLED OVER A SURFACE AREA OF 1/4 ACRES. THE TOP OF PIPE DEPTH AT THE LEAK POINT WAS 18 INCHES, WITH THE SUB-SOILER RANGE BEING 27 INCHES. ON INVESTIGATING THE ONE-CALL REPORT (SUBMITTED BY THE TELEPHONE CO.), THE LAND OWNER INDICATED THAT HE WAS AWARE OF THE PIPELINE LOCATION AND THAT HE WOULD NOT SUB-SOIL OVER THE LINE. CONSEQUENTLY, IN THE FUTURE THE LINE WILL BE MARKEDFOR SUBSOILING OPERATIONS.
2017-09-29 08:50 | YES | NO | 19890009 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1988-12-20 | 1500 | CA | SAN BERNARDINO | MONTCLAIR | NO |  | NO | THIRTY-FIVE FEET NORTH OF SOUTHERN PACIFIC RAILROAD TRACKS IN MONTCLAIR BETWEEN MONTE VISTA AVENUE AND CENTRAL AVENUE, AT RRMP 517.7. |  | LINE PIPE | PIPE |  | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1793.5295 | 3618.2735 | GASOLINE | 3 | 224 | 124 | NO | NO | 20 | 0.28 | 60000 | WELDED |  | 1200 | 43 | YES | 24 | 1551 | 0 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | JOHN M. ABBOUND, SENIOR VICE PRESIDENT - OPER. AND ENGINEER | 2134867720 | PIPELINE WAS HSUT DOWN AT APPROXIMATELY 0940, 12/20/88, AND BLOCK VALVES ON BOTH SIDES OF DERAILMENT WERE CLOSED ON COMPLETION OF BLEED-IN PROCESS AT APPROXIMATELY 1019, 12/20/88. AT 1445, 12/20/88, FIELD PERSONNEL REPORTED THAT IN THE PROCESS OF MOVING DERAILED RAILROAD CAR OVER THE PIPELINE THEY HAD PUMCTURED THE PIPELINE AT 1100 FACING DOWNSTREAM, OPENING A HOLE OF APPROXIMATELY 1/4" X 1/2", LETTING APPROXIMATELY 224 BBLS OF UNLEADED PREMIUM GASOLINE ESCAPE, 124 BARRELS WERE RECOVERED. A 22-FOOT SECTION OF PIPELINE WAS CUT OUT AND REPLACED. PIPELINE RETURNED TO NORMAL OPERATIONS AT 0350, 12/23/88.
2017-09-29 08:50 | YES | NO | 19890010 |  | 12360 | MERIDIAN OIL HYDROCARBONS INC | NO | 1988-10-26 | 930 | TX | UPTON |  | NO |  | NO | EAST OF UNION TEXAS PEMBROOK PLANT AND ABOUT 300 YARDS SOUTH OF BLOCK VALVE #3. |  | LINE PIPE | PIPE |  | 0 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 11200 | 10043.7652 | 20262.3313 | NATURAL GAS LIQUID | 3 | 800 | 0 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  |  | NO SECOND PAGE.
2017-09-29 08:50 | YES | NO | 19890011 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1989-01-04 | 1240 | AL | CHILTON |  | NO |  | NO | APPROXIMATELY 1,642 FEET FSOUTH OF PLANTATION'S CLANTON PUMP STATION. (I.E. APPROX. 1050 FEET SOUTH OF AL. HIGHWAY 22). |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 68993.1207 | 139186.9919 | FUEL OIL | 3 | 210 | 200 | NO | NO | 8 | 0.22 | 46000 | WELDED |  | 1570 | 920 | YES | 24 | 1920 | 5 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R.M. CROOK, VICE PRESIDENT/OPERATIONS | 4043645880 | AT APPROXIMATELY 12:40 PM. CST ON JANUARY 4, 1989, A LEAK OCCURRED ON PLANTATION'S 8", .219 WALL THICKNESS, GRADE X-46 SEAMLEASS PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN HELENA, ALABAMA AND MONTGOMERY, ALABAMA. THE PIPELINE HAD PREVIOUSLY BEEN DAMAGED BY A PARTY OR PARTIES UNKNOWN AND AT AN UNKNOWN TIME.A SPLIT OCCURRED WHICH WAS 9 INCHES LONG BY 1/2 INCH WIDE AT ITS WIDEST POINT, LOCATED AT THE FOUR O'CLOCK POSITION ON THE PIPE, IN A GROOVE CAUSED BY FOREIGN DAMAGE. THERE WERE NO OPERATIONAL UPSETS AND THE PIPELINE WAS OPERATING WITHIN DESIGN CRITERIA. THE PIPELINE WAS REPAIRED BY REPLACING A 21 FOOT LONG SECTION.
2017-09-29 08:50 | YES | NO | 19890012 |  | 805 | ATLANTIC PIPELINE CORP | YES | 1988-12-11 | 1100 | PA |  | PENNSYLVANIA | NO |  | NO | PROPERTY OWNED BY CONRAIL BETWEEN ESSINGTON AVE. AND THE SCHUYLKILL RIVER. |  | LINE PIPE | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 134514.7131 | 271370.5089 | FUEL OIL | 1 | 595 | 342 | NO | NO | 16 | 0.31 | 35000 | WELDED |  | 668 | 4 | YES | 8 | 835 | 3 | 85 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.G. HIESTER, OPERATIONS MANAGER | 2156788005 | ON THURSDAY, DECEMBER 8, 1988 AT 10:45 AM. THE ATLANTIC PIPELINE CORP. RECEIVEDA CALL FROM MR. WILLIAM KLEINERT, EXXON TERMINAL SUPERVISOR, WHO REPORTED THE DISCOVERY OF OIL STAINS ON CONRAIL PROPERTY ADJACENT TO THE EXXON TERMINAL. WE BEGAN IMMEDIATELY TO INVESTIGATE AND DISCOVERED A SLOW DROP IN PRESSURE DURING A PRESSURE CHECK OF OUR 16" PIPELINE. EXCAVATION BEGAN LATER IN THE DAY AND CONTINUED UNTIL 2400 WITHOUT FINDING A LEAK IN OUR PIPELINE. EXCAVATION RESUMED THE FOLOWING MORNING, DECEMBER 9, 1988 AND CONTINUED THROUGHOUT THE WEEKEND. DIFFICULT CONDITIONS CAUSED THE EXCAVATION TO PROCEED SLOWLY AND CAUTIOUSLEY. ON SATURDAY, DECEMBER 10, 1988 AT A SECOND SITE, OUR LINE WAS EXPOSED AND FOUND TO BE CASED. CORROSION OF OUR CASING WAS EVIDENT AND ON SUNDAY A SMALL CORROSION HOLE WAS DISCOVERED ON OUR PIPELINE AND INSIDE OF THE CASED AREA. A TEMPORARY 6" PATCH WAS WELDED OVER THE HOLE AND AT 14:45 PM. OUR PIPELINE WAS REPRESSURED. PERMANENT REPAIRS WERE MADE ON DECEMBER 11, 1988 WHEN A 60 FEET PIECE OF THE PIPE WAS
2017-09-29 08:50 | YES | NO | 19890013 |  | 18273 | SHELL PIPE LINE CORP | NO | 1988-12-22 | 915 | TX | WINKLER | KERMIT | NO |  | NO | NW 1/4, SW 1/4, SECTION 27, BLOCK 5 PSL SURVEY FIVE MILES SOUTH OF KERMIT HENDRICK-BARNSLEY 10-INCH. |  | LINE PIPE | PIPE |  | 1936 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3803 | 3410.3964 | 6880.147 | CRUDE OIL | 1 | 690 | 550 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 900 | 845 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19890014 |  | 18273 | SHELL PIPE LINE CORP | YES | 1988-12-24 | 1636 | MO | MARIES | VIENNA | NO |  | NO | SE 1/4, SW 1/4, SECTION 29, T-40-N, R-8-2 EAST OF GASCONADE RIVER OZARK 22-INCH. |  | LINE PIPE | LONGITUDINAL WELD |  | 1949 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 20000000 | 17935295.074 | 36182734.5147 | CRUDE OIL | 1 | 20554 | 11500 | NO | NO | 22 | 0.34 | 46000 | WELDED |  | 1035 | 910 | YES | 12 | 1000 | 0 | 49 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | AN OPERATIONAL UPSET OCCURRED WHEN SWITCHING TO A CONNECTING PIPELINE, CAUSING APRESSURE SURGE IN THE OZARK PIPELINE. THE INCREASED PRESSURE, WHICH DID NOT EXCEED 110% OF MAXIMUM OPERATING PRESSURE, CAUSED A PIPE JOINT TO SPLIT OPEN ALONG ITS LONGITUDINAL ERW SEAM.THE SPLIT INITIATED AT A MANUFACTURING DEFECT (HOOKCRACK) IN THE LONGITUDINAL ERW SEAM. SUPPLEMENTAL REPORT ON 5/9/94 INCREASEPROPERTY DAMAGE FROM 14000000 TO 20000000.
2017-09-29 08:50 | YES | NO | 19890015 |  | 18718 | SUN PIPELINE CO | YES | 1988-12-22 | 0 | PA | ADAMS |  | NO |  | NO | APPROXIMATELY 325 FT. WEST OF WHERE PIPELINE CROSSES HUNTERSTOWN ROAD IN ADAMS CO., NEAR THE CITY OF GETTYSBURG. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 67257.3565 | 135685.2544 | GASOLINE | 2 | 3 | 0 | NO | NO | 6 | 0.28 | 30000 | WELDED |  | 1200 | 0 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT, MANAGER RISK MANAGEMENT | 9185866231 | ON DECEMBER 22, 1988, AT APPROXIMATELY 1030 HRS., THIRD PARTY SURVEYORS WERE WORKING IN A FIELD WHICH IS TRAVERSED BY SUN PIPE LINE CO.'S 6-INCH HIGH PRESSURE PETROLEUM PRODUCTS PIPELINE FACILITY. WHEN THE SURVEYORS WERE IN CLOSE PROXIMITY TO THE PIPELINE RIGHT-OF-WAY THEY DETECTED A PETROLEUM TYPE ODOR AND REPORTED IT TO SUN PIPE LINE CO. UPON EXCAVATING OUR FACILITY THAT SAME DAY,A "SWEAT" TYPE LEAK WAS DISCOVERED AT PIPELINE STATION NUMBER 692+65 AT 1730 HRS. THE "SWEAT" WAS TEMPORARILY REPAIRED WITH A SPLIT SLEEVE* AND PERMANENT REPAIRS, WHICH CONSISTED OF REPLACING A 20 FOOT LONG SECTION WITH NEW LINE PIPE, WERE COMPLETED ONJANUARY 4,1989. THE DATE THAT THE PIPE STARTED TO "SWEAT" IS UNKNOWN, HOWEVER, THE LENGTH OF DAMAGED COATING AND THE DEGREE OF SATURATION OF THE SURROUNDING SOIL ARE PHYSICAL OBSERVATIONS WHICH SUPPORT SUN PIPE LINE'S THEORY THAT THE "SWEAT" TYPE CONDITION HADN'T BEEN OCCURRING FOR A LONG PERIOD OF TIME AND ONLY A SMALL VOLUME OF PRODUCT HAD BEEN DISCHARGED DURING THE LIFE OF THE "SWEAT".
2017-09-29 08:50 | YES | NO | 19890016 |  | 809 | ARCO PIPE LINE CO | NO | 1988-12-29 | 1100 | LA |  |  | YES | 29 05' 20.94 - 89 00' 36. | NO | APPROX. 3 1/4 MILES NNW OF ARCO OIL & GAS PLATFORM A, BLOCK 60, SOUTH PASS, PLAQUEMINES PARISH , LA. |  | LINE PIPE | NO DATA |  | 1975 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 112095.5942 | 226142.0907 | CRUDE OIL | 1 | 45 | 0 | NO | NO | 10 | 0.37 | 46000 | WELDED |  | 1440 | 450 | YES | 8 | 1830 | 6 | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DISKI, SOUTHERN AREA MANAGER | 3163311300 | APPROXIMATELY 11:00 AM. ON DECEMBER 29, 1988, WE WERE NOTIFIED BY SHELL OIL & GAS OF A SHEEN APPROX. 3 1/4 MILES NNW OF ARCO OIL & GAS PLATFORM A, BLOCK 60, SOUTH PASS, PLAQUEMINES PARISH, LA. A WORKING BARGE AND DIVE CREW WAS MOBILIZED ON 12/30/88. THE ORIGIN OF LEAK WAS IDENTIFIED AT 2:00 M. ON 1/3/89 AND A PLIDCOSPLIT SLEEVE WAS INSTALLED.
2017-09-29 08:50 | NO | NO | 19890017 |  | 26136 | PARAMOUNT PETROLEUM CORP | NO | 1988-12-22 | 330 | CA | LOS ANGELES | BELLFLOWER | NO |  | NO | NORTH EAST CORNER OF INTERSECTION OF DOWNEY AVENUE AND ARTESIA BLVD. |  | LINE PIPE | GIRTH |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12500 | 11209.5594 | 22614.2091 | FUEL OIL | 3 | 30 | 30 | NO | NO | 8 | 0.31 | 12500 | WELDED |  | 700 | 300 | YES | 4 | 905 | 1 | 86 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVE DRAGT,ENVIRONMENTAL MANAGER | 2135312060 | REFINERY SHIFT COORDINATOR WAS NOTIFIED BY LOS ANGELES COUNTY FIRE DEPARTMENT OF OIL LEAK AT NORTH EAST CORNER OF ARTESIA BLVD. AND DOWNEY AVENUE. SHIFT COORDINATOR WENT TO SITE OF LEAK TO DETERMINE IF MATERIAL COULD BE COMING FROM PARAMOUNT PETROLEUM CORP. PIPELINE.LEAKING MATERIAL WAS DETERMINED TO BE TYPE OF PRODUCT THAT PARAMOUNT WAS RECEIVING BY PIPELINE ADJACENT TO AREA WHERE LEAK APPEARED. PIPELINE OPERATION WAS SHUT DOWN BY SHIFT COORDINATOR. SHIFT COORDINATOR THENNOTIFIED PARAMOUNT PETROLEUM EMERGENCY RESPONSE PERSONNEL TO DEAL WITH THE LEAKAND ITS REMEDIATION. SUBSEQUENT TO THE DISCOVERY OF THE LEAK THE LOS ANGELES FLOOD CONTROL DISTRICT AND THE POLICE DEPT. WERE NOTIFIED OF THE LEAK. ONCE THE MAGNITUDE OF THE LEAK WAS DETERMINED APPROPRIATE LABOR AND CLEAN UP CONTRACTORS WERE BROUGHT ON SITE. CONTAINMENT BOOMS WERE DEPLOYED IN THE FLOOD CONTROL CHANNELS TO CONTAIN AND RECOVER THE OIL WHICH HAD LEAKED FROM THE PIPELINE. PARAMOUNT PETROLEUM PERSONNEL IN CONJUCTION WITH PERSONNEL FROM THE LOS ANGELES FLOOD CONTROL DISTRICT AND THE FISH & GAME DEPARTMENT COORDINATED THE EFFORT TO CONTAIN AND CLEAN UP THE OIL WHICH HAD LEAKED FROM THE LINE.
2017-09-29 08:50 | YES | NO | 19890018 |  | 5075 | FARMERS UNION CENTRAL EXCHANGE INC - CENEX PIPELIN | YES | 1989-01-28 | 1208 | MT | YELLOWSTONE | HUNTLEY | NO |  | NO | 1 MILE EAST OF HUNTLEY, MONTANA, APPROXIMATELY 200 YARDS SOUTH OF OLD HIGHWAY 10 SEC. 19, T2N, R28E, YELLOWSTONE COUNTY MONTANA. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 17500 | 15092.2452 | 30447.1545 | GASOLINE | 1 | 1050 | 140 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1440 | 1350 | YES | 24 | 1800 | 0 | 54 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | 14 DAY AERIAL SURVEY | NO | NO | RICHARD J. LOHAF, MANAGER PIPELINES AND TERMINALS | 4062529326 | THE PIPELINE LEAK OCCURRED APPROXIMATELY 15 FT. FROM THE EDGE OF A PLOWED FIELD. THE LINE MARKED WITH A YELLOW MARKING STAKE AT THE EDGE OF THE FIELD. THE LINE WAS 10-12 IN. UNDERGROUND AT POINT OF LEAK. WE HAVE STRONG EVIDENCE THAT THELINE WAS DAMAGED BY A PLOW OR SOME OTHER TYPE OF FARM EQUIPMENT. THIS POSSIBLYOCCURRED SOME MONTHS AGO. WE HAVE HAD NO REQUEST FOR LINE LOCATION OR DEPTH INTHIS AREA.
2017-09-29 08:50 | NO | NO | 19890019 |  | 22907 | WYCO PIPE LINE CO | YES | 1989-01-09 | 300 | SD | PENNINGTON | RAPID CITY | NO |  | NO | SECTION 33, TOWNSHIP 2 NORTH, RANGE 8 EAST, PENNINGTON COUNTY, SOUTH DAKOTA. |  | TANK FARM | NO DATA |  | 1965 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 0 | 0 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. P. TALY, AREA MANAGER | 3032866411 | A LEADED REGULAR GASOLINE TANK OVERFLOWED AT WYCO'S RAPID CITY TERMINAL. APROXIMATLEY 300 B OF LEADED REGULAR GASOLINE OVERFLOWED AND WAS CONTAINED IN THE TANKDIKE. THE PRODUCT WAS VACUUMED UP AND RETURNED TO TANKAGTE. THE ACCIDENT WAS CAUSED BY A TANK GAUGE STICKING. AA BACK UP ALARM SYSTEM ALSO FAILED.
2017-09-29 08:50 | YES | YES | 19890020 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1989-01-16 | 1710 | WY | LINCOLN |  | NO |  | NO | TOWNSHIP 21 - NORTH, RANGE 114, SECTION 27 |  | NO DATA | VALVE |  | 1980 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 3 | 3 | 0 | 51189 | 44146.1107 | 89060.5366 | NATURAL GAS LIQUID | 2 | 6 | 0 | YES | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | PIPELINE WARNING SIGNS | NO | NO | S. F. ISAACS, PRESIDENT | 9185811800 | FOUR MEN WERE ATTEMPTING TO THAW OUT AN ICE PLUG IN A METER RUN. THEY HAD OPENED A 1" BLOWDOWN VALVE A QUARTER OF A TURN SO THEY COULD TELL WHEN THE ICE PLUG STARTED TO THAW. THE ICE PLUG BROKE FREE FASTER THAN EXPECTED, CAUSING PRODUCT TO BE RELEASED. TEH PRODUCT GOT INTO THEFIRE BOX OF THE PROTABLE STEAM CLEANER AND IGNITED.
2017-09-29 08:50 | YES | NO | 19890021 |  | 19226 | TEXACO PIPELINE INC | YES | 1989-01-24 | 1057 | TX | WINKLER |  | NO |  | NO | SECTION 39, BLOCK B05 PUBLIC SCHOOL LANDS, APPROXIMATELY 3 MILES SOUTH OF KERMIT, TEXAS AND APPROXIMATELY 2 MILES WEST OF STATE HIGHWAY 18. |  | LINE PIPE | PIPE |  | 1948 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 258724.2026 | 521951.2195 | CRUDE OIL | 1 | 23534 | 5849 | NO | NO | 20 | 0.31 | 46000 | WELDED |  | 1033 | 974 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID R. SEATON, DISTRICT MANAGER | 8177230761 | WINK STATION WAS PUMPING FROM SHELL HENDRICKS TANKS AND JAL STATION WAS SHUT DOWN. WINK STATION WAS RUNNING UNITS 1,3 & 4 AND ODESSA STATION WAS RUNNING UNITS1 & 3. WINK DISCHARGE PRESSURE WAS 800 PSI AND ODESSA DISCHARGE PRESSURE WAS 460 PSI. MIDLAND STATION OPERATOR OPENED JAL BLOCK VALVE AT WINK AND GAVE JAL STATION OPERATOR OK TO START UP. JAL STATION UNITS 1 & 2 WERE STARTED AT 1018 AND SHELL HENDRICKS VALVE WAS CLOSED. WINK STATION DISCHARGE PRESSURE ROSE TO 820 PSI AT 1020. ODESSA STATION UNIT NO. 1 WAS SHUT DOWN AT 1025. JAL STATION NO. 3 UNIT WAS STARTED AT 1053 AND WINK STATION DISCHARGE PRESSURE ROSE TO 995 PSI.WINK STATION SHUT DOWN AT 1057 BY LOW SUCTION PROTECTIVE DEVICE. MIDLAND STATION OPERATOR SHUT DOWN ODESSA STATION NO. 1 UNIT AND NOTIFIED JAL STATION OPERATOR TO SHUT DOWN ALL UNITS. JAL STATION WAS DOWN AT 1107.
2017-09-29 08:50 | YES | NO | 19890022 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1989-01-08 | 645 | AZ | MARICOPA |  | NO |  | NO | ON SOUTHERN PACIFIC RAILROAD RIGHT-OF-WAY AT RRMP 840.6. APROXIMATELY 9 MILES DOWNSTREAM FORM OUR MONTEZUMA, ARIZONA REMOTE STATION. |  | LINE PIPE | PIPE |  | 1955 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TURBINE FUEL | 3 | 4843 | 92 | NO | NO | 12 | 0.25 | 46000 | WELDED |  | 1350 | 1280 | YES | 24 | 1715 | 0 | 55 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. M. ABBOUD, SENIOR VICE PRESIDENT-OPER. AND ENGINEERING | 2134867720 | APPROXIMATELY 0645, 1-8-89, OUR INPUT STATION PERSONNEL REPORTED A PRESSURE DROP AT OUR MONTEZUMA REMOTE STATION. THE ENTIRE LINE WAS SHUT DOWN AT 0647, 1-8-89. FIELD PERSONNEL WERE IMMEDIATELY DISPATCHED TO CHECK THE PIPELINE. LINE RUPTURE WAS APPROXIMATELY 9 MILES DOWNSTREAM OF THE MONTEZUMA STATION. BLOCK VALVES WERE CLOSED ONBOTH SIDES OF RUPTURED SECTION OF PIPE. A NEW SECTION INSTALLED. LINE RUPTURE WAS CAUSED BY A FAULTY PIPE SEAM.
2017-09-29 08:50 | YES | YES | 19890023 |  | 2552 | COLONIAL PIPELINE CO | YES | 1989-01-03 | 1025 | NC | CUMBERLAND |  | NO |  | YES | FORT FRAGG ARMY MILITARY RESERVATION. |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 25000 | 21560.3502 | 43495.935 | GASOLINE | 3 | 20 | 0 | NO | NO | 6 | 0.19 | 52000 | WELDED |  | 930 | 124 | YES | 24 | 1490 | 0 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES A. COX - TECHNCAL & REGULATORY MANAGER | 4048412296 | AT APPROXIMATELY 10:25 AM. ON TUESDAY, JANUARY 3, 1989, COLONIAL PERSONNEL AT GREENSBORO WERE NOTIFIED BY ARMY POST ENGINEERS AT FORT GRAGG, THAT ITS 6" PIPELINE FROM APEX TO FAYETTEVILLE, NORTH CAROLINA, HAD BEEN PUNCTURED BY AN ARMY MOTOR GRADER PERFORMING MAINTENANCE ON A FIREBREAK ON THE FORT BRAGG ARMY RESERVATION. THE PIPELINE WAS IMMEDIATELY SHUT DOWN AND THE CUMBERLAND COUNTY FIRE AND POLICE DEPARTMENTS WERE NOTIFIED. THE PIPELINE WAS BLOCKED AT APEX AND LILLINGTONSTATIONS, AND THE SEGMENT BETWEEN LILLINGTON AND FAYETTEVILLE WAS ALLOWED TO DRAIN INTO TANKAGE AT TEXACO'S FAYETTEVILLE TERMINAL. PRIOR TO THE ARRIVAL OF COLONIAL'S REPONSE AND MAINTENANCE CREW, MILTARY MAINTENANCE PERSONNEL CONSTRUCTED EARTHEN PITS AND DAMS TO CONTAIN THE GASOLINE. IN ADDITION, THEY INSTALLED A TEMPORARY WATER SERVICE CLAMP ON THE 6" LINE TO HALT THE ESCAPE OF PRODUCT. COLONIAL'S MAINTENANCE PERSONNEL ARRIVED AT APPROXIMATLEY 1:00 PM. AND FOND THAT THE CLAMP HAD BEEN SUCCESSFULLY INSTALLED. LATER THEY LEARNED THAT ONE OF THE CIVILIAN MAINTENANCE EMPLOYEES WORKING FOR THE ARMY HAD BEEN OVERCOME BY FUMES. THISINCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER IN WASHINGTON AT APPROXIMATELY 5:30 PM. WHEN IT WAS DETERMINED THAT THE CONTRACT EMPLOYEE HAD BEEN HOSPITALIZED. CLEAN UP AND RECOVERY EFFORTS WERE CONTINUED BY COLONIAL AND THE FORT BRAGG ENVIRONMENTAL PERSONNEL.
2017-09-29 08:50 | YES | NO | 19890024 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-01-10 | 1229 | NM | LEA |  | NO |  | NO | LINE 80-1-10- "EUNICE PLANT - LINE 80-1". SEC. 25, R38E, T20S. SOUTH OF HOBBS, NM, APPROXIMATELY 10 MILES ON HWY. 18, THEN APPROX. 3 MILES EAS ON DIRT ROAD. |  | LINE PIPE | PIPE |  | 1975 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45229 | 39006.1232 | 78691.1057 | NATURAL GAS LIQUID | 2 | 3623 | 0 | NO | NO | 6.63 | 0.16 | 42000 | WELDED |  | 1180 | 500 | YES | 24 | 1547 | 3 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE FLYER | NO | YES | B. L. THORMAN, MANAGER OF ENG. & TECHNICAL SERVICES | 9186614721 | THE LINE FLYER REPORTED THE PRESENCE OF A CONSTRUCTION COMPANY TO THE AREA OFFICE. THE MAINTENANCE SUPERVISOR WENT OUT ON 12/28/88 TO THIS LOCATION, BUT THEREWAS NO ONE AT THE SITE. HE PROCEEDED TO MARK THE LOCATION OFTH LINE, AND HE LEFT HIS BUSINESS CARD WITH PHONE NUMBERS FOR THEM TO CALL. THE CONSTRUCTION COMPANY NEVER NOTIFIED PHILLIPS PIPE LINE. THE LINE WAS PUNCTURED BY CONSTRUCTION COMPANY'S BULLDOZER ON 1/10/89.
2017-09-29 08:50 | YES | NO | 19890025 |  | 4906 | EXXON PIPELINE CO | YES | 1989-01-13 | 1015 | LA | ASCENSION |  | NO |  | NO | LEAK OCCURRED AT STATION NO. 2067+60 ON THE BELLE ROSE TO ANCHORAGE 16" NO. 1 LINE. THIS POINT IS APPROXIMATELY 2 MILES WEST OF DANALDSONVILLE AND 1250 FT. WE |  | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 120737.9612 | 243577.2358 | CRUDE OIL | 1 | 9377 | 9357 | NO | NO | 16 | 0.25 | 42000 | WELDED |  | 909 | 405 | YES | 0 | 1000 | 0 | 53 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | G. P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT 1115 HOURS ON 1/13/89, EPC WAS NOTIFIED OF A CRUDE OIL SPILL IN THE VICINITYOF OUR PIPELINE SYSTEM IN ASCENSION/IBERVILLE PARISH, LOUISIANA. PUMP UNITS ON THE SYSTEM WERE TURNED OF AT 1119 AND COMPANY OFFICIALS WERE DISPATCHED TO NTHE SITE TO VERIFY THE SPILLAGE. AT 1215 HOURS THE SPILLAGE (9377 BBLS) WAS VERIFIED AND COMPANY PERSONNEL BEGAN SHUTTING OFF ALL INJECTIONS INTO THE SYSTEM. AT 1230 HOURS CLEANUP AND REPAIR PERSONNEL WERE SENT TO THE SITE. AT 1620 HURS ALLAPPROPRIATE BLOCK VALVES WERE CLOSED ISOLATING THE SPILL AREA. THE MAJORITY OF TH SPILL WAS CONTAINED IN A DRAINAGE CANAL WITH BOOMS. CLEANUP WAS ACCOMPLISHEDWITH ABSORBENTS AND VACUUM TRUCKS. THE REMAINDER OF THE OIL WAS LOST INTHE ADJAACENT SUGAR CANE FIELD SOUTH OF THE SITE. THE PIPELINE REPAIR WAS FINALIZED ON1/16/89. A TOTAL OF 9357 BARRELS WERE RECOVERED. DAMAGE CONSISTED OF A HOLE 4INCHES BY 9 INCHES EXTENDING FROM 12 50 2 O'CLOCK. REPAIR WAS ACCOMPLISHED BY REPLACING 21 FEET OF THE PIPE WITH 16", 0.375" W.T., X-52, SEAMLESS PIPE GOOD FOR 1755 PSI. THE MOP IS NOT AFFECTED BY THE INSTALLATION OF THE NEW PIPEL.
2017-09-29 08:50 | YES | NO | 19890026 |  | 4906 | EXXON PIPELINE CO | NO | 1989-01-11 | 0 | LA | WEST BATON ROUGE |  | NO |  | NO | LEAK OCCURRED AT STATION NO. 2687+53 ON THE BLUE WATER - EXXON CHEM 8" ETHANE SYSTEM. LOCATION OF THE LEAK IS APPROXIMATELY 2 MILES NORTH E. OF BRUSLY, LA. |  | LINE PIPE | PIPE |  | 1964 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50400 | 43465.666 | 87687.8049 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 8 | 0.22 | 52000 | OTHER |  | 1440 | 750 | YES | 48 | 2000 | 2 | 64 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. P. MURRAY, OPEATIONS MANAGER | 7136565956 | AT 1000 HOURS ON FRIDAY, JANUARY 13, 1989 A HUNTER NOTIFIED EPC OF AN ICE BLOCKCOMING OUT OF THE GROUND IN ONE OF OUR PIPELINE RIGHT-OF-WAYS. COMPANY PERSONNEL WERE SENT TO VERIFY THE REPORT, IDENTIFY WHICH OF THE SIX PIPELINES IN THE ROW WAS LEAKING, AND SHUT THE SYSTEM DOWN. FROM THE SIZE OF THE ICE BLOCK, IT WASESTIMATE THAT THEPIPELINE HAD BEEN LEAKING FOR APPROXIMATELY 2 DAYS. AT APPROXIMATELY 1700 HOURS EXXON CHEM TOOK SUCTION ON THE LINE TO REDUCE THE PRESSURE DOWN TO 530 PSI, AND AT 2200 HOURS, EPC STARTED FLARING THE ETHANE REMAINING IN THE LINE. EXCAVATION AT THE LEAK SITE BEGAN AT 1200 HOURS ON 1/14/89 AFTER ALL THE ETHANE AHD ABEEN FLARED. ONCE UNCOVERED, IT WAS DISCOVERED THAT A LAMINATION IN THE PIPE WALL HAD CAUSED THE LEAK AND THE DICISION TO REPLACE APPROXIMATLY 50-FEET OF LINE WAS MADE. THE PIPELINE WAS THEN PURGED WITH NITROGEN TO REMOVE ANYREMAINING ETHANE AND 49-FEET OF PIPE WAS REPLACED. AT 0300 HOURS ON 1/16/89 THE LINE WAS PLACED BACK IN SERVICE.
2017-09-29 08:50 | YES | NO | 19890027 |  | 9175 | JAYHAWK PIPELINE CORP | YES | 1989-01-23 | 959 | KS | HARVEY |  | NO |  | NO | NW/4 SEC. 31/T24S/R1W, APPROXIMATELY 2 1/2 MILES WEST OF SEDGWICK, KANSAS. |  | LINE PIPE | NO DATA |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8624.1401 | 17398.374 | CRUDE OIL | 1 | 500 | 385 | NO | NO | 10 | 0.25 | 46000 | WELDED |  | 1250 | 450 | YES | 8 | 1570 | 4 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | WARNING SIGNS | NO | YES | DENNIS E SMITH, PRESIDENT | 3162679669 | AN EMPLOYEE OF THE TOWNSHIP OF SEDGWICK, KANSAS, WAS DIGGING A HOLE INA FIELD WITH A FRONT END LOADER WHEN HE STRUCK AND PUNCTURED JAYHAWK'S 10-3/4" PIPELINE 21/2 MILES WEST OFTHE TOWN OF SEDGWICK, KANSAS. THE EQUIPMENT OPERATOR NOTIFIEDJAYHAWK BY TELEPHONE OF THE ACCIDENT AT 0959, JANUARY 23,1989. THE LINE WAS SHUT DOWN AT 1004 AND THE UPSTREAM BLOCK VALVE CLOSED. VACUUM TRUCKS AND REPAIR CREW WERE DISPATCHED TO THE LEAK LOCATION. THE PUNCTURE WAS ON THE TOP PORTION OFTHE PIPE AND THE INITIAL UPWARD SPRAY OF CRUDE OIL STAINED A 50' X 200' AREA NORTH OF TH LEAK DUE TO A SOUTH WIND. THE OIL SPILL AND DRAINAGE FILLED A DUG OUTAREA AT THE LEAK SITE AND THE OVERFLOW WAS DIRECTED AND CONTAINED IN 6' X 300' AREA IN A DRY WATERWAY SOME 50' SOUTH OF THE LEAK. THE EQUIPMENT OPEATOR'S QUICK RESPONSE TO ERECT EARTHEN DAMS ON THE DRY WATERWAY CONTAINED THE OIL IN A RATHER SMALL AREA. THREE HUNDRED AD EIGHTY FIVE BARRELS OF CRUDE OIL WAS RECOVERED WITH AN ESTIMATE OF 115 BARRELS SOAKED INTO THE GROUND. THE SOAKED AREA IN THE DRY WATERWAY WAS BURNED WITH PERMISSION FROM THE STATE ENVIRONMENTAL AGENCY'S LOCAL REPRESENTATIVE ON JANUARY 24, 1989. A 13' PRE-TESTED JOINT OF FLEX46 10 3/4" PIPE WAS INSTALLED TO REPLACE THE PUNCTURE AND THE SURROUNDING PIPE AREA. X-RAYS WERE TAKEN AND OKAYED AT 0130, JANUARY 24, 1989. THE LINE WAS RETURNED TO SERVICE THAT MORNING.
2017-09-29 08:50 | YES | NO | 19890028 |  | 443 | AMOCO PIPELINE CO | YES | 1989-01-26 | 830 | ND | DUNN |  | NO |  | NO | NE SECTION 19, R145N, R97W. |  | PUMPING STATION | OTHER | PACKING NUT ON PUMP. | 0 | OTHER | PACK. NUT ON PUMP CAME OF | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 86.2414 | 173.9837 | CRUDE OIL | 1 | 200 | 195 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. PETERSON, AREA MANAGER | 6124254750 | PACKING NUT ON POSITIVE DISPLACEMENT PUMP CAME LOOSE, ALLOWING CRUDE OIL TO LEAK PAST PACKING.
2017-09-29 08:50 | YES | NO | 19890029 |  | 809 | ARCO PIPE LINE CO | YES | 1989-01-31 | 1320 | IL | COOK |  | NO |  | NO | TANK FARM LOCATED AT COMPANY'S MONEE STATON, COOK COUNTY, NEAR RICHTON PARK, ILLINOIS. |  | TANK FARM | TANK |  | 1979 | OTHER | TANK ROOF DRAIN HOSE FAIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7200 | 6209.3809 | 12526.8293 | CRUDE OIL | 1 | 67 | 65 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O. D. HARRIS - MANAGER - NORTHER AREA OPERATIONS | 3163311300 | AT APPROXIMATELY 1300 HOURS ON JANUARY 31, 1989 A ROOF WATER DRAIN HOSE ON TANK#1505 RUPTURED CAUSING APPROXIMATELY 67 BBLS. OF MID-CONTINENT GRADE CRUDE OIL TO BE SPILLED INSIDE THE TANK DIKE. OPERATOR ON DUTY HAD BEEN DRAINING WATER FROM THE ROOF AND HAD OPENED THE WATER DRAIN VALVE A FEW HOURS EARLIER.
2017-09-29 08:50 | YES | NO | 19890030 |  | 3012 | D - S PIPELINE CORP | NO | 1989-02-17 | 1700 | TX | HASKELL |  | NO |  | NO | SECTION 1, BLOCK 50, GEORGE HARRIS SURVEY, HASKELL COUNTY, TX 7 MILES NNW OF TH CITY OF STAMFORD, TX |  | LINE PIPE | OTHER | 10" THREAD & COLLAR PIPE | 1927 | OTHER | CONSTRUCTION DEFECT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 34550 | 29796.404 | 60111.3821 | CRUDE OIL | 3 | 1900 | 1070 | NO | NO | 10 | 0.37 | 25000 | THREADED |  | 480 | 200 | YES | 24 | 600 | 6 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS, MANAGER, PIPELINE SAFETY | 8063783583 | AT APPROXIMATELY 1700 HOURS ON 17 FEB. 89, OUR TEXAS PLAINS 10" PIPELINE DEVELOPED A LEAK ALLOWING 1900 BARRELS OF VACUUM GAS OIL TO ESCAPE, OF WHICH 1070 BARRELS WAS SUBSEQUENTLY RECOVERED. THE SPILL OIL DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE CAUSE WAS ATTRIBUTED TO "CONSTRUCTION DEFECT" WHEN INSPECTIONOF THE THREAD AD COLLAR JOINT REVEALED THE TAPERED PIPE THREAD WAS 5 TO 6 THREADS FROM BEING PROPERLY SEATED AND COMPLETELY SCREWED INTO THE COLLAR AT THE TIMEOF CONSTRUCTION. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY CUTTIG OUT THE DEFECTIVE THREAD AND COLLAR, REPLACING IT WITH A 6'6" PUP OF PRE-TESTED 10.750" DIAMETER 0.365 WALL PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | NO | NO | 19890031 |  | 4906 | EXXON PIPELINE CO | NO | 1989-02-25 | 1800 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | LEAK OCCURRED AT STATION NO. 316+93 ON TE BATON ROUGE REFINERY TO SORRENTO DOME 12-INCH BUTANE LINE.LOCATION OF THE LEAK IS NEAR RIVER ROAD & BRIGHTSIDE LANE. |  | LINE PIPE | VALVE |  | 1971 | OTHER | VALVE SEAL FAILURE. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17248.2802 | 34796.748 | NATURAL GAS LIQUID |  | 24 | 0 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. ;MURRAY, OPERATIONS MANAGER | 7136565956 | AT 1120 HOURS O SUNDAY, FEBRUARY 26, 1989, MR. LOUIS PITTS NOTIFIED EXXON'S BATON ROUGE REFINERY OFF A LEAK NEAR THE LEVEE AT RIVER ROAD AD BRIGHTSIDE LANE. EPC WAS IMMEDIATELY NOTIFIED AND COMPANY PERSONNEL WERE SENT TO VERIFY THE REPORT, IDENTIFY WHICH PIPELINE WAS LEAKING, AND SHUT DOWN TE SYSTEM TEH BUTANE LIN WAS SHUT IN AT 1230 HOURS. AT 1700 HOURS, A RETAINING WALL BUILT AROUND THE LEAK SITE TO ISOLATE IT FROM THE RIVER. AT 1900 HOURS, THE LEAK WS VERIFIED AS ORIGINATING THROUGH THE BODY OF A 2-INCH NITROGEN AND BEGAN FALRING THE REMAINING BUTANE. AT 0720 HOURS ON 2/27/89, THE LINE SECTION FROM THE REFINERY PAST THE DISCHARGE SITE WAS DISPLACED WITH NITROGEN. AT 2300 HOURS, COMAPNY PERSONNEL REMOVED THE LEAKING VALVE AND CAPPED THE 2-INCH LINE. AT 2200 HOURS ON 2/28/89, THE LINE WAS PLACED BACK IN SERVICE.
2017-09-29 08:50 | YES | NO | 19890032 |  | 18273 | SHELL PIPE LINE CORP | YES | 1989-03-04 | 1827 | TX | CHAMBERS | MONT BELVIEU | NO |  | NO | MONT BELVIEU FACILITY, 1.25 MILES WEST OF HIGHWAY 146. |  | PUMPING STATION | VALVE |  | 1982 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 75820 | 65388.2301 | 131914.4715 | NATURAL GAS LIQUID | 2 | 2150 | 0 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | A RELEIF VALVE ON TE XRAL MANIFOLD PIPING FAILEED IN OPEN POSITION. THE VALVE WAS SUBSEQUENTLY REPAIRED.
2017-09-29 08:50 | YES | NO | 19890033 |  | 2552 | COLONIAL PIPELINE CO | NO | 1989-01-23 | 1950 | NC |  | GREENSBORO | NO |  | NO |  |  | TANK FARM | TANK |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 2221 | 2201 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES A. COX | 4048412296 | FIRE DEPARTMENT AND COLONIAL PERSONNEL JOINTLY ISOLATED THE AREA AREOND THE TANK FARM WHICH CONTAINED EXPLOSIVE VAPORS. THE TANK WAS WASHED DON WITH WATER ANDFOAM APPLIED TO THE GASOLINE WHICH WAS ALL CONTAINED WITHIN THE TANK DIKE. BY 2200, A FOAM BLANKET COMPLETELY COVERED THE SPILLED PRODUCT, NAD THE FIRE CHIEF AUTHORIZED COLONIAL PERSONNEL TO USE PNEUMATIC PUMPS TO REMOVE THE GASOLINE FROMTHE DIKE AREA TO ADJACENT TANK 813. THIS WAS ACCOMPLISHED BY MAKING HOSE CONNECTIONS FROM THE PUMPS THROUGHT THE SUB-SURFACE FOAM INJECTION PIPING AT THE BASE OF TANK 813. BY 0700, THE BULK OF THE SPILLED PRODUCT HAD BEEN RECOVERED, AND THE FIRE DEPART. PROCEEDED TO FLOOD THE DIKE WITH WATER TO CONSOLIDATE THE FOAM AND SMALL QUANTITIES OF PRODUCT FROM THE SOIL AD GRAVEL CONTINUES. AT THE TIME OF THE SPILL, THE VAREC REMOTE GAUGING SYSTEM WAS NOT FUCTIOING. THE OEPRATOR RESPONSIBLE FOR RECEIVING PRODUCTS INTO TANKAGE FAILED TO CHECK THE LAND GAUGE ONTEH TANK TO VERIFY THE LEVEL OF PRODUCT THEREIN. TEH OPEATOR HAD ERRONEOUSLY USED THE BATCH VOLUME RATHER THAN TANK VOLUME TO PLAN HIS NEXT SWITCH. THE MAX-FILL ALARM SHOULD HAVE ACTIVATED. HOWEVER, THE DISPLACER CABLE WAS FOUND TO BE PINCHED BY THE ALARM TESTING LEVER WHICH PREVENTED IT FROM MOVING. ON JANUARY 24, TH VAREC GAUGING SYSTEM WAS REPAIRED AND THE MAX-FILL ALARM TESTING LEVER WAS ALSO ADJUSTED TO PREVENT BINDING WITH THE CABLE. INSPECTION AND APPROPRIATE ADJE
2017-09-29 08:50 | YES | NO | 19890034 |  | 15681 | PLATTE PIPELINE CO | YES | 1989-02-11 | 605 | NE | MORRILL |  | NO |  | NO | REDINGTON STATION, SECTION 7 T18N, R52W, MORRILL COUNTY, NE APPROXIMATELY 7 1/2 MILES SW OF THE TOWN OF REDINGTON. |  | PUMPING STATION | PUMP |  | 1975 | OTHER | FATIGUE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 94865.541 | 191382.1138 | CRUDE OIL | 1 | 69 | 0 | YES | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.R. STANLEY, PRESIDENT | 4194222121 | EARLY SATRUDAY MORNING, FEB. 11, 1989, A 1/2" PIPE NIPPLE LOCATED ON THE DISCHARGE PIPING OF AN INJECTION PUMP FAILRED. OIL WAS SPRAYED ON THE PUMP AND ADJACENT EQUIPMENT AND WS SUBSEQUENTLY IGNITED BY AN UNKNOWN SOURCE. MOST OF THE RELEASED OIL WAS CONSUMED BY THE FIRE. NO CONTAINMENT WAS NECESSARY FOR THE OIL RESIDUE REMAINING, AND NO WATER WAS AFFECTED. FINAL CLEAN UP AND DISPOSAL PROCEDURES WERE CONDUCTED WITH THE APPROVAL OF THE NEBRASKA DEPART. OF ENVIR. CONTROL.THE APPARENT CAUSE OF TH PIPE NIPPLE FAILURE WAS VIBRATION INDUCED FATIGUE. WEHAVE INSPECTED OUR FACILITIES WITH SIMILAR PUMP INSTALLATIONS AND HAVE CORRECTED ANY CONDITION FOUND THAT HAD THE POTENTIAL FOR THIS TYPE OF FAILURE.
2017-09-29 08:50 | NO | NO | 19890035 |  | 12127 | MARATHON PIPE LINE CO | YES | 1988-10-01 | 2130 | IL | MADISON | WOOD RIVER | NO |  | NO | SECTION 26 T5N, R92, WOOD RIVER TOWNSHIP, MADISON COUNTY. |  | LINE PIPE | PIPE |  | 0 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 52800 | 47349.179 | 95522.4191 | TOLUENE | 3 | 8 | 8 | NO | NO | 6 | 0.25 | 35000 | WELDED |  | 1900 | 1050 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE-PRESIDENT | 4194223009 | ON OCTOBER 1,1988, A LEAK WS DISCOVERED ON THE 6" SPUR OF STHE WABASH 12" PRODUCTS LINE AT OUR WOOD RIVER, IL STATION. CLEAN UP ACTIVITIES WERE INITIATED IMMEDIATELY RESULTING IN THE REVOCERY OF 7 1/2 BBLS OF THE 8 BBLS RELEASED. THE LINEWAS TEMPORARILY REPAIRED WITH A PLIDCO CLAMP ON OCTOBER 2, 1988. A PERMANENT REPAIR WAS ACCOMPLISHED O OCTOBER 4, 1988 BY REPLACING THAT SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19890036 |  | 4906 | EXXON PIPELINE CO | YES | 1989-03-02 | 1410 | TX | GREGG |  | NO |  | NO | LEAK OCCURRED AT STATION 100+40 (LONGVIEW TEAGUE PARK) SOME 2 MILES NORTH OF LONGVIEW STATION ON THE TALCO - LONGVIEW 8 INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1936 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18240 | 15730.4315 | 31734.6341 | CRUDE OIL | 1 | 100 | 85 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 740 | 40 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | G.P. MURRAY, OPERATIONS MANAGER | 7136565956 | AT 1410 HOURS ON MARCH 2, 1989 A LEAK WAS REPORTED TO EPC'S LONGVIEW DISTRICT HEADQUARTERS BY AERIAL PATROL. THE LEAK WAS LOCATED IN LOGVIEW'S TEAGUE PARK O TE TALCO - LONGVIEW 8" TRUCKLINE. EXXON PIPELINE COMPANY'S OTCC CONTROLLER WS IMMEDIATELY NOTIFIED AND THE LINE WAS SHUT DOWN AT 1415 HOURS. A MAINTENANCE CREWALONG WITH CONTRACTED EQUIPMENT AND VACUUM TRUCKS WER DISPATCHED TO THE LEAK SITE TO MAKE REPAIRS AND INITIATE CLEANUP. THE OIL HAD RUN INTO A SMALL CREEK KNOWN AS GUTHRIE CREEK SO A SMALL DAM ALONG WITH A FLUME PIPE WAS INSTALLED TO PREVENT FURTHER CONTAMINATION OF THE WATERWAY. TEMPORARY REPAIRS CONSISTED OF INSTALLING LEAK CLAMPS AND THE LINE WAS RESTORED TO SERVICE AT 1600 HOURS. PERMANENT REPAIRS HAVE BEEN SCHEDULED AND WILL CONSIST OF REPLACING APPROSIMATELY 40-60 FEET OF 8" PIPE. CLEANUP IS EXPECTED TO BE COMPLETED BY 3/10/89.
2017-09-29 08:50 | YES | NO | 19890037 |  | 12628 | MOBIL PIPELINE CO | YES | 1989-03-01 | 1010 | TX | HOWARD | BIG SPRING | NO |  | NO | TWO MILES SOUTH OF THE CITY OF BIG SPRING ON EAST SIDE OF HWY. 87. |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 11211.3821 | 22617.8862 | CRUDE OIL | 1 | 1186 | 854 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 709 | 330 | YES | 2 | 780 | 4 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AERIAL SURVEILLANCE | NO | NO | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | A D-8 DOZER OWNED AND OPERATED BY PRICE CONSTRUCTION INC. HIT AND RUPTURED THE 12" MIDLAND TO CORSICANA CRUDE OIL PIPELIE WHILE WORKING FOR THE TEXAS STATE HIGHWAY DEPARTMENT RECONSTRUCTION U.S. HIGHWAY 87. THE 12" PIPELINE WAS SHOWN ON THE HIGHWAY DEPARTMENT'S CONSTRUCTION PLANS AND MARKED AT THE HIGHWAY R.O.W. LINE, APPROXIMATELY 30 FEET FROM THE LOCATION OF THE RUPTURE. THE 12" PIPELINE WAS TEMPORARILY SHUT DOWN AT THE TIME THE PIPEINE WAS STRUCK. APPROPRIATE VALVES WERE CLOSED TO ISOLATE AND MINIMIZE HE SPILL. THE DAMAGED PIPE WAS REMOVED FROM EH PIPELINE AND REPLACED WITH 8 FEET OF NEW LINE PIPE.
2017-09-29 08:50 | YES | NO | 19890038 |  | 2731 | CHEVRON PIPELINE CO | NO | 1989-02-27 | 1600 | TX | WINK |  | NO |  | NO | CHEVRON PIPE LINE STATION/WINK, TEXAS, ONE MILE WEST OF HWY. 115 ON COUNTY ROAD 201. |  | TANK FARM | OTHER | FAULTY PLUG BLEW OUT LINE | 1989 | OTHER | FAILED PLUG | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 120 | 30 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. KINNEAR, DIVISION MANAGER | 9156877551 | 4" PLUG BLEW OUT OF LINE.
2017-09-29 08:50 | NO | NO | 19890039 |  | 18718 | SUN PIPELINE CO | YES | 1989-02-28 | 700 | OK | OKLAHOMA | MIDWEST | NO |  | NO | SW/4 SECTION 3, TOWNSHIP 11N, RANGE 2 WEST. THE ACTUAL SPILL LOCATION WAS ABOUT 500 FEET WEST OF MAPLE DRIVE BETWEEN RENO AVE. AND 15TH ST., ADJACENT TO MID DEL |  | LINE PIPE | PIPE |  | 1933 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 15523.4522 | 31317.0732 | GASOLINE | 3 | 3 | 2 | NO | NO | 8 | 0.32 | 28350 | WELDED |  | 610 | 410 | YES | 8 | 954 | 12 | 86 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT, MANAGER OF RISK MANAGEMENT | 9185866231
2017-09-29 08:50 | NO | NO | 19890040 |  | 18273 | SHELL PIPE LINE CORP | YES | 1989-03-09 | 1035 | LA | PLAQUEMINES | NAIRN | NO |  | YES | DELTA 20-INCH., SECTION 47, T-19-S, R-28-E. |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8624.1401 | 17398.374 | CRUDE OIL | 1 | 2 | 2 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 840 | 250 | YES | 12 | 1050 | 0 | 58 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19890041 |  | 2387 | CITGO PIPELINE CO | YES | 1989-03-15 | 1500 | TX | MIDLAND | MIDLAND | NO |  | NO | STATION # 1170+43 |  | LINE PIPE | PIPE |  | 1955 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 9800 | 8451.6573 | 17050.4065 | CRUDE OIL | 1 | 653 | 298 | NO | NO | 8 | 0.32 | 42000 | WELDED |  | 580 | 90 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | CARTER R. | 9153325942 | A CONTRACTOR LAYING A PIPELINE FOR AN OUTSIDE COMPANY HIT CITGO'S LINE WITH A TRENCHER. CITGO'S LINE HAD 48 INCHES OF COVER AT THE LOCATION WHERE IT WAS DAMAGED. THE PIPELINE WAS NOT IN OPERATION AT THE TIME OF THE ACCIDENT.
2017-09-29 08:50 | NO | NO | 19890042 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1989-02-11 | 100 | GA | DORAVILLE |  | NO |  | NO | WEST OF COMMUNITY SEPARATOR NEAR PLANTATION PIPE LINE'S PUMPING STATION - DORAVILLE, GA. |  | LINE PIPE | PUMP |  | 1950 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 26000 | 22422.7642 | 45235.7724 | CONDENSATE - WATER | 1 | 40 | 40 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | OTHER | FREESING WEATHER | Null | ONE CALL |  | NO | NO | ROY M. CROOK, VICE PRESIDENT - OPERATIONS | 4043645880 | FREEZING WEATHER DURING THE EARLY MORNING OF FEBRUARY 11, 1989, CAUSED WATER INA TRANSFER PUMP AT THE COMMUNITY SEPARATOR TO FREEZE AND SPLIT THE PUMP CASE.WHEN THE ICE THAWED PRODUCT SEEPED FROM THE PUMP THROUGH THE GROUND TO A SMALL STREAM. A RESIDENT, A SHORT WAY DOWNSTREAM FROM THE LEAK SITE, NOTIFIED AUTHORITIES AND THEY IN TURN NOTIFIED PLANTATION. THE SEEPAGE WAS CLOSED OFF , THE STREAM CLEANED UP AND THE PUMP REPAIRED. THE GRION IV OFFICE, FEDERAL EPA, IN ATLANTA WAS NOTIFIED OF THE SPILL AND THEIR REPRESENTATIVE AND A GEORGIA EPD REPRESENTATIVE INVRSTIGATED THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19890043 |  | 1682 | BP OIL PIPELINE CO | NO | 1989-03-10 | 1200 | OH |  | CLEVELAND | NO |  | NO | 30 FEET UPRIVER OF NORFOLF & WESTERN RAILROAD BRIDGE CROSSING OVER THE CUYAHOGA RIVER IN CLEVELAND, OHIO. |  | LINE PIPE | PIPE |  | 1956 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17248.2802 | 34796.748 | GASOLINE | 3 | 474 | 80 | NO | NO | 6 |  |  | WELDED |  | 10 | 100 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL NEDROW, ENVIRONMENTAL COORDINATOR | 5138988104 | THE CUYAHOGA COUNTY SEWER DISTRICT CALLED OUR TERMINAL AT BRADLEY ROAD IN CLEVELAND TO REPORT A GASOLINE LEAK ON THE CUYAHOGA RIVER. THIS WAS AT 12:00, AND THE PIPELINE WAS NOT IN OPERATION AT THE TIME. AFTER THREE HOURS OF INVRSTIGATIONWE DETERMINED THAT THE GASOLINE WAS COMING FROM OUR LINE. THE LEAK WAS LOCATEDDIRECTLY BENEATH THE RIVER. WE IMMEDIATELY INITIATED THE LEAK RESPONSE PROCEDURE AND BEGAN PROPER CLEAN-UP AND NOTIFICATION ACTIVITIES.
2017-09-29 08:50 | NO | NO | 19890044 |  | 1682 | BP OIL PIPELINE CO | NO | 1989-03-02 | 700 | LA | JEFFERSON |  | NO |  | NO | BARATARIA BAY, LAT. 29 DEGREE, 16'22" LONG. 89 DEGREE 56'44". |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 2 | 0 | NO | NO | 12 | 0.31 | 35000 | WELDED |  | 1100 | 750 | YES | 0 | 1375 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | SIGNS & NAV. LIGHTS | Null | Null | L.L. OWEN, REGION SUPT. | 5043926601 | A SHEEN WAS DETECTED IN AREA OF PIPELINE BY COMPANY EMPLOYEES AT 0700 CST ON MARCH 2, 1989. ON SITE INVESTIGATION CONFIRMED THE PRESENCE OF A LIGHT SHEEN IN THE VICINITY OF SOHIO'S 12-INCH PIPELINE. THE LINE WAS SHUTDOWN UNTIL IT COULD BE DETERMINED THAT A PIPELINE LEAK EXISTED. WORK BEGAN ON MARCH 3 TO UNCOVER THELINE AND CLAMP THE LEAK. DUE TO SHALLOW WATER AND HARD PACKED SAND, THE LINE WAS NOT EXPOSED AND CLAMPED UNTIL MARCH 9. TWO ADDITIONAL DENTS CAUSED BY AN UNKNOWN VESSEL, WERE ALSO FOUND AND 50 FOOT OF PIPE WAS REPLACED ON MARCH 10.
2017-09-29 08:50 | YES | NO | 19890045 |  | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1989-03-28 | 1947 | CA | MERCED |  | NO |  | NO | SEC. 19, T11S, R10E, MDB&M, SALT CREEK AREA, APPROX. 2 MILES WEST OF INTERSTATE 5. |  | LINE PIPE | PIPE |  | 1967 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 25872.4203 | 52195.122 | CRUDE OIL | 1 | 10000 | 8000 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 936 | 930 | Null | 0 | 0 | 3 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.W. PENNER | 8053270110 | THE LEAK OCCURRED DURING A PERIOD OF SMOOTH PIPELINE OPERATIONS 45 MINUTES AFTER THE LAST PUMP START. LOW SUCTION PRESSURE AT LOS BANOS STATION SHUT DOWN ITS ONLY OPERATING UNIT. THE PIPELINE WAS SUBSEQUENTLY SHUT DOWN AND CLOSED IN.
2017-09-29 08:50 | YES | NO | 19890046 |  | 443 | AMOCO PIPELINE CO | NO | 1989-02-25 | 1200 | TX | WOOD |  | NO |  | NO | QUITMAN OIL FIELD, ANNIE THOMAS LEASE, DOWNSTREAM OF INJECTION PUMP. 1/4 MILE N. OF HWY 182; APPROX.4 MILES NORTHWEST OF QUITMAN, TEXAS. |  | LINE PIPE | VALVE |  | 1955 | OTHER | FAILED CAST IRON VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1293.621 | 2609.7561 | CRUDE OIL | 1 | 280 | 175 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.O. PINCHBACK, PIPELINE MAINTENANCE FOREMAN | 2147597131 | LOW AMBIENT TEMPERATURES CAUSED VISCOSITY OF HEAVY QUITMAN CRUDE TO INCREAS. RESULTING PRESSURE INCREASE FROM CLOGGED LINE CAUSED BONNETT TO FAIL IN GATE VALVE. VALVE WAS LAYER DETERMINED TO BE CAST IRON. THE CRUDE WAS BEING GATHERED FROM FIELD LEASE TANK.
2017-09-29 08:50 | YES | NO | 19890047 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-03-13 | 736 | CO | WELD |  | NO |  | NO | MCCULLOCH-BORGER - POWDER RIVER LINE - MP 403-50+00, SEC. 8, T5N,R63W, 1 MILE NORTH AND 6 MILES EAST OF KERSEY, CO. |  | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 27597.2483 | 55674.7967 | NATURAL GAS LIQUID | 2 | 2119 | 0 | NO | NO | 6.63 | 0.16 | 52000 | WELDED |  | 1700 | 853 | YES | 24 | 2335 | 8 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | NO | B.L. THORMAN, MANAGER OF ENG. & TECH. SERVICES | 9186614721 | EMPLOYEE FOR LINE LOWERING CONTRACTOR WAS MOVING DOZER TO A NEW SITE EARLY IN TEH MORNING OF MONDAY, MARCH 13, WHEN HE RAN OVER A SECTIONOF VERY SHALLOW PIPE AND RUPTURED IT.
2017-09-29 08:50 | YES | NO | 19890048 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-03-07 | 910 | KS | WYANDOTTE | KANSAS CITY | NO |  | NO | SE 1/4, NW 1/4, SEC 34, T10S, R25E, WYANDOTTE COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2587.242 | 5219.5122 | GASOLINE | 3 | 150 | 100 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 900 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | AT 9:10 A.M. ON 3/7/89 A CALL WAS RECEIVED FROM DON JONES OF THE KANSAS CITY FIRE DEPARTMENT TO REPORT GASOLINE LEAKING FROM A VENT PIPE NEAR THE INTERSECTION OF STANLEY REOAD AND CHRYSLER ROAD. ALL PIPELINES WERE SHUTDOWN IMMEDIATELY. THE CAUSE OF THE LEAK WAS DETERMINED TO BE AN EXTERNAL CORROSION PIT WHICH FAILED. THE PIT WAS LOCATED ON THE CARRIER PIPE INSIDE THE CASING WHERE THE #3-8" KANSAS CITY - OMAHA LINE CAROSSED THE UNION PACIFIC RAILROAD AT MP 1+00. THE PIPELINE WAS REAPRIED BY REPLACING TH 56' OF CARRIER PIPE THROUGH THE CASING WITH NEWPIPE. THE LINE WAS RESTORED TO OPERATION ON 3/9/89. CLEAN UP AND RECOVERY EFFORTS HAVE BEEN COORDINATED WITH STATE ENVIRONMENTAL OFFICIAL.
2017-09-29 08:50 | YES | NO | 19890049 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-03-31 | 2030 | OK | KAY | OKLAHOMA CITY | NO |  | NO | LEAK OCCURED ON WPL STATION PROPERTY ADJACENT TO TK. #609 INSIDE THE CONTAINMENT DIKE. THE STATION IS LOCATED IN THE SE/4 SE/4 SECTION 4, T25N, R2E KAY COUNTY |  | TANK FARM | BOLTED FITTING |  | 1952 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 324 | 280 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS. | 9185884850 | ON MARCH 31, 1989, A 6" DRESSER SLEEVE COUPLING (EXPANSION JOINT) FAILED ON THEDISCHARGE SIDE OF THE TANK PUMP FOR TANK #609. PRODUCT WAS BEING PUMPED TO THEMAINLINE UNIT AT THE TIME OF FAILURE. STATION PERSONNEL MADE AN IMMEDIATEL INVESTIGATION WHEN THE MAINLINE UNIT BEGAN TO CAVITATE. FURTHER INVRSTIGATION REVEALED THAT THE O-RING SEAL IN THE DRESSER SLEEVE HAD DETERIORATED, AND HAD DIRECTLY CONTRIBUTED TO THE FAILURE. ALSO CONTRIBUTING TO THE FAILURE WAS THE FLOATING PUMP FOUNDATION THAT HAD ALLOWED THE PIPE TO MOVE. THE DRESSER SLEEVES WILL BEREMOVED FROM TEH DISCHARGE SIDE OF ALL THESTATION TANK PUMPS ( THE SUCTION SIDEDRESSER SLEEVE WILL ACCOMODATE ANY INDICENTAL EXPANSION). ALL RELEASED PRODUCTWAS CONTAINED WITH THE TANK DIKE. PREVIOUS WATER ACCUMULATION INSIDE THE DIKE MINIMIZED SOIL CONTAMINATION. ALL RECOVERY EFFORTS HAVE BEEN COORDINATED WITH APPROPRIATE STATE OFFICIALS.
2017-09-29 08:50 | YES | NO | 19890050 |  | 13131 | CONOCO INC | YES | 1989-03-21 | 1400 | MT | CUT BANK |  | NO |  | NO | NW 1/4, SECTION 18, RANGE 5W, TOWNSHIP 33N IN GLACIER COUNTY, MONTANA. |  | PUMPING STATION | PIPE |  | 1968 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2587.242 | 5219.5122 | CRUDE OIL | 1 | 162 | 162 | NO | NO | 8 | 0.16 | 1354 | WELDED |  | 1440 | 0 | YES | 0 | 0 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.G. HUBBARD, MANAGER, ENVIRON. AFFAIRS, SUPPLY & TRANS. DEP | 7132932032
2017-09-29 08:50 | NO | NO | 19890051 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-03-18 | 838 | OK | OSAGE |  | NO |  | NO | SE/4 NW/5 SECTION 5, T23N, R11E, OSAGE COUNTY OKLAHOMA. |  | LINE PIPE | PIPE |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1724.828 | 3479.6748 | FUEL OIL | 3 | 15 | 13 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 1150 | 1561 | YES | 0 | 1561 | 3 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE RPESIDENT-OPERATIONS | 9185884850 | THE LINE FAILED DURING A HYDROSTATIC PRESURE TEST. THE HYDROSTATIC TEST WATER THAT WAS RELEASED CONTAINED APPROXIMATELY 15 BARRELS OF #2 FUEL OIL THAT EVENTUALLY REACHED CLEM CREEK AND RESULTED IN A FISH KILL OF 300 SMALL PERCH. THE FUELOIL ORIGINATED FROM A SHORT SECTION OF THE LINE THAT HAD A SMALLER DIAMATER PREVENTED THE PASSAGE OF A PIG WHICH WOULD OTHERWISE HAVE REMOVED ANY REMAINING PRODUCT FROMTHE LINE. CLEAN-UP EFFORTS HAVE BEEN COORDINATED WITH APPROPRIATE STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | NO | NO | 19890052 |  | 443 | AMOCO PIPELINE CO | YES | 1989-03-29 | 0 | OK | KIOWA |  | NO |  | NO | NORTH OF ROOSEVELT, OK. EAST OF U.S. HIGHWAY 183, SE 1/4, SECTION 19, TOWNSHIP 5N, RANGE 17W. |  | PUMPING STATION | OTHER | DRAIN LINE | 1945 | OTHER | VALVE LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 0 | 1700 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. CARICO, AREA MANAGER -CUSHING OPERATIONS | 9182257271 | A 2" PLUG VALVE LEAK ALLOWED PUMP DISHCARGE PRESSURE TO RUPTURE A LOWER RATED STATION DRAIN LINE.
2017-09-29 08:50 | YES | NO | 19890053 |  | 12127 | MARATHON PIPE LINE CO | YES | 1989-03-16 | 2000 | IN | LAKE | GRIFFITH | NO |  | NO | LOTAVILLE STATION, 1200 REDER ROAD, GRIFFITH, INDAINA SECTION 1, T35N, R9W, ST. JOHN TOWNSHIP, LAKE COUNTY, INDIANA. |  | PUMPING STATION | VALVE |  | 1986 | OTHER | FAILUE OF GARLOCK GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 258724.2026 | 521951.2195 | FUEL OIL | 3 | 201 | 195 | NO | NO |  |  |  | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE PRESIDENT | 4194222121 | ON THURSDAY, MARCH 16, 1989, AT APPROXIMATELY 2000 HOURS MARATHON PIPE LINE COMPANYS ("MPLC"). 10" LOTTAVILLE, INDIANA TO MUSKEGON, MICHIGAN LINE SHOWED A SHORT TERM LOSS. SYSTEM WAS SHUT DOWN AND INTEGRITY TESTING WAS CONDUCTED UNTIL A 2" X1/16" SECTION OF A 10" GARLOCK GASKET WAS FOUND TO HAVE FAILED. FUEL OIL WAS RELEASED ON TO THE GROUND AND INTO A FIELD OWNED BY MPLC. THE FILEL CONTAINED FIELD TILE WHICH ENABLED TH FUEL OIL TO REACH A DRAINAGE DITCH.
2017-09-29 08:50 | YES | NO | 19890054 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1989-03-26 | 1245 | MN | PENNINGTON | SANDERS TOWNSHIP | NO |  | NO | MILE POST 860.7 INTERSECTION OF COUNTY ROADS 7 AND 72 IN SANDERS TOWNSHIP. |  | LINE PIPE | LONGITUDINAL WELD |  | 1967 | FAILED WELD | DEFECT IN LONG. WELD | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 99177.611 | 200081.3008 | CRUDE OIL | 1 | 300 | 270 | NO | NO | 34 | 0.28 | 860 | WELDED |  | 642 | 369 | YES | 8 | 802 | 0 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. SHAUDOHAR, GENERAL MANAGER CORPORATE AFFAIRS | 7153941404 | AT APPROXIMATELY 1230 HRS. LOCAL TIME, A LANDOWNER NOTICED A POOL OF OIL INTEH FIELD. HE NOTIFIED LAKEHEAD PIPE LINE PERSONNEL AND BOTH THE 34" AND ADJOINING 26" LINES WERE SHUT DOWN AT 1245 HRS. AFTER A PERIOD OF UNSUCCESSFUL SEARCHING FOR THE EXACT LOCATION OF THE LINE FAILURE, AND SOME INDICATIONS THAT THE LEAK WAS ON THE 26" LINE, LINE 3 (34") WAS RESTARTED AT 2130 HRS. LAKEHEAD AND EMERGENCY RESPONSE PERSONNEL WERE ON SITE AT ALL TIMES. THE LINE HELD PRESSURE UT WASREDUCED TO HALF-RATE AT 0330 HRS. SHORTLY AFTER THAT THE LEAK WAS IDENTIFIED AND THE LINE SHUT DOWN AT 0400 HRS. AFTER EXCAVATION, A 1 1/4" CRACK WAS DISCOVERED ALONG THE LONGITUDINAL WELD (S.A.W. PIPE). NO EXTERNAL CORROSION WAS EVIDENT. A PLIDCO SLEEVE WAS BOLTED ON AND THE LINE RESTORED TO SERVICE AT REDUCED PRESSURE AT 0810 MARCH 27, 1989. THE SLEEVE WAS WELDED AND PERMANENT REPAIRS COMPLETED AMRCH 28, 1989.
2017-09-29 08:50 | YES | NO | 19890055 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1989-04-09 | 700 | MN | ST LOUIS |  | NO |  | NO | 2 1/2 MI. SOUTH OF HIGHWAY 2 ON TOWNSHIP ROAD 5903 (JOHNSON RD.) TO POINT LOCATED ON SE 1/4 OF NE 1/2, SECTION 17, TOWNSHIP 50N IN RANGE 19W. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 60368.9806 | 121788.6179 | CRUDE OIL | 1 | 100 | 30 | NO | NO | 26 | 0.28 | 52000 | WELDED |  | 662 | 456 | YES | 24 | 857 | 6 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR, GENERAL MANAGER CORPORATE AFFAIRS | 7153941404 | GREAT LAKES GAS PERSONNEL WERE ON THEEIR RIGHT-OF-WAY (WHICH IS IN THE VICINITYOF LAKEHEAD'S) WHEN THEY NOTICED OIL ON THE GROUND. LAKEHEAD PIPE LINE EMERGENCY NUMBER AT SUPERIOR, WISCONSIN WAS NOTIFIED AT 0700 MST AND LINE 2 AND 3 WERE SHUT DOWN AT 0705 MST. LAKEHEAD EMERGENCY MAINTENANCE PERSONNEL WERE SENT TO THE LEAK SITE, ARRIVING AT 8:30 MST. AFTER EXCAVATING THE AREA, IT WAS DISCOVEREDTHAT A 4' BY 6' ROCK HAD CAUSED A 20" LONG, 2" DEEP GOUGE IN THE 6:00 O'CLOCK POSITION ON LINE 2 (26"). THE RESULTING 4" LONG HAIRLINE CRACK LEAKED AN ESTIMATED 100 BARRELS OF CRUDE OIL. CLEANUP ACTIVITIES STARTED IMMEDIATELY AND ON APRIL 12, 1989, THE MINNESOTA POLLUTION CONTROL AGENCY AGREED TO ALLOW BURNING OF REMAINING UNCOVERED OIL. THE GOUGE WAS REAPRIED WITH 30" PLIDCO SLEEVE AND THE LINE RESTORED TO FULL OPERATING PRESSURE APRIL 10, 1989.
2017-09-29 08:50 | YES | NO | 19890056 |  | 809 | ARCO PIPE LINE CO | YES | 1989-04-11 | 900 | TX | ANDREWS |  | NO |  | NO | 10 1/2 MILES NORTHWEST OF ANDREWS, TEXAS -- STATION #1558466. |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2030 | 1750.7004 | 3531.8699 | CRUDE OIL | 1 | 129 | 40 | NO | NO | 8 | 0.22 | 35000 | WELDED |  | 953 | 530 | YES | 12 | 953 | 12 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, SOUOTHERN AREA MANAGER | 3193311300
2017-09-29 08:50 | YES | NO | 19890057 |  | 26086 | SEADRIFT PIPELINE CORP | NO | 1989-04-27 | 1740 | TX | BRAZORIA |  | NO |  | NO | BET. STATE HIGHWAY 36 AND COUNTY ROAD 23. LEAK WAS APPROXIMATELY 1/4 MILE WEST OF MILE MARKER 89. |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17248.2802 | 34796.748 | L. P. G. | 2 | 50 | 0 | NO | NO | 6 | 0.25 | 42000 | WELDED |  | 1864 | 950 | YES | 24 | 2660 | 1 | 61 | EXTERNAL | Null | YES | OTHER | ELECTROLYTIC | NO DATA |  | Null | NO DATA |  | Null | Null | J. L. WYATT, ENVIRONMENTAL ENGINEER | 5127883176 | THE LEAK WAS REPORTED TO THE PIPELINE DISPATCHER BY THE LOCAL RANCH FOREMAN WHO NOTICED AN ICE BALL ON THE GROUND. THE LINE PRESSURE WAS REDUCED BY PUMPS AT THE MARKHAM STATION, THE LPG WAS FORCED THROUGH THE LINE WITH NITROGEN, AND THE LINE WAS ISOLATED WITH VALVES NEAR STATE HIGHWAY 36 AND COUNTY ROAD 25. HE DEFECTIVE SECTION OF PIPE WAS REPLACED WITH NEW PIPE AND THE LINE WAS RETURNED TO SERVICE ON APRIL 29.
2017-09-29 08:50 | NO | NO | 19890058 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1989-05-16 | 930 | MN | ITASCA |  | NO |  | NO | 1/3 M. NORTH OF U.S. HIGHWAY 2 TO POINT LOCATED IN NW1/4 OF SE1/4 OF SECTION 23, TOWNSHIP 56N IN RANGE 27W IN DEER RIVER TOWNSHIP, ITASCA COUNTY, MINNESOTA. |  | LINE PIPE | LONGITUDINAL WELD |  | 1967 | OTHER | 1/2" LONG HAIRLINE CRACK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 32300 | 27855.9725 | 56196.748 | CRUDE OIL | 1 | 15 | 10 | NO | NO | 34 | 0.34 | 52000 | WELDED |  | 611 | 56 | YES | 8 | 764 | 14 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR, GENERAL MANAGER CORPORATE AFFAIRS | 7153941404 | LAKE HEAD PERSONNEL BASED AT OUR DEER RIVER, MN PUMP STATION WERE NOTIFIED OF A CRUDE OIL SMELL BY A PASSING MOTORIST AT 0630 MST, MAY 16, 1989. THE LINE WAS WALKED IN THE VICINITY DESCRIBED BY THE MOTORIST AND THE LEAK WAS VISUALLY CONFIRMED ON TEH 34" LINE 3. THIS LINE WAS CURRENTLY IDLE DUE TO SCHEDULED CONSTRUCTION AT OUR CLEARBROOK PUMP STATION. AFTER THE AREA WAS EXCAVATED, A 1/2" HAIRLINE CRACK WAS DISCOVERED AT THE TOP EDGE OF THE LONGITUDINAL SEAM (S.A.W. PIPE). NO EXTERNAL CORROSION WAS EVIDENT. A PLIDCO REPAIR SLEEVE WAS BOLTED IN PLACE AT 1900 MST, MAY 16, 1989 AND WELDED FOR PERMANENT REPAIR AT 1700 MST, MAY 17,, 1989.
2017-09-29 08:50 | YES | NO | 19890059 |  | 13162 | NAVAJO REFINING CO | NO | 1989-05-01 | 1530 | TX | EL PASO |  | NO |  | NO | ACCIDENT HAPPENDED AT MILE POST 189.5 APPROXIMATELY 17 MILES EAST OF EL PASO, TX. |  | LINE PIPE | VALVE |  | 1953 | OTHER | MAINTANER HIT 2" VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 23940 | 20646.1914 | 41651.7073 | DIESEL FUEL | 1 | 876 | 40 | NO | NO | 8 | 0.25 | 1460 | WELDED |  | 1200 | 200 | YES | 4 | 719 | 23 | 89 | NO DATA | Null | YES | OTHER | IMPRESSED CURRENT | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES TOWNSEND, CATHODIC PROTECTION SUPV. | 5057483311 | PIPELINE RIGHT-OF-WAY WAS BEING CLEARED BY GRADER PREPARINT RIGHT OF WAY FORTRENCHER SO PORTIONS OF THE PIPELINE COULD BE REPLACED WITH NEW COATED PIPE. GRADER HIT AN UNKNOWN BURIED 2" GATE VALVE BREAKING VALVE FROM PIPELINE. GRADER OPERATOR NOTIFIED CONTRACTOR FOREMAN WHO THEN NOTIFIED COMPANY FOREMAN WHO NOTIFIED THE CONTROL CENTER TO SHUT THE PIPELINE DWON AND DISPATCHED MEN TO CLOSE UPSTREAM BLOCK VALVE. PRIOR TO GRADER CLEARING RIGHT-OF-WAY PIPELINE WAS STAKED AND SPOTTED AND EXPOSED EVERY 50 YRDS IN AN EFFORT TO AVOID DAMAGING LINE. GRADER OPERATOR WAS ACCOMPANIED BY AN ADDITIONAL PERSON ON THE GROUND LOOKING FOR AREAS OF CONCERN.
2017-09-29 08:50 | YES | NO | 19890060 |  | 12127 | MARATHON PIPE LINE CO | YES | 1989-05-08 | 1100 | MI | MONROE |  | NO |  | NO | SECTION 9, T8S, R7E, BEDFORD TOWNSHIP., MONROE CO. 1 1/2 MILES EAST OF SAMARIA. |  | TANK FARM | PIPE |  | 0 | OTHER | FAILED TANK MIXER SHAFT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12936.2101 | 26097.561 | CRUDE OIL | 2 | 165 | 164 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE PRESIDENT | 4194222121 | ON MAY 8, 9189 AT APPROXIMATELY 1100 HRS. CST, THE MIXER SHAFT ON TANK 706 AT MARATHON PIPE LINE COMPANY'S SAMARIA STATION FAILED CAUSING A GAP IN THEH SEAL. 165 BBLS. OF PETROLEUM CURDE OIL WAS RELEASED INTO THE TANK DIKE AREA. EMERGENCY RESPONSE PROCEDURES WERE INITIATED IMMEDIATELY. THE TANK WAS DRAINED TO MINIMIZE THE SPILL EXTENT AND 164 BBLS. WERE RECOVERED FROMTHE DIKED AREA BY VACUUM TRUCKS. AT THE REQUEST OF THE MONROE COUNTY HEALTH DEPARTMENT, SOIL WAS REMOVED FROM THE DIKED AREA AND DISPOSED OF IN ACCORDANCE WITH THEIR REQUIREMENTS. ON MAY 10, 1989, THE TANK MIXER WAS REMOVED FOR REPAIR AND THE TANK WAS RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19890061 |  | 395 | AMOCO OIL CO | YES | 1989-04-24 | 1350 | IA | DUBUQUE |  | NO |  | NO | NW 1/4, SECTION 4, T88N, R2E |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 431207.0044 | 869918.6992 | GASOLINE | 1 | 800 | 50 | NO | NO | 10 | 0.28 | 0 | WELDED |  | 1298 | 100 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RICHARD E. PETERSON, AREA MANAGER | 6124254750 | TILING CONTRACTOR HIT LINE WITH TILING MACHINE CAUSING A 2" RIP IN APE WALL. CONTRACTOR DID NOT CONTACT THE STATE ONE-CALL, OR PIPELINE OPERATOR PRIOR TO EXCAVATING.
2017-09-29 08:50 | YES | NO | 19890062 |  | 809 | ARCO PIPE LINE CO | YES | 1989-04-17 | 1930 | MO | BOONE |  | NO |  | NO | 5 MILES WEST OF CENTRALIA, MO IN W/2/ NW/4/ 1-51-12, S OF MISSOURI RT 22. |  | LINE PIPE | PIPE |  | 1921 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 4657.0356 | 9395.122 | GASOLINE | 3 | 169 | 4 | NO | NO | 8 | 0.32 | 35000 | THREADED |  | 710 | 255 | YES | 24 | 895 | 14 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | O.D. HARRIS, NORTHERN AREA MANAGER | 3163311300 | FARMER STRUCK LINE WITH CHISEL PLOW WHILE PREPARING FIELD FOR SPRING PLANTING
2017-09-29 08:50 | YES | NO | 19890063 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1989-04-20 | 2130 | ND | PEMBINA |  | NO |  | NO | 1/4 MILE NORTH OF U.S. HIGHWAY 81 TO POINT LOCATED ON SE 1/4 OF SW 1/4 OF SEC. 32, TOWNSHIP 162N IN RANGE 51W IN JOLIETTE TOWNSHIP, PEMBINA COUNTY, ND. |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 74100 | 63904.878 | 128921.9512 | CRUDE OIL | 1 | 30 | 20 | NO | NO | 34 | 0.31 | 52000 | WELDED |  | 619 | 307 | YES | 8 | 774 | 19 | 75 | EXTERNAL | Null | YES | OTHER | ANAEROBIC BACTERIAL | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. STAUDONAR, GENERAL MANAGER CORPORATE AFFAIRS | 7153941404 | A PASING MOTORIST NOTIFIED THE NORTH DAKOTA STATE POLICE (NDSP) OF A STRONG PETROLEUM ODOR IN THE VICINITY OF LAKEHEAD'S JOLIETTE, ND PUMPING STATION. THE NDSP CONTACTED LAKEHEAD PIPE LINE'S EMERGENCY NUMBER OF SUPERIOR, WISCONSIN AT 2153 MST, 4/20/89. LINES 1,2 AND 3 COMPLETTED SHUT DOWN AT 2242 MST. LAKEHEAD EMERGENCY PERSONNEL WERE CALLED OUT AND BEGAN ARRIVING AT THE LEAK SITE AT 0045 MST 4/21/89, WITH THE LEAK VISUALLY CONFIRMED AT 0445 MST (DAYBREAK) ON THE 34" LINE 3. A NARROW BAND OF EXTERNAL CORROSION, OCCURRING IN AN AREA DIVIDED BY A WALL THICKNESS CHANGE, CAUSED PINHOLES AT THE 7:00 O'CLOCK POSITION ON THE .312 W.T. SECTION AND THE 3:00 O'CLOCK POSITION ON THE .281 W.T. SECTION. AN ESTIMATED 30 BARRELS OF CRUDE OIL LEAKED FROM THE LINE WITH 20 BARRELS RECOVERED. THE REMAINING OIL WAS BURNED UNDER THE AUTHORIZATION OFTHE NORTH DAKOTA DEPARTMENT OF HEALTH. THE LEAK WAS REPAIRED WITH TWO 30" PLIDCO SLEEVES AND THE LINE WAS RETURNED TO FULL SERVICE APRIL 27, 1989.
2017-09-29 08:50 | YES | NO | 19890064 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1989-04-27 | 1450 | KS | CHAUTAUQUA | COFFEYVILLE | NO |  | NO | RANGE 8 EAST, TOWNSHIP 32 SOUTH, SECTION 23, CHAUTAUQUA COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1982 | OTHER | SMALL CRACK IN DENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1271 | 1096.1282 | 2211.3333 | FUEL OIL | 2 | 50 | 0 | NO | NO | 6 | 0.13 | 2264 | WELDED |  | 1630 | 1306 | YES | 24 | 2220 | 22 | 82 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | THIS LINE WAS BEING STARTED UP AFTER BEEN DOWN FOR SEVERAL DAYS. SHORTLY AFTER PRODUCT STARTED FROM COFFEYVILLE, PRESSURE AND FLOW CONDITIONS DID NOT APPEAR NORMAL. DISPATCHER HAD THE LINE SHUT DOWN WHILE HE CHECKED CONDITIONS WITH THE TWO AREA OPERATORS ON EITHER END. IT WAS DURING THIS TIME THAT HE RECEIVED A LEAK REPORT.
2017-09-29 08:50 | YES | NO | 19890065 |  | 10313 | KOCH PIPELINE INC | YES | 1989-04-28 | 30 | OK | GRANT |  | NO |  | NO | SEC 17, T27N, R5W. |  | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 1000 | 0 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1440 | 970 | YES | 24 | 2000 | 2 | 74 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARC S. DEVARENNES, DIVISION ENGINEER | 4053952377 | A SMALL LEAK WAS DISCOVERED 4/25/89 AND CORRECTIVE ACTION WAS TAKEN TO REPLACE THE AFFECTED SECTION OF PIPE. REPAIRS WERE MADE AND SUBSEQUENT TO THE PURGING OF THE LINE, THE TEMPORARY REPAIR FAILED RESULTING IN THE REPORTED PRODUCT LOSS.
2017-09-29 08:50 | YES | NO | 19890066 |  | 12127 | MARATHON PIPE LINE CO | YES | 1989-04-14 | 1820 | IL | MADISON | WOOD RIVER | NO |  | NO | WOOD RIVER STATION, SOUTH 6TH ST. SEC. 27, T5N, R92, MADISON COUNTY, WOOD RIVER, ILLINOIS. |  | TANK FARM | OTHER | TANK DRAIN VALVE OPEN | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4312.07 | 8699.187 | TOLUENE | 3 | 211 | 200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE PRESIDENT | 4194222121 | AT 6:30 PM ON 4/17/89, PRODUCT WAS DISCOVERED LEAKING FROM A TANK BOTTOM DRAIN AT MARATHON PIPE LINE COMPANY'S WOOD RIVER STATION. INVESTIGATION REVIEALED THAT AND EMPLOYEE INSTRUCTED TO DRAIN WATER FROM TANK ROOFS MISTAKENLY OPENED THE WRONG VALVE, RESULTING IN A RELEASE ROM TANK 1297 OF AN ESTIMATED 422BBLS., APPROXIMATELY HALF OF WHICH WAS RAFFINATE AND HALF OF WHICH WAS WATER. ALL THE RAFFINATE AND WATERR WAS CONTAINED IN TEH TANK'DIKE AREA WITH CLEANUP ACTIVITY MONITORED BY THE ILLINOIS EPA. THE DOT WAS NOTIFIED ON 4/18/89 AT 11:50 AM. CST BY TELEPHONE WHEN THE ESTIMATED CLEANUP COSTS REACHED $5,000.00.
2017-09-29 08:50 | YES | NO | 19890067 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-05-18 | 1850 | OK | TULSA |  | NO |  | NO | IN A PASTURE 700 FEET EAST OF N. SHERIDAN ROAD (NW/4, NW/4 SECTION 23, T2 IN, R 13 E TULSA COUNTY, OKLAHOMA). |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3018.449 | 6089.4309 | OIL AND GASOLINE | 3 | 75 | 15 | NO | NO | 12 | 0.3 | 30000 | WELDED |  | 750 | 689 | YES | 8 | 968 | 11 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | ON 5/18/89 AT 1850 HOURS, A LOCAL RESIDENT (88901 N. HUDSON) CALLED OUR DISPATCHING CENTER TO REPORT THAT SHE HAD SEEN PETROLEUM PRODUCT ON A NEIGHBORINGCREEK (MILE POST 113 #3-12" CUSHING-HEYWORTH). THE LINE WAS IMMEDIATELY SHUT DOWN AND CREWS WERE DISPATCHED TO INVESTIGATE. THE LOCAL SUPERVISOR CONFIRMED THE PRESENCE OF A LEAK AT 2037 HOURS. MAIN LINE VALVES WERE CLOSED AT MILE POST 107 AND MILE POST 117. EXCAVATION OF THE SITE REVEALED A SMALL EXTERNAL CORROSION PIT AS THE SOURCE OF THE LEAK. PIPE TO SOIL POTENTIALS TAKEN AT THE SITE INDICATED A VOLTAGE LEVEL OF -1.15. THE LINE WAS TEMPORARILY CLAMPED OFF TO STOP THE LEAK. AFTER THE CONTAMINATED SOIL WAS REMOVED AND CONDITIONS WERE SAFE TO WELD, PERMANENT REPAIRS WERE INITIATED (NEW PIPE SPOOL). FIVE TEMPORARY DAMS WERE CONSTRUCTED TO CONTAIN THE PRODUCT THAT HAD REACHED THE CREEK. APPROXIMATELY 20 BARRELS WERE RECOVERED BY VACUUM TRUCK; THE BALANCE WAS BURNED OF THE CREEK AFTER OBTAINING AUTHORIZATION FROM STATE ENVIRONMENTAL OFFICIALS. THE CONTAMINATED SOIL WAS REMOVED AND HAULED TO A SANITARY LAND FILL.
2017-09-29 08:50 | YES | NO | 19890068 |  | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1989-06-20 | 1930 | TX | HOWARD |  | NO |  | NO | 1.14 MILES SOUTH EAST OF INTERSTATE 20 AND 3.98 MILES EAST OF BIG SPRING, TEXAS. |  | LINE PIPE | PIPE |  | 1957 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 43120.7004 | 86991.8699 | CRUDE OIL | 1 | 300 | 260 | NO | NO | 6 | 0.19 | 30000 | WELDED |  | 1146 | 50 | YES | 8 | 1433 | 11 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED, REGULATORY COMPLIANCE SUPV. | 9152673673 | AT APPROXIMATELY 7:30P.M. ON JUNE 20, 1989 (TUESDAY), COSDEN'S BIG SPRING, TEXAS, CONTROL CENTER WAS NOTIFIED BY ROBERT ROBINSON, A MEMBER OF A LANDOWNERFAMILY, THAT OIL HAD BEEN FOUND IN BEALL'S CREEK. THIS WAS THE FIRST INDICATION OF PIPELINE LEAK. THE CONTROL CENTER IMMEDIATELY NOTIFIED COMPANY PERSONNEL AND THE COLORADO RIVER MUNICIPAL WATER DISTRIC (CRMWD) OF THE ACCIDENT SO THAT CONTAINMENT AND CLEAN-UP ACTIVITIES COULD BE INITIATED. THREE (3) JOINTS OF PIPE (EACH 40' IN LENGTH( WERE FOUND TO BE SPLIT LONGITUDINALLY ALONG THEIR ENTIRE LENGTHS, EACH SPLIT APPROX. 1/4" IN WIDTH. THE JOINTS OF PIPE HAD BEEN PREVIOUSLY SPLIT DUE TO THE FORCE EXERTED BY HYDRO-TEST WATER HAVING FROZEN AND RUPTURED THE JOINTS. THE PIPELINE'S HYDROTEST WATER HAD JUST BEENDISPLACED WITH OIL. THE LEAKAGE EVENTUALLY FLOWED DOWNSTREAM A STRAIGHT LINE DISTANCE OF APPROXIMATELY 3 MILES. THE OIL WAS CONTAINED BY SPILL-BOOMS, PICKED UP BY VACUUM TRUCKS, ND SORBENT MATERIALS. THE THREE (3) JOINTS OF SPLIT PIPE WERE REPLACED AND RE-HYDROTESTED. RECOVERED OIL WAS TAKEN TO COMPANYFACILITIES AND DISPOSED OF IN AN ENVIRONMENTALLY SATISFACORY MANNER. CLEAN-UP WAS COMPLETED AND CERTIFIED SATISFACTORY BY REGULATORY AGENCIES ON JUNE 27, 1989.
2017-09-29 08:50 | YES | NO | 19890069 |  | 443 | AMOCO PIPELINE CO | NO | 1989-06-18 | 1130 | TX | GALVESTON |  | YES | 28 O3' 93 57' 16.623 | YES | APPROXIMATELY 100 MILES SOUTHEAST OF GALVESTON, TEXAS OFFSHORE IN GULF OF MEXICO. |  | LINE PIPE | PIPE |  | 1978 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 431207.0044 | 869918.6992 | CRUDE OIL | 1 | 10 | 0 | NO | NO | 10 | 0.37 | 52000 | WELDED |  | 2160 | 1400 | YES | 24 | 2700 | 9 | 78 | NO DATA | Null | YES | NO DATA |  | SHIP ANCHOR |  | Null | NO DATA |  | Null | Null | HOWARD B. SPALDING, SUPERVISOR-OPERATIONS | 4099483407 | SCATTERED "BLOSSOMS" WERE OBSERVED DURING AN AERIAL PATROL AT ABOUT 11:30 AMON 6/18/89. CAL DIVE INTERNATIONAL ARRIVED ON LOCATION ON 6/19/89. THE 10"LINE HAD BEEN PULLED UP FROM THE OCEAN FLOOR BY APPROXIMATELY 15"-18". A HORIZONTAL DEFLECTION OF ABOUT 18" WAS DISCOVERED BY THE DIVERS. DUE TO THE TYPE OF DAMAGE, IT WAS NECESSARY TO INSTALL A 10" SPOOL PIECE APPROXIMATELY 45'LONG. IT WAS INSTALLED USING "GRIPPER" REPAIR TOOLS. THE REPAIR WAS COMPLETED AND THE SECTION RETURNED TO SERVICE AT APPROXIMATELY 9:30 A.M. ON SATURDAY, JULY 1, 1989.
2017-09-29 08:50 | YES | NO | 19890070 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1989-06-16 | 738 | AR | UNION | EL DORADO | NO |  | NO | 20" LINE P2, M.P. 238.5; UNION COUNTY, ARKANSAS, APPROXIMATELY 3 MILES SOUTHEAST OF EL DORADO, ARKANSAS, NEAR HIBANK ROAD. ALIGNMENT DRAWING NO. TPF-P2-40 AND |  | LINE PIPE | PIPE |  | 1944 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 16400 | 14143.5897 | 28533.3333 | GASOLINE | 3 | 566 | 332 | NO | NO | 20 | 0.38 | 35000 | WELDED |  | 700 | 147 | YES | 24 | 1174 | 1 | 57 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | TEXAS PREVENTION CONTROL | YES | YES | TOM U. HANNIGAN, VICE PRESIDENT - OPERATIONS. | 0000000000 | EXCAVATOR CALLED AND THE 20" LINE WAS MARKED AT THE TIME THE 6" WATER LINE CORSSING WAS ORIGINALLY INSTALLED DURING AUGUST, 1980. FOUR AN ACCOUNT OF THEACCIDENT, REFER TO THE ATTACHED SHEET OF PAPER.
2017-09-29 08:50 | YES | YES | 19890071 |  | 6856 | GULF CENTRAL PIPELINE CO | YES | 1989-07-04 | 2300 | AR | INDEPENDENCE |  | NO |  | NO |  |  | LINE PIPE | VALVE |  | 1968 | OTHER | LEAKING ON MAINLINE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HENRY PARKER, MAINTENANCE SUPERINTENDENT | 3144865488 | AT 23:00 ON JULY 4,1989 OUR DISPATCHER IN WICHITA, KANSAS RECIEVED A CALL FROM DALE RUST (WITH INDEPENDENCE CO. EMERGENCY SQUAD) WHO WAS AT THE SAM GRISSOM RESIDENCE APPROXIMATELY 8 MILES NORTH OF BATEVILLE, AR. MR. RUST SAID THEY SMELLED AMMONIA. AT MIDNIGHT, JAMES LITAKER OF GULF CENTRAL REPORTED A SMALL LEAK AT BLOCK VALVE 3-37 AT MILESPOST 3-206. THE LEAK WAS FOUND TO BE A LEAKING BLIND FLANGE ON THE CHECK VALVE BODY. WE LATER LEARNED THAT MRS. GRISSOM COMPLAINED OF A UPSET STOMACH AND DIFFICULITY IN BREATHING AND WENT TO THE HOSPITAL WHERE A DOCTOR SAID SHE WAS HAVING AN ALLERGY REACTION.
2017-09-29 08:50 | YES | NO | 19890072 |  | 443 | AMOCO PIPELINE CO | YES | 1989-06-17 | 1026 | IL | KNOX |  | NO |  | NO | SIX MILES EAST OF KNOXVILLE, IL., ON ILLINOIS STATE HIGHWAY 150 IN KNOX COUNTY, IL. |  | LINE PIPE | PIPE |  | 1931 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 129362.1013 | 260975.6098 | GASOLINE | 3 | 2286 | 1793 | NO | NO | 12 | 0.34 | 35000 | WELDED |  | 719 | 705 | YES | 8 | 899 | 8 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.A. STAHL - AREA MANAGER | 2197382384 | TWELVE INCH PRODUCTS PIPELINE WAS BEING STARTED UP TO ESTABLISH FLOW IN THE PIPELINE SO A STOPPEL FITTING COULD BE WELDED TO THE PIPELINE. AS THE PRESSURE CAME UP THE LONGITUDIAL SEAM ON A JOINT OF ERW PIPE RUPTURED DUE TO A MANUFACCTURERS DEFECT IN THE WELD AND RESULTED IN A SPILL OF UNLEADED GASOLINE.
2017-09-29 08:50 | YES | NO | 19890073 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-06-22 | 800 | TX | SCURRY | SNYDER | NO |  | NO | 8 MILES NORTH OF THE CITY OF SNYDER, TEXAS ON TEXAS HWY. 208. LEAK SITE IS ON CHEVRON PIPE LINE CO. PROPERTY LOCATED AT THE NORTH SNYDER TANK FARM & STATION. |  | TANK FARM | OTHER | ROOF DRAIN HOSE | 0 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 80 | 75 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.M. COOK, COMPLIANCE COORDINATOR | 9156877559 | ROUTINE INSPECTION OF TANK FARM BY CHEVRON PIPE LINE GAUGER, DOUG FOSTER, AT8:00AM. JUNE 22, 1989, FOUND THE ROOF DRAIN LEAKING CRUDE AT TANK NO. 510. HE CLOSED THE ROOF DRAIN VALVE AND CALLED HIS SUPERVISOR.
2017-09-29 08:50 | YES | YES | 19890074 |  | 26125 | CALNEV PIPELINE CO | YES | 1989-05-25 | 805 | CA | SAN BERNARDINO |  | NO |  | NO | 350' NORTH OF HIGHLAND AVENUE ON THE EAST SIDE OF THE SOUTHERN PACIFIC RAILROAD TRACK. |  | LINE PIPE | PIPE |  | 1970 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 2 | 0 | 2 | 31 | 0 | 31 | 0 | 0 | 0 | GASOLINE | 2 | 0 | 0 | YES | NO | 14 | 0.31 | 52000 | WELDED |  | 1670 | 1560 | YES | 28 | 2085 | 1 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | PAUL B. STRENGELL, MANAGER OF ENGINEERING | 7143879502 | A SOUTHERN PACIFIC RAIROAD TRAIN DERAILED ON MAY 12, 1989 AT THE SITE OF THESUBSEQUENT PIPELINE RUPTURE. THE PIPELINE WAS SHUT DOWN DURING THE CLEAN-UPOPERATIONS. CLEAN-UP WAS MONITORED BY PIPELINE PERSONNEL AND THE PIPELINE EXCAVATED AND INSPECTED AT SEVERAL LOCATIONS. THE LINE WAS RESTARTED ON MAY 16. ON MAY 25, 1989, DURING STABLE PIPELINE OPERATIONS, THE PIPELINE RUPTUREDSPILLING GASOLINE AND CAUSING A FIRE.
2017-09-29 08:50 | NO | NO | 19890075 |  | 19226 | TEXACO PIPELINE INC | YES | 1989-06-03 | 1540 | TX | MIDLAND | MIDLAND | NO |  | NO | T&PRR CO. SURVEY BLOCK 38 SECTION 45 T-1-S COUNTY ROAD 1150 SOUTH NEAR INTERSTATE 20 BASIN MIDLAND STATION. |  | TANK FARM | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 25 | 0 | NO | NO | 12.75 | 0.38 | 35000 | WELDED |  | 133 | 7 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID R. SEATON - WICHITA FALLS DISTRICT MANAGER | 8177230761 | AT 24:00 ON JUNE 2, 1989, OPERATOR NOTICED A LOSS OF 0.01' FROM TK 1321, THEMAINLINE RELIEF TANK. LOSS CONTINUED AT THE RATE OF APPROXIMATELY 0.01' PERHOUR. AT APPROXIMATELY 12:00 ON JUNE 3, 1989, MECHANICAL SUPERVISOR LOCATED A TANK VALVE LEAKING INTO THE STATION SUMP. LEAK WAS ELIMINATED. AT 15:00, AN ARCO GAUGER ON BASIN TANK FARM SMELLED CRUDE OIL. FURTHER INVESTIGATION BY COMPANY PERSONNEL LOCATED A LEAK ON THE 12" MAINLINE RELIEF LINE LOCATEDWITHIN THE BASIN STATION. BASED ON THE TANK LOSS, INITIAL LEAK ESTIMATE WAS150 BARRELS. AT 17:22, LEAK WAS REPORTED TO OPS/DOT BY H.K. SUMRALL, DISTRICT ENGINEER. THE REPORT #8724 WAS GIVEN TO PETTY OFFICER JOHN GREZ. LINE WAS EXCAVATED AND A TEMPORARY REPAIR MADE. LEAK BARRELS WERE RE-ESTIMATED AT 25 BARRELS. THE REMAINING CRUDE OIL LOST FROM TANKAGE LEAKAGE INTO THE STATION SUMP. PLEASE NOTE CHANGE IN SPECIFIC LOCATION DESCRIPTION.
2017-09-29 08:50 | YES | NO | 19890076 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1989-06-13 | 700 | TX | CARSON |  | NO |  | NO | SECTION 90, 8. & G.N. R.R., BLOCK 4. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 104104 | 89780.748 | 181124.0325 | NATURAL GAS LIQUID | 2 | 10495 | 0 | NO | NO | 6 | 0.14 | 1788 | WELDED |  | 1208 | 262 | YES | 24 | 1679 | 1 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | OTHER | PIPELINE WARNING SIGNS | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | FLOODWATERS AND/OR DEBRIS CAUSED PIPELINE TO RUPTURE.
2017-09-29 08:50 | NO | NO | 19890077 |  | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1989-06-06 | 1845 | OK | SEMINOLE |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 34496.5604 | 69593.4959 | CRUDE OIL | 1 | 30 | 0 | NO | NO | 10 | 0.35 | 26000 | WELDED |  | 500 | 690 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MERLE LAND, AREA SUPERINTENDENT | 4052758280 | ON JUNE 6,1989, KOCH OIL COMPANY'S TOMAHAWK PIPELINE WAS SHUT DOWN TO CHANGEOUT A ROAD CROSSING. TO MAKE THIS CHANGE OUT A BLOCK VALVE BETWEEN THE PUMPSTATION AND THE ROAD CROSSING WAS CLOSED TO FACILITATE DRAIN UP. AT APPROXIMATELY 6:45 PM. THE STATIONS REMOTE SUPERVISORY CONTROL SYSTEM WAS DAMAGED BYA SEVERE LIGHTNING STORM AND INADVERTLY ALLOWED THE FACILITY TO RESTART AGAINST A BLOCKED LINE. THE RESULTING RUPTURE WAS DUE TO THE FACT THAT THE PRESSURE KILL SWITCHES, SET AT 500 #, DID NOT REACT FAST ENOUGH TO STOP THE POSITIVE DISPLACEMENT PUMPS BEFORE THE FAILURE OCCURED. TO REDUCE THE POSSIBILITY OF FUTURE ACCIDENTS, THE FOLLOWING CHANGES HAVE BEEN MADE. AUTOMATIC BYPASS VALVES HAVE BEEN INSTALLED AND SET AT 450#, STATION CONTROLS HAVE BEEN REPROGRAMMED TO REACT QUICKER TO EXCESSIVE PRESSURE, AND OPERATING PROCEDURE FOR ABNORMAL CONDITIONS SUCH AS BLOCKED LINES HAVE BEEN REVISED.
2017-09-29 08:50 | YES | NO | 19890078 |  | 12628 | MOBIL PIPELINE CO | YES | 1989-05-28 | 1200 | TX | TITUS | MT. PLEASANT | NO |  | NO | 3/4 MILE WEST OF STATE HWY. 1402 ON TITUS COUNTY ROAD NW 41 ADJACENT TO EAST PINEY CREEK BRIDGE - PIPIELINE MILEPOST 121.9. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 38808.6304 | 78292.6829 | CRUDE OIL | 1 | 309 | 245 | NO | NO | 20 | 0.31 | 42000 | WELDED |  | 800 | 250 | YES | 2 | 995 | 8 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | AT 1212 HOURS, A LANDOWNER IN THE VICINITY OF THE PIPELINE REPORTED A LEAK AT MILEPOST 121.9 ON THE CORSICANA, TX TO PATOKA, IL 20" PIPELINE TO THE OPERATIONS CONTROLLER. THE PIPELINE WAS IMMEDIATELY SHUT DOWN. INSPECTION OF THEPIPELINE BY COMPANY PERSONNEL REVEALED AN INDENTATION WITH A HOLE AT THE 10 O'CLOCK POSITION ON THE ABOVEGROUND SPAN OF EAST PINEY CREEK. CRUDE OIL WAS SPRAYING INTO THE CREEK AND ACROSS A SMALL WOODEN BRIDGE. APPARENTLY, THE HOLE WAS CAUSED BY A RIFLE SHOT FROM THE BRIDGE. THE LANDOWNER REPORTED HEARING 3 GUNSHOTS APPROXIMATELY ONE HOUR PRIOR TO DETECTING THE LEAK. THE 20" PIPELINE WAS REPAIRED BY WELDING TWO FEET OF FULL WRAP OVER THE DAMAGED AREA.
2017-09-29 08:50 | YES | NO | 19890079 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-05-05 | 1430 | TX | BLANCO |  | NO |  | NO | BENEDUM-SWEENY LINE - MP 214, 1500 FEET DUE SOUTH OF FM 1323 ON GILLESPIE/BLANCO COUNTY LINE. |  | LINE PIPE | LONGITUDINAL WELD |  | 1928 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 5174.4841 | 10439.0244 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 10.78 | 0.37 | 36000 | WELDED |  | 930 | 783 | YES | 24 | 1475 | 5 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENG. & TECHNICAL SERVICES | 9186614721 | PROPERTY OWNER DISCOVERED PRODUCT LEAKING AND NOTIFIED COMPANY OFFICE. MAINTENANCE CREWS WERE DISPATCHED TO THE SCENE. THE LINE WAS SHUT DOWN, EXCAVATED, AND SECTION OF PIPE REPLACED.
2017-09-29 08:50 | YES | NO | 19890080 |  | 26078 | PLACID OIL CO | NO | 1989-05-24 | 930 | LA | LA SALLE | CATAHOULA LAKE | NO |  | NO | 92.05/31.31 - T6N, R4E, LASALLE PARISH, LA. |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 64681.0507 | 130487.8049 | CRUDE OIL | 1 | 7 | 0 | NO | NO | 4 | 0.25 | 42000 | WELDED |  | 200 | 125 | YES | 24 | 500 | 1 | 86 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.G. GANEY, PIPELINE SUPERINTENDENT | 3189922131 | FOUR INCH TRANSMISSION LINE LAID IN 1962 ON TOP OF GROUND. SAME LINE SCRAPED, DOPED, AND BURIED 18 INCHES IN 1982. LEAK OCCURRED AT 0930 HOURS, MAY 24,1989. PIPELINE SHUT IN AT 1000 HOURS, LEAK STOPPED. CORROSION HOLE FOUND BY DIVERS. CLAMP INSTALLED. VALVES BLOCKED ON BOTH ENDS. REMAINING OIL VACUMMED FROM LINE, DISPLACED WITH WATER, AND LINE PERMANENTLY ABANDONED IN PLACE.
2017-09-29 08:50 | YES | NO | 19890081 |  | 5075 | FARMERS UNION CENTRAL EXCHANGE INC - CENEX PIPELIN | YES | 1989-06-18 | 1305 | ND | MCKENZIE | NEWTOWN | NO |  | NO | OCCURED IN A DRY LAND FIELD. LOCATION WAS NOT NEAR ANY STRUCTURES OR WATERWAY |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12936.2101 | 26097.561 | DIESEL FUEL | 3 | 827 | 757 | NO | NO | 8 | 0.19 | 0 | WELDED |  | 1200 | 400 | YES | 24 | 1550 | 1 | 60 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | Null | RICHARD J. LOHOF, MANAGER PIPELINE AND TERMINALS | 4062529326
2017-09-29 08:50 | YES | NO | 19890082 |  | 13131 | CONOCO INC | YES | 1989-06-12 | 1440 | NE | KIMBALL |  | NO |  | NO | S30, R53W, T14N - ADJACENT TO COUNTY ROAD #63. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 7761.7261 | 15658.5366 | DIESEL FUEL | 3 | 309 | 0 | NO | NO | 6 | 0.22 | 46000 | WELDED |  | 1440 | 507 | YES | 0 | 2000 | 1 | 54 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | PAUL HENEHAN , DIRECTOR OF ACCESS & REGULATION | 3036494096 | AT 1440 ON 06/12/89, A KIMBALL COUNTY MAINTAINER STRUCK CONOCO PIPE LINE COMPANY'S 6-INCH PRODUCTS PIPELINE WHILE SHAPING THE ROAD DRAINAGE DITCHES. THEPUNCTURE OCCURRED WHILE THE LINE WAS SHUT DOWN AND DIESEL FUEL WAS IN THIS LINE SEGMENT. THE COUNTY ROAD CREW CALLED IN ATHE LEAK AND COMPANY CLEANUP PERSONNEL WERE DISPATCHED TO THE SITE. DUE TO THE SANDY SOIL IN THIS AREA, NO BARRELS WERE RECOVERED. WITH PERMISSION FROM CHUCK BREWER OF THE NEBRASKA DEPARTMENT OF WATER QUALITY, THE CONTAMINATED SOIL WAS SPREAD OUT ON THE DIRT ROAD WHICH WAS BEING WORKED ON WHEN THE LEAK OCCURRED.
2017-09-29 08:50 | YES | YES | 19890083 |  | 13131 | CONOCO INC | NO | 1989-06-06 | 1250 | MO | LACLEDE |  | NO |  | NO | SE/4 OF SECTION 34, T36N, R15W LACLEDE COUNTY, MISSOURI. |  | LINE PIPE | PIPE |  | 1930 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 1 | 0 | 1 | 0 | 0 | 0 | 200000 | 172482.8018 | 347967.4797 | L. P. G. | 2 | 2816 | 0 | YES | YES | 10 | 0.37 | 35000 | WELDED |  | 900 | 181 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | ROAD GRADER | Null | ONE CALL |  | NO | YES | LARRY G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | ON JUNE 6, 9189 TWO LACLEDE COUNTY ROAD GRADERS WERE LOWERING THE BAR DITCH ON A COUNTY ROAD BETWEEN CAMDEN AND LACLEDE COUNTY WHEN THE SECOND GRADER STRUCK AND RUPTURED THE NUMBER 2 - 10 INCH LINE OF CONOCO PIPE LINE COMPANY. THELINE WAS INACTIVE AT THE TIME BUT WAS FILLED WITH PROPANE. WHEN THE GRADER STRUCK THE LINE, AN EXPLOSION AND FIRE OCCURRED WHICH RESULTED IN THE DEATH OF THE COUNTY EMPLOYEE. THE LINE WAS HEAVILY MARKED WITH SIGNS INDICATING THELOCATION OF THE LINE AS WELL AS LISTING AN EMERGENCY 1-800 NUMBER. THE COUNTY DID NOT CONTACT THE OPERATOR PRIOR TO COMMENCEMENT OF THE ROAD GRADING ACTIVITY.
2017-09-29 08:50 | YES | NO | 19890084 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-06-07 | 2045 | OK | OKLAHOMA | OKLAHOMA | NO |  | NO | THE BREAK OCCURRED IN THE N. CANADIAN RIVER NEAR THE S. BANK IN THE NE/4 SECTION 22 T 13 N, R1W OKLAHOMA COUNTY, OKLAHOMA. |  | LINE PIPE | GIRTH |  | 1946 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 63000 | 54332.0826 | 109609.7561 | FUEL OIL | 3 | 2653 | 10 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 700 | 623 | YES | 8 | 968 | 1 | 83 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185884850 | ON 6/7/89 AT APPROXIMATELY 20:45 HOURS (BASED UPON POST ACCIDENT REVIEW OF PRESSURE CHARTS) THE #2-8" CUSHING TO OKLAHOMA CITY PIPELINE FAILED AT THE NORTH CANADIAN RIVER CROSSING (MP 12+47) NEAR JONES, OKLAHOMA. THE RIVER WAS IN FLOOD STAGE AT THE TIME AND WAS CARRYING A SUBSTANTIAL AMOUNT OF DEBRIS (LARGE TREES, ETC.). THE COMBINATION OF DEBRIS AND STRONG RIVER CURRENTS CAUSED THE PIPE TO OVERLOAD AND ULTIMATELY RESULTED IN FRACTURE OF AN ADJACENT GIRTH WELD, RELEASING 2653 BBLS OF X-GRADE INTO THE RIVER. DISPATCHING INITIALLY RESPONDED BY SENDING A TECHNICIAN TO OKLAHOMA CITY TO INVESTIGATE A SUSPECTED METERING EQUIPMENT MALFUNCTION. HOWEVER, FURTHER INVESTIGATION INDICATED A LINE FAILURE HAD OCCURRED AND AT 23:05 HOURS THE LINE WAS SHUT DOWN AND CREWS WERE DISPATCHED TO LOCATE AND ISOLATE THE LEAK. THE DELAYED DETECTION OF THE LEAK RESULTED FROM THE FAILURE OF DISPATCH OPERATORS TO PROPERLY REVIEW LINE OPERATING PARAMETERS. DISCIPLINARY DISMISSALS AND SUSPENSIONS WERE MADE AS APPROPRIATE. RECOVERY BOOMS WERE EMPLOYED AT SEVERAL DOWN-STREAM LOCATIONS; HOWEVER, THE TURBULENT FLOOD WATER CONDITIONS DISPERSED THE RELEASED PRODUCT TO THE EXTENT THAT NO RESIDUAL PRODUCT WAS DETECTED. STATE AND LOCAL ENVIRONMENTAL OFFICIALS WERE ON SITE DURNG THE RECOVERY EFFORTS AND DOWN-STREAM MUNICIPALITIES WERE NOTIFIED AS APPROPRIATE. A METALLURGICAL REPORT INDICATED THAT THE FAILED WELD (INSTALLED IN 1946) DID NOT MEET THE CURRENT API 1104 STANDARD. A NEW 160 FOOT PIPE SPOOL WAS INSTALLED TO REPAIR THE LINE. THE CROSSING WILL BE COMPLETELY REPLACED WITH APPROXIMATELY 1100 FT OF .322 WALL X 42 CONCRETE COATED PIPE AS SOON AS WATER LEVELS DROP SUFFICIENTLY TO PERMIT INSTALLATION.
2017-09-29 08:50 | NO | NO | 19890085 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1989-06-29 | 1100 | AL | TALLADEGA |  | NO |  | NO | DAMAGE WAS LOCATED 712' EAST OF AL HIGHWAY 34. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8624.1401 | 17398.374 | GASOLINE | 3 | 1 | 0 | NO | NO | 30 | 0.31 | 52000 | WELDED |  | 699 | 374 | YES | 24 | 973 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | OTHER | UNKNOWN | Null | NO DATA |  | Null | Null | ROY M. CROOK, VICE PRESIDENT- OPERATIONS | 4043645916 | FOLLOWING A TUBOSCOPE MAGNETIC FLUX INSPECTION RUN OF THIS PIPELINE, PLANTAION BEGAN INVESTIGATING LOCATIONS SHOWN BY THE LINALOG CHART AS HAVING THE MOSTSEVERE ANOMALIES. ALTHOUGH THERE WAS NO EVIDENCE ON THE GROUND SURFACE, EXCAVATION EXPOSED THE PIPE RESTING ON A LARGE ROCK AND GASOLINE ODORS INDICATING LEAKING PRODUCT. THE UPSTREAM BLOCK VALVE WAS CLOSED AND THE PUMPS DOWNSTREAM PULLED PRODUCT AWAY FROM THE SITE. A HAIRLINE CRACK WAS OBSERVED IN THEDENTED PIPE WHEN THE ROCK WAS REMOVED, BUT THERE WAS NO LIQUID PRODUCT. THEPIPE WAS REPAIRED BY THE INSTALLATION OF A FULL ENCIRCLEMENT PRESSURE VESSELSLEEVE OVER AN EPOXY FILLER IN THE DENT. THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED AT 3:10 PM. CDST N JUNE 29, 1989 (REPORT # 10566). THE ENVIRONMENTALPROTECTION AGENCY, REGION IV OFFICE WS NOTIFIED AT 3:05 PM. CDST ON JUNE 29,1989. THE ALABAMA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT WAS NOTIFIED AT 3:00 AM. CDST ON JUNE 29, 1989. (SEE RPTID 890086 AND 890087).
2017-09-29 08:50 | NO | NO | 19890086 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1989-06-26 | 1000 | AL | TALLADEGA |  | NO |  | NO | DAMAGE WAS LOCATED 974' WEST OF ALABAMA ROAD 468. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 10348.9681 | 20878.0488 | GASOLINE | 3 | 1 | 0 | NO | NO | 30 | 0.31 | 52000 | WELDED |  | 699 | 364 | YES | 24 | 973 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | OTHER | ROCK UNDER PIPE | Null | NO DATA |  | Null | Null | ROY M. CROOK, VICE PRESIDENT-OPERATIONS | 4043645916 | FOLLOWING A TUBOSCOPE MAGNETIC FLUX INSPECTION RUN OF THIS PIPELINE, PLANTATION BEGAN INVESTIGATING LOCATIONS SHOWN BY THE LINALOG CHART AS HAVING THE MOST SEVERE ANOMALIES. EXCAVATION AT THIS SITE EXPOSED THE PIPE RESTING ON A FOUR-FOOT DIAMETER ROCK AND GASOLINE ODORS INDICATING LEAKING PRODUCT, ALTHOUGHTHERE WAS NO EVIDENCE OF LIQUID PRODUCT IN THE DITCH. THE LINE WAS SHUT DOWNAND BLOCK VALVES ON EITHER SIDE OF THE SITE WERE CLOSED. AFTER THE ROCK WAS REMOVED THE LINE BEGAN TO LEAK. THE GASOLINE WAS CAUGHT IN A LARGE CONTAINER AND PUMPED INTO WAITING TANKER TRUCKS. THE LINE WAS REPAIRED BY REMOVING A SIX-FOOT SECTION OF PIPE AND INSTALLED A NEW PRE-TESTED SECTION.THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED AT 11:26 AM CDST ON 6/26/89 (REPORT # 10331). (SEE RPTID 890085 AND 890087).THE ENVIRONMENTAL PROTECTION AGENCY, REGION IV OFFICE WAS NOTIFIED AT 12:20PMCDST ON 6/26/89.THE ALABAMA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT WAS NOTIFIED AT 10:50AM CDST ON 6/26/89.
2017-09-29 08:50 | NO | NO | 19890087 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1989-06-30 | 1030 | AL | TALLADEGA |  | NO |  | NO | DAMAGE WAS LOCATED 4,710' WEST OF ALABAMA ROAD 276. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8624.1401 | 17398.374 | GASOLINE | 3 | 1 | 0 | NO | NO | 30 | 0.31 | 52000 | WELDED |  | 699 | 378 | YES | 24 | 973 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | OTHER | ROCK UNDER PIPE | Null | NO DATA |  | Null | Null | ROY M. CROOK, VICE PRESIDENT-OPERATIONS | 4043645916 | FOLLOWING A TUBOSCOPE MAGNETIC FLUX INSPECTION RUN OF THE PIPELINE, PLANTATIOSEVERE ANOMALIES. ALTHOUGH THERE WAS NO EVIDENCE ON THE GROUND SURFACE,EXCAVATION EXPOSED THE PIPE RESTING ON A LARGE ROCK AND GASOLINE ODORS INDICATINGLEAKING PRODUCT. THE UPSTREAM BLOCK VALVE WAS CLOSED AND THE PUMPS DOWNSTREAMPULLED PRODUCT AWAY FROM THE SITE. A HAIRLINE CRACK WAS OBSERVED IN THE DENTED PIPE WHEN THE ROCK WAS REMOVED, BUT THERE WAS NO LIQUID PRODUCT. THE PIPEWAS REPAIRED BY THE INSTALLATION OF A FULL ENCIRCLEMENT PRESSURE VESSEL SLEEVE OVER AN EPOXY FILLER IN THE DENT. (SEE RPTID 890085 AND 890086).THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED AT 2:55 CDST ON 6/30/89 (REPORT #10646).THE ENVIRONMENTAL PROTECTION AGENCY, REGION IV OFFICE WAS NOTIFIED AT 2:48PMCDST ON 6/30/89.THE ALABAMA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT WAS NOTIFIED AT 2:39 CDSTON 6/30/89.
2017-09-29 08:50 | NO | NO | 19890088 |  | 18273 | SHELL PIPE LINE CORP | NO | 1989-07-05 | 1135 | CA | LOS ANGELES | LOS ANGELES | NO |  | NO |  |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 30184.4903 | 60894.3089 | GASOLINE | 3 | 1 | 0 | NO | NO | 4 | 0.24 | 35000 | WELDED |  | 1440 | 60 | YES | 4 | 2160 | 3 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | TRI-STATE UTILITIES COMPANY MADE AN INITIAL NOTIFICATION TO THE ONE-CALL SYSTEM APPROXIMATELY ONE MONTH PRIOR TO THE ACCIDENT. A SHELL PIPE LINE CORPORATION REPRESENTATIVE MET WITH A TRI-STATE REPRESENTATIVE SHOWED THE TRI-STATE REPRESENTATIVE THE LOCATION OF SHELL'S PIPELINE AND DETERMINED THAT THE INITIAL PHASE OF THE EXCAVATION WOULD NOT EXPOSE SHELL'S PIPELINE. THE SHELL PIPE LINE REPRESENTATIVE GAVE THE TRI-STATE REPRESENTATIVE A CARD AND WITH SPECIFIC INSTRUCTIONS TO CALL SHELL PIPE LINE BEFORE EXCAVATING IN THE VICINITY OF THE SHELL PIPELINE. TRI-STATE FAILED TO CALL SHELL PIPE LINE AND, ON JULY 5, 1989, EXPOSED SHELL'S PIPELINE. TRI-STATE THOUGHT IT WAS AN ABONADONED GAS COMPANY PIPELINE AND DRILLED A SMALL DIAMETER HOLE IN THE PIPE TO DETERMINE ITS CONTESTS. THE PIPELINE WAS TEMPORARILY SHUTDOWN WITH APPROXIMATELY 60 PSI OF PRESSURE. AFTER DRILLING THE HOLE, TRI-STATE CLAMPED THE PIPE AND CALLED SHELL PIPE LINE.
2017-09-29 08:50 | YES | NO | 19890089 |  | 809 | ARCO PIPE LINE CO | YES | 1989-07-06 | 1130 | TX | TARRANT |  | NO |  | NO | THE 14" LINE TO TANK #2303 WITHIN THE FIREWALL OF TANK #2301 IN ARLINGTON STATION-ARLINGTON, TEXAS. |  | TANK FARM | PIPE |  | 1948 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 31920 | 27528.2552 | 55535.6098 | JET FUEL | 3 | 1600 | 80 | NO | NO | 14 | 0.31 | 0 | WELDED |  | 100 | 500 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. IRISKI, OPERATIONS MANAGER - SOUTHERN AREA | 3163311300 | THE 14" TANK LINE DEVELOPED A LEAK AT THREE (3) CORROSION PITS LOCATED AT THE 6 O'CLOCK POSITION DUE TO EXCESS PRESSURE.
2017-09-29 08:50 | YES | NO | 19890090 |  | 10012 | KANEB PIPELINE CO | YES | 1989-07-05 | 1147 | KS | BUTLER | AUGUSTA | NO |  | NO | W 1/2 OF SECTION 22, R-4-3, T-27-S. |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4312.07 | 8699.187 | GASOLINE | 3 | 1171 | 600 | NO | NO | 8 | 0.25 | 2029 | WELDED |  | 1200 | 535 | YES | 24 | 1506 | 4 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | MACK E. BROWN, VICE PRESIDENT OF ENGINEERING & OPERATIONS | 3162621408 | THE L.A. KNEBLER CONSTRUCTION COMPANY OF AUGUSTA, KANSAS GAVE NOTICE TO THE KANSAS ONE CALL SYSTEM TO REMOVE TREES FROM AN EMPTY LOT IN THE CITY OF AUGUSTA, WHICH KANEB PIPE LINE COMPANY DID RESPOND BY TELEPHONE STATING THAT WE WERE CLEAR BECAUSE WE DID NOT CROSS THE AREA INVOLVED. AFTER THEY HAD REMOVED THE TREES, THEY EVIDENTLY WERE LEVELING THE SITE BY REMOVING THE TOP SOIL AND HAD BUILT TWO LONG NARROW PARALLEL STOCK PILES OUTSIDE THEIR WORK AND NOTIFICATION AREA, INSIDE A WIDE DRAINAGE DITCH AREA, AND BOTH PILES CROSSED OUR PIPELINE. EARTH MOVING SCOOPS WERE USED TO BUILD THE STOCK PILES AND ONE OF THESCOOPS SLID OFF THE TOP OF ONE STOCK PILE IN BETWEEN THE TWO AND IN ITS MOVEMENT AROUND TRYING TO GET OUT FROM BETWEEN THE PARALLEL STOCK PILES IT HAD GOUGED INTO THE GROUND AND PIERCED A HOLE ABOUT THE SIZE OF A MAN'S THUMB IN OURPIPELINE WITH THE CORNER OF ITS HYDRAULIC OPERATED BLADE.
2017-09-29 08:50 | YES | NO | 19890091 |  | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1989-07-13 | 800 | ND | PEMBINA |  | NO |  | NO | APPROXIMATELY 1/2/MILE SOUTH OF U.S. 5 AND 1 MILE WEST OF INTERSTATE 29 AND JUNCTION OF U.S. 5 IN PEMBINA COUNTY, NORTH DAKOTA. |  | LINE PIPE | PIPE |  | 1965 | FAILED PIPE | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1293621.0131 | 2609756.0976 | CRUDE OIL | 1 | 31300 | 9000 | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 835 | 579 | YES | 10 | 751 | 6 | 75 | EXTERNAL | Null | YES | OTHER | ANAEROBIC BACTERIAL | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR, GENERAL MANAGER, CORPORATE AFFAIRS | 7153941404 | A CLEANING AND KALIPER PIG TRAIN BECAME LODGED IN LINE 3 AT MP 805 AT A CROSSOVER TO THE 48" LOOP. THE LINE WAS SHUTDOWN, AND THE CROSSOVER CLOSED, FREEING THE PIG. HOWEVER, THE LINE FAILED TO REPRESSURIZE AFTER STARTUP. LINE WAS AGAIN SHUT DOWN AND VISUALLY INSPECTED UPSTREAM. THE LEAK WAS DISCOVERED AT APPROXIMATELY 0800 MST AT MP 793. SUBSEQUENT EXCAVATION SHOWED SPLIT AT 5:00 POSITION APPROXIMATELY 14" WIDE RUNNING 12'. LONGITUDINAL SEAM WAS NOT INVOLVED. AREA OF SPLIT SHOWED EXTERNAL CORROSION. PIPE SEGMENT IS BEING SENT TO LAB FOR METALLURGICAL ANALYSIS. A CONTROLLED BURN WAS AUTHORIZED BY THE NORTH DAKOTA HEALTH DEPARTMENT AND THE AREA BURNED 7/17/89.
2017-09-29 08:50 | NO | NO | 19890092 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | YES | 1989-07-13 | 1300 | CA | CONTRA COSTA | MARTINEZ | NO |  | NO | APPROXIMATELY 680 FREEWAY AND WATER FRONT ROAD, IN MARSHY AREA. |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 20 | 10 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 500 | YES | 24 | 1464 | 1 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS AND ENGR. | 2134867720 | THE LEAK WAS AT A POINT WHERE LINE HAD BEEN DAMAGED SOMETIME IN THE PAST ANDDAMAGE WAS NEVER REPORTED. PIPE DEVELOPED A STRESS CRACK OVER A PERIOD OF TIME RESULTING IN SMALL LEAK. ESTIMATED 20 BARRELS IN MARSHY AREA 30' X 100'.
2017-09-29 08:50 | YES | NO | 19890093 |  | 2731 | CHEVRON PIPELINE CO | NO | 1989-07-19 | 1030 | TX | WARD | MONAHANS | NO |  | NO | 5 MILES N.W. OF HONAHANS, TX. SEC. 19 BLK. F G&MMB&A SURVEY. |  | PUMPING STATION | TANK |  | 1976 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 300 | 280 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES | MECH & POWER FAILURE | Null | NO DATA |  | Null | Null | R.M. COOK, COMPLIANCE COORDINATOR | 9156877559 | TANK OVERFLOWED. VALVE DID NOT CLOSE COMPLETELY DO TO MECHANICAL FAILURE AND LOSS OF POWER IN ELECTRICAL STORM. PICKED UP 280 BBLS OF CRUDE OIL AND HAULED TO MONAHANS PUMP STATION. SITE CLEANED UP. NO THREAT TO THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19890094 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-07-13 | 1425 | IA | JASPER |  | NO |  | NO | LINE SECTION #036. NW 1/4, NE 1/4, SEC. 29, T79N, R19W. |  | LINE PIPE | PIPE |  | 1951 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 0 | 0 | YES | NO | 8 | 0.32 | 35000 | WELDED |  | 900 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | AT 14:25 HOURS ON 7/13/89, A SMALL FLASH FIRE OCCURRED ON OUR #5-8" DESMOINES TO CHICAGO PIPELINE (MP 26+07) DURING SOME SCHEDULED MAINTENANCEACTIVITY. IN PREPARATION FOR A HYDROSTATIC TEST, THE SUBJECT LINE (IN PROPANESERVICE) HAD BEEN PURGED OF PRODUCT WITH NITROGEN (PRECEEDED BY BUTANE,GASOLINE, AND FUEL OIL BUFFERS) TO FACILITATE REMOVAL OF SOME PREVIOUSPIPELINE REPAIRS. THE CONTRACTOR WAS REMOVING AN 8 FOOT LONG SPOOL CONTAININGA SET OF FLANGES AND WAS MAKING THE SECOND AND FINAL CUT (WITH A TORCH) WHENTHE FLASH OCCURRED. THE FIRST CUT HAD BEEN MADE WITHOUT ENCOUNTERING ANYPROBLEMS. NO VISIBLE SIGNS OF ANY RELEASED PRODUCT WERE EVIDENCED AT THE SITE.APPARENTLY A SMALL POCKET OF PROPANE OR BUFFER MIXTURE WAS REMNANT IN THE LINEFOLLOWING THE PURGE PROCESS. WHEN MIXED WITH A SUFFICIENT AMOUNT OF OXYGEN(SUPPLIED THROUGH THE OPENING LEFT BY THE FIRST CUT), A FLAMMABLE ATMOSPHEREWAS CREATED AND IGNITED BY THE TORCH. THIS APPEARS TO HAVE BEEN JUST ANISOLATED CONDITION SI NCE MORE THAN 30 SUCH SECTIONS HAD PREVIOUSLY BEENREMOVED WITHOUT ENCOUNTERING ANY PROBLEMS. HOWEVER, AS A PRECAUTIONARYMEASURE, ADDITIONAL ATMOSPHERIC CHECKS USING A COMBUSTIBLE GAS DETECTOR WEREMADE ON THE REMAINING CUT OUTS. SUPPLEMENTAL REPORT 9/26/94 INDICATED CHANGEIN PART D FROM "OTHER" TO "INCORRECT OPERATION BY OPERATOR PERSONNEL." FORQUESTIONS, CONTACT RICHARD HARRIS (918) 588-3454.
2017-09-29 08:50 | YES | NO | 19890095 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-06-21 | 1550 | OK | ROGERS | OOLAGAH | NO |  | NO | NW/4,NE/4, SECTION 22, T23N, R15E, ROGERS COUNTY, OKLAHOMA, ON NORTH END OF OOLAGAH PUMP STATION. |  | PUMPING STATION | OTHER | SCREW FITTING ON MAIN LIN | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 21560.3502 | 43495.935 | GASOLINE | 3 | 1730 | 956 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | YES | H.E. JANZEN, VICE PRESIDENT-OPERATIONS | 9185883850 | ON 6/21/89 WHILE DISMANTLING THE IDLE OOLAGAH PUMP STATION (#3-12" TULSA-HEYWORTH, MP 129+39) A WPL CONTRACTED BACKHOE BRUSHED AGAINST A 2" 800# DRAIN-UP VALVE TAPPED ON TO THE MAINLINE ADJACENT TO THE 12" STATION ISOLATIONVALVE. THE RESULTING IMPACT DISLODGED THE SMALL VALVE AND CAUSED THE RELEASE.THE VALVE WAS SCREWED ONTO A NIPPLE THAT WAS ATTACHED TO A THREADEDWELD-0-LET. IT WAS DISCOVERED THAT THE DRAIN-UP VALVE WAS ONLY PARTIALLYSCREWED ONTO THE NIPPLE. THE FITTINGS WERE REPAIRED AND THE VALVE WASREPLACED WITH A CAP. THE RELEASED PRODUCT WAS CONTAINED ON THE STATIONPROPERTY, HOWEVER, AS A PRECAUTIONARY MEASURE AN ADJACENT GRAVEL ROAD WASTEMPORARILY CLOSED DUE TO THE DIRECTION OF THE PREVAILING WINDS. ALLAPPROPRIATE AGENCIES WERE NOTIFIED AND THE CLEAN-UP EFFORTS HAVE BEENCOORDINATED WITH STATE ENVIRONMENTAL OFFICIALS. SUPPLEMENTAL REPORT 9/26/94INDICATES CHANGE TO PART D, FROM "OTHER" TO "OUTSIDE FORCE DAMAGE". CONTACTRICHARD HARRIS (918) 588-3454 WITH QUESTIONS.
2017-09-29 08:50 | YES | NO | 19890097 |  | 443 | AMOCO PIPELINE CO | YES | 1989-06-26 | 530 | IA | LEE | FORT MADISON | NO |  | NO | RABBIT ISLAND - FOOT OF 35TH STREET LEE COUNTY - FORT MADISON, IOWA. |  | NO DATA | SCRAPER TRAP |  | 1986 | OTHER | FAILED GASKET IN TRAP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 172482.8018 | 347967.4797 | DIESEL FUEL | 3 | 1320 | 1282 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.A. STAHL - AREA MANAGER | 2197382384 | LINE WAS IN OPERATION WHEN A GASKET FAILED ON A SCRAPER TRAP CLOSURE. THIS ALLOWED DIESEL FUEL TO ESCAPE FROM THE 12" PRODUCTS PIPELINE AND RUN INTO A NEARBY SLOUGH.
2017-09-29 08:50 | YES | NO | 19890098 |  | 443 | AMOCO PIPELINE CO | NO | 1989-07-19 | 1630 | TX | GREGG |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 540 | 510 | NO | NO | 8 | 0.25 | 0 | WELDED |  | 771 | 0 | YES | 24 | 964 | 10 | 75 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | R.D. PINCHBACK | 2147597131
2017-09-29 08:50 | YES | NO | 19890099 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1989-06-23 | 200 | KS | MCPHERSON |  | NO |  | NO | RANGE 5 WEST, TWONSHIP 19 SOUTH, SECTION 24, MCPHERSON COUNTY, KS. |  | LINE PIPE | OTHER | BRINE WATER STORAGE PIT | 1960 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 47250 | 40749.0619 | 82207.3171 | NATURAL GAS LIQUID | 2 | 5000 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | CAVERN OVERFILLED DUE TO OPERATOR ERROR.
2017-09-29 08:50 | NO | NO | 19890100 |  | 756 | ASSOCIATED NATURAL GAS CO | NO | 1989-07-18 | 1215 | TX | WHARTON |  | NO |  | NO | TWO MILES W. OF TX STATE HIGHWAY #71. THREE MI. NORTHWEST OF NEW TAITON, TX. TWO HUNDRED FT. EAST OF OUR MI. POST #22. IN A RICE FIELD OWNED BY JEROME DOROTIK |  | LINE PIPE | PIPE |  | 1955 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1724.828 | 3479.6748 | L. P. G. | 1 | 10 | 0 | NO | NO | 5 | 0.28 | 3460 | NO DATA |  | 1395 | 1120 | YES | 8 | 1850 | 4 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN C. BAGLEY, DISTRICT SUPERINTENDENT | 5127982791 | ON 7/18/89 RECEIVED CALL FROM TENNECO (KATHY KORENEK) REPORTED A POSSIBLE LEAK ON OUR 5" LPG LINE. OUR PIPELINE OPERATOR WAS NOTIFIED WENT TO MILE POST #22 AND DETERMINED IT WAS OUR LINE. PUMPING WAS SHUT DOWN IMMEDIATELY. BLOCKVALVE #3, #4, & LADD SITE-IN WERE CLOSED. LINE WAS BLOWED DOWN BETWEEN VALVES. LEAK SITE WAS EXCAVATED. LEAK WAS FOUND UNDER TENNECO 30" GAS LINE APPROXIMATELY 8' DEEP. PLIDCO SPLIT CLAMP WAS INSTALLED (1500 PSIG WORKING PRESSURE). WE SUSPECT LEAK WAS CAUSED BY INADEQUATE CATHODIC PROTECTION DUE TO STRAY CURRENT INTERFERENCE FROM TENNECO'S GAS LINE. LEAK SITE LOCATION WAS LEFT OPEN TO INSTALL INTERFERCE BOND AND TEST SITE WHEN LAND OWNERS CROPS ARE HARVESTED TO AVOID FURTHER CROP DAMAGE. WORK WILL BE COMPLETED BY 10/31/89. UNTIL THAT TIME LOCATION WILL BE MONITORED WEEKLY BY ASSOCIATED NATURAL GAS EMPLOYEES.
2017-09-29 08:50 | YES | NO | 19890101 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-07-24 | 838 | KS | WYANDOTTE |  | NO |  | NO | PAOLA-KANSAS CITY 10" LINE - MP 44-30+53SE/4 OF SEC. 11, R24E, T11S NEXT TO THE EASTBOUND ON-RAMP FROM 57TH ST. ONTO INTERSTATE 70 IN KANSAS CITY, KANSAS. |  | LINE PIPE | OTHER | 2" BYPASS VALVE | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 68993.1207 | 139186.9919 | GASOLINE | 3 | 1650 | 430 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | A KANSAS TURNPIKE AUTHORITY EMPLOYEE WAS MOWING THE HIGHWAY RIGHT-OF-WAY ADJACENT TO WHERE THE ABOVEGROUND VALVE SITE IS LOCATED. AS HE TURNED HIS TRACTOR AROUND, THE TAIL MOWER ATTACHMENT HIT THE 2" BYPASS VALVE AND SHEARED THE 2" NIPPLE AT THE THREADS. THE LINE WAS IN OPERATION AT THE TIME OF THE LEAK.
2017-09-29 08:50 | NO | NO | 19890102 |  | 15674 | PLANTATION PIPE LINE CO | YES | 1989-08-05 | 900 | LA | EAST BATON ROUGE |  | NO |  | NO | OCCURRED IN KAISER ALUMINUM'S BAUXITE PLANT APPROX. 200 FT S. OF U.S. HWY 190 AND APPROX. 650 FT E. OF THE MISSISSIPPI RIVER. |  | LINE PIPE | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 15523.4522 | 31317.0732 | GASOLINE | 3 | 2 | 2 | NO | NO | 12.75 | 0.38 | 35000 | WELDED |  | 320 | 150 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK, VICE PRESIDENT-OPERATIONS | 4043645916 | PLANTATION OWNS AND OPERATES 4 PARALLEL 12" DIAMETER PIPELINES WHICH RUN BETWEEN ITS DOCK STATION AND ITS BATON ROUGE TANK FARM, A DISTRANCE OF 6.2 MILES. ON AUGUST 4, 1989, WHILE PERFORMING WEEKLY ON-FOOT INSPECTIONS, IT WAS DISCOVERED THAT A CONTRACTOR WORKING IN AN OLD DEACTIVATED BAUXITE PLANT HAD SPILLED A MIXTURE OF OIL AND GASOLINE ON THE PIPELINE RIGHT OF WAY INSIDE THE PLANT. ON AUGUST 5, 1989, WHILE EXCAVATING THE PIPELINE TO DETERMINE IF THIS MIXTURE HAD DAMAGED THE PIPE COATING, GASOLINE WAS FOUND TO BE DRIPPING FROM ACASING ON THE NO. 1 DOCK LINE. THE CASING AND THE PIPE INSIDE THE CASING WERE REMOVED AND A NEW SECTION OF PIPE WAS INSTALLED ON AUGUST 10, 1989. A PINHOLE WAS DISCOVERED AT THE 6 O'CLOCK POSITION IN A PITTED AREA OF THE PIPE WHICH WAS INSIDE THE CASING. THE ENVIRONMENTAL PROTECTION AGENCY, REGION VI OFFICE, WAS NOTIFIED AT 1925 CDST ON AUGUST 5, 1989. THE LA DEQ WAS NOTIFIED AT1940 CDST ON AUGUST 5, 1989. AN ONSITE VISIT WAS MADE BY A REPRESENTATIVE OF THE LA DEQ AT 2030 CDST ON AUGUST 5, 1989. THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED AT 1125 CDST ON AUGUST 7, 1989 ( REPORT #13551).
2017-09-29 08:50 | YES | NO | 19890103 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-08-06 | 1105 | OK | OKLAHOMA |  | NO |  | NO | HIGH STREET TERMINAL (A353). |  | TANK FARM | TANK |  | 1984 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 95 | 86 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | AT 11:05 ON AUGUST 16,1989, IT WAS DISCOVERED THAT A RELIEF TANK AT OUR HIGHSTREET TERMINAL IN OKLAHOMA CITY WAS OVERFLOWING. THE TANK BEGAN TO FILL WHEN THE NITROGEN PRESSURE LEAKED FROM THE NITROGEN LOADED (CHARGED) RELIEF VALVE CAUSING THE VALVE TO OPEN. THE NITROGEN PRESSURE IS NORMALLY MAINTANED JUST BELOW 275 PSI TO PROTECT THE 150# ANSI MANIFOLD FITTINGS FROM PRESSURE FLUCTUATIONS DURING MAIN LINE RECEIPTS. THE INTERMEDIATE AND HIGH LEVEL TANK ALARMS ALSO MALFUNCTIONED; THUS THE TANK CONTINUED TO FILL UNNOTICED. ALL THE RELEASED PRODUCT WAS CONTAINED WITHIN THE TANK DIKE. REMINANT RAIN WATER IN THE DIKE ENABLED MAINTENANCE CREWS TO RECOVER MOST OF THE RELEASED PRODUCT. THE TANK LEVEL ALARMS HAVE BEEN REPAIRED AND AN ADDITIONAL ALARM HAS BEEN ADDED TO THE NITROGEN SUPPLY TANK TO ALERT OF PRESSURE LOSS.
2017-09-29 08:50 | YES | NO | 19890104 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1989-08-07 | 645 | MS | SUNFLOWER |  | NO |  | NO | 1/4 M. N. OF COUNTY LINE ROAD (SUNFLOWER & HUMPHREYS) - APPROXIMATELY 5 MILES WEST OF ISOLA, MS - NE QUART OF SW QUART SEC 35 T17N R5W - MORE SPECIFICALLY N. |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 118000 | 101764.853 | 205300.813 | CRUDE OIL | 1 | 1622 | 1310 | NO | NO | 22 | 0.3 | 52000 | WELDED |  | 960 | 600 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | I.B. NEWMAN - MANAGER OF PIPELINE OPERATION | 2147570207 | THE 22" LINE RUPTURED IN THE AREA OF RECENT (8/6/89) DOZER ACTIVITY INSIDE THE NORTH LEVEE OF A DRY CATFISH POND OWNED BY A MS PARTNERSHIP COMPOSED OF R.L. MAXWELL (50%) AND 4 OTHERS AND KNOWN AS RIVERMAX. THE 22" OPENING RELEASED CRUDE OVER APPROXIMATELY 10-15 ACRES. APPROXIMATELY 4800 YDS OF DIRT CONTAINING THE UNRECOVERED CRUDE WERE RELOCATED FROM THE POND AREA TO BE USED FORROAD FILL MATERIAL AS PER MS BUREA OF POLLUTION CONTROL (BOB ROGERS) RECOMMENDATION. THE PIPELINE HAD BEEN PROBED & FLAGGED ON 6/30/89. MR. MAXWELL HAD BEEN CAUTIONED BY PHONE ON 3 OCCASIONS IN JULY '89 TO ADVISE MID-VALLEY PRIOR TO PERFORMING WORK. MID-VALLEY RECEIVED NO ONE-CALL NOTIFICATION OR PHONE CALL NOTIFICATION OF PROPOSED ACTIVITY PRIOR TO THE STRIKE AND/OR LEAK. THE FLAGS (WITH PIPE DEPTH WRITTEN ON THEM) WERE CLEARLY VISIBLE AT THE TIME OF THE LEAK.
2017-09-29 08:50 | YES | NO | 19890105 |  | 12628 | MOBIL PIPELINE CO | YES | 1989-07-11 | 1050 | OK | JEFFERSON |  | NO |  | NO | 5-1/4 MILES WEST OF HEALDTON, OK. |  | LINE PIPE | OTHER | UNKNOWN | 1926 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1700 | 1466.1038 | 2957.7236 | CRUDE OIL | 1 | 80 | 68 | NO | NO | 6 | 0.28 | 35000 | NO DATA |  | 700 | 300 | YES | 2 | 768 | 7 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AERIAL SURVEILLANCE | NO | NO | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | THE PIPELINE WAS HIT AND PUNCTURED BY A ROOT PLOW. ANOTHER PIPELINE COMPANY'S AERIAL PATROL WAS IN THE VICINITY WHEN THE ACCIDENT OCCURRED. HE NOTIFIEDTHEIR OFFICE AND THEY IN TURN CALLED OUR OFFICE IN HEALDTON, OK. THE STATION WAS IMEDIATELY SHUT DOWN AND THE MAINTENANCE CREW AND TANK TRUCKS WERE DISPATCHED TO THE LEAK SITE. THE DAMAGED SECTION OF THE PIPELINE WAS REPAIRED BY REPLACING A 12 FT. SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19890106 |  | 19536 | TOTAL PIPELINE CORP | NO | 1989-08-11 | 1100 | OK | MURRAY | WYNNEWOOD | NO |  | NO | NW 1/4 SECTION 26- TOWNSHIP 2N-RANGE 1E MURRAY COUNTY, OKLAHOMA. |  | PUMPING STATION | VALVE |  | 1975 | OTHER | MALFUNCTION OF VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3449.656 | 6959.3496 | CRUDE OIL | 1 | 75 | 35 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL JOHN COOPER - CORROSION ENGINEER | 4052291638 | 8" SUCTION MOV ON 800 HP. MAINLINE PUMP DID NOT SEAT PROPERLY WHEN REMOTELY CLOSED BY OPERATOR. 500 HP. PUMP WAS STARTED AND BEGAN DISCHARGING AT 400 PSIG. THIS CAUSED THE THERMAL RELIEF VALVE SET AT 200 PSIG. ON THE 800 HP. 8"SUCTION LINE TO RELIEVE INTO THE SUMP TANK. WHEN THE SUMP OVERFILLED, THE LINE TO THE SCRAPER TRAP DRAIN BACKED UP CAUSING CRUDE OIL TO SPILL ONTO THE GRAVEL STATION SITE.
2017-09-29 08:50 | NO | NO | 19890107 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-07-31 | 1630 | MN | DAKOTA |  | NO |  | NO | SE 1/4, SW 1/4 SECTION 21 T27N R23W. LINE SECTION #FO43. |  | LINE PIPE | WELDING FITTING |  | 1974 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4312.07 | 8699.187 | GASOLINE | 3 | 6 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | HOWARD JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | ON 7/31/89 A FAILURE OCCURRED AT THE NORTH INTERFACE DETECTOR SITE ON THE #4-12" ROSEMOUNT TO MINNEAPOLIS PIPELINE. DURING THE PROCESS OF REMOVING THE VALVE BOX FROM AROUND THE INTERFACE DETECTOR PROBE, A SMALL (2") FITTING WAS DAMAGED RESULTING IN A RELEASE OF PRODUCT. WHILE LIFTING THE VALVE BOX, THE CONTRACTOR DID NOT IMMEDIATELY NOTICE THAT A 2" VALVE ON THE DETECTOR PIPING WAS CHAINED TO THE INSIDE OF THE VALVE BOX. THE RESULTING STRAIN DEFORMED THENIPPLE THAT WAS THREADED INTO THE VALVE, AND PARTIALLY STRIPPED THE THREADS. THE PIPING WAS APPROPRIATELY REPAIRED, AND CLEAN UP ACTIVITIES WERE COORDINATED WITH STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19890108 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1989-08-01 | 840 | AR | UNION |  | NO |  | NO | 20" LINE P2, M.P. 238.5; UNION COUNTY, AR, APPROXIMATELY 3 MILES SE OF EL DORADO, AR, NEAR HIBANK ROAD. ALIGNMENT DRAWING NO. TPF-P2-40 AND A COPY OF A PORTION |  | LINE PIPE | PIPE |  | 1944 | OTHER | GASKET ON LEAK FAILED. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5800 | 5002.0013 | 10091.0569 | GASOLINE | 2 | 317 | 311 | NO | NO | 20 | 0.38 | 35000 | WELDED |  | 700 | 563 | YES | 24 | 1174 | 1 | 57 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HANNIGAN, VICE RPESIDENT-OPERATIONS | 7137594700 | ON AUGUST 1, 1989, AT 08:40 HOURS (C.D.T.), A LEAK WAS REPORTED TO TEXAS EASTERN PERSONNEL BY THE UNION COUNTY SHERIFF'S DEPARTMENT. THE BOOSTER STATIONSSOUTH OF THE LEAK SITE WERE SHUT DOWN IMMEDIATELY, AND THE AFFECTED LINE SECTION WAS ISOLATED BY CLOSING VALVES ON EACH SIDE OF THE ACCIDENT SITE. RECOVERY OF SPILLED GASOLINE WAS INITIATED BY TEXAS EASTERN MAINTENANCE CREWS WITHIN ONE HOUR OF NOTIFICATION OF TEXAS EASTERN. A SUMP WAS EXCAVATED AT THE SPILL SITE, ALLOWING PICKUP OF GASOLINE ON THE GROUND BY VACUUM TRUCKS. SPILL BOOMS WERE STRATEGICALLY PLACED TO CONTROL ANY POTENTIAL RELEASES OF PRODUCT TO SURFACE WATER. FLOATING GASOLINE WAS THEN RECOVERED FROM SURFACE WATER USING SKIMMER PUMPS OR BY USING SORBENT PADS. THE INITIAL SITE CLEANUP WAS COMPLETED AT 1200 HOURS ON AUGUST 4, 1989. SPILL BOOMS WERE LEFT IN PLACE, AND THE SITE IS PRESENTLY BEING MONITORED DAILY. FINAL SITE CLEANUP WILL TAKE PLACE AFTER PERMANENT REPAIRES TO THE 20" PIPE HAVE BEEN COMPLETED, AND ALL CONTAIMINATED SOIL WILL BE REMOVED FROM THE SITE AND TRANSPORTED TO TEXAS EASTERN'S PROPERTY, WHERE IT WILL UNDERGOING BIOLOGICAL REMEDIATION. AFTER UNCOVERING THE 20" LINE, TEXAS EASTERN MAINTENANCE PERSONNEL DISCOVERED THAT THE LEAK HAD BEEN CAUSED BY THE FAILURE OF A RUBBER GASKET USED WITH A LEAK CLAMP THAT WAS INSTALLED ON JUNE 16, 1989, AS A TEMPORARY REPAIR. IMPROVED TEMPORARY REPAIRES TO THE LINE WERE COMPLETED ON AUGUST 1, 1989. PERMANENT REPAIRS TO THE 20" PIPE ARE SCHEDULED FOR SEPTEMBER 12, 1989.
2017-09-29 08:50 | YES | NO | 19890109 |  | 2731 | CHEVRON PIPELINE CO | NO | 1989-08-06 | 1400 | TX | WARD | WICKETT | NO |  | NO | 1/2 MILES E. OF HUTCH #1035 LACT, WICKETT, TEX. SEC. 7 BLK. 16 UNIVERSITY LAND SURVEY. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 43.1207 | 86.9919 | CRUDE OIL | 1 | 75 | 70 | NO | NO | 6 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | SOIL | NO DATA |  | Null | NO DATA |  | Null | Null | R.M. COOK, COMPLIANCE COORDINATOR | 9156877559 | CHEVRON PRODUCTION HAD A HIGH PRESSURE WATER LEAK THAT WAS SHOOTING A STREAMOF WATER RIGHT AT OUR PIPELINE. EXTERNAL CORROSION AND THE HIGH PRESSURE WATER LEAK CAUSED THE FAILURE OF THE PIPE. 70 BBLS. OF CRUDE WAS PICKED UP AND HAULED TO CHEVRON'S MONAHANS STATION. LEAK WAS REPAIRED WITH A 6" VEGA CLAMP. LEAK SITE WAS CLEANED UP AND NO THREAT TO THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19890110 |  | 809 | ARCO PIPE LINE CO | YES | 1989-08-14 | 900 | LA | PLAQUEMINES |  | NO |  | NO | APPROXIMATELY 3-1/4 NNW OF ARCO OIL & GAS PLATFORM A, BLK. 60, SOUTH PASS, PLAQUEMINES PARISH, LA X=2,742,044 Y= 161,163 SOUTH PASS BLK 6. |  | LINE PIPE | GIRTH |  | 1975 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 88000 | 75892.4328 | 153105.6911 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 10 | 0.37 | 46000 | WELDED |  | 1440 | 450 | YES | 8 | 1830 | 30 | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, SOUHTERN AREA MANAGER | 3163311300 | APPROXIMATELY 0900 TIME ON AUGUST 14, 1989, WE WERE NOTIFIED BY AIR LOGISTICS PILOT OF A SHEEN ON THE WATER 3-1/4 MILES NNW OF ARCO OIL & GAS PLATFORM "A", BLOCK 60, SOUTH PASS, PLAQUEMINES PARISH, LA. A WORKING 4 POINT BOAT ANDONE CREW WAS MOBILIZED ON 8/15/89. THE ORIGIN OF LEAK WAS IDENTIFIED AT 0320 AM ON 8/17/89, AND PLIDCO SPLIT SLEEVE WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19890111 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1989-08-22 | 1530 | OK | PAYNE | CUSHING | NO |  | NO | PAYNE COUNTY, OKLAHOMA, CITY OF CUSHING. |  | LINE PIPE | NO DATA |  | 1979 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1724.828 | 3479.6748 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 30 | 0.32 | 0 | WELDED |  | 150 | 80 | YES | 8 | 0 | 1 | 79 | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | D.W. DURRETT, MANAGER OF RISK MANAGEMENT | 9185866231 | LEAK HAS BEEN SADDLED AND REPAIRS WILL BE COMPLETED BY 9/15/89.
2017-09-29 08:50 | YES | NO | 19890112 |  | 13131 | CONOCO INC | NO | 1989-09-04 | 1000 | OK | GARFIELD |  | NO |  | NO | FROM BISON, OK GO 5.5 MILES EAST THEN .T MILES SOUTH INTO FIELD. NE/4 OF SECTION 25-TOWNSHIP 20N-RANGE 6W-GARFIELD COUNTY, OK. |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 862.414 | 1739.8374 | L. P. G. | 2 | 2 | 0 | YES | NO | 4 | 0.13 | 288 | WELDED |  | 1440 | 282 | YES | 8 | 1440 | 1 | 84 | EXTERNAL | Null | YES | OTHER | RECTIFIER .68 | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | SMALL CORROSION HOLE WAS EMITTING SOME PROPANE/BUTANE/CASING HEAD (PBC) WHICH WAS IGNITED BY LIGHTNING. FIRE APPROXIMATELY 2 FEET HIGH OCCURRED. LINE WAS REPAIRED AND PUT BACK IN SERVICE.
2017-09-29 08:50 | NO | NO | 19890113 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-09-01 | 1230 | WA | WALLA WALLA | BURBANK | NO |  | NO | SOUTHWEST CORNER OF THE INTERSECTION OF GRAIN MILL RD AND SECOND AVE. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 1 | 1 | NO | NO | 6 | 0.28 | 42000 | WELDED |  | 2120 | 0 | YES | 8 | 2650 | 9 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | P.K. CATTON, ENGINEER | 8012685313 | THE PIPE LINE WAS BEING PREPARED FOR A TIE-IN. THE PIPE WAS DRAINED DOWN BYA 2" HOSE ON A VACUUM TRUCK. WHEN THE TRUCK COULD NOT GET ANY MORE THE 2" HOSE WAS EXCHANGED WITH A 1" HOSE THAT COULD BE INSERTED THROUGH THE 2" HOT TAPPED VALVE. AT THIS POINT THE LINE WAS ABOUT 1/2 FULL. THE VACUUM MUST HAVE SHIFTED BECAUSE THE LINE FILLED UP WITH DIESEL AND OVERFILLED THE CATCH BASINBEFORE THE VALVE COULD BE SHUT OFF. SPILLING APPROXIMATELY 1 & 1/2 GALLONS WHICH WAS PICKED UP WITH SORBANT PADS.
2017-09-29 08:50 | YES | NO | 19890114 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-09-01 | 1830 | WA | WALLA WALLA | BURBANK | NO |  | NO | THE SOUTHWEST CORNER OF THE INTERSECTION OF GRAIN MILL RD. AND SECOND AVE. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2156.035 | 4349.5935 | DIESEL FUEL | 3 | 78 | 77 | NO | NO | 6 | 0.28 | 42000 | WELDED |  | 2120 | 0 | YES | 8 | 2650 | 9 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | PETER K. CATTON | 0000000000 | THE PIPELINE CONTRACTOR WAS TYING IN A NEW SECTION OF LINE. THE SECTION WAS 12,000' LONG THE NORTHERN END WAS OPEN AND ABOUT TO BE CAPPED WHEN THE SOUTHERN END, UNDER VACUUM, WAS COLD CUT. WHEN THE PRESSURE EQUALIZED SOME OF THEISOLATED PRODUCT IN THE OLD LINE CAME OUT THE NOTHERN, LOWER, END.
2017-09-29 08:50 | YES | NO | 19890115 |  | 15490 | PHILLIPS PIPE LINE CO | NO | 1989-08-16 | 1045 | TX | HUTCHINSON |  | NO |  | NO | PAMPA-BORGER 6"B LINE "BA" APPROXIMATELY 6 MILES EAST OF BORGER, TX SEC. 123, BLOCK 4, SURVEY I&GNRR. |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3449.656 | 6959.3496 | CRUDE OIL | 1 | 90 | 0 | NO | NO | 6.63 | 0.25 | 35000 | WELDED |  | 500 | 250 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECH. SERVICES. | 9186614721 | LANDOWNER DETECTED OIL ON THE GROUND, AND HE CALLED OUR AREA OFFICE IN BORGER. THE MAINTENANCE CREW WENT OUT AND DUG UP THE LINE AND FOUND THAT EXTERNALCORROSION HAD CAUSED A HOLE IN THE PIPE. AN EMERGENCY CLAMP WAS INSTALLED ON THE LINE.
2017-09-29 08:50 | NO | NO | 19890116 |  | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1989-08-14 | 830 | TX | BRAZOS |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 14661.0381 | 29577.2358 | CRUDE OIL | 1 | 10 | 2 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1077 | 100 | YES | 8 | 1346 | 3 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIMMY MUNN - SR. REGULATORY AFFAIRS REPRESENTATIVE | 9152673673 | AT 8:30AM, 8/14/89, LANDOWNER TELEPHONED TO REPORT A POSSIBLE LEAK WITH SOMEOIL FLOATING ON HER SMALL STOCK POND. SHE REPORTED THAT SHE HAD DISCOVERED THIS THE PREVIOUS DAY, BUT THAT THERE DIDN'T APPEAR TO BE ANY OIL COMING OUT OF THE GROUND AT THE TIME. WITHIN ONE HOUR, OUR MAN FROM HEARNE STATION WAS ON THE SCENE, BUT COULD NOT DETERMINE THE SOURCE OF THE OIL AS THERE WERE PRODUCING WELLS IN THE VICINITY. THE OIL ON THE POND APPEARED WEATHERED AND MAYHAVE BEEN ON THE POND FOR SOME TIME. AS A PRECAUTION, OUR FIRST ACTIONS WERETO BUILD 3 FLUMES WITH HAY FILTER FENCES DOWNSTREAM (IN DRY CREEKBED) OF THESTOCKPOND IN CASE OF RAIN OR OVERFLOW WHICH COULD CONTAMINATE THE DRY CREEKBED. ON THE NEXT DAY (8/15/89) OUR PIPELINE WAS STRIPPED OUT NEAR THE LOCATIONAND A SLOW SEEP WAS DISCOVERED AT THE WELD OF AN OLD "BELL" PATCH AT 9:15AM. A TWENTY FOOT SECTION OF PIPE CONTAINING THE OLD PATCH WAS REPLACED. CONTAMINATED SOIL WAS REMOVED AND REPLACED. THE POND WAS CLEANED USING SPILL BOOMS AND SORBENT PADS.
2017-09-29 08:50 | YES | NO | 19890117 |  | 809 | ARCO PIPE LINE CO | YES | 1989-09-11 | 1145 | MO | JACKSON |  | NO |  | NO | 2-1/2 MILES N OF BLUE SPRINGS, MO IN N.E. 1/4/ OF SECTION 13, 5-49N, R-31W. |  | LINE PIPE | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 25872.4203 | 52195.122 | FUEL OIL | 3 | 169 | 163 | NO | NO | 8 | 0.32 | 0 | NO DATA |  | 700 | 270 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | O.D. HARRIS-MANAGER, NORTHERN AREA OPERATIONS | 3163311300 | CONTRACTOR WAS MOVING EARTH WITH TRACK LOADER IN SALVAGE YARD. DROVE TOOTH OF LOADER INTO PIPE.
2017-09-29 08:50 | YES | NO | 19890118 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | NO | 1989-09-05 | 1045 | OR | LINN |  | NO |  | NO | PLMP 99.6, APPROXIMATELY 14.5 MILES NORTH OF EUGENE, OREGON. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 241 | 13 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1280 | 513 | YES | 24 | 1600 | 8 | 62 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | NO | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS AND ENGR. | 2134867720 | A DITCHING CONTRACTOR WAS DIGGING A DITCH FOR THE INSTALLATION OF A DRAINAGESYSTEM FOR THE FARM WHEN HE HIT THE MAINLINE PIPELINE AT PLMP 99.6.
2017-09-29 08:50 | YES | NO | 19890119 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1989-09-15 | 833 | IA | CRAWFORD |  | NO |  | NO | SECTION 3, TOWNSHIP 84 NORTH, RANGE 41 WEST. |  | LINE PIPE | OTHER | UNKNOWN | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30382 | 26201.8624 | 52859.7398 | L. P. G. | 2 | 3381 | 0 | NO | NO | 6.63 | 0.16 | 2166 | WELDED |  | 1550 | 424 | YES | 24 | 2011 | 7 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE WARNING SIGNS | NO | Null | S.F. ISAACS | 9185811800 | LINE WAS STUCK BY MOTOR GRADER WHILE DOING ROAD MAINTENANCE.
2017-09-29 08:50 | YES | NO | 19890120 |  | 13131 | CONOCO INC | YES | 1989-09-14 | 2302 | MT | JUDITH BASIN |  | NO |  | NO | TOWNSHIP 15N RANGE 13E, SECTION SE SEC 4, MILE POST 217. |  | LINE PIPE | PIPE |  | 1968 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 129362.1013 | 260975.6098 | CRUDE OIL | 1 | 3571 | 1240 | NO | NO | 12 | 0.25 | 60000 | WELDED |  | 2100 | 1961 | YES | 0 | 0 | 1 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWIGHT D. JACKSON, MANAGER, OPERATIONS ENGINEERING | 7132932130 | PIPELINE DISPATCH PERSONNEL OBSERVED A PRESSURE VARIATION ON THE PIPELINE SYSTEM. DISPATCH PERSONNEL IMMEDIATELY BEGAN EVALUATION OF PIPELINE CONDITIONS.BASED ON OBSERVED CONDITIONS, DISPATCH PERSONNEL PROMPTLY BEGAN SYSTEM SHUTDOWN PROCEDURES. SYSTEM SHUTDOWN COMPLETE FOLLOWING SHUTDOWN OF ALL SYSTEM PUMP UNITS. PIPELINE FIELD PERSONNEL NOTIFIED OF POSSIBLE LEAK CONDITION AND DISPATCHED TO THE ANTICIPATED LEAK AREA ALONG WITH EMERGENCY EQUIPMENT AND CREW. NOTIFICATION PROVIDED TO APPROPRIATE REGULATORY AGENCIES. LEAK CONFIRMEDBY ONSITE PERSONNEL INSPECTION. EFFORTS IMMEDIATELY MADE TO CONTAIN THE SPILLED PRODUCT AND PROTECT THE LOCAL ENVIRONMENT. ONCE CONTAINMENT ACHIEVED, REPAIR AND CLEANUP PROCEDURES WERE INITIATED. PIPELINE REPAIRS WERE COMPLETEDAND THE LINE PLACED BACK IN SERVICE AT A VOLUNTARY 20% REDUCTION OF THE PRESSURE AT THE TIME OF THE LEAK. A PIPE REPLACEMENT PROGRAM IS CURRENTLY BEING EVALUATED RELATIVE TO THIS INCIDENT. REPLACEMENT OF SEGMENTS OF THE PIPE WILL OCCUR AS SOON AS MATERIAL AVAILABILITY AND WEATHER CONDITIONS PERMIT.
2017-09-29 08:50 | YES | NO | 19890121 |  | 18273 | SHELL PIPE LINE CORP | NO | 1989-09-07 | 1830 | CA | LOS ANGELES | WOODLAND HILLS | NO |  | NO | T-2-N, R-17-N, VENTURA 10-INCH CRUDE LINE. |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 431207.0044 | 869918.6992 | CRUDE OIL | 1 | 75 | 0 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 1400 | 450 | YES | 4 | 1970 | 8 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | CONTRACTOR STRUCK THE PIPELINE WHILE CLEARING LAND FOR CONSTRUCTION OF A NEWROAD. CONTRACTOR BEGAN THE WORK WITHOUT NOTIFICATION OF SHELL PIPE LINE CORPORATION OR THE ONE-CALL SYSTEM, DESPITE THE FACT THAT A PIPELINE MARKER WAS WITHIN 100 FEET OF THE POINT OF IMPACT.
2017-09-29 08:50 | YES | NO | 19890122 |  | 18273 | SHELL PIPE LINE CORP | NO | 1989-09-13 | 700 | OK | PAYNE | CUSHING | NO |  | NO | NE 1/4, NE 1/4, SECTION 15, T-17-N, R-5-E TWO MILES SOUTH OF MAIN STREET ON LINWOOD CUSHING TANK FARM. |  | TANK FARM | OTHER | ROOF DRAIN HOSE. | 1941 | OTHER | NATURAL WEAR AND TEAR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5550 | 4786.3977 | 9656.0976 | CRUDE OIL | 1 | 710 | 705 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | ROOF DRAIN HOSE RUPTURED, ALLOWING CRUDE OIL TO ESCAPE FROM THE TANK ONTO THE GROUND. ALL OIL WAS CONTAINED WITHIN THE TANK DIKE.
2017-09-29 08:50 | YES | NO | 19890123 |  | 18718 | SUN PIPELINE CO | YES | 1989-09-11 | 1100 | OK | OKFUSKEE |  | NO |  | NO |  |  | PUMPING STATION | OTHER | UNKNOWN | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 172.4828 | 347.9675 | GASOLINE | 3 | 58 | 58 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.W. DURRETT, MANAGER, RISK MANAGEMENT | 9185866231 | AUTO BODY BLEED FAILED ON VALVE #5, CAUSING SUMP TO OVERFLOW. PRODUCT PICKED UP WITH VACUUM TRUCK. RESET VALVE #5 CLOSE LIMITS.
2017-09-29 08:50 | YES | NO | 19890124 |  | 18519 | SOUTHERN PACIFIC PIPELINE CO | NO | 1989-09-13 | 1339 | OR | MARION | SALEM | NO |  | NO | IN MILL CREEK APPROXIMATELY HALF A MILE NORTH OF SALEM STATION AT PLMP 54.16. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 17248.2802 | 34796.748 | GASOLINE | 3 | 553 | 55 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1275 | 80 | YES | 24 | 1600 | 8 | 62 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | STANDARDS PIPELINE MARKER | NO | NO | J.M. ABBOUND, SENIOR VICE PRESIDENT, OPERATIONS & ENGINEERIN | 2134867720 | THE PIPELINE WAS DAMAGED BY A CONTRACTOR RUNNING OVER THE LINE CAUSING A LEAK IN MILL CREEK APPROXIMATELY HALF A MILE UPSTREAM OF OUR SALEM BOOSTER STATION. THE PIPELINE WAS IMMEDIATELY SHUT DOWN AND PRODUCT DRAINED INTO ALBANY,DOWNSTREAM OF LEAK SITE, UNTIL MAIN LINE BLOCK VALVES WERE CLOSED TO MINIMIZE PRODUCT LOSS.
2017-09-29 08:50 | YES | NO | 19890125 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-09-18 | 830 | MS | PASCAGOULA |  | NO |  | NO | BAYOU CASOTTE SHIP CHANNEL, ABOUT 1 MILE FROM PASCOUGOULA, MISSISSIPPI. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 300 | 200 | NO | NO | 20 | 0.34 | 52000 | WELDED |  | 1080 | 9 | YES | 8 | 1620 | 6 | 82 | NO DATA | Null | Null | NO DATA |  | SHIP ANCHOR |  | Null | OTHER | COASTAL ZONE NOTIFICATION | YES | YES | R.L. DOWNIE, DIVISION MANAGER | 5043642496 | DURING DREDGING OF BAYOU CASOTTE BY THE CORPS OF ENGINEERS, THE DREDGE DAVE BLACKBURN DROPPED AN ANCHOR PILING ON THE LINE, PUNCTURING THE LINE AND OPENING ABOUT A 6" HOLE. THE DREDGING WAS MONITORED BY A CHEVRON INSPECTOR. THE LINE WAS SHUT DOWN AT THE TIME OF THE ACCIDENT DUE TO THE DREDGING. THE BREAK WAS IMMEDIATELY NOTICED BY BOTH PERSONNEL ON THE DREDGE AND OPERATOR AT EMPIRE TERMINAL. CHEVRON'S PASCAGOULA REFINERY WAS NOTIFIED AND PROCEEDED WITHEMERGENCY ACTION. THEIR RESPONSE INCLUDED NOTIFICATION OF THE NATIONAL RESPONSE CENTER AND MISSISSIPPI STATE AGENCIES, DEPLOYMENT OF BOOMS, CALL OUT OF ADDITIONAL CLEANUP EQUIPMENT, ETC. THE SPILL CLEANUP AND LINE REPAIR HAVE BEEN COMPLETED WITH MINIMAL IMPACT ON THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19890126 |  | 300 | ALL AMERICAN PIPELINE CO | YES | 1989-09-16 | 10 | CA | SAN BERNARDINO | BARSTOW | NO |  | NO | 12-GAUGE STATION, BARSTOW, CA. |  | LINE PIPE | PIPE |  | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 344965.6035 | 695934.9593 | CRUDE OIL | 3 | 650 | 500 | NO | NO | 12.75 | 0.38 | 35000 | FLANGED |  | 1482 | 1456 | YES | 4 | 1890 | 4 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES C. FRIEN, DIVISION MANAGER | 8053985651 | SURGE RELIEF VALVE OPENED PREMATURELY CAUSING CONTROL VALVE TO GO TO THE CLOSED POSITION. AT THAT TIME ALL OF THE FLOW WAS DIVERTED THROUGH THE SURGE RELIEF VALVE CAUSING EXCESSIVE VIBRATION THAT BLEW OUT A FLEXTOLIC GASKET AND BROKE A 2" DRAIN LINE.
2017-09-29 08:50 | YES | NO | 19890127 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1989-10-17 | 1618 | TX | HARRIS |  | NO |  | NO | DECKER DRIVE AND BAKER ROAD. BAYTOWN TEXAS TERMINAL. |  | TANK FARM | TANK |  | 1971 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1724.828 | 3479.6748 | GASOLINE | 3 | 115 | 91 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HANNIGAN, VICE PRESIDENT- OPERATIONS | 7137594700 | A FIRST SHIFT OPERATOR TRANSCRIBED A TANK GAUGE READING TO A LOG SHEET IN ERROR. THIS READING REFLECTED LESS PRODUCT IN THE TANK THAN IT ACTUALLY CONTAINED. THE SECOND SHIFT OPERATOR OBSERVED PRODUCT ESCAPING THE TANK FROM THE OVERFLOWS. HE IMMEDIATELY SHUT OFF FLOW TO THE TANKS AND PUMPED PRODUCT FROM THE TANK UNTIL IT STOPPED OVERFLOWING. ALL SPILL PRODUCT WAS CONTAINED WITHIN THE TANK FIREWALL. THE SITE WILL BE FERTILIZED AND AEREATED TO ENHANCE RETURNTO GRASS COVER.
2017-09-29 08:50 | YES | NO | 19890128 |  | 26134 | MOBIL OIL CORP - WEST COAST PIPELINES | NO | 1989-10-04 | 1130 | CA | KERN |  | NO |  | NO | SEC: 1 TWNSP 32S RANGE 24E 100' SOUTH OF HWY 119, 1/8 MILE WEST OF HARRISON STREET. |  | LINE PIPE | OTHER | UNKNOWN | 1925 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4312.07 | 8699.187 | CRUDE OIL | 1 | 150 | 140 | NO | NO | 6 | 0.28 | 2400 | THREADED |  | 325 | 250 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.R. JEFFRIES, MANAGER, WEST COAST PIPE LINES | 2132122905 | MOBILE WAS NOTIFIED OF PIPELINE LEAK BY CHEVRON PIPELINE COMPANY AT 11:30A.M. ON OCTOBER 4,1989. MOBILE PERSONNEL RESPONDED TO THE LEAK SITE AND ISOLATEDTHE G-10 PIPELINE BY SHUTTING THE PUMP DOWN AND CLOSING BLOCK VALVES. VACUUM TRUCKS WERE USED TO RECOVER 140 BBLS. OF THE ESTIMATED 150 BBLS. SPILLED. MAGNESSIUM ANODE WAS INSTALLED TO MITIGATE LOCALIZED CORROSION. THE PIPELINEWAS REPAIRED BY INSTALLING A 5' FULL ENCIRCLEMENT WELDED WRAP.
2017-09-29 08:50 | YES | NO | 19890129 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-10-20 | 1258 | NM | BERNALILLO | ALBUQUERQUE | NO |  | NO | (IF LOCATION IS NEAR OFFSHORE PLATFORMS, BUILDINGS, OR OTHER LANDMARKS, SUCH AS HIGHWAYS, WATERWAYS, OR RAILROADS. |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | CORROSION, EXTERNAL | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 21560.3502 | 43495.935 | JET FUEL | 3 | 437 | 163 | NO | NO | 6.63 | 0.25 | 42000 | WELDED |  | 2001 | 200 | YES | 8 | 2642 | 11 | 88 | EXTERNAL | Null | YES | OTHER | UNKNOWN | DAMAGE BY OTHERS |  | Null | OTHER | TV, MAIL-OUTS, PERSONAL | NO | NO | RENE M. COOK, COMPLIANCE COORDINATOR | 9156877559 | EQUIPMENT OPERATOR FOR UNIVERSAL CONSTRUCTORS COMPANY WAS GRADING AND REMOVING DIRT WITH A FRONT-END LOADER AND STRUCK PIPELINE. COMPANY CONTROL CENTER NOTED PRESSURE DROP AND INITIATED SHUTDOWN PRECEDURES. A REPRESENTATIVE OF UNIVERSAL CONSTRUCTORS LOCATED A PIPELINE MARKER IN THE AREA AND PHONED THE CONTROL CENTER TO REPORT THE INCIDENT. THE AREA WAS DIKED OFF TO CONTAIN THE SPILL. STANDING PRODUCT REMOVED BY VACUUM TRUCKS. CONTAMINATED DIRT REMOVED FROM SITE TO LANDFILL DESIGNATED BY COUNTY HEALTH DEPARTMENT REPRESENTATIVE WHO RESPONDED. THE LOCAL FIRE DEPT. HAD BEEN NOTIFIED AND RESPONDED AS A PRECAUTIONARY MEASURE AS WELL AS THE STATE POLICE. TEMPORARY REPAIRS MADE; LINE BACK IN SERVICE 17:12 HRS.
2017-09-29 08:50 | YES | NO | 19890130 |  | 443 | AMOCO PIPELINE CO | YES | 1989-10-11 | 2100 | KS | BARTON |  | NO |  | NO | 1 3/8 MILES EAST OF SUSANK, KANSAS. |  | LINE PIPE | PIPE |  | 1974 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 11751 | 10134.227 | 20444.8293 | NATURAL GAS LIQUID | 2 | 4000 | 0 | NO | NO | 6 | 0.19 | 0 | WELDED |  | 2125 | 846 | YES | 0 | 0 | 1 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D. A. SHROYER-AREA MANAGER | 3032864611 | REVELL OIL FIELD CONSTRUCTION WORKING FOR H-30 DRILLING COMPANY WAS DIGGING APIT FOR DRILLING RIG, HIT PIPELINE CAUSING SPILL OF NGL PRODUCT.
2017-09-29 08:50 | YES | NO | 19890131 |  | 10313 | KOCH PIPELINE INC | NO | 1989-10-04 | 1830 | OK | GARFIELD |  | NO |  | NO | SW-SE-NE SEC. 12 T24N R6W. |  | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30294 | 26125.97 | 52706.6341 | L. P. G. | 2 | 2640 | 0 | NO | NO | 6.63 | 0.19 | 0 | WELDED |  | 1440 | 250 | YES | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | NO | MARC S. DEVARENNES, DIVISION ENGINEER | 4053952377 | AT APPROXIMATELY 1830 HRS. ON 10/04/89 A DITCHING MACHINE OPERATED BY MARSAUENTERPRISES HIT AND RUPTURED A 6-INCH PIPELINE OWNED AND OPERATED BY KOCH PIPELINES, INC.. THERE WERE NO INJURIES.
2017-09-29 08:50 | NO | NO | 19890133 |  | 809 | ARCO PIPE LINE CO | YES | 1989-10-24 | 1100 | IL | MARSHALL |  | NO |  | NO | SECTION 15,5-29-N, R-1-W, MARSHALL COUNTY, ILLINOIS APPROXIMATELY 1/2 MILE EAST OF TOWN OF LAROSE. |  | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 495.8881 | 1000.4065 | FUEL OIL | 3 | 15 | 12 | NO | NO | 8 | 0.32 | 24000 | THREADED |  | 740 | 480 | YES | 24 | 925 | 7 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.D. HARRIS, MANAGER - PRODUCT BUSINESSES | 0000000000 | LEAK OCCURRED FROM A PIN HOLE CORROSION PIT - 15 BBLS OUT - 12 RECOVERED PIPE WAS PARTIALLY EXPOSED BECAUSE OF DEEPLY ERODED AREA - FUEL OIL TRAVELED TO CROW CREEK.
2017-09-29 08:50 | YES | NO | 19890134 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1989-10-20 | 1530 | TX | HARRIS | HOUSTON | NO |  | NO | DECKER DRIVE AND BAKER ROAD, BAYTOWN TEXAS TERMINAL, VICINITY MAP TPA-V-15 ATTACHED. |  | TANK FARM | OTHER | 2" THREAD CONN. ON TANK | 1989 | OTHER | 2" THREADED CONN. LOOSEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 620.9381 | 1252.6829 | GASOLINE | 3 | 79 | 65 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HANNIGAN, VICE PRESIDENT-OPERATIONS | 7137594700 | A 2" THREADED PLUG ON THE WATER DRAW-OFF CONNECTION LOCATION ON THE SUCTION LINE OF TANK 624 BECAME LOOSE AS A RESULT OF VIBRATION CAUSED BY PRODUCT MOVEMENT IN THE LINE. AN ESTIMATED 79 BARRELS OF PRODUCT ESCAPED THROUGHT THE LOOSENED 2" CONNECTION. THE SPILLED PRODUCT WAS CONTAINED IN AN EXCAVATED SUMPALLOWING FOR THE PRODUCT TO BE PUMPED INTO DRUMS. TEMPORARY REPAIRS WERE MADE BY TIGHTENING THE 2" CONNECTION TO THE PROPER TORGUE. SCHEDULED PERMANENTREPAIRS CALL FOR THE 2" THREADED CONNECTION TO BE REMOVED AND REPLACED WITH A BLIND FLANGE. THE SITE WILL BE FERTILIZED AND AERATED TO ENHANCE RETURN TOGRASS COVER.
2017-09-29 08:50 | YES | NO | 19890135 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1989-11-10 | 2005 | AR | UNION |  | NO |  | NO | HIGHWAY 167 NORTH EL DORADO TERMINAL NO. 2, UNION COUNTY ARKANSAS. |  | TANK FARM | TANK |  | 1989 | OTHER | BOOSTER PUMP MOTOR FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9700 | 8365.4159 | 16876.4228 | GASOLINE | 3 | 4 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HANNIGAN, VICE PRESIDENT - OPERATIONS | 7137594700 | WHILE PUMPING PRODUCT FROM TANKAGE TO AN OUTGOING PIPELINE, A 100 H.P. BOOSTER PUMP MOTOR BEARING FAILED, HEATED UP AND CAUSED THE PUMP SEAL TO FAIL. LEAKING PRODUCT WAS IMMEDIATELY IGNITED. THE PUMP WAS IMMEDIATELY SHUT DOWN, ISOLATED, AND THE FIRE WAS EXTINGUISHED. REPAIRS ARE PRESENTLY UNDERWAY TO REPLACE THE MOTOR AND EXPECT TO BE COMPLETED ON NOVEMBE 16, 1989.
2017-09-29 08:50 | YES | NO | 19890136 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-10-18 | 945 | KS | WYANDOTTE |  | NO |  | NO | TANK #181 A KANSAS CITY TERMINAL (ADDRESS: 2029 FAIRFAX TRAFFICWAY, KANSAS CITY, KS). |  | TANK FARM | OTHER | TANK OVERFILL | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 75 | 75 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENG. & TECHNICAL SERVICES | 9186614721 | TANK #181 WAS BEING FILLED BY 10" PAOLA-KANSAS CITY LINE AT 3250 BPH. THE OPERATOR MISSED THE TOP GAUGE ON TANK #181 WHICH IS 33'0", AND THE TANK OVERFLOWED AT APPROXIMATELY 37'0". APPROXIMATELY 75 BBLS. SPILLED ON THE GROUND WHICH WAS MIXED WITH RAIN WATER INSIDE THE DIKE.
2017-09-29 08:50 | YES | NO | 19890138 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1989-11-06 | 700 | AR | UNION |  | NO |  | NO | 167 NORTH ELD DORADO TERMINAL NO. 2, UNION COUNTY, ARKANSAS. |  | TANK FARM | TANK |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4600 | 3967.1044 | 8003.252 | KEROSENE | 3 | 67 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HANNIGAN, VICE PRESIDENT - OPERATIONS | 7137594700 | A SHORTAGE OF PRODUCT WAS DETECTED IN TANK NO. 1210. A VISUAL INSPECTION INDICATED PRODUCT SEEPAGE NEAR THE TANK'S SHELL. THE TANK WAS IMMEDIATELY EMPTIED OF PRODUCT, CLEANED, ADN REPAIRS ARE BEING PLANNED. THE SITE WILL BE TERTILIZED AND AEREATED TO ENHANCE RETURN OF GRASS COVER.
2017-09-29 08:50 | YES | NO | 19890139 |  | 19226 | TEXACO PIPELINE INC | NO | 1989-10-05 | 1800 | MT | DAWSON |  | NO |  | NO | SECTION 8 TOWNSHIP 15N/RANGE 55E |  | LINE PIPE | PIPE |  | 1955 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 862.414 | 1739.8374 | CRUDE OIL | 3 | 605 | 595 | NO | NO | 10 | 0.25 | 2140 | WELDED |  | 1200 | 1800 | YES | 12 | 1804 | 10 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GREGG A. WERGER, DIVISION ENGINEER | 4066873304 | PIPELINE WAS UNDER 1500 PSI MINIMUM PRESSURE TEST. THE FAILURE OCCURRED IN THE LATER STAGES OF THE TEST IN THE LOW AREA OF TEST SECTION. LINE FLYER ANDEQUIPMENT WAS ON SITE FOR DAMAGE PREVENTION DURING TEST. THE FAILURE WAS LOCATED ADN REPAIRS COMMENCED IMMEDIATELY. THE PIPELINE WAS REPAIRED ON 10/6/89. CLEAN-UP COMPLETED ON 10/9/89.
2017-09-29 08:50 | YES | NO | 19890140 |  | 2731 | CHEVRON PIPELINE CO | NO | 1989-10-30 | 830 | TX | CRANE | CRANE | NO |  | NO | SANDHILLS PUMP STATION/APPROX.16 MI.W. CRANE, TX. |  | PUMPING STATION | PIPE |  | 1941 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 50 | 40 | NO | NO | 6 | 0.63 | 30 | WELDED |  | 0 | 30 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.M. COOK-COMPLIANCE COORDINATOR | 9156877559 | #2 UNIT AT SANDHILLS STATION LOCKED OUT AT APPROX. 8:15AM 10/30/89. GAUGER ENTERER STATION AT APPROX. 8:30 AM. AND FOUND LEAK. LEAK WAS CAUSED BY INTERNAL CORROSION AND WAS CONFINED TO COMPANY PROPERTY AROUND MANIFOLD AREA. OILWAS RECOVERED AND THE SITE CLEANED UP WITH NO TREAT TO THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19890141 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-09-28 | 800 | IA | BLACK HAWK |  | NO |  | NO | WATERLOO TERMINAL #D203. |  | TANK FARM | PIPE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 56 | 56 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN - VICE PRESIDENT, OPERATIONS | 9185884850 | ON 9/28/89 A 56 BBL RELEASE OF REGULAR GASOLINE OCCURRED AT OUR WATERLOO TERMINAL, WHEN A DRAIN VALVE TIED TO THE LOADING RACK METER FACILITY WAS INADVERTANTLY LEFT OPEN. PRODUCT FLOWED THROUGH THE DRAIN SYSTEM INTO THE SUMP, UPSETTING THE WATER SEAL IN THE OIL/WATER SEPERATOR WHICH CAUSED PRODUCT TO BE DISCHARGED INTO THE WATER RETENTION POND. ALL RELEASED PRODUCT WAS CONTAINED WITHIN THE RETENTION POND AND WAS LATER COMPLETELY RECOVERED.
2017-09-29 08:50 | YES | NO | 19890142 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-10-07 | 1050 | MO | JOHNSON |  | NO |  | NO | E 1/2, NE 1/4, SECTIN 21, T47N, R27W, LINE SECTION #B080. |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 25872.4203 | 52195.122 | GASOLINE | 3 | 200 | 85 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 1440 | 209 | YES | 8 | 2059 | 9 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | ON OCTOBER 7, 1989 THE #7-8" OLATHE TO COLUMBIA LINE (MP 47+18) WAS STRUCK BY A FRONT END LOADER OPERATED BY ROBERT LEBEAU (ROUTE 1, BOX 84, CENTERVIEW, MISSOURI). MR. LEBEAU WAS LEVELING A SITE IN PREPARATION FOR SETTING A MOBILEHOME WHEN HE STRUCK THE LINE. THE LINE WAS NOT OPERATING AT THE TIME OF THEPUNCTURE, HOWEVER, IT WAS PRESSURED TO APPROXIMATELY 200 PSI. MR. LEBEAU RAN TO THE NEAREST LINE MARKER TO OBTAIN OUR EMERGENCY NUMBER, THEN CALLED OUR DISPATCHING CENTER. MAINTENANCE CREWS WERE DISPATCHED TO THE SITE TO INITIATE CLEAN-UP AND REPAIR OPERATIONS. APPROXIMATELY 85 BBLS OF FREE PRODUCT WAS RECOVERED. THE REMAINING SOILS WERE HAULED TO A NEARBY LANDFILL. CLEAN-UP EFFORTS WERE COORDINATED WITH THE EPA AND THE MISSOURI DNR. MR. LEBEAU CLAIMSTHAT HE DID NOT NOTICE THE LINE MARKERS WHEN HE BEGAN TO EXCAVATE (MARKERS WERE LOCATED 50' WEST AND 600' EAST OF THE SITE). WILLIAMS PIPE LINE IS A MEMBER OF THE MISSOURI ONE-CALL SYSTEM, HOWEVER, MR. LEBEAU DID NOT BOTHER TO CAL
2017-09-29 08:50 | YES | NO | 19890144 |  | 10313 | KOCH PIPELINE INC | YES | 1989-10-18 | 1615 | OK | WOODS |  | NO |  | NO | NE/4, NE/4 SEC. 2, T25N, R14W, WOODS COUNTY, OKLAHOMA. |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 35151 | 30314.7148 | 61157.0244 | L. P. G. | 2 | 2089 | 0 | NO | NO | 6.63 | 0.22 | 46000 | WELDED |  | 1440 | 630 | YES | 24 | 1800 | 1 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | UNKNOWN | NO | YES | MARC S. DEVARENNES, DIVISION ENGINEER | 4053952377 | DURING A MAINTENANCE OPERATION, THE LINE WAS INADVERTENTLY HIT AND PUNCTURED, WHICH RESULTED IN THE RELEASE OF PRODUCT. BLOCK VALVES WERE SHUT, THE SITEWAS MONITORED BY COMPANY PERSONNEL, AND THE DAMAGE REPAIRED ON 10/20/89.
2017-09-29 08:50 | YES | NO | 19890145 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1989-11-07 | 1321 | IA | JEFFERSON |  | NO |  | NO | SECTION 31, TOWNSHIP 71 NORTH, RANGE 9 WEST, JEFFERSON COUNTY, IA. |  | PUMPING STATION | PUMP |  | 1977 | OTHER | SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300451 | 259113.1513 | 522735.8862 | L. P. G. | 2 | 50 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | SEAL FAILED AND CAUSED FIRE.
2017-09-29 08:50 | YES | NO | 19890146 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1989-10-20 | 945 | CA | LOS ANGELES | CARSON | NO |  | NO | 24696 S. WILMINGTON AVE. CARSON, CALIFORNIA WITHIN THE CARSON CRUDE DISTRIBUTION TERMINAL PUMP CONTAINMENT AREA. |  | TANK FARM | VALVE |  | 1977 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3018.449 | 6089.4309 | CRUDE OIL | 1 | 90 | 90 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD B. KUPREWICZ, VICE PRESIDENT OPERATIONS | 2134289017 | BLEEDER BENT VALVE LEFT IN OPEN POSITION FOLLOWING ROUTINE MAINTENANCE. THE PUMP WAS STARTED ON 10/29/89 RESULTING IN A RELEASE OF OIL WHICH WAS CONTAINED IN PUMP CONTAINMENT AREA.
2017-09-29 08:50 | NO | NO | 19890147 |  | 4805 | EXPLORER PIPELINE CO | YES | 1989-11-08 | 345 | OK | TULSA | TULSA | NO |  | NO | EXPLORER PIPELINE COMPANY WEST TULSA METER STATION. APPROXIMATELY 1/4/ MILES SOUTH OF 21ST STREET ON 33 WEST AVE. TULSA OKLAHOMA. |  | NO DATA | TANK |  | 1971 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 862.414 | 1739.8374 | GASOLINE | 1 | 17 | 16 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. SANDS - VICE PRESIDENT OPERATIONS | 9184935106 | AT APPROXIMATELY 3:45, NOVEMBER 8, 1989, EXPLORER'S GLENPOOL TERMINAL OPERATOR WAS NOTIFIED BY A WILLIAMS PIPELINE OPERATOR THAT EXPLORER'S WEST TULSA STATION SUMP TANK WAS OVERFLOWING. EXPLORER PERSONNEL AND A VACUUM TRUCK WEREDISPATCHED TO THE SITE. AT 4:10 AN EXPLORER DELIVERYMAN ARRIVED AT THE SITEAND CLOSED A SAMPLE LINE VALVE THAT HAD BEEN MISTAKENLY LEFT OPEN, ALLOWING FLOW INTO AN UNDERGROUND SUMP TANK. A VACUUM TRUCK ARRIVED ON THE SCENE AT 5:15 AND BEGAN RECOVERING PRODUCT. UNLEADED GASOLINE HAD FLOWED INTO AN ADJACENT DIKED TANK AREA OF WILLIAMS PIPELINE COMPANY. APPROXIMATELY 16 BARRELS OF THE ESTIMATED 17 BARREL SPILL WAS RECOVERED BY THE VACUUM TRUCK. CLEANUP OPERATIONS WERE COMPLETED BY 15:30 NOVEMBER 8, 1989.
2017-09-29 08:50 | YES | NO | 19890148 |  | 809 | ARCO PIPE LINE CO | YES | 1989-10-26 | 1445 | TX | MONTAGUE |  | NO |  | NO | KMONTAGUE CO., 6 MILES NORTH OF THE CITY OF NOCONA, OFF OF S.H. 103 SAMULE LITTLE SUR., A-417. |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 6036.8981 | 12178.8618 | CRUDE OIL | 1 | 160 | 2 | NO | NO | 12 | 0.38 | 24000 | THREADED |  | 550 | 300 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.D. HARRIS - MANAGER, PRODUCT BUSINESS | 3163311300
2017-09-29 08:50 | YES | NO | 19890149 |  | 3445 | DIXIE PIPELINE | YES | 1989-10-31 | 1307 | MS | CLARKE |  | NO |  | NO | CARMICHAEL, MS PUMP STATION; ON COUNTY ROAD IN NE 1/4 OF SECTIO 22, T2N, R17E, CLARKE COUNTY, MS. |  | PUMPING STATION | OTHER | PIPE NIPPLE ON PUMP | 1970 | OUTSIDE FORCE DAMAGE | FAILED PIPE NIPPLE | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 500 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.D. OLSON, WESTERN DISTRICT MANAGER | 5046544112 | A CRACK DEVELOPED IN A ONE-IN. STEEL PIPE NIPPLE ON THE STATION PUMP AND EVENTUALLY LEAKED.
2017-09-29 08:50 | YES | NO | 19890150 |  | 18273 | SHELL PIPE LINE CORP | NO | 1989-02-28 | 1240 | TX | WARD | MONAHANS | NO |  | NO | SE 1/4, SW 1/4, SECTION 3, BLOCK 20, PUBLIC SCHOOL LANDS SURVEY EIGHT MILES EAST OF MONAHANS. HENDRICK-BARNSLEY NO. 2-6-INCH. |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 862.414 | 1739.8374 | CRUDE OIL | 1 | 60 | 45 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 800 | 400 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | A RECENT REVIEW OF OUR RECORDS INDICATED THAT WE HAD INCORRECTLY CATEGORIZEDCERTAIN PIPELINE AS GATHERING LINES AFTER THAT REVISION BECAM EFFECTIVE. WHEREAS THE PIPELINES ARE LESS THAN 8 INCHES IN DIAMETER, THEY DO NOT, INFACT, BEGIN AT PRODUCTION FACILITIES. ACCORDINGLY, WE HAVE DETERMINED THAT TWO ACCIDENTAL RELEASES THAT OCCURRED IN 1989 AND ONE IN 1988 WERE ERRONEOUSLY NOT REPORTED TO YOU.
2017-09-29 08:50 | YES | NO | 19890151 |  | 18273 | SHELL PIPE LINE CORP | NO | 1989-04-11 | 1300 | TX | WINKLER | KERMIT | NO |  | NO | NW 1/4, SW 1/4, SECTION 17, BLOCK 11, PUBLIC SCHOOL LANDS SURVEY EIGHT MILES SOUTH OF KERMIT HENDRICK-BARNSLEY NO. 2 - 6-INCH. |  | LINE PIPE | OTHER | SCREWED PIPE NIPPLE | 1928 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 862.414 | 1739.8374 | CRUDE OIL | 1 | 270 | 240 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 800 | 400 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | SHELL CONTRACTOR RAN OVER A 2" VALVE CAUSING THE VALVE AND NIPPLE TO BE PULLED OUT OF COLLAR.
2017-09-29 08:50 | YES | NO | 19890152 |  | 18273 | SHELL PIPE LINE CORP | YES | 1989-11-03 | 1300 | TX | GAINES | SEMINOLE | NO |  | NO | NW 1/4, NW 1/4, SECTION 19, BLOCK A-9 15 MILES WEST OF SEMINOLE AND THREE MILES NORTH WASSON-HOBBS 6-INCH. |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2875 | 2479.4403 | 5002.0325 | CRUDE OIL | 1 | 85 | 60 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 900 | 500 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | YES | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | THE LINE WAS PUNCTURED BY FRONT END LOADER.
2017-09-29 08:50 | YES | NO | 19890153 |  | 2552 | COLONIAL PIPELINE CO | YES | 1989-08-03 | 1700 | NC | GUILFORD |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S GREENSBORO JUNCTION TANK FARM 411 GALLIMORE DAIRY ROAD. |  | TANK FARM | TANK |  | 1963 | OTHER | CRACK IN THE SUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 297 | 297 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER TECHNICAL & REGULATORY | 4048412296 | AT APPROXIMATELY 1700 ON AUGUST 3, 1989, A COLONIAL EMPLOYEE NOTICED DEAD GRASS ON THE GASOLINE MANIFOLD SIDE OF THE TANK DIKE NEAR TANK 834 AT THE GREENSBORO JUNCTION TANK FARM. HE INSPECTED THE AREA AND NOTICED A MODERATE SMELLOF GASOLINE VAPORS. ON AUGUST 4, THE GREENSBORO RAM TEAM EXCAVATED THE AREAAND RECOVERED APPROXIMATELY 7 BARRELS OF GASOLINE. COLONIAL NOTIFIED THE NORTH CAROLINA DIVISION OF ENVIRONMENTAL MANAGEMENT. THE INITIAL ESTIMATED BARRELS LOSS AT THE TIME WAS 10 BARRELS. WORKING WITH THESE STATE ENVIRONMENTALINSPECTORS, ADDITIONAL HOLES WERE DUG FOR INSPECTION WELLS. AFTER REVIEWINGTHE RESULTS, THREE 36" RECOVERY WELLS WERE INSTALLED. TANK 834 WAS CLEANED AND, AFTER AN EXTENSIVE INSPECTION, FOUND TO CONTAIN A SMALL CRACK IN THE SUMP. THE SUMP WAS REPAIRED AND THE TANK WAS RETURNED TO SERVICE. ON NOVEMBER 30, AN INSPECTION OF PRODUCT RECOVERY RECORDS, BY AN EMPLOYEE FROM COLONIAL'SENVIRONMENTAL SECTION, REVIEALED THAT A TOTAL OF 297 BARRELS HAD BEEN REMOVED FROM THE THREE RECOVERY WELLS. SINCE THE AMOUNT OF PRODUCT RECOVERED EXCEEDED 50 BARRELS IT WAS DETERMINED THAT A DOT REPORT SHOULD BE FILED.
2017-09-29 08:50 | YES | NO | 19890154 |  | 12434 | MID - CONTINENT PIPELINE CO | NO | 1989-10-18 | 700 | OK | PAYNE | CUSHING | NO |  | NO | CUSHING, OKLAHOMA IN TANK DIKE 66. ALL PRODUCT WAS CONTAINED INSIDE TANK DIKE. |  | LINE PIPE | VALVE |  | 1980 | INCORRECT OPERATION BY OPERATOR PERSONNEL | HIGH PRESSURE | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4312.07 | 8699.187 | CRUDE OIL | 1 | 160 | 159 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.W. DURRETT, MANAGER OF RISK MGMT. | 9185866231 | UNDER CERTAIN OPERATING CONDITIONS THIS 150# ANSI CHECK VALVE WAS EXPOSED TOTHE DISCHARGE PRESSURE FROM THE #5 UNIT AT LITTLE FARM. A 6"-600# ANSI GATEVALVE HAS BEEN INSTALLED UPSTREAM OF THIS VALVE TO PREVENT THIS FROM HAPPENING AGAIN.
2017-09-29 08:50 | YES | NO | 19890155 |  | 19226 | TEXACO PIPELINE INC | NO | 1989-11-02 | 645 | MT | DAWSON |  | NO |  | NO | NE 1/4 SECTION 28 T14N R55E. |  | LINE PIPE | PIPE |  | 1955 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 431.207 | 869.9187 | CRUDE OIL | 1 | 400 | 398 | NO | NO | 12 | 0.25 | 2040 | WELDED |  | 1200 | 820 | YES | 12 | 1500 | 1 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GREGG WERGER/DIVISION ENT. | 4066873304 | THE PIPELINE WAS BEING PRESSURED FOR AN 8 HOUR STATIC PRESSURE TEST. A SEAM FAILED DURING PRESSURE UP AT 6:45 AM AT APPROXIMATELY 820 PSI. PIPELINE JOINT REPLACEMENT AND CLEAN UP WAS COMPLETED ON THE FILLOWING DAY (11/13/89).
2017-09-29 08:50 | YES | NO | 19890156 |  | 13131 | CONOCO INC | NO | 1989-11-01 | 822 | OK | CREEK | SAPULPA | NO |  | NO | NEAR CITY OF SAPULPA'S SEWAGE TREATMENT PLANT. SE/4 - SECTION 23 - T18N - R11E - CREEK COUNTY, OK. |  | LINE PIPE | PIPE |  | 1920 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2156.035 | 4349.5935 | GASOLINE | 1 | 500 | 394 | NO | NO | 8 | 0.32 | 35000 | THREADED |  | 600 | 399 | YES | 24 | 750 | 1 | 77 | EXTERNAL | Null | YES | OTHER | ELECTROYSIS | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY G. HUBBARD, MANAGER, ENVIRONMENTAL AFFAIRS | 7132932032 | ON 11/1/89, CONOCO PIPE LINE COMPANY'S 8 INCH PETROLEUM PRODUCTS PIPELINE EXPERIENCES A CORROSION LEAK IN SE/4 OF SECTION 23, TOWNSHIP 18N, RANGE 11E, CREEK COUNTY, OKLAHOMA.
2017-09-29 08:50 | YES | NO | 19890157 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-11-16 | 1015 | MO | JASPER |  | NO |  | NO | CARTHAGE TERMINAL |  | TANK FARM | OTHER | CAVERN WELL SHAFT | 1968 | OTHER | WATER SEAL IN WELL LOST | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 736000 | 634736.7104 | 1280520.3252 | L. P. G. | 2 | 2000 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT-OPERATIONS | 9185883850 | ON NOVEMBER 16, WHILE CONDUCTING ROUTINE MAINTENANCE ON THE PUMP WELL SHAFT,PROPANE WAS RELEASED FROM THE CAVERN, AND IGNITED. IT APPEARS THAT THE WATERSEAL IN THE PUMP CASING SHAFT WAS DISRUPTED DUE TO THE RISE IN CAVERN PRESSURE RESULTING FROM THE CAVERN BEING OVERFILLED. LOCAL FIRE DEPARTMENTS FROM JASPER AND CARTHAGE RESPONDED. THE FIRE WAS EXTINGUISHED ON 11/17/89 BY PUMPING WATER BACK DOWN THE WELL TO RE-ESTABLISH THE WATER SEAL. THE ADJACENT HIGHWAY AND RAILROAD WERE CLOSED WHILE THE FIRE WAS BURNING. SOME RESIDENTS FROMTHE NEARBY TOWN OF JASPER WERE ALSO EVACUATED. ALL APPROPRIATE AGENCIES WERE NOTIFIED. RESTORATION ACTIVITY CONTINUES.
2017-09-29 08:50 | YES | NO | 19890158 |  | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1989-09-19 | 216 | TX | ECTOR | NOTREES | NO |  | NO | BLOCK 45, TOWNSHIP 1 SOUTH, SECTION 17, T. & P. R.R. CO. 1/2 MILE WEST OF FARM MARKET ROAD 2019 ON STATE HIGHWAY 302. |  | LINE PIPE | LONGITUDINAL WELD |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 19450 | 16773.9525 | 33839.8374 | L. P. G. | 2 | 1194 | 0 | NO | NO | 8.63 | 0.19 | 1831 | WELDED |  | 1315 | 1240 | YES | 24 | 1727 | 6 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | PIPELINE RUPTURED @ 1240 PSIG SHORTLY AFTER STARTING MAIN LINE UNIT.
2017-09-29 08:50 | YES | NO | 19900001 |  | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1989-12-26 | 430 | TX | HASKELL |  | NO |  | NO | A.J. SMITH SURVEY, ABSTRACT 365, HASKELL COUNTY, TEXAS. | 2375 | PUMPING STATION | OTHER | FLANGE GASKET FAILURE | 1988 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 474.3277 | 956.9106 | CRUDE OIL | 1 | 110 | 100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | PAT MULLEN, AREA SUPERINTENDENT | 8178642662 | EXTREME COLD WEATHER CAUSED GASKET TO FAIL CAUSING OIL TO SPRAY OUT ON PREMISES.
2017-09-29 08:50 | NO | NO | 19900002 |  | 11733 | LOOP INC | YES | 1989-12-20 | 910 | LA | GRAND ISLE |  | YES | 28 53' 60", 90 01' 30" | NO | LOCATED IN GRAND ISLE BLOCK 59, APPROXIMATELY 20 MILES SOUTH OF GRAND ISLE, LA. LOOP MARINE TERMINAL PUMPING PLATFORM. | 22751 | PUMPING STATION | WELDING FITTING |  | 1980 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 43120.7004 | 86991.8699 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 30 | 0.38 | 5200 | WELDED |  | 620 | 508 | YES | 24 | 1100 | 1 | 80 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.G. WATSON, VICE-PRESIDENT, ENG. ENVIRONMENTAL & SAFETY | 5043685667 | ON WEDNESDAY, 12/20/89 AT 0831 LOOP COMMENCED OFFLOADING A TANKER AT ITS FACILITY IN GRAND ISLE BK 59. THE OFFLOADING RATE WAS 6500 CU.METER/HR AT APPROXIMATELY 0910 AN EMPLOYEE SIGHTED AN OIL SHEEN ORIGINATING FROM BENEATH THE PUMPING PLATFORM AND DISCOVERED A LEAK IN A WELD THAT CONNECTS A FUTURE 30" DISCHARGE LIN TO THE 48" DISCHARGE HEADER, ONTHE PUMPING PLATFORM. IT WAS LATER DETERMINED TO BE A 20" CRACK IN THE WELD AT THE CONNECTION OF THE 30" PIPE TO THE 48" X 30" BRANCH TEE. THE SYSTEM WAS IMMEDIATELY SHUT DOWN AND DEPRESSURED BY 0945. A TOTAL OF 50 GALLONS WAS ESTIMATE TO HAVE BEEN SPILLED. THECRACKED WELD IS IN A DORMANT (NON-ACTIVE) BRANCH LINE FOR THE DISCHARGE OF AFUTURE MAIN OIL LINE PUMP WHICH WOULD BE INSTALLED IN THE NEXT EXPANSION OF THE SYSTEM.
2017-09-29 08:50 | YES | NO | 19900003 |  | 2731 | CHEVRON PIPELINE CO | NO | 1989-12-20 | 1400 | TX | JEFFERSON | BEAUMONT | NO |  | NO |  | 22768 | LINE PIPE | GIRTH |  | 1924 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 5500 | 4400 | NO | NO | 10.75 | 0.39 | 46000 | WELDED |  | 275 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH , DIVISION MANAGER | 9048393100 | WELD FAILED ON LINE. CRUDE OIL GRAVITY FLOWED BACK OUT OF TANKAGE. VALVES AT TANK WERE OPEN. DUE TO NORMAL PROCEDURE FOR SUN RELIEF, OIL LEAK CONTAINED IN DITCH/CANALS & BEING RECOVERED. BAYON BOOMED OFF AND TRIBUTARIES BOOMED. BAYOU PATITIONED WITH BOOMS AND VACUUM TRUCKS PULLING FROM PARTITION. OIL/WATER BEING RETURNED TO TANKAGE.
2017-09-29 08:50 | YES | NO | 19900004 |  | 737 | ASHLAND PIPELINE CO | YES | 1989-12-13 | 900 | MS | FRANKLIN |  | NO |  | YES | SECTION 17, T5N, R2E; APPROXIMATELY 6 1/2 MILES SOUTH OF ROXIE, MS. APPROXIMATELY 100' SOUTH OF FOREST ROUTE 102, HOMOCHITTO NATIONAL FOREST. | 22286 | LINE PIPE | GIRTH |  | 1947 | FAILED WELD | SUBSIDENCE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 27597.2483 | 55674.7967 | CRUDE OIL | 1 | 605 | 240 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 600 | 340 | YES | 0 | 1439 | 1 | 47 | NO DATA | Null | Null | NO DATA |  | SUBSIDENCE |  | Null | ONE CALL |  | Null | Null | DAVID M. SZTROIN, PE.E, PROJECT ENGINEER | 3187574138 | THE 10" PIPELINE WAS LOWERED IN JULY, 1987. THE SURROUNDING BACKFILL WAS OFA SANDY, CLAY SOIL. DURING LOWERING OPERATIONS, THE PIPELINE WAS APARENTLY INADEQUATELY SUPPORTED. DUE TO THE LARGE OVERBURDEN (PIPELINE HAD OVER 20' OF COVER), THE PIPELINE WAS SUBJECTED TO INCREASING AMOUNTS OF STRESS AS THE CLAY CONSOLIDATED OVER THE 2 1/2 YEARS SINCE THE LOWERING PROJECT. THIS SITUATION, COUPLED WITH THE FACT THAT THE GIRTH WELD HAD IMPROPER PENETRATION WHENTHE PIPELINE WAS ORIGINALLY LAID IN 1947, CAUSED THE GIRTH WELD TO CRACK.
2017-09-29 08:50 | YES | NO | 19900005 |  | 26085 | SCURLOCK OIL CO | NO | 1989-12-24 | 1100 | TX | GREGG | KILGORE | NO |  | NO | ONE-HALF MILE OF THE SOUTH OF HIGHWAY 135 IN RABBIT GREEK. | 23042 | LINE PIPE | GIRTH |  | 0 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2587.242 | 5219.5122 | CRUDE OIL | 1 | 850 | 0 | NO | NO | 6.63 | 0.24 | 24000 | WELDED |  | 720 | 100 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | THOMAS G. HRNCIR, REGIONAL ENGINEER | 2149845252 | A SCURLOCK OIL COMPANY 6-5/8" DIAMETER PIPELINE FAILED IN A GIRTH WELD WHEN TEMPERATURES DROPPED TO BELOW 0F CAUSING THE PIPE TO CONTRACT. CRUDE OIL LEAKED FROM THE LINE INTO RABBIT CREEK. A DISCREPANCY IN LINE FLOW WAS DISCOVERED BY A COMPANY GAUGER DURING HIS MIDNIGHT CHECK. IT WAS DETERMINED TO SHUT THE LINE DOWN UNTIL THE DISCREPANCY COULD BE RESOLVED. COMPANY PERSONNEL WAS INSTRUCTED TO INSPECT THE RIGHT-OF-WAY AND A LEAK WAS DISCOVERED BY THE AERIAL PATROL AT 11:00 A.M. ON 12/24/89. COMPANY PERSONNEL AND CONTRACT CREWS ISOLATED THIS PARTICULAR SECTION OF LINE AND DEPLOYED BOOMS TO CONTAIN THE OIL IN THE CREEK. A CLAMP WAS PLACED ON THE LINE AND THIS PORTION OF LINE SHUT DOWN UNTIL PERMANENT REPAIRS CAN BE MADE.
2017-09-29 08:50 | YES | YES | 19900006 |  | 26085 | SCURLOCK OIL CO | NO | 1989-12-27 | 800 | TX | GREGG | KILGORE | NO |  | NO | ONE-HALF MILE TO THE SOUTH OF HIGHWAY 135 IN RABBIT CREEK. |  | LINE PIPE | GIRTH | DOZIER KNOCKED DOWN LINE | 0 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 0 | 2 | 13000 | 11211.3821 | 22617.8862 | CRUDE OIL | 1 | 450 | 0 | YES | NO | 6.63 | 0.24 | 24000 | WELDED |  | 720 | 100 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | THOMAS G. HRNCIR, REGIONAL ENGINEER | 2149845252 | CLEAN UP WAS IN PROGRESS FROM A LEAK THAT OCCURRED ON 12/24/89, WHEN ON 12/27/89 A CONTRACT DOZIER OPERATOR WAS CLEARING ACCESS ALONG THE CREEK BANK, ACCIDENTALLY PUSHED A TREE INTO AN OVERHEAD POWER LINE CAUSING THE LINE TO SNAP AND THE WIRES TO FALL INTO THE CREEK CAUSING SPARKS AND IGNITING THE OIL. FIRE FIGHTERS, POLICE DEPARTMENT AND LOCAL AGENCIES RESPONDED TO THE FIRE.THE FIRE WAS BROUGHT UNDER CONTROL AND EXTINGUISHED IN 1.5 HRS. CLEAN UP EFFORTS AGAIN RESUMER.
2017-09-29 08:50 | YES | NO | 19900007 |  | 19536 | TOTAL PIPELINE CORP | NO | 1989-12-18 | 0 | OK | COTTON |  | NO |  | NO | SE 1/4 SECTION 17 - TOWNSHIP 4 SOUTH - RANGE 13 WEST. |  | TANK FARM | TANK |  | 1920 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 43120.7004 | 86991.8699 | CRUDE OIL | 1 | 12000 | 10200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | MICHAEL JOHN COOPER - CORROSION ENGINEER | 4052291638 | THE PROPERTY OWNER NEAR THE STATION NOTIFIED A TOTAL EMPLOYEE THAT THERE WASA PROBLEM WITH OUR STORAGE TANK AT DEVOL, OKLAHOMA. UPON ARRIVING AT THE SCENE, THE EMPLOYEE FOUND OUR 55,000 BBL. STORAGE TANK OVERFLOWING INTO THE DIKE AND THE STATION PUMP DOWN ON HIGH PRESSURE SHUTDOWN. HE IMMEDIATELY STARTEDTHE STATION AND TRIED TO PHONE FOR ASSISTANCE,BUT THE PHONE LINE WAS DEAD. HE THEN WENT TO THE ADJACENT LANDOWNER'S HOUSE AND CALLED OUT TOTAL'S CREW TOBEGIN CLEANUP PROCEDURES. AFTER FURTHER INVESTIGATION, IT WAS FOUND THAT THELANDOWNER ADJACENT TO THE PUMP STATION HAD HIRED A CONTRACTOR TO DIG A BURN PIT ON HIS PROPERTY. WHILE DIGGING THE PIT, THE CONTRACTOR HAD SEVERED THE PHONE LINE WHICH FED TOTAL'S PUMP STATION. THE SEVERED CABLE COMPLETELY DISABLED ALL ALARM SYSTEMS AND COMMUNICATIONS WITH THE PUMP STATION. THEREFORE, WHEN THE STATION WENT DOWN ON HIGH PRESSURE SHUTDOWN, AND WHEN THE TANK REACHED A CRITICAL LEVEL AND BEGAN TO OVERFLOW, TOTAL PERSONNEL WERE NOT AWARE OF THE SITUATION. PREVENTION OF FUTURE SPILLS: 1) TOTAL PIPELINE IS CURRENTLY INSTALLING SATELITE SCADA CONTROL EQUIPMENT IN PUMP STATIONS IN THE SOUTHWEST DIVISION. IN THE FUTURE, ALL ALARM SYSTEMS, TANK LEVELS, PRESSURE, FLOW RATES, ETC. WILL BE MONITORED 24 HOURS DAILY AT OUR SCADA CONTROL CENTER IN DENVER, COLORADO. THIS SHOULD PREVENT AN ACCIDENT OF THIS NATURE FROM OCCURRING IN THE FUTURE. 2) UNTIL THE SCADA SYSTEM IS IN FULL OPERATION, AN EMPLOYEE WILL VISUALLY INSPECT ALL PUMP STATIONS ONCE EACH DAY ON WEEKENDS. 3) TOTALPIPELINE IS CURRENTLY INSTALLING THE SCADA CONTROL CONTROL EQUIPMENT AT DEVOL STATION AND SHOULD BE IN FULL OPEATION BY JANUARY 30, 1990.
2017-09-29 08:50 | YES | NO | 19900008 |  | 2552 | COLONIAL PIPELINE CO | YES | 1989-12-18 | 1027 | VA | ORANGE | UNIONVILLE | NO |  | NO |  | 05101 | LINE PIPE | PIPE |  | 1963 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 64681.0507 | 130487.8049 | KEROSENE | 3 | 5043 | 4759 | NO | NO | 32 | 0.28 | 52000 | WELDED |  | 657 | 545 | YES | 24 | 831 | 11 | 63 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER-TECHNICAL & REGULATORY | 4048412296 | ON DECEMBER 18, 1989, COLONIAL'S LINE 4 DISPATCHER WAS COMPLETING A DELIVERY TO MITCHELL JUNCTION AND BEGINNING A DELIVERY AT CHANTILLY STATION. WHILE COMPLETING THIS OPERATION, AT 10:32 AM, HE OBSERVED THAT LOUISA STATION'S DISCHARGE PRESSURE WAS ABNORMALLY LOW, AND HE SHUT THE PIPELINE DOWN AND NOTIFIED HIS SUPERVISOR. THE RICHMOND AREA MANAGER WAS NOTIFIED OF THE POSSIBILITY OF A LEAK, AND ADVISED TO ARRANGE FOR AERIAL SURVEILLANCE AND FOR MAINTENANCECREWS TO BE MOBILIZED. THE REGULAR AERIAL PATROL HAD JUST COMPLETED MITCHELL JUNCTION TO FAIRFAX AND WAS REDIRECTED SOUTH TOWARD LOUISA STATION. THE RICHMOND AREA MANAGER ALSO JOINED THE SURVEILLANCE IN A HELICOPTER. AT 1:03 PM, THE LEAK SITE WAS LOCATED ONE MILE NORTH OF LOCUST GROVE STATION. KEROSENEWAS OBSERVED IN MINE RUN, WHICH EMPTIES INTO THE RAPIDAN RIVER. MAINTENANCECREWS DEPLOYED BOOMS, BUILT DAMS, AND CONDUCTED RECOVERY OPERATIONS AT VARIOUS LOCATIONS BETWEEN THE LEAK SITE AND RT 610 ON THE RAPIDAN RIVER.THE SPLIT ON TPIPE, 5'2" LONG WITH A GAP OF 6" AT THE WIDEST POINT, OCCURRED ADJACENT TO THE LONGITUDINAL SEAM IN THE BASE METAL AT THE TOE OF THE WELD. THE PIPELINEWAS REPAIRED BY REMOVING 34'2" OF PIPE CONTAINING THE FRACTURE AND REPLACINGIT WITH PRETESTED LINE PIPE AND A 7-DEGREE FITTING. ALL GIRTH WELDS PASSED A RADIOGRAPHIC INSPECTION. THE PIPE SPECIMEN HAS BEEN SENT TO A METALLURGICAL LABORATORY FOR ANALYSIS. A TOTAL OF 4,759 BARRELS OF THE 5,043 BARRELS LOST FROM THE PIPELINE HAVE BEEN RECOVERED. CLEANUP EFFORTS ARE STILL IN PROGRESS. NOTICE BY TELEPHONE WAS GIVEN TO THE NATIONAL RESPONCE CENTER. A SUBSEQUENT REVIEW OF THE PIPELINE OPERATING DATA REVEALED THAT THE LEAK OCCURED AT APPROXIMATELY 10:27 AM.
2017-09-29 08:50 | YES | NO | 19900009 |  | 443 | AMOCO PIPELINE CO | YES | 1989-12-30 | 730 | OK | CREEK |  | NO |  | NO | EAST OF CITY OF DRUMRIGHT, OK, EAST OF HIGHWAY 99, NORTH OF HIGHWAY 33, SW 1/4 SECTION 33, TOWNSHIP 18N, RANGE 7E, ON COMPANY STATION. |  | TANK FARM | PIPE |  | 1919 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 300 | 285 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. CARICO, AREA MANAGER | 9182257271 | A PIT (INTERNAL) LEAK DEVELOPED IN A 6" TRUCK UNLOADING LINE.
2017-09-29 08:50 | YES | NO | 19900010 |  | 18273 | SHELL PIPE LINE CORP | YES | 1989-12-09 | 1430 | TX | ARCHER | HOLLIDAY | NO |  | NO | SE 1/4, SE 1/4, SECTION 23, SPRR SURVEY EIGHT MILES EAST OF HOLLIDAY MCCAMEY-CUSHING 10-INCH. | 22031 | LINE PIPE | PIPE |  | 1927 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 5174.4841 | 10439.0244 | CRUDE OIL | 1 | 750 | 650 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 930 | 700 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | LANDOWNER'S OPERATOR HIT LINE WITH DOZER.
2017-09-29 08:50 | YES | NO | 19900011 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-12-08 | 1624 | IL | MONTGOMERY |  | NO |  | NO | BORGER-E. CHICAGO "BLUE" LINE - MP 741-2165 SEC. 20, T9N, R4W. APPROXIMATELY 1 1/2 MILES NORTHWEST OF BUTLER, IL OFF COUNTY ROAD 14 & HWY. 127. | 21983 | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 47432.7705 | 95691.0569 | L. P. G. | 2 | 3283 | 0 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1150 | 493 | YES | 24 | 1470 | 4 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | A HIRED HAND OF THE PROPERTY OWNER PUNCTURED THE 8" BLUE LINE WITH A CHISEL PLOW ON HIS TRACTOR WHILE TILLING A FIELD.
2017-09-29 08:50 | YES | NO | 19900012 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-12-26 | 1800 | TX | UPTON | CRANE | NO |  | NO | APPROX 5 MI NE OF CRANE, TX/CRANE TO MIDLAND #1-8 SECTION 5 BLOCK C SURVEY T&P RR.CO FIELD NAME MCELROY MILE POST 5 | 23282 | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 172.4828 | 347.9675 | CRUDE OIL | 1 | 200 | 150 | NO | NO | 8.63 | 0.32 | 24000 | WELDED |  | 800 | 800 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | R.M. COOK-COMPLIANCE COORDINATOR | 9156877559 | LEAK DUE TO EXTERNAL CORROSION ON PIPE. SPILL REPORTED BY EXXON PIPELINE EMPLOYEE. CRUDE OIL CONTAINED IN LOW AREA AND PICKED UP BY VACUUM TRUCKS AND HAULED TO CPL CRANE STATION FOR REINJECTION INTO SYSTEM. LINE SECTION WAS REPAIRED WITH NEW COATED AND WRAPPED PIPE. SITE CLEANED UP. NO THREAT TO THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19900013 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-12-19 | 1200 | TX | SCURRY | SNYDER | NO |  | NO | APPROX .25 MI SW SNYDER,TX SECTION 125 BLOCK 25 SURVEY H&T RR.CO FIELD NAME SHARON RIDGE LEASE NAME SHARON RIDGE STATION | 22704 | PUMPING STATION | PUMP |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | RETAINING STUDS BREAK | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 200 | 196 | NO | NO | 0 | 0 | 0 | OTHER |  | 1200 | 1160 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | R.M. COOK-COMPLIANCE COORDINATOR | 9156877559 | LEAK DUE TO LOOSE PACKING GLAND WHICH CAUSED RETAINING STUDS TO BREAK AND ALLOW THE CRUDE TOFLOW TO THE GROUND. LINE SEGMENT AROUND PUMP BLOCKED OFF AND THE PUMP DRAINED INTO SUMP. OIL WAS CONTAINED WITHIN THE BURN AROUND THE PUMPS, PICKED UP AND REINJECTED INTO THE SYSTEM.
2017-09-29 08:50 | YES | NO | 19900014 |  | 2731 | CHEVRON PIPELINE CO | YES | 1989-12-12 | 1005 | TX | MITCHELL | WESTBROOK | NO |  | NO | BETWEEN COAHOMA & C-CITY,TX 2.6 MI S IS20 SECTION 10 BLOCK 29 SURVEY T&P RR.CO FIELD NAME EAST HOWARD FIELD LEASE NAME MID/COA | 22206 | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1293.621 | 2609.7561 | L. P. G. | 2 | 30 | 0 | NO | NO | 10.75 | 0.37 | 24000 | WELDED |  | 880 | 350 | YES | 8 | 1213 | 1 | 85 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | R.M. COOK-COMPLIANCE COORDINATOR | 9156877559 | LEAK DUE TO EXTERNAL CORROSION. WILL VERIFY AFTER LINE IS EXPOSED FOR REPLACEMENT. LEAK HAD MINIMAL AFFECT ON PROPERTY WHICH COVERED APPROX. 75 FOOT SQUARE OF FROZEN GROUND AROUND LEAK. LEAK REPORTED BY MOBIL PIPELINE CP TECHNICIAN. CHEVRON PIPE LINE COAHOMA STATION SUPERVISOR ARRIVED AT LEAK AREA FIRST AND ISOLATED AREA BY BLOCKING ROAD OFF UNTIL ASSISTANCE ARRIVED. MAIN LINEVALVES WERE CLOSED AND LINE SEGMENT ISOLATED. APPROXIMATELY 300 FEET OF PIPE WILL BE REPLACED BEFORE LINE SEGMENT WILL BE OPERATIONAL. SITE CLEANED UP.NO THREAT TO THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19900015 |  | 809 | ARCO PIPE LINE CO | YES | 1989-12-23 | 800 | OK | POTTAWATOMIE |  | NO |  | NO | SECTION 27, T-10-N, R-3-E, 2 MILES SOUTH & 1 1/2 MILES WEST OF SHAWNEE, OKLAHOMA. |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1350 | 1164.2589 | 2348.7805 | FUEL OIL | 1 | 120 | 110 | NO | NO | 12 | 0.38 | 24000 | OTHER |  | 500 | 20 | YES | 24 | 700 | 1 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.D. HARRIS, MANAGER, PRODUCT BUSINESS | 3163311300 | EXTERNAL CORROSION PIT CAUSED DISCHARGE OF PRODUCT ONTO A 50' DIAMETER DRY AREA IN PASTURE NEAR PIPELINE.
2017-09-29 08:50 | YES | NO | 19900016 |  | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1989-12-18 | 0 | AR | LAWRENCE |  | NO |  | NO | EGYPT STATION, SECTION 20, TOWNSHIP 15N, RANGE 1E - VICINITY MAP TPA-V-28 ATTACHED. |  | PUMPING STATION | PUMP |  | 1979 | OTHER | PUMP SEAL FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3300 | 2845.9662 | 5741.4634 | DIESEL FUEL | 3 | 100 | 90 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HANNIGAN, VICE PRESIDENT-OPERATIONS | 7137594700 | DURING THE EARLY HOURS OF DECEMBER 18, 1989, AT AN UNKNOWN EXACT TIME, THE "A" PUMPING UNIT ON 16" LINE P62 EXPERIENCED AN INBOARD SEAL FAILURE. THE LEAKING PRODUCT DRAINED TO A SUMP TANK WHICH FILLED AND OVERFLOWED INTO THE STATION YARD. SINCE THIS STATION IS NOT MANNED 24 HOURS A DAY, THE SPILL WAS NOTDISCOVERED UNTIL 0730 HOURS WHEN THE OPERATOR ARRIVED TO CHECK THE STATION.THE PUMP WAS IMMEDIATELY SHUT DOWN; THE SPILLED PRODUCT WAS CONTAINED ON OURPROPERTY WITHIN A CONCRETE RETAINING WALL AND AN EARTHEN DIKE ON A DRAINAGE DITCH. A VACUUM TRUCK WAS USED TO PICK UP THE RECOVERABLE PRODUCT. THE SITEWILL BE FERTILIZED AND AERATED TO RETURN IT TO ITS ORIGINAL CONDITION.
2017-09-29 08:50 | YES | NO | 19900017 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-12-11 | 1330 | NE | OMAHA |  | NO |  | NO | OMAHA TERMINAL # C211. | 22163 | TANK FARM | VALVE |  | 1957 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 6899.3121 | 13918.6992 | FUEL OIL | 3 | 110 | 102 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN-VICE PRESIDENT-OPERATIONS | 9185883850 | AT 13:30 ON DECEMBER 11, OPERATIONS PERSONNEL DISCOVERED PRODUCT LEAKING FROMA CRACKED MIXER NOZZLE VALVE ON TANK #1402. THE TANK HAD PREVIOUSLYCONTAINED HYDROSTATIC TEST WATER. APPARENTLY, SOME REMNANT WATER HAD BEENTRAPPED IN THE BASE OF THE VALVE,AND FROZE WHEN AMBIENT TEMPERATUREDROPPED. THE EXPANSION OF THE ICE CRACKED THE VALVE AND RELEASED 110 BBLS.OF FUEL OIL FROM THE TANK. ALL RELEASED PRODUCT WAS CONTAINED WITHIN THETANK DIKE. APPROXIMATELY 200 YARDS OF SOIL WAS REMOVED DURING THE CLEANUPEFFORTS. SUPPLEMENTAL REPORT 9/26/94 INDICATED A CHANGE IN PART D/CAUSE OFACCIDENT FROM "OTHER - WATER IN VALVE FROZEN" TO "OUTSIDE FORCE DAMAGE."CONTACT RICHARD HARRIS (918) 588-3454 WITH QUESTIONS.
2017-09-29 08:50 | YES | NO | 19900018 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-12-14 | 1445 | OK | TULSA |  | NO |  | NO | TULSA TERMINAL #A295. | 22366 | TANK FARM | OTHER | DRESSER COUPLING | 1972 | OTHER | TEMP. RESTRAINT FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 431.207 | 869.9187 | GASOLINE | 3 | 610 | 570 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN-VICE PRESIDENT - OPERATIONS | 9185883850 | ON DECEMBER 14 AT 14:45 A LEAK WAS DISCOVERED IN THE DELIVERY PIPING ADJACENT TO THE TANK PUMP FOR TANK #605. THE RELEASE ORIGINATED FROM A DRESSER COUPLING (EXPANSION JOINT)ON THE DISCHARGE SIDE OF THE TANK PUMP. MAINTENANCE PERSONNEL HAD REMOVED THE PUMP IN PREPARATION FOR INSTALLATION OF A NEW EXPANSIONJOINT. THE DISCHARGE PIPING WAS ISOLATED WITH A BLIND FLANGE AND TEMPORARY RESTRAINTS WERE INSTALLED TO SECURE THE EXPANSION JOINT TO PREVENT IT FROM SLIDING APART. DURING A SUBSEQUENT PUMP OPERATION TO THE LOADING RACK (WHICH SHARED THE SAME DELIVERY LINE) THE RESTRAINTS FAILED, AND RELEASED 610 BBLS. OF GASOLINE. ALL RELEASED PRODUCT WAS CONTAINED WITHIN THE TANK DIKE ENABLING NEARLY TOTAL RECOVERY. CLEANUP EFFORTS HAVE BEEN COORDIANTED WITH APPROPRIATE STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19900019 |  | 1845 | BUCKEYE PIPELINE CO LP | YES | 1989-12-18 | 1011 | IN | WABASH | CHESTER | NO |  | NO | BUCKEYE PIPE LINE CO. STA. #5132+00, APPR. 850 F. EAST OF S.R. 13 ALONG ABANDONED ERIE LACKAWANNA RR RIGHT OF WAY, 300 FT. S.OF SIGNS ROAD (WABASH CO. RD.950 N) | 22610 | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1293.621 | 2609.7561 | GASOLINE | 3 | 1250 | 200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R.S. EASTWOOD, MANAGER, SAFETY AND ENVIRONMENTAL PROTECTION | 2158208300 | PIPELINE WAS DAMAGED BY HEAVY EQUIPMENT CAUSING A GOUGE IN THE PIPELINE SOMETIME PRIOR TO THE FAILURE.
2017-09-29 08:50 | YES | NO | 19900020 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-12-30 | 1500 | TX | KIMBLE | UNKNOWN | NO |  | NO | BENEDUM-SWEENY LINE - MP 155-36+62. 10 MILES SOUTHEAST OF LONDON, TX. | 00221 | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 6899.3121 | 13918.6992 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 10.78 | 0.37 | 30000 | WELDED |  | 910 | 720 | YES | 24 | 1450 | 4 | 75 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING AND TECHNICAL SERVICES | 9186614721 | SMALL PINHOLE LEAK CAUSED BY EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19900021 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-01-03 | 1730 | TX | COLORADO | UNKNOWN | NO |  | NO | BENEDUM-SWEENY LINE - MP 340-48+26. 6 MILES NORTHWEST OF NEW ULM, TEXAS. | 00313 | LINE PIPE | PIPE |  | 1928 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8322.2692 | 16789.3784 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 10.77 | 0.28 | 30000 | WELDED |  | 1100 | 513 | YES | 24 | 1415 | 10 | 78 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING AND TECHNICAL SERVICES | 9186614721 | LEAK OCCURRED IN LONGITUDINAL ELECTRIC WELD IN PIPE. IT APPEARS THIS JOINT OF PIPE HAD A DEFECT AND WAS REPAIRED AT THE FACTORY OR IN THE FIELD.
2017-09-29 08:50 | NO | NO | 19900022 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-12-25 | 230 | SD | SIOUX FALLS | UNKNOWN | NO |  | NO | SIOUX FALLS TERMINAL #E213. |  | TANK FARM | OTHER | EXPANSION JOINT | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 21560.3502 | 43495.935 | FUEL OIL | 3 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN , VICE PRESIDENT - OPERATIONS | 9185883850 | BETWEEN THE EVENING OF DECEMBER 24TH (17:40) AND EARLY MORNING ON DECEMBER 25TH (02:30) TWO PIPING LEAKS WERE DISCOVERED AT OUR SIOUX FALLS TERMINAL. THE LEAKS ORIGINATED FROM THE FILLET WELDS ON THE PIPELINE ANCHOR SUPPORTS (TANK LINE 1337 & 1339) THAT WERE USED TO RESTRAIN THE PIPES LATERAL MOVEMENT FORM THERMAL EXPANSION. EXPANSION JOINTS WERE INSTALLED ON THESE LINES TO PROVIDE FLEXIBILITY AND TO ACCOMMODATE ANY THERMAL EXPANSION OR CONTRACTION MOVEMENT. THE LOCATION EXPERIENCED A 60 DEGREE TEMPERATURE SHIFT WITHIN A 24 HOURPERIOD, WHICH THE EXPANSION JOINTS WERE DESIGNED TO HANDLE. HOWEVER, DUE TOEXCESSIVE INTERNAL PRESSURE (PRODUCT EXPANSION), THE JOINTS EXTENDED APPROXIMATELY 5 TIMES THE NORMAL DISTANCE CAUSING EXCESSIVE STRAIN ON THE PIPE ANCHORS WHICH EVENTUALLY GAVE WAY. DURING THE SUBSEQUENT INVESTIGATION, ALL THE THERMAL RELIEF DEVICES WERE CHECKED AND FOUND TO BE OPERATIVE. IT IS THEORIZED THAT ICE MAY HAVE ACCUMULATED AND TEMPORARILY BLOCKED OR RESTRICTED THE RELIEF LINES RESULTING IN THE PRESSURE BUILDUP. AS A PRECAUTIONARY MEASURE, ADDITIONAL RELIEF CAPACITY WAS INSTALLED ON ALL LINES IN THE STATION MANIFOLD, RACK MANIFOLD, AND THE TANK PUMP AND RECIEVE LINES. ALL THE REMAINING PIPE ANCHORS WERE ALSO INSPECTED (VISUALLY AND BY MAGNETIC PARTICLE) TO INSURE ADEQUATE STRENGTH AND SUPPORT. ALL CLEANUP ACTIVITY WAS COORDINATED WITH APPROPRIATE STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | NO | NO | 19900023 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1989-12-24 | 1740 | SD | SIOUX FALLS | UNKNOWN | NO |  | NO | SIOUX FALLS TERMINAL # E213. | 23070 | TANK FARM | OTHER | EXPANSION JOINT | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 21560.3502 | 43495.935 | FUEL OIL | 3 | 6 | 6 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | BETWEEN THE EVENING OF DECEMBER 24TH (17:40) AND EARLY MORNING ON DECEMBER 25THH (02:30) TWO PIPING LEAKS WERE DISCOVERED AT OUR SIOUX FALLS TERMINAL. THELEAKS ORIGINATED FROM THE FILLET WELDS ON THE PIPELINE ANCHOR SUPPORTS (TANKLINE 1337 & 1339) THAT WERE USED TO RESTRAIN THE PIPES LATERAL MOVEMENT FROM THERMAL EXPANSION. EXPANSION JOINTS WERE INSTALLED ON THESE LINES TO PROVIDE FLEXIBILITY AND TO ACCOMMODATE ANY THERMAL EXPANSION OR CONTRACTION MOVEMENT. THE LOCATION EXPERIENCED A 60 DEGREE TEMPERATURE SHIFT WITHIN A 24 HOUR PERIOD, WHICH THE EXPANSION JOINTS WERE DESIGNED TO HANDLE. HOWEVER, DUE TO EXCESSIVE INTERNAL PRESSURE (PRODUCT EXPANSION), THE JOINTS EXTENDED APPROXIMATELY 5 TIMES THE NORMAL DISTANCE CAUSING EXCESSIVE STRAIN ON THE PIPE ANCHORS WHICH EVENTUALLY GAVE WAY. DURING THE SUBSEQUENT INVESTIGATION, ALL THE THERMAL RELIEF DEVICES WERE CHECKED AND FOUND TO BE OPERATIVE. IT IS THEORIZEDTHAT ICE MAY HAVE ACCUMULATED AND TEMPORARILY BLOCKED OR RESTRICTED THE RELIEF LINES RESULTING IN THE PRESSURE BUILDUP. AS A PRECAUTIONARY MEASURE, ADDITIONAL RELIEF CAPACITY WAS INSTALLED ON ALL LINES IN THE STATION MANIFOLD, RACK MANIFOLD, AND THE TANK PUMP AND RECIEVE LINES. ALL THE REMAINING PIPE ANCHORS WERE ALSO INSPECTED (VISUALLY AND BY MAGNETIC PARTICLE) TO INSURE ADEQUATE STRENGTH AND SUPPORT. ALL CLEANUP ACTIVITY WAS COORDINATED WITH APPROPRIATE STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19900024 |  | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1989-11-22 | 700 | TX | CRANE | UNKNOWN | NO |  | NO | AMERICAN PETROFINA PIPE LINE COMPANY'S CRANE PUMP STATION/TANK FARM: APPROXIMATELY 1 1/4 MILES. EAST OF HWY 1601 AND 5 3/4 MI. NW. OF THE TOWN OF CRANE, TX. | 20907 | TANK FARM | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 60368.9806 | 121788.6179 | CRUDE OIL | 1 | 4935 | 1435 | NO | NO | 12 | 0 | 0 | FLANGED |  | 0 | 0 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED , REGULATORY COMPLIANCE SUPV. | 9152673673 | REPORTED TO THE NRC AT 10:40 AM. NOVEMBER 22, 1989, BY BOB REED. REPORTED TO P/O HEARD; NRC REPORT NO. 20907. SUCTION LINE TO STORAGE TANK NO.1705 FAILED DUE TO CORROSION, CAUSING CRUDE OIL TO GRAVITATE OUT OF TANK AND INTO CONTAINMENT FIRE-WALL SURROUNDING TANK. OIL WAS PICKED-UP BY VACUUM TRUCKS AND PUMPED INTO SAME TANK, AND SUCTION LINE WAS REPLACED. NO SPILLAGE OCCURRED OUTSIDE OF TANK'S CONTAINMENT FIRE-WALL.
2017-09-29 08:50 | YES | NO | 19900025 |  | 22387 | WEST EMERALD PIPE LINE CORP | YES | 1990-01-04 | 1100 | NM | QUAY |  | NO |  | NO | SEC. 4, TOWNSHIP 10 NORTH, RANGE 27 EAST, QUAY COUNTY, NM 2 MILES NORTH OF INTERSTATE 40 AT MONTOYA, NEW MEXICO. |  | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 52500 | 43691.9131 | 88144.2366 | GASOLINE | 3 | 1000 | 722 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1440 | 745 | YES | 0 | 0 | 1 | 81 | EXTERNAL | Null | YES | OTHER | MIRCOBIO. INFL. CORR | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS, MANGER OF PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APPROXIMATELY 1100 HOURS ON JANUARY 3, 1990, DURING THE CONSTRUCTION OF ANEW 10" PIPELINE PARALLEL TO OUR EXISTING 6" PIPELINE, PRODUCT WAS FOUND IN THE DRY BED OF PAJARITO CREEK. CREWS BEGAN EXCAVATING IMMEDIATELY TO FIND THESOURCE. AT 1100 HOURS ON JANUARY 4, 1990, A PINHOLE LEAK WAS DISCOVERED IN OUR 6" ALBUQUERQUE REFINED PRODUCTS PIPELINE WHICH ALLOWED 1000 BARRELS OF UNLEADED GASOLINE TO EXCAPE, OF WHICH 722 BARRELS HAVE BEEN SUBSEQUENTLY RECOVERED. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE CAUSE OF THE EXTERNAL CORROSION WAS INVESTIGATED BY A THIRD PARTY CHEMIST AND ATTRIBUTED TO MIC (MICROBIOLOGICAL INFLUENCED CORROSION). THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING 793 FEET OF PIPE, HYDROSTATICALLY TESTED, AND THE
2017-09-29 08:50 | YES | NO | 19900026 |  | 2552 | COLONIAL PIPELINE CO | YES | 1990-01-02 | 1200 | MS | LAUDERDALE | MERIDIAN | NO |  | NO |  |  | PUMPING STATION | VALVE |  | 1978 | OTHER | CLAPPER SHAFT SEAL FAIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 3 | 90 | 88 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER - TECHNICAL AND REGULATORY | 4048412296 | AT APPROXIMATELY 12:00, CST, ON JANUARY 2, 1990, A SHEEN OF FUEL OIL WAS NOTICED ON THE RETENTION POND AT COLONIAL'S MERIDIAN PUMP STATION. THE SOURCE OF PRODUCE WAS A FAILED SHAFT SEAL ON THE NO. 2 UNIT CHECK VALVE ON THE NO. 2 PIPELINE STATION. A TEMPORARY CONNECTION WAS MADE TO CAPTURE LEAKING PRODUCTAND DIVERT IT TO THE STATION SUMP TANK. ABSORBENT MATERIALS WERE PLACED ON THE RETENTION POND, AND RECOVERY HOLES WERE DUG IN THE STATION YARD TO COLLECT PRODUCT. THE STATION HAS AN UNDERGROUND DRAINAGE SYSTEM WHICH IS DESIGNED TO COLLECT SUCH SPILLED PRODUCT AND PERCOLATED STORM WATER. THE SUBSURFACE DRAINAGE SYSTEM DISCHARGES INTO THE OIL-WATER SEPARATOR. PRODUCT IS SKIMMED FROM THE SEPARATOR AND PIPED TO THE STATION SUMP. WATER WAS APPLIED TO THE STATION AREA TO FLUSH THE RELEASED PRODUCT INTO THE SUBSURFACE DRAINAGE SYSTEM.THE MISSISSIPPI STATE OIL AND GAS BOARD WAS NOTIFIED ON JANUARY 8, 1990. THE SHAFT SEAL WAS REPLACED ON JANUARY 11, 1990. THE INITIAL ESTIMATE OF PRODUCT LOST WAS 10 BARRELS; HOWEVER, SUBSEQUENT CLEANUP EFFORTS HAVE RESULTED IN 87 1/2 BARRELS BEING RECOVERED.
2017-09-29 08:50 | YES | NO | 19900027 |  | 809 | ARCO PIPE LINE CO | YES | 1990-01-06 | 1000 | TX | NAVARRO |  | NO |  | NO | NAVARRO COUNTY, FIVE MILES NORTH OF THE CITY OF WORTHAM, JOHN SMITH SURVEY, ABSTRACT #779. |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12483.4037 | 25184.0676 | CRUDE OIL | 1 | 548 | 40 | NO | NO | 18 | 0.28 | 52000 | WELDED |  | 1169 | 770 | YES | 8 | 1487 | 1 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, MANAGER CRUDE BUSINESS UNIT | 3163311300 | LEAK DUE TO EXTERNAL GALVANIC CORROSION.
2017-09-29 08:50 | YES | NO | 19900028 |  | 12628 | MOBIL PIPELINE CO | YES | 1990-01-03 | 634 | TX | MIDLAND |  | NO |  | NO | 1-1/2 MI. E. OF MOBILE PIPE LINE CO. MIDLAND STA. AT M.P. 1.6 ON TX. P/L CO. PROPERTY; BLK. 38, SEC. 40, T&P RAILROAD SURVEY, T-1-S, MIDLAND COUNTY,TX. | 00167 | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 13700 | 11401.5088 | 23001.4484 | CRUDE OIL | 1 | 195 | 108 | NO | NO | 14 | 0.25 | 1640 | WELDED |  | 1172 | 1017 | YES | 2 | 1330 | 9 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | FENCE POST AUGER | Null | NO DATA |  | NO | NO | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | A DROP IN PRESSURE WAS NOTED BY OUR DALLAS OPERATIONS CONTROL DEPT. AT 0634HOURS ON 1/3/90. THE LINE WAS SHUT DOWN AT 0637 HOURS. THE BLOCK VALVE AT M.P. 16 WAS CLOSED AT 0757 HOURS. THE PIPELINE WAS PATROLLED BY AERIAL SURVEY (CONTRACT PILOT - AIR MASTERS) WITH A MOBIL PIPE LINE COMPANY EMPLOYEE ON BOARD. A CRUDE OIL LEAK WAS SPOTTED AT M.P. 1.6 AT 0819 HOURS. FIELD MAINTENANCE CREWS AND EQUIPMENT WERE DISPATCHED TO LEAK SITE. REPAIRS AND CLEAN-UP PROCEDURES WERE INITIATED. APROXIMATELY 21 FT. OF 14" LINE PIPE INSTALLED. LEAK CAUSED BY LINE RUPTURE DUE TO UNKNOWN OUTSIDE PARTIES. INSPECTION OF THEDAMAGED PIPE REVEALED THAT A FENCE POST AUGER HAD APPARENTLY HIT THE PIPELINE IN THE PAST, WEAKENING THE PART OF THE PIPE THAT EVENTUALLY RUPTURED.
2017-09-29 08:50 | YES | NO | 19900029 |  | 4906 | EXXON PIPELINE CO | NO | 1990-01-16 | 1400 | TX | HARRIS | HOUSTON | NO |  | NO | LEAK OCCURRED AT GATE PLANT "R" ON THE SUGARLAND TO PIERCE JUNCTION CRUDE OIL PIPELINE. |  | LINE PIPE | SCRAPER TRAP |  | 1982 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 14147.8576 | 28541.9433 | CRUDE OIL | 1 | 210 | 204 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. MOORE - OPERATIONS MANAGER | 7136565956 | EMPLOYEES HAD NOTIFIED EXXON MARKETING WHEN THEY SAW "WATER/GAS" SPRAYING INTO THE AIR NEAR A PIPE COMING OUT OF THE GROUND. REY ACOSTA SENT LEE ROY WILLIAMS TO THE SITE (ARRIVED AT 3:00 PM.) AND HE FOUND CRUDE OIL SPRAYING FROM SCRAPER TRAP. HE BYPASSED TRAP AND BLED THE TRAP TO THE SUMP. A BLEEDER VALVE WAS FOUND TO BE LOSSENED AND THE OIL WAS ESCAPING THROUGH THE BLEEDER PORTS. AFTER THE BLEEDER WAS SECURED,THE TRAP WAS LINED UP AND THE SYSTEM RESTARTED AT 4:00. CLEANUP BEGAN IMMEDIATELY WITH THE HELP OF EPC MAINTENANCE CREWSAND CONSTRACTORS. THE LEAK WAS LIMITED TO DITCHES AND GRASSY OILFIELD. IT W
2017-09-29 08:50 | YES | NO | 19900030 |  | 18718 | SUN PIPELINE CO | YES | 1990-01-13 | 725 | OK | SEMINOLE | SEMINOLE | NO |  | NO | SPORTSMAN LAKE ROAD, SEMINOLE, OKLAHOMA. | 00908 | PUMPING STATION | VALVE |  | 0 | OTHER | VALVE FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 350 | 300 | NO | NO | 2 | 0.25 | 0 | THREADED |  | 765 | 520 | YES | 8 | 0 | 1 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | ON JANUARY 13, 1990 AT APPROXIMATELY 6:40 AM, A LEAK OCCURED AT THE SUN PIPELINE SEMINOLE PRODUCT PUMP STATION. THE LEAK RESULTED IN APPROXIMATELY 350 TO 440 BARRELS OF UNLEADED GASOLINE SPILLED ON STATION GROUNDS THAT MIGRATED OUTOF THE STATION TO AN OPEN DRAINAGE DITCH AND COLLECTED ON A POND 1200 FEET AWAY. THE AREA WAS A LIGHTLY POPULATED RESIDENTIAL SECTION AND RESULTED IN THREE HOMES BEING EVACUATED; THE ROAD TO AND FROM SAID AREA WAS BLOCKED OFF AS A PRECAUTIONARY MEASURE. THE LOCAL FIRE DEPARTMENT AND POLICE DEPARTMENT ASSISSTED. AT THE TIME OF THE LEAK, ALLEN STATION WAS PUMPING NO-LEAD GASOLINE TO TANKAGE AT DRUMRIGHT AND OKLAHOMA CITY TERMINALS. BOTH BEARDON AND SEMINOLE WERE UTILIZED AS BOOSTER STATIONS. THE CAUSE OF THE LEAK WAS THE BODY FAILURE OF A 2 INCH DRAIN VALVE LOCATED ON THE SEMINOLE STATION DISCHARGE TRAP. THE DISCHARGE TRAP WAS AT MAIN LINE DISCHARGE PRESSURE SINCE THE 4 INCH PIG LAUNCHING VALVE WAS OPEN. THERE WERE 300 BBLS. RECOVERED DURING THE CLEANUP.
2017-09-29 08:50 | YES | NO | 19900031 |  | 26088 | SIGMOR PIPELINE CO | NO | 1990-01-03 | 930 | TX | LIVE OAK | THREE RIVERS | NO |  | NO | WM. O'DOCHERTY SURVEY, A-55, LIVE OAK COUNTY, TEXAS. |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 3745.0211 | 7555.2203 | DIESEL FUEL | 3 | 260 | 168 | NO | NO | 8 | 0.22 | 52000 | WELDED |  | 1901 | 1800 | YES | 24 | 2377 | 4 | 79 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS, MANAGER OF PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APOROXIMATELY 0930 HOURS ON JANUARY 3,1990, OUR 8" SAN ANTONIO REFINED PRODUCTS PIPELINE RUPTURED ALLOWING 260 BARRELS OF DIESEL TO ESCAPE, OF WHICH 168 BARRELS WERE SUBSEQUENTLY RECOVERED. THE RUPTURE OCCURRED ON OUR REFINERYPROPERTY AND THE SPILL QUICKLY CONTAINED WITHIN THE PLANT. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE INITIAL CAUSE WAS ATTRIBUTED TO MATERIAL DEFECT IN THE PIPE FROM THE MILL,OVER WHICH THE COATING WAS SUBSEQUENTLY APPLIED SHIELDING THE PIPE FROM EFFECTIVE CATHODIC PROTECTION PREVENTING CONTROL OF THE CORROSION. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING A FULL JOINT OF PIPE WITH PRE-TESTED PIPE AND THE LINE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19900032 |  | 443 | AMOCO PIPELINE CO | NO | 1990-01-22 | 745 | TX | RAINS |  | NO |  | NO | APP. 4 MILES OUTH OF THE TO N OF EMORY, TEXAS. APP. 400 YDS. SE. OF HW#69. | 01552 | LINE PIPE | GIRTH |  | 1964 | FAILED WELD | OTHER | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CONDENSATE - WATER | 3 | 140 | 135 | NO | NO | 6 | 0.13 | 0 | WELDED |  | 951 | 130 | YES | 24 | 2669 | 6 | 77 | NO DATA | Null | YES | NO DATA |  | OTHER | UNDERTERMINED | Null | OTHER | DISCOVERED BY PRODUCER | NO | NO | PAT M. LLANCY, P.L.M.F. | 2147597131
2017-09-29 08:50 | YES | NO | 19900033 |  | 14295 | OLYMPIC PIPE LINE CO | YES | 1990-02-07 | 1355 | WA | SNOHOMISH | WOODINVILLE | NO |  | NO | 1.5 MILES NORTH OF WOODINVILLE/BOTHELL - 21925 45TH AVE. SE, BOTHELL, WASHINGTON OLYMPIC 16-INCH PRODUCTS PIPELINE PUMP STATION. NE 1/4, NE 1/4, SECTION 28, TOW | 7456 | PUMPING STATION | BOLTED FITTING |  | 1971 | OTHER | VALVE FLANGE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 83222.6916 | 167893.7839 | DIESEL FUEL | 3 | 317 | 230 | NO | NO | 14 | 0.31 | 2028 | FLANGED |  | 1440 | 1460 | YES | 30 | 1800 | 10 | 71 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | F. HOPF, MANAGER OLYPIC PIPE LINE COMPANY | 2062357738 | OPERATIONS CONTROLLER STARTED PIPELINE AND PUMP UNITS AGAINST CLOSED BLOCK VALVE. HIGH PRESSURE ALARMS WERE RECEIVED FROM TWO (2) DOWNSTREAM PRESSURE TRANSMITTERS AND THE PIPELINE WAS IMMEDIATELY SHUT DOWN; HOWEVER, THE STATION OUTLET BYPASS VALVE FLANGE GASKET FAILED AT SOME POINT FOLLOWING OR DURING A PRESSURE SURGE OF APPROXIMATELY 1460 PSI. THE RELEASE WAS CONTAINED ON THE STATION PROPERTY. NOTE: THE MAINLINE IS 16", THE GASKET WHICH FAILED WAS ON A 14" STATION BYPASS VALVE ON THE DISCHARGE OF THE STATION.
2017-09-29 08:50 | YES | NO | 19900034 |  | 2690 | CARSWELL PIPELINE CO | NO | 1990-01-25 | 1627 | TX | PALO PINTO |  | NO |  | NO | APPROX. 1 MILE EAST OF FM 4; APPROX. 50 YD. SOUTH OF INTERSTATE 20. ON E.W. CARTER CATTLE COMPANY PROPERTY. | 01827 | LINE PIPE | PIPE |  | 1921 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 57000 | 47436.9342 | 95699.4568 | JET FUEL | 3 | 298 | 29 | NO | NO | 6 | 0.25 | 40000 | THREADED |  | 400 | 360 | YES | 8 | 503 | 4 | 85 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | TERRY PRITCHARD - CHIEF PROCESS ENGINEER | 9156748473 | AT APPROX. 1627 ON 1/25/90, THE CARSWELL PPL WAS PUNCTURED BY A SCRAPER OPERATOR HIRED BY E.W. CARTE CATTLE CO. THIS WAS NOTICED BY A SUDDEN LOSS OF PRESSURE AT OUR BROCK PUMP STATION SUCTION PRESSURE. THE ABILENE PIPELINE CONTROL OPERATOR IMMEDIATELY BEGAN REDUCING PIPELINE FLOW AND CONTACTED THE SHIFT FOREMAN ON DUTY. 1640 - THE PIPELINE SYSTEM WAS SHUT DOWN. 1650 - THE SCRAPER OPERATOR CALLED REPORTING THE PIPELINE LEAK & ITS LOCATION. 1655 - ALEDO TERMINAL PERSONNEL DISPATCHED TO SITE. SNEED CONTRACTOR, INC., EASTLAND, CONTACTED TO RESPOND TO LEAK SITE. 1730 - ABILENE SPILL RESPONSE TEAM LEFT PRIDE REFINING'S ABILENE REFINERY. 1740 - THE DAMAGED PIPELINE SECTION WAS ISOLATED BY PIPELINE BLOCK VALVES. DAMMING OF SPILL BEGAN TO CONTAIN SPILL. 1845 - ABILENE SPILL RESPONSE TEAM REACHED LEAK SITE. CLEAN UP BEGAN. 1855 - PIPELINE CLAMP INSTALLED AROUND PUNCTURE. 1900 - THE RAILROAD COMMISSION AND DOT WERE NOTIFIED TO THE SPILL. SPILL CLEAN UP CONTINUED THROUGH THE NIGHT AND FORE FIVE DAYS. THE TWC REP FROM DUNCANVILLE COORDINATED THE REQUIREMENTSOF THE CLEAN UP. THE PIPELINE WAS REPAIRED BY REMOVING APPROXIMATELY 20 FEET OF PIPE AND REPLACING WITH NEW TESTED PIPE OF THE SAME DIAMETER. THE PIPELINE WAS STARTED UP 1535 ON JANUARY 26, 1990.
2017-09-29 08:50 | YES | NO | 19900035 |  | 13162 | NAVAJO REFINING CO | YES | 1989-10-17 | 2145 | TX | EL PASO | EL PASO | NO |  | NO | ON WEST SIDE OF ZARAGOSA RD. IN EL PASO, TX IN 1700 BLOCK OF NORTH ZARAGOSA. | 18444 | LINE PIPE | PIPE |  | 1959 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 108581 | 93641.7755 | 188913.2846 | GASOLINE | 3 | 187 | 15 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1200 | 1370 | YES | 7 | 750 | 11 | 89 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES G. TOWNSEND-CATHODIC PROTECTION SUPERVISOR | 5057483311 | AT APROX. 9:45 PM. ON OCTOBER 17, 1989 PRODUCT FOREMAN AND AN ELECTRICAL ENGINEERING CONSULTANT WERE IN THE PROCESS OF COMPLETING FINAL ELECTRICAL CHANGES TO THE PIPELINE SUPERVISORY CONTROL SYSTEM. THESE CHANGES WERE BEING MADE TO ENHANCE THE ABILITY OF THE CONTROL SYSTEM. AT SOME POINT DURING THESE FINAL ELECTRICAL TIE-INS THE BACK PRESSURE CONTROL VALVE, WHICH MONITORS NAD CONTROLS MAINLINE PRESSURE SHUT, BLOCKING THE FLOW IN THE PIPELINE. WITHIN MINUTES OF THE VALVE CLOSING, THE PIPELINE OPERATOR IN ARTESIA, NEW MEXICO NOTICED THE DECREASE INFLOW. BEFORE THE ARTESIA PIPELINE OPERATOR COULD CALL THE EL PASO TERMINAL THE EL PASO CITY POLICE NOTIFIED THE PRODUCT FOREMAN AT THE EL PASO TERMINAL OF A LEAK ON ZARAGOSA ROAD. THE PRODUCT FOREMAN IN EL PASO NOTIFIED THE ARTESIA PIPELINE OPERATOR AND LINE WAS IMMEDIATELY SHUTE DOWN. PRODUCT FOREMAN WENT TO VALVE APPROS. 1/4 MILE UPSTREAM OF LEAK AND SHUT VALVEWHICH STOPPED THE FLOW OF THE ESCAPING GASOLINE. NAVAJO EMPLOYEES AND EQUIPMENT AS WELL AS CONTRACTOR EMPLOYEES AND EQUIPMENT WERE IMMEDIATELY DISPATCHED TO REPAIR PIPELINE AND CLEAN SPILL AREA. PIPELINE WAS REPAIRED AND RESUMEDOPERATIONS AT APPROX. 3:00 A.M. 10/18/89. CLEAN UP OF SPILL AREA WAS COMPLETED 11/2/89. THE NORMAL OPERATING PRESSURE AT THIS POINT ON THE PIPELINE IS LESS THAN 200 PSIG WHEN FLOWING. FOR THAT REASON WE NORMALLY LEAK TEST THIS PORTION OF THE PIPELINE AT APPROXIMATELY 750 TO 800 PSIG. HOWEVER WITH THE CONTROL VALVE CLOSING WE HAVE CALCULATED THAT THE PRESSURE MAY HAVE REACHED 1370 PSIG BEFORE FAILING. TELEPHONE NOTICE 10/18/89 CONTROL #18444-BRADSHAW.
2017-09-29 08:50 | YES | NO | 19900036 |  | 2552 | COLONIAL PIPELINE CO | YES | 1990-01-30 | 0 | LA | EAST FELICIANA |  | NO |  | NO | COLONIAL PIPELINE CO. BATON ROUGE JUNCTION. |  | TANK FARM | TANK |  | 1971 | OTHER | FLOATING ROOF DRAIN FAIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 600 | 560 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER-TECHNICAL AND REGUALTORY | 4048412296 | AT APPROX. 7:50 EST ON JANUARY 30, 1990, THE SENIOR OPERATOR CHECKED TANK NO. 124 WHICH WAS RECEIVING A MAINLINE GASOLINE DELIVERY. HE DISCOVERED PRODUCT FLOWING FROM THE ROOF DRAIN. ALL PRODUCT WAS CONTAINED WITHIN THE DIKED AREA. THE SENIOR OPERATOR IMMEDIATELY RADIOED THE OPERATOR IN THE CONTROL ROOM AND THE DELIVERY WAS SWITCHED TO TANK NO. 125. IN ORDER TO REMOVE PRODUCT FROM TANK NO. 124 A LIFTING OF 43,000 BARRELS PER HOUR WAS INITIATED. AT 0900 THE OPERATOR TERMINATED THE DELIVERY TO TANK NO. 125, OPENED THE INCOMING MANIFOLD VALVES TO TANK NO. 124 AND TANK NO. 125 ALLOWING 10,000 BARRELS TO GRAVITATE TO TANK NO. 125. AT 9:30 EST THE LEAK WAS STOPPED BY INSERTING A FOUR INCH EXPANDABLE PLUG INTO DRAIN DISCHARGE. WATER WAS APPLIED TO THE FLOOR OF THE DIKED AREA TO MINIMIZE PRODUCT PERCOLATING INTO THE SOIL. A FIRE RETARDANT FOAM WAS SPRAYED ON THE SURFACE OF THE POOLED PRODUCT TO REDUCE THE POTENTIAL FOR IGNITION AND EVAPORATION. PRODUCT WAS RECOVERED USING VACUUM TRUCKSAND TRANSFERRED TO A FACILITY SUMP WHERE IT WAS RETURNED TO THE PIPELINE SYSTEM. APPROX. 600 BARRELS OF GASOLINE WERE ACTUALLY RELEASED AND 560 BARRELS WERE RECOVERED. THE 40 BARRELS NOT RECOVERED ARE BELIEVED TO HAVE EVAPORATED. THE LOUISIANA DEPT. OF ENVIR. QUALITY WAS NOTIFIED AT 10:30 EST ON JANUARY30. AFTER THE TANK WAS OPENED AN INSPECTION REVF LOG 37FAILED IN A SECTIONOF DRAIN LINE ADJACENT TO THE ROOF SUMP. A MORE DETAILED INVESTIGATION WILLBE CONDUCTED AFTER THIS SEGMENT HAS BEEN REMOVED.
2017-09-29 08:50 | YES | NO | 19900037 |  | 2552 | COLONIAL PIPELINE CO | YES | 1990-02-10 | 630 | NJ | MIDDLESEX |  | NO |  | NO | 400 BLAIR ROAD. WOODBRIDGE TOWNSHIP. |  | TANK FARM | TANK |  | 1963 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 2 | 330 | 330 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  |  | AT APPROX. 6:30 EST ON FEB. 10, 1990, THE OPERATOR OPENED THE TANK DIKE DRAIN TO RELEASE WATER WHICH WAS ACCUMULATING DUE TO HEAVY RAIN. AFTER OPENING THE VALVE, THE OPERATOR DETECTED PRODUCT AT THE DRAIN DISCHARGE AND IMMEDATELYBEGAN CLOSING THE DRAIN VALVE. AN INSPECTION OF THE DIKE AREA REVEALED FUELOIL IN THE VICINITY OF NO. 1474. AT THE TIME TANK NO. 1474 CONTAINED 4,018 BARRELS SO A DELIVERY WAS INITIATED TO ONE OF COLONIAL'S SHIPPERS FROM THIS TANK AT 7:00 EST. BY 7:5O EST TANK NO. 1474 WAS EMPTY. WATER WAS APPLIED TO THE DIKE AREA TO MINIMIZE THE POSSIBILITY OF PRODUCT PERCOLATING INTO THE SOIL. PRODUCT IN THE DIKED AREA WAS RECOVERED USING VACUUM TRUCKS AND TRANSFERRED TO A FACILITY SUMP WHERE IT WAS RETURNED TO TEH PIPELINE SYSTEM. ONLY ABOUT SIX BARRELS ESCAPED THROUGH THE DIKE DRAIN AND THIS PRODUCT WAS TRAPPED INTHE FACILITY RETENTION POND, IMPOUNDED USING BOOMS AND COLLECTED USING ABSORBENT MATERIALS. APPROX. 330 BARRELS OF PRODUCT HAVE BEEN RECOVERED. A RECOVERY WELL CONTINUES TO COLLECT PRODUCT IN VERY SMALL QUANTIITES. THE NEW JERSYEY DEPARTMENT OF ENVIRONMENTAL PROTECTION WAS NOTIFIED AT 9:24 EST AND THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 9:46 EST (REPORT NO. 7812). A VISUALINSPECTION OF THE OUTSIDE OF TANK NO. 1474 DID NOT REVEAL ANY PROBLEMS. THIS TANK HAS BEEN CLEANED AND WILL BE THOROURGHLY INSPECTED FOR THE SOURCE OF THE LEAK ON MARCH 19, 1990.
2017-09-29 08:50 | NO | NO | 19900038 |  | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-01-24 | 900 | CA | CONTRA COSTA | MARTINEZ | NO |  | NO | 1/4 MILE EAST OF BENICIA BRIDGE, 1/4 MILE SOUTH OF CARQUINEZ STRAIT. | 01712 | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 28 | 0 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 550 | YES | 24 | 1464 | 1 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS & ENGINEERING | 2134867720 | THE LEAK WAS AT A POINT WHERE IT HAD BEEN HIT & DAMAGED IN THE PAST & NOT REPORTED. PIPE DEVELOPED A STRESS CRACK OVER A PERIOD OF TIME WHICH RESULTED INA SMALL LEAK.
2017-09-29 08:50 | YES | NO | 19900039 |  | 22387 | WEST EMERALD PIPE LINE CORP | YES | 1990-02-05 | 800 | NM | GUADALUPE |  | NO |  | NO | SEC. 3, TOWNSHIP 9 NORTH, RANGE 16 E., GUADALUPE COUNTY, NM 2.8 MILES N. OF INTERSTATE 40 AT MILAGRO, NEW MEXICO. |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 36950 | 30750.7846 | 62036.7532 | DIESEL FUEL | 3 | 938 | 147 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | COMPANY PROGRAM | Null | YES | GERALD CHILDERS, MANAGER OF PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APPROXIMATELY 0800 HOURS ON FEBRUARY 5, 1990, DURING THE CONSTRUCTION OF A NEW 10" PIPELINE PARALLEL TO OUR EXISTING 6" PIPELINE, A DITCHING MACHINE STRUCK AND RUPTURED OUR 6" ALBUQUERQUE REFINED PRODUCTS PIPELINE 0.1 MILE DOWNSTREAM OF OUR DAHLIA PUMP STATION DISCHARGE. THE ACCIDENT ALLOWED 938 BARRELS OF DIESEL FUEL TO ESCAPE, OF WHICH 147 BARRELS WERE SUBSEQUENTLY RECOVERED. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING 10 FEET OF PIPE WITH TESTED PIPE, AND THE LINE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19900040 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-01-26 | 310 | TX | COCHRAN |  | NO |  | NO | ODESSA-BORGER (LINE WA) - MP 113-07+00. APPROX. 22-23 MILES NORTH OF PLAINS, TX ON HWY. 214, THEN APPROX. 8 MILES EAST ON HWY. 1585, THEN SOUTH APPROX. 4 MILES | 01867 | LINE PIPE | PIPE |  | 1948 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12483.4037 | 25184.0676 | CRUDE OIL | 1 | 250 | 40 | NO | NO | 12.75 | 0.25 | 45000 | WELDED |  | 1270 | 1149 | YES | 8 | 1615 | 10 | 82 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | FAILURE OCCURED IN SECTION OF PIPE AT A PRESSURE LESS THAN MOP.FAILURE APPARENTLY OCCURED IN THE SEAM OF THE PIPE.
2017-09-29 08:50 | NO | NO | 19900041 |  | 15490 | PHILLIPS PIPE LINE CO | YES | 1989-11-13 | 900 | KS | JOHNSON |  | NO |  | NO | PAOLA-KANSAS CITY 8" LINE - MP 37-12+45 SECTION 16, T12S, R24E, BETWEEN SHAWNEE MISSION DRIVE AND MIDLAND ROAD AND JUST WEST OF PFLUMM ROAD. | 20264 | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 34496.5604 | 69593.4959 | DIESEL FUEL | 3 | 5 | 2 | NO | NO | 8.63 | 0.19 | 40000 | WELDED |  | 1100 | 200 | YES | 24 | 1250 | 10 | 74 | EXTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING AND TECHNICAL SERVICES | 9186614721 | CORROSION LEAK OCCURRED IN CASING UNDER SHAWNEE MISSION PARKWAY ROAD.
2017-09-29 08:50 | YES | NO | 19900043 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1990-01-21 | 1145 | TX | BRAZORIA |  | NO |  | NO | BRAZORIA COUNTY, DAMON TEXAS AT CORNER OF WHY 36 AND COUNTY RD. 264 W. 200 FT. SOUTH OF STATE HWY 36. | 01470 | LINE PIPE | PIPE |  | 1965 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12483.4037 | 25184.0676 | GASOLINE | 3 | 326 | 326 | NO | NO | 12 | 0.2 | 1465 | WELDED |  | 1050 | 1029 | YES | 24 | 1315 | 1 | 65 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WADE D. HUNT, DISTRICT PIPELINE SUPERINTENDENT | 7138776580 | LINE WAS RUNNING IN NORMAL OPERATING PROCEDURE AND BLEW OUT, DISPATCHER SAW PRESSUE DROP AND SHUT LINE DOWN, AND NOTIFIED APPROPRIATE PERSONEL.PART G - 376 BARRELS RECOVERED (INCLUDES 50 BBL OF WATER)
2017-09-29 08:50 | YES | NO | 19900044 |  | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1990-01-18 | 800 | TX | GRIMES | RURAL | NO |  | NO | APPROX. 4.25 MILES SW OF THE COMMUNITY OF LOLA IN NORTH-WESTERN GRIMES COUNTY; 2.1 M. W. OF GRIMES COUNTY RD. NO. 103, AND 5,701 E. OTH THE NAVASOTE RIVER. | 01310 | LINE PIPE | PIPE |  | 1928 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 291279.4206 | 587628.2438 | CRUDE OIL | 1 | 400 | 0 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1060 | 0 | YES | 8 | 1347 | 3 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED - REGULATORY COMPLIANCE SUPV. | 9152673673 | AT APPROX. 8 AM. JANUARY 18, 1990, FINA'S PIPELINE CONTROL CENTER OPERATOR AT BIG SPRING, TEXAS, NOTED AN EXCESSIVE THERMAL PRESSURE BUILD-UP ON THE HEARNE TEMPLE SEGMENT OF THE PIPELINE, RECORDING ON INSTRUMENTS FOR THE WEST SIDEOF HEARNE STATION. A DECISION WAS MADE TO EQUALIZE THE LINE PRESSURE BY OPENING-UP INTO THE HEARNE-SHIRO SECTOR OF THE LINE (THE NEXT EASTERMOST SECTOR). AS THIS WAS BEING DONE, THE OPERATOR NOTED AN IMMEDIATE PRESSURE DROP SUCHTHAT A LINE RUPTURE COULD BE EXPECTED TO HAVE OCCURRED. IMMEDIATELY, CREWS WERE ALERTED TO BEGIN LAND-PATROLLING FOR A LEAK. INCLEMENT WEATHER IN THE AREA HAMPERED EFFORTS TO QUICKLY LOCATE THE LEAK, AS NORMAL PATROL AIRCRAFT WERE GROUNDED. A HELICOPTER WAS CHARTERED LOCALLY AND THE LEAK WAS LOCATED BETWEEN 3:30-4:00 PM. IN A CREEK IN A REMOTE AREA, WITH THE PIPELINE INUNDATED.AS SOON AS HIGH WATER LEVELS IN THE LEAK AREA SUBSIDED, THE LEAKAGE WAS STOPPED BY APPLICATION OF A REPAIR CLAMP. A BROKEN AND DEFECTIVE WELD IN A PREVIOUS REPAIR WAS FOUND TO BE THE SOURCE OF THE LEAK. APPROX. 860' OF REPLACEMENT PIPE WAS INSTALLED IN THE LEAK AREA, RE-ROUTING THE PIPELINE AROUND AN AREA IN WHICH EMBANKMENT EROSION WAS ENDANGERING THE INTEGRITY OF THE EXISTING PIPELINE.PART K - NOTE: PIPELINE WAS SHUT-DOWN AT TIME OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19900045 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1989-10-22 | 1500 | TX | KLEBERG | RICARDO | NO |  | NO |  | 18699 | LINE PIPE | OTHER | UNKNOWN | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 44131 | 38059.1926 | 76780.7642 | GASOLINE | 1 | 1516 | 20 | NO | NO | 4.5 | 0.02 | 2912 | WELDED |  | 1275 | 1155 | YES | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | D.C. HUNT, JR. | 5122894701 | PIPELINE WAS STRUCK BY A PLOW ON AN EARLIER DATE WHICH IS UNKNOWN. THERE WAS ABOUT AN 18" GASH ON TOP OF PIPELINE. THE LINE RUPUTRED AT THIS POINT.
2017-09-29 08:50 | YES | NO | 19900046 |  | 4906 | EXXON PIPELINE CO | YES | 1990-02-20 | 100 | TX | HARRIS |  | NO |  | NO | INSIDE THE DIKE AROUND TANK 1997, WEBSTER STATION, 20004 OLD GAVLESTON ROAD, WEBSTER, TEXAS. | 09123 | TANK FARM | OTHER | MIXER ON TANK 1997 | 1959 | OTHER | PIN SHIFTED OUT OF PLACE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6100 | 5076.5842 | 10241.5208 | CRUDE OIL | 1 | 200 | 195 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. MOORE - OPERATIONS MANAGER | 7136565956 | FIELD SERVICEMAN CONTACTED GAUGING SUPERVISOR AT 12:05 PM. ON 2/2090 AND REPORTED THAT THERE WAS OIL IN THE FIREWALL OF TANK 1997 AT WEBSTER STATION COMING FROM THE TANK MIXER. GAUGING SUPERVISOR WAS AT TANK 1997 AT 12:25 PM. AND CONFIRMED THE INCIDENT. A VACUUM TRUCK WAS CALLED. HAVING RAINWATER IN THE FIREWALL, BOOMS WERE SET UP TO MINIMIZE THE SPREAD OF THE OIL WITHIN THE FIREWALL. THE LEAK WAS COMING FROM THE TANK MIXER. A STEEL PIVOT PIN (TOP) HAD WORKED ITS WAY LOOSE ALLOWING THE MIXER TO TILT BACKWARDS PULLING THE BALL JOINT OUT OF THE PACKING GLAND ALLOWING THE OIL TO ESCAPE FROM THE TANK. MECHANICS AND ELECTRICIANS WERE ABLE TO PLACE A TARP OVER THE SPEWING OIL, PUSH THE MIXER BACK INTO AN UPRIGHT POSITION AND REPLACE THE PIN. A BROKEN CIRCLIP WAS FOUND TO HAVE FALLEN FROM THE PIN ALLOWING THE PIN TO WORK ITS WAY OUT. NEW FULL ENCIRCLEMENT SNAP RINGS WERE PLACED ON THE PIN. THE PACKING GLAND WASTIGHTENED AND NO OIL WAS SEEN TO BE LEAKING. CLEAN UP OPERAIONS STARTED IMMEDIATELY.
2017-09-29 08:50 | YES | NO | 19900047 |  | 4906 | EXXON PIPELINE CO | NO | 1990-02-13 | 2045 | TX | CRANE |  | NO |  | NO | APPROX. 9 MILES NORTH OF CRANE, TEXAS, ON OUR 18" TRUNKLINE FROM ECTOR TO CRANE, STATION NUMBER 1782+19. |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 145000 | 120672.9028 | 243445.9867 | CRUDE OIL | 1 | 20027 | 18739 | NO | NO | 18 | 0.25 | 52000 | WELDED |  | 930 | 800 | YES | 36 | 1205 | 2 | 57 | EXTERNAL | Null | YES | GALVANIC | COATING DAMAGED 3RD PARTY | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. MOORE - OPERATIONS MANAGER | 7136565956 | ON FEBRUARY 14, 1990, AT 0715 HR, ORYX ENERGY CO. REPORTED TO EXXON PIPELINECOMPANY THE PRESENCE OF AN OIL LEAK. EPC VERIFIED THE PROBABILITY OF A LEAKAND SHUT DOWN THE SYSTEM AT 0727 HRS. A REPAIR/CLEANUP GANG ARRIVED AT 0900HR. AND PROCEEDED WITH THE REPAIRS AND CLEANUP. ARRANGEMENTS WERE MADE TO BRING IN VACUUM TRUCKS, BACKHOES, AND DOZERS TO ASSIST WITH CLEANUP. A FORTY-FOOT SECTION OF PIPE WAS INSTALLED & THE REPAIR WAS COMPLETED BY 1125 ON 2/15. PARTIAL OPERATION OF SYSTEM WAS BEGUN SHORTLY AFTER. THE CLEANUP WAS COMPLETE BY 1600 HRS ON 2/16/90 WHICH INCLUDED PICKING UP OIL WITH VACUUM TRUCKS AND THE REMAINDER WAS TURNED INTO THE SOIL AND COVERED WITH DRY SOIL. THE LEAK WAS CAUSED BY A RUPTURE IN THE BODY OF THE PIPE CAUSED BY CORROSION AT THE TOP OR 12:00 O'CLOCK POSITION. THIS CORROSION POSSIBLY RESULTED FROM COATING DAMAGE WHICH MAY HAVE OCCURRED WHEN A CROSSING PIPELINE WAS LAID ABOUT 1981. THIS LINE (4" PVC), PERPENDICULAR TO THE 18", WAS LAID ABOUT 1 FOOT ABOVE AND 2 FEET OVER FROM THE CENTER OF THE RUPTURED AREA. THE PIPELINE CONTAINED A 16" LONGITUDINAL SPLIT THAT WAS 7" WIDE AND WAS DEFLECTED 5".
2017-09-29 08:50 | YES | NO | 19900048 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1990-02-26 | 910 | IL | COOK | CHICAGO | NO |  | NO | CHICAGO TERMINAL # D206. | 09815 | TANK FARM | BOLTED FITTING |  | 1940 | OUTSIDE FORCE DAMAGE | FROSTHEAVE | NATURAL FORCE DAMAGE | TEMPERATURE | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | 11235.0634 | 22665.6608 | GASOLINE | 3 | 325 | 310 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | FROSTHEAVE |  | Null | NO DATA |  | Null | Null | HOWARD E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | ON 2/6/90 A LEAK WAS DISCOVERED IN THE #812 TANK DIKE AT OUR CHICAGO, ILLINOIS TERMINAL. FROSTHEAVE HAD CAUSED A 10" FLANGED CONNECTION ON THE PUMP PIPING TO PARTIALLY SEPARATE RESULTING IN A 325 BARREL RELEASE OF GASOLINE. A RECENT PUMP INSTALLATION HAD CHANGED THE GROUND SURFACE CONTOUR SUCH THAT THE BOTTOM OF THE HORIZONTAL PIPING WAS SETTING ON THE GROUND SURFACE. FROSTHEAVEPUSHED UP ON THE FLANGED CONNECTION AND STRETCHED THE BOLTS ENOUGH TO SEPARATE THE TOP OF THE FLANGED CONNECTION. THE AREA BENEATH THE PIPE HAS SINCE BEEN DUG OUT TO PROVIDE ADDITIONAL CLEARANCE. DUE TO THE FROZEN GROUND CONDITIONS, NEARLY ALL OF THE RELEASED PRODUCT WAS RECOVERED. APPRPRIATE STATE ENVIRONMENTAL OFFICIALS WERE CONTACTED REGARDING THE RELEASE.
2017-09-29 08:50 | YES | NO | 19900049 |  | 22610 | WILLIAMS PIPELINE CO | YES | 1990-02-18 | 1400 | SD | WATERTOWN |  | NO |  | NO | WATERTOWN TERMINAL #E215. | 08876 | TANK FARM | OTHER | PIPE COUPLING CONNECTION | 0 | OTHER | GASKET FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 5825.5884 | 11752.5649 | GASOLINE | 3 | 332 | 101 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | ON FEBRUARY 18, 1990, A LEAK OCCURRED IN THE SWING ARM MANIFOLD CHANGE ROOM AT OUR WATERTOWN TERMINAL. A GASKET IN ONE OF THE WING ARM QUICK COUPLER CONNECTIONS FAILED DURING A MAIN LINE RECEIPT OPERATION AND RELEASED 332 BBLS. OF UNLEADED GASOLINE. APPROXIMATELY 101 BBLS. HAVE BEEN RECOVERED TO DATE.RECOVERY EFFORTS CONTINUE AND HAVE BEEN COORDINATED WITH STATE AND LOCAL ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19900050 |  | 4430 | EMERALD PIPE LINE CORP | YES | 1990-02-16 | 1100 | KS | SEWARD |  | NO |  | NO | SECTION 9, TOWNSHIP 34 SOUTH, RANGE 31 WEST, SEWARD COUNTY, KANSAS 13 MILES EAST AND 5 MILES NORTH OF LIBERAL, KANSAS. |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 23400 | 19474.1098 | 39287.1454 | L. P. G. | 2 | 2295 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COMPANY PROGRAM | NO | NO | GERALD CHILDERS, MANAGER OF PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APPROXIMATELY 1100 HOURS ON FEBRUARY 16, 1990, A DITCHING MACHING OPERATED BY A THIRD-PARTY STRUCK AND RUPTURED OUR 6" OKAN PRODUCTS PIPELINE. THE ACCIDENT ALLOWED 2,295 BARRELS OF PROPANE TO ESCAPE, ALL OF WHICH RAPIDLY VAPORIZED PREVENTING ANY RECOVERY. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING 3 FT 4 IN OF LINE WITH PRETESTED PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19900051 |  | 10313 | KOCH PIPELINE INC | NO | 1990-02-19 | 1610 | OK | TULSA |  | NO |  | NO | NW/4, SEC. 16 T19N, R21E. | 08993 | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 17854 | 14858.5794 | 29975.7562 | L. P. G. | 2 | 672 | 0 | NO | NO | 6.63 | 0.22 | 46000 | WELDED |  | 1440 | 220 | YES | 24 | 1972 | 1 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | NO | MARC S. DEVARENNES, DIVISION ENGINEER | 4053952377 | AT APPROXIMATELY 16:00 HOURS ON FEBRUARY 19, 1990, A DOZER OPERATED BY SHERWOOD CONSTUCTION HIT AND RUPTURED A PIPELINE OWNED AND OPERATED BY KOCH PIPELINES, INC. THERE WERE NO INJURIES.
2017-09-29 08:50 | YES | NO | 19900052 |  | 26134 | MOBIL PIPELINE CO - MOBIL WEST COAST PIPELINE | NO | 1990-03-05 | 700 | CA | KERN | BELRIDGE | NO |  | NO | SEC: TWNSP 29 S RANGE: 21E APPROX: 1/4 MILE EAST OF HWY 33. |  | PUMPING STATION | PUMP |  | 1988 | OTHER | EQUIPMENT MALFUNCTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | CRUDE OIL | 1 | 500 | 450 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MR. J.R. JEFFRIES, MANAGER, WEST COAST PIPE LINES | 2132122905 | THE LEAK ORIGINATED FROM THE #7 PUMP AT BELRIDGE STATION. THE LOCK NUT HOLDING THE ROD IN PROPER ADJUSTMENT LOOSENED CAUSING THE ROD TO UNSCREW AND LENGTHEN: AT WHICH TIME IT PUSHED THE PISTON INTO THE LINER COVER, CRACKING IT. REPAIR WAS MADE BY REPLACING LINER COVER.
2017-09-29 08:50 | YES | NO | 19900053 |  | 12628 | MOBIL PIPELINE CO | NO | 1990-02-19 | 1700 | TX | PANOLA | CARTHAGE | NO |  | NO | APPROXIMATELY 12 MILES EAST OF CARTHAGE, TX, AND SOUTH OF STATE HWY. 123, APPROXIMATELY 200 YDS. - SWAMP AREA. | 08995 | LINE PIPE | OTHER | GASKET FAILED CAUSE LEAK | 1926 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 19300 | 16061.9795 | 32403.5003 | GASOLINE | 2 | 142 | 120 | NO | NO | 8 | 0.32 | 2400 | WELDED |  | 415 | 250 | YES | 2 | 540 | 9 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT , OPERATIONS | 2146582226 | AT APPROXIMATELY 9:00 AM. MONDAY, FEBRUARY 19, 1990, DALLAS DISPATCHING SUPERVISOR, NOTIFIED LONGVIEW AREA THAT FOLLOWING A ROUTINE SHUTDOWN OF THE HEBERT-WASKOM PRODUCTS LINE AT APPROXIMATELY 4:00AM., A PRESSURE DROP HAD BEEN DETECTED. AFTER FURTHER INVESTIGATION, DALLAS DISPATCHING PERSONNEL DETERMINED THE PRESSURE HAD OCCURRED BETWEEN CENTER AND WASKOM TERMINALS. AT APPROXIMATELY 9:20 AM., DALLAS CONTROLLERS CALLED THE PATROL PILOT TO FLY THE LINE. AT11:00 AM., LONGVIEW CONSTUCTION PERSONNEL WERE DISPATCHED TO WALK THE LINE AFTER THE PATROL PLANE REPORTED NOTHING UNUSUAL ON THE WASKOM-CENTER FLIGHT. AT APPROXIMATELY 5:00 PM.A SITE AT MP 152.9 WAS FOUND WHERE GASOLINE WAS COMING TO THE SURFACE. PERSONNEL FOUND AN ILLEGAL TAP HAD BEEN INSTALLED ON THE LINE. THE GASKETS USED IN THE INSTALLATION FAILED AND GASOLINE WAS LEAKING FROM THE CONNECTION. GASOLINE HAD FLOWED INTO A DRAINAGE DITCH. THIS DITCH ALLOWS WATER TO FLOW INTO AN UNNAMED TRIBUTARY OF SOCAGEE CRK, WHICH IS APPROXIMATELY 2 MILES FROM THE LEAK SITE. IMMEDIATELY UPON DISCOVERING THE LEAK, SPILL CONTROL BOOMS WERE PLACED IN THE TRIBUTARY TO SOCAGEE CREEK TO CONTAIN ANYGASOLINE THAT MIGHT REACH THE CREEK. REPAIR WAS MADE TO THE PIPELINE ON 2/19/90 BY WELDING A STEEL PATCH ON THE AFFECTED AREA OF PIPELINE.
2017-09-29 08:50 | NO | NO | 19900055 |  | 10313 | KOCH PIPELINE INC | YES | 1990-03-10 | 1200 | OK | POTTAWATOMIE |  | NO |  | NO | SEC. 21, R3E, T9N. | 11755 | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 832.2269 | 1678.9378 | L. P. G. | 2 | 1 | 0 | NO | NO | 8.63 | 0.19 | 46000 | WELDED |  | 1440 | 400 | YES | 24 | 1801 |  |  | EXTERNAL | Null | YES | OTHER | FOREIGN INTERFERENCE | NO DATA |  | Null | NO DATA |  | Null | Null | MARC S. DEVARE, DIVISION ENGINEER | 4053952377 | LANDOWNER CONTACTED THE POTTAWATOMIE COUNTY SHERIFF'S ON 3/10/90. THE SHERIFF'S OFFICE THEN CONTACTED KOCH PIPELINES, INC. WHICH RESULTED IN REPRESENTATIVE BEING DISPATCHED TO THE AREA AND DETERMINING THAT THERE WAS NO IMMEDIATE DANGER, THE REPRENTATIVE CONTACTED MAINTENANCE PERSONNEL WHO WERE DISPATCHED TO THE SITE. THE DAMAGE WAS REPAIRED ON 3/10/90.
2017-09-29 08:50 | NO | NO | 19900056 |  | 737 | ASHLAND PIPELINE CO | YES | 1990-03-02 | 810 | MS | MISSISSIPPI RIVER |  | NO |  | NO | MISSISSIPPI RIVER AT MILE POST MARKER 373.4, OR 10 MILES NORTH OF VADALIA, LA - NATCHEZ, MS, MISSISSIPPI RIVER BRIDGE. | 10498 | LINE PIPE | OTHER | UNKNOWN | 1967 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | CRUDE OIL | 1 | 15 | 0 | NO | NO | 8 | 0.5 | 35000 | WELDED |  | 600 | 30 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | DELANE D. BURNETTE, COMPLIANCE COORDIANTOR | 3187574138 | ASHLAND FIRST BECAME AWARE OF A POSSIBLE LEAK FROM A REPORT BY AN ASHLAND FIELD GAUGER THAT HE SMELLED WHAT HE THOUGHT WAS DIESEL FUEL AT A CERTAIN LOCATION ON THE MISSISSIPPI RIVER. HE WAS DIRECTED TO BOAT TO OUR 8" RIVER CROSSING TO DETERMINE IF THE SOURCE OF PETROLEUM WAS ORIGINATING FROM ASHLAND'S PIPELINE. AT 8:10AM., HE ADVISED BY RADIO THAT THE RELEASE WAS COMING FROM ASHLAND'S 8" NORTH RIVER CROSSING. THE LINE SEGMENT WAS VALVED OFF ON EACH SIDE OF THE RIVER AT 9:30 AM; WHICH STOPPED THE RELEASE OF OIL FROM THE PIPELINE.THE EXACT CAUSE OF THE RELEASE IS NOT KNOWN AT THIS TIME, HOWEVER IT IS SUSPECTED THAT RECENT INSTALLATION OF RIVER BANK STABILIZATION REVETMENT BY THE U.S. ARMY CORPS OF ENGINEERS MAY BE RELATED TO THE RELEASE.
2017-09-29 08:50 | YES | NO | 19900057 |  | 5522 | FOUR CORNERS PIPELINE CO | YES | 1990-03-01 | 1000 | UT | SAN JUAN | MONTEZUMA CREEK | NO |  | NO | T40S, R23E, SEC 31 SAN JUAN COUNTY, UTAH 1.5 MILES WNW OF MONTEZUMA CREEK, UTAH. | 10379 | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | CRUDE OIL | 1 | 300 | 230 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 100 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | INTERNAL CORR. ON LINE | NO DATA |  | Null | NO DATA |  | Null | Null | C.B. WHORTON, MANAGER, HEALTH, SAFETY AND ENVIRONMENTAL | 2134289271 | THE 8 INCH "TEXACO BURTON" GATHERING LINE EXPERIENCED AN INTERNAL CORROSION LEAK ON MARCH 1, 1990.
2017-09-29 08:50 | NO | NO | 19900058 |  | 12470 | MID - VALLEY PIPELINE CO | YES | 1990-03-06 | 0 | MS | ISSAQUENA |  | NO |  | NO | T12N, R8W, SEC 21; MID-VALLEY'S MAYERSVILLE, MS TANK TERMAINAL; APPROXIMATELY 1 MILE SOUTH OF MAYERSVILLE, MS ON STATE HWY 1. | 11970 | TANK FARM | PIPE |  | 1949 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 19000 | 15812.3114 | 31899.8189 | CRUDE OIL | 1 | 25 | 20 | NO | NO | 20 | 0.25 | 35000 | WELDED |  | 100 | 20 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | I.B. NEWMAN, MGR. OF PIPELINE OPERATIONS | 2147570207 | AT 12:30 PM. ON 3/6/90, MID-VALLEY EMPLOYEES AT MID-VALLEY'S MAYERSVILLE TANK TERMINAL, WHILE WORKING NEAR THE TANK LINE MANIFOLD AREA, SMELLED CRUDE OIL. ON CLOSER INSPECTION THEY DISCOVERED THAT CRUDE OIL WAS ESCAPING THROUGH AN APPROXIMATELY 3/16" DIAMETER HOLE AT THE 6 O'CLOCK POSITION ON THE TK #10 - 20" LINE (ABOVE GROUND), LOCATED APPROXIMATELY 30 FT. WEST OF THE TINSLEY HEADER. THE LINE, HAVING BEEN COMMON TO STATION SUCTION PRESSURE BUT WITHOUT FLOW, WAS IMMEDIATELY ISOLATED AND A WOODEN PEG WAS DRIVEN IN THE HOLE. THE OIL WAS COMPLETELY CONTAINED WITHIN THE DIKED AREA OF THE MANIFOLD. AFTER PERFORMING ULTRASONIC INSPECTIN OF WALL THICKNESS TO CONFIRM NO OTHER PITTING, A 30" SPLIT SLEEVE WAS PERMANENTLY INSTALLED OVER THE HOLE IN THE LINE.
2017-09-29 08:50 | YES | YES | 19900059 | 1990-04-09 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1990-03-13 | 639 | NY | SCHOHARIE |  | NO |  | NO | 8"LINE P-41, M.P. 128.33, SCHOHARIE COUNTY NEAR NORTH BLENHEIM, NEW YORK ALIGNMENT SHEET TPF-P41-47 ATTACHED. | 12132 | LINE PIPE | PIPE |  | 1964 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 2 | 0 | 2 | 5 | 0 | 5 | 734000 | 610854.5564 | 1232340.3742 | L. P. G. | 2 | 133 | 0 | YES | YES | 8.63 | 0.38 | 35000 | WELDED |  | 1220 | 844 | YES | 24 | 1756 |  | 64 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HAUNIGAN, VICE PRESIDENT - OPERATIONS | 7137594700 | AT 0639 HRS. C.S.T. ON MARCH 13,1990, A RESIDENT OF NORTH BLENHEIM, NEW YORK, CALLED OUR WATKINS GLEN, NEW YORK, OFFICE TO REPORT A WHITE CLOUD APPROACHING THE TOWN. THE PHONE LINE DISCONNECTED, PROBABLY BECAUSE THE WHITE PROPANECLOUD WAS UNINTENTIONALLY IGNITED BY AN UNKNOWN SOURCE, CAUSING AN EXPLOSION AND FIRE. THE UPSTREAM STATIONS OF THE PIPELINE WERE IMMEDIATELY SHUT DOWN, A BLOCK VALVE UPSTREAM OF THE ACCIDENT SITE WAS CLOSED, AND THE SELKIRK TERMINAL DOWNSTREAM OF THE ACCIDENT SITE CONTINUTED TO RECEIVE PRODUCT TO REDUCETHE PRESSURE ON THE PIPELINE. THE NEAREST DOWNSTREAM VALVE WAS THEN CLOSED AT 0800 HRS. TO ISOLATE THE ACCIDENT SITE. ESCAPING PRODUCT WAS ALLOWED TO BURN WHILE A STOPPLE WAS SET A SHORT DISTANCE UPSTREAM OF THE SITE. AFTER THEFIRE WENT OUT, THE DAMAGED PIPE WAS REMOVED AND REPLACED WITH NEW PIPE. THECAUSE OF THE ACCIDENT IS NOT KNOWN PENDING COMPLETION OF THE FAILURE AND ANALYSIS BY BATTELL MEMORIAL INST.
2017-09-29 08:50 | YES | NO | 19900060 | 1990-04-09 | 443 | AMOCO PIPELINE CO | YES | 1990-03-06 | 1630 | KS | MIAMI | LOUISBURG | NO |  | Null | SW/4 SEC. 23, TOWNSHIP 165, RANGE 25E-1/2 MILE W. OF THE KANSAS/MISSOURI STATE LINE AND APPROX. 1 MI. NORTH OF KANSAS HWY 68 (SEE ATTACHMENT). | 11126 | LINE PIPE | OTHER | SEAL ON INSTR. PROBE | 1954 | INCORRECT OPERATION BY OPERATOR PERSONNEL | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 62417.0187 | 125920.338 | CRUDE OIL | 1 | 250 | 234 | NO | NO | 24 | 0.38 | 0 | WELDED |  | 0 | 475 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.B. WEISS, AREA MANAGER | 8168995387 | AN INSTRUMENT PROBE UTILIZED TO MONITOR GRAVITY CHANGES IN A BATCHED CRUDE LINE AND MOUNTED IN THE OUTLET OF A TEE FITTING WAS INSERTED TOO DEEPLY INTO THE TEE. WHILE RUNNING A SCRAPER THROUGH THE LINE, IT STRUCK THE POROE WITH SUFFICIENT FORCE TO CAUSE CRUDE OIL TO ESCAPE THROUGH A DAMAGED ELECTRICAL SEAL FITTING. COMPANY PERSONNEL WERE ON SITE WITHIN LESS THAN AN HOUR AND HAD THE OIL CONTAINED WITHIN TWO HOURS BY STRATEGICALLY PLACING CONTAINMENT AND ABSORBENT BOOMS ALONG PONEY CREEK. THE INCIDENT WAS REPORTED TO PETTY OFFICER FANDAHL OF THE NATIONAL RESPONSE CENTER AT 2045 EST ON 3/6/90 AND LOGGED AS REPORT NO. 11126. EPA, KANSAS, AND MISSOURI NOTIFICATIONS WERE ALSO MADE. THE CLEANUP IS ESSENTIALLY COMPLETED AND NO ENVIRONMENTAL IMPACT IS ANTICIPATED.
2017-09-29 08:50 | YES | NO | 19900061 | 1990-04-10 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1990-03-02 | 1145 | OK | DRUMRIGHT |  | NO |  | NO | SEC. 27-7E-18N. |  | PUMPING STATION | OTHER | SUMP OVERFILLED | 0 | OTHER | OIL BACKED UP FROM PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 83.2227 | 167.8938 | CRUDE OIL | 1 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DONALD G. MEARS, DOT SPECIALIST | 9185866803 | CRUDE OIL BACKED UP FROM SUMP TANK INTO ENGINE ROOM AND CAME IN CONTACT WITHTHE EXHAUST MANIFOLD. PUMP WENT DOWN AND DISPATCHERS CALLED FOR HELP IN STARTING ENGINE. WHEN MECHANIC ARRIVED AT PUMP STATION, STATION WAS ON FIRE. MECHANIC RETURNED TO OFFICE FOR HELP. SEVERAL EMPLOYEES RETURNED TO PUMP STATION AND BLOCKED IN FUEL GAS AND EXTINGUISHED FIRE. DRUMRIGHT VOLUNTEER FIRE DEPARTMENT ARRIVED AFTER THE FIRE WAS OUT.
2017-09-29 08:50 | YES | NO | 19900062 | 1990-04-16 | 809 | ARCO PIPE LINE CO | YES | 1990-03-13 | 2115 | OK | JEFFERSON |  | NO |  | NO | 16 MILES SOUTHWEST OF RINGLING - S.E. 1/4 SEC. 32, T6S, R4W IN RED RIVER CROSSING. |  | LINE PIPE | PIPE |  | 1919 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 648066 | 539337.9686 | 1088062.5299 | CRUDE OIL | 1 | 3600 | 0 | NO | NO | 12 | 0.38 | 35000 | THREADED |  | 580 | 100 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, MANAGER CRUDE BUSINESS UNIT | 3163311300 | A PRESSURE DROP WAS NOTED AT 2115 ON MARCH 13, 1990. LINES WAS SHUT DOWN ONMARCH 13,1990 AT APPROXIMATELY 2200. ON THE MORNING OF MARCH 14, THE LINE WAS FLOWN BY PATROL PILOT AND OIL WAS OBSERVED IN THE RIVER EAST OF RIVER CROSSING. SPILL CLEAN UP CREW WAS CALLED AND CLEAN UP BEGAN ON MARCH 15,1990.
2017-09-29 08:50 | YES | NO | 19900063 | 1990-04-20 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1990-03-19 | 650 | NM | SAN JUAN |  | NO |  | NO | WITHIN FCPL CURDE OIL PUMP STATION TANK FARM LOCATED SEVEN MILES NORTH OF RED MESA SCHOOL, UTAH ON THE NAVAJO NATION RESERV. LAT. 37 01' 03" LONG. 109 24' 03". |  | TANK FARM | TANK |  | 0 | OTHER | LEV. MONITOR. SYS. FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16644.5383 | 33578.7568 | CRUDE OIL | 1 | 12000 | 10722 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.B. WHORTON, MANAGER, HEALTH, SAFETY AND ENVIRONMENTAL | 2134289271 | THE TANK LEVEL MONITORING SYSTEM FAILED ON A CRUDE OIL TANK WHICH IS LOCATEDWITHIN THE DIKED AREA OF THE FCPL RED MESA TANK FARM.THE TANK FARM IS LOCATED IN SAN JUAN COUNTY, UTAH. THE FAILED SYSTEM PREVENTED A HIGH LEVEL ALARM INDICATION AND THE SUBSEQUENT OVERFILLING OF THE TANK AND RELEASE OF CRUDE OILINTO THE DIKED AREA ON MARCH 19.1990.
2017-09-29 08:50 | YES | NO | 19900064 | 1990-04-24 | 12470 | MID - VALLEY PIPELINE CO | YES | 1990-04-01 | 1125 | KY | GRAYSON |  | NO |  | NO | APPROX. 8 MILES SOUTHWEST OF LEITCHFIELD, KY. (LAT. 37 DEG. 23' 3" N. LONG. 86 DEG. 20' 14" W). | 15295 | LINE PIPE | PIPE |  | 1949 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 166445.3832 | 335787.5679 | CRUDE OIL | 1 | 75 | 55 | NO | NO | 22 | 0.3 | 52000 | WELDED |  | 816 | 503 | YES | 24 | 1020 | 1 | 49 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | UNKNOWN | 2147570207 | A LANDOWNER REPORTED THERE WAS OIL ON CLAYLICK BRANCH. THE LEAK WAS TOO SMALL TO BE DETECTED BY PRESSURE AND FLOW INSTRUMENTATION AT CLARKSON STATION, SOME 8 MILES DOWNSTREAM OF THE LEAK SITE. THE PIPELINE WAS IMMEDIATELY SHUT DOWN, PENDING FURTHER INVESTIGATION. OIL RAN DOWN A HILL INTO CHENNETH BRANCH, WHICH IS A TRIBUTARY OF CLAYLICK BRANCH. UPON EXCAVATION, A STEEL CABLE AND A SMALL SEAM OF COAL WAS DISCOVERED NEAR THE PIPELINE. FAILURE OF PIPE WALL WAS APPARENTLY CAUSED BY ISOLATED EXTERNAL CORROSION PROMOTED BY THE PRESENCE OF THE STEEL CABLE BURIED ALONG THE PIPELINE. CORROSION WAS ENHANCE BY THE PRESENCE OF A SMALL SEAM OF COAL RUNNING UNDERNEATH THE PIPELINE. IN ADDITION, AN UNDERGROUND SPRING KEPT THIS LOCATION SATURATED WITH WATER. OTHER PITTING WAS DISCOVERED IN THE LOCAL AREA, BUT THE CORROSION WAS CONFINED TO A 12-FOOT AREA NEAR THE CABLE AND THE COAL.
2017-09-29 08:50 | YES | NO | 19900065 | 1990-04-25 | 10319 | KOCH GATHERING SYSTEMS INC | YES | 1990-04-15 | 630 | OK | KINGFISHER |  | NO |  | NO |  | 17279 | PUMPING STATION | TANK |  | 1949 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2496.6807 | 5036.8135 | CRUDE OIL | 1 | 1000 | 900 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SHERMAN SMITH, AREA FOREMAN | 4052758280 | FAILURE OF TANK GAUGE.
2017-09-29 08:50 | YES | NO | 19900066 | 1990-04-25 | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-03-30 | 1045 | TX | HUTCHINSON |  | NO |  | NO | BORGER-AMARILLO LINE - MP 0-28+00. APRPOXIMATELY 1/2 MILE EAST OF BORGER REFINERY. | 15107 | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 45772.4804 | 92341.5812 | DIESEL FUEL | 1 | 1650 | 600 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1212 | 1197 | YES | 8 | 1690 | 10 | 84 | EXTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | THE TOP 6" OF THE 8" O.D. PIPE WAS EXPOSED IN BOTTOM OF "DRY STREAM BED" DUETO EROSION. STREAM ALTERNATES BETWEEN WET AND DRY CONDITIONS DEPENDING ON RAINS. DUE TO EXPOSURE TO THE ELEMENTS (WATER, SUNLIGHT, ETC.), THE COATING FAILED. THE CYCLING WET AND DRY CONDITIONS RESULTED IN GENERAL CORROSION OF THE PIPE METAL IN THIS PARTICULAR AREA, UNTIL PIPE FAILURE OCCURRED.
2017-09-29 08:50 | YES | NO | 19900067 | 1990-05-01 | 443 | AMOCO PIPELINE CO | YES | 1990-04-01 | 1500 | IA | POTTAWATTAMIE |  | NO |  | NO | SECTION 16, T-77N, R44W. | 15320 | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | FUEL OIL | 2 | 145 | 10 | NO | NO | 6 | 0.25 | 1902 | WELDED |  | 1440 | 390 | YES | 24 | 1793 | 4 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | M.B. WEISS, AREA MANAGER | 8168995387 | THE LINE WAS PUNCTURED AT AN OVERHEAD CROSSING OF THE BOYER RIVER BY A RIFLEFIRED AT CLOSE RANGE FROM THE EAST BANK. AT THE TIME OF THE INCIDENT THE LINE WAS NOT IN OPERATION. AFTER NOTIFICATION, AMOCO PERSONNEL WERE ON SITE WITHIN 2 1/2 HOURS. THE LINE WAS PLUGGED. CONTAINMENT AND RECOVERY EFFORTS WERE PROMPTLY INITIATED. THE INCIDENT WAS REPORTED TO PETTY OFFICER JIM ROBINSON OF THE NATIONAL RESPONSE CENTER AT 1831 EST ON 4/1/90 AND LOGGED AS REPORTNO. 15320. SIXTY FEET OF FURNACE OIL CONTAMINATED BANK WERE MOVED TO A STATE APPROVED LANDFILL IN LOGAN, IOWA. TO DATE, THE VANDAL RESPONSIBLE HAS NOT BEEN APPREHENDED.
2017-09-29 08:50 | YES | NO | 19900068 | 1990-04-30 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1990-03-30 | 2230 | PA | ARMSTRONG | BUFFALO TOWNSHIP | NO |  | NO | APPROXIMATELY 3 MILES NORTH OF FREEPORT, PA, AND APROXIMATELY 700 FEET WEST OF KNAPP RUN. REFER TO BUCKEYE PIPE LINE CO. DRAWING NO. 11391-A DATED 4/16/90. | 15167 | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | LANDSLIDE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRANSMIX (PART. REFINED PETRO) | 3 | 1800 | 0 | NO | NO | 10.75 | 0.28 | 42000 | WELDED |  | 1100 | 635 | YES | 12 | 1708 | 10 | 89 | NO DATA | Null | Null | NO DATA |  | LANDSLIDE |  | Null | ONE CALL |  | Null | Null | DEAN R. MOYER, REGULATORY COMPLIANCE COORDINATOR | 2158208300 | PIPELINE DAMAGED BY LANDSLIDE.
2017-09-29 08:50 | NO | NO | 19900069 | 1990-05-09 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-04-08 | 115 | CA | SOLANO |  | NO |  | NO | INSIDE CONTAINMENT AREA OF SFPP'S ELMIRA STATION. | 16299 | PUMPING STATION | VALVE |  | 0 | OTHER | VANDALISM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 49933.615 | 100736.2704 | DIESEL FUEL | 3 | 48 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS & ENG. | 2134867720 | VANDALS MADE A FORCED ENTRY AND TAMPERED WITH EQUIPMENT, OPENED DRAIN VALVE TO SUMP. HIGH SUMP ALARM AND UNIT SEAL LEAKAGE INDICATED ON BOTH UNITS ALONG WITH A STATION LOCKOUT WERE RECEIVED AT0043, 04-08-90. THE AREA SUPERVISOR WAS CALLED AND IMMEDIATELY WENT TO ELMIRA STATION AND OBSERVED THE ABOVE AND TOOK CORRECTIVE ACTION THAT STOPPED THESPILL.
2017-09-29 08:50 | YES | NO | 19900070 | 1990-04-30 | 12628 | MOBIL PIPELINE CO | YES | 1990-03-28 | 1745 | TX | CLAY |  | NO |  | NO | W.C. DONLEY SURVEY AB 129, CLAY COUNTY, TEXAS, 4 MILES EAST OF HENRIETTA, TX. | 14840 | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 48740 | 40562.7399 | 81831.4303 | CRUDE OIL | 1 | 95 | 8 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 533 | 150 | YES | 2 | 586 | 10 | 68 | EXTERNAL | Null | YES | OTHER | ISOLATED CELL | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582381 | COMPANY AERIAL PATROL PILOT DISCOVERED LEAK AT MP 30.3, AND RECOVERY AND CLEANUP PROCEDURES WERE INITIATED. SPILL CONTAINMENT BOOMS WERE INSTALLED IN UNNAMED TRIBUTARY OF LITTLE WICHITA RIVER. NO OIL REACHED LITTLE WICHITA RIVER. LEAK WAS CAUSED DUE TO EXTERNAL CORROSION. PERMANENT REPAIR MADE BY INSTALLING A FULL ENCIRCLEMENT WELDED SPLIT SLEEVE.
2017-09-29 08:50 | YES | NO | 19900071 | 1990-05-23 | 2388 | OXY USA INC | NO | 1990-04-21 | 1815 | LA | CALCASIEU |  | NO |  | NO | 523 T115 R10W CALCASIEU PARISH LOUISIANA 1/2 MILE FROM LA 27 TO RUPTURE EAST. | 18337 | LINE PIPE | PIPE |  | 1957 | FAILED PIPE | CORROSION, INTERNAL | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 416.1135 | 839.4689 | L. P. G. | 2 | 1000 | 0 | NO | NO | 8.63 | 0.32 | 2613 | WELDED |  | 560 | 575 | YES | 24 | 700 | 1 | 57 | INTERNAL | Null | YES | OTHER | BACTERIAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | GARRY R. PRICE, OPERATIONS SUPT. | 3185834642 | ON SATURDAY, APRIL 21, 1990 AT APPROXIMATELY 6:15 P.M., OXY PERSONNEL RECEIVED A PHONE CALL AND IMMEDIATELY RESPONDED TO A PIPELINE BLOWOUT IN 523, T115,R10W, CALCASIEU PARISH, LOUISIANA. THE PIPELINE WAS IDENTIFIED AS OXY USA INC.'S PIPELINE NUMBER 33A IN FIELD GRADE BUTANE SERVICE. PIPELINE VALVES WERE SHUTIN, ISOLATING APPROXIMATELY 21402 FEET OF 8 INCH PIPELINE. A FLARE WASSET AT THE SOUTH END OF THE ISOLATED SECTION AND THE BUTANE WAS FLAIRED FOR APPROXIMATELY 12 HOURS UNTIL THE FLARE WOULD NOT SUSTAIN SAFE COMBUSTION. NOLIQUID SHEEN OR LIQUID DISCOLORATIONS WERE OBSERVED ON THE SURROUNDING LANDSCAPE OR ON THE NEARBY CHOUPIQUE BOYOU. THE ACTION TAKEN TO RESPOND TO AND CONTAIN THE PIPELINE BREAK INCLUDED: A. ESTABLISHMENT OF A SAFETY PERIMETER BY LOCAL FIRE DEPT. & OXY PERSONNEL. B. CALCASIEU PARISH SHERIFF'S DEPT. DEPUTIES AND COAST GUARD OFFICIALS CLOSED CHOUPIQUE BAYOU, BLOCKED THE THRIFT PIPELINE ROAD AND WERE REPORTED TO HAVE EVACUATED RESIDENTS OF APPROXIMATELY 5HOMES UNTIL PILOT LIGHTS COULD BE SHUT OFF. NO MEDICAL ADVICE WAS REQUIRED.
2017-09-29 08:50 | YES | NO | 19900072 | 1990-05-22 | 4904 | EXXON CO USA | NO | 1990-05-06 | 550 | LA |  |  | YES | 28 15'56"N 91 45'5"W | YES | SEE ATTACHED. |  | LINE PIPE | OTHER | PIPE NIPPLE | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 208056.729 | 419734.4599 | CRUDE OIL | 1 | 900 | 0 | NO | NO | 8.63 | 0.5 | 35000 | FLANGED |  | 1440 | 0 | YES | 8 | 2160 | 10 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | T.S. BROOKS, SR. SUPERVISING ENGINEER | 5045614753 | ON MAY 6, 1990, AN OIL SPILL SIGHTING OF UNDETERMINED ORIGIN IN THE EUGENE ISLAND AREA OF THE GULF OF MEXICO WAS REPORTED BY EXXON TO THE NATIONAL RESPONSE CENTER (REPORT NO. 20677) AS WELL AS TO THE MINERALS MANAGEMENT SERVICE. AT THAT TIME, EXXON BEGAN SHUTTING IN PRODUCTION PLATFORMS AND CHECKING SYSTEMS IN THE AREA OF THE SIGHTING TO DETERMINE IF AN EXXON FACILITY WAS THE SOURCE OF THE SPILL. IT IS BELIEVED THAT TEXACO MAY HAVE ALSO REPORTED A SIGHTING. TEXACO AND EXXON COORDINATED INVESTIGATION TO DETERMINE THE SPILL SOURCE AND MOBILIZATION OF SPILL CLEANUP EQUIPMENT. AT THE TIME OF THE SIGHTING, THE SEAS WERE 3-5 FEET, WITH THE WINDS FROM THE NORTH AT 10-15 MPH AND A SOUTHERLY CURRENT. THE RAINBOW SHEEN COVERED AN AREA OF APPROXIMATELY 2 MILES BY 5 MILES AND WAS MOVING TO THE SOUTH. ON THE AFTERNOON OF MAY 9, 1990, TEXACOINFORMED EXXON THAT A DAMAGED SUBSEA ONE-INCH VALVE ON AN OUT-OF-SERVICE EXXON PIPELINE WAS BELIEVED TO BE THE SOURCE OF THE SPILL. EXXON CONTACTED THE MMS AND USCG AND ADVIXED THEM OF THIS INFORMATION ON THE SAME DAY. THIS PIPELINE (MMS PIPELINE SEGMENT NO. 4030) ORGINATES AT EXXON'S EUGENE ISLAND BLOCK314 "B" PLATFORM AND TERMINATES AT A SUBSEA TIE-IN TO A EUGENE ISLAND PIPELINE SYSTEM. THE ONE-INCH VALVE WAS LOCATED AT THE SUBSEA TIE-IN AND WAS TO BEUSED DURING THE INSTALLATION OF SEGMENT 4030 TO PRESSURE TEST THE SUBSEA COMPONENTS AND DURING ABANDONMENT FOR RELIEVING PRESSURE BETWEEN THE BLOCK VALVEAND CHECK VALVE. EXXON HAS NOT PRODUCED OIL THROUGH THIS PIPELINE SINCE OCTOBER, 1988, AT WHICH TIME THE PIPELINE WAS FLUSHED WITH INHIBITED SEAWATER AND AN EIGHT-INCH SUBSEA BLOCK VALVE WAS CLOSED ON EXXON'S LINE NEAR THE TIE-IN. FOLLOWING THE DAMAGE TO THIS ONE-INCH VALVE, CRUDE OIL APPARENTLY FLOWED THROUGH AN OPEN VALVE OWNED BY AND LOCATED ON THE EUGENE ISLAND PIPELINE SYSTEMINTO THE TIE-IN SPOOL AND OUT OF THE HOLE CAUSED BY THE BREAKING OFF OF THEONE-INCH VALVE. DIVERS RECOVERED THE DAMAGED ONE-INCH VALVE. THE SOURCE OFDAMAGED TO THE VALVE REMAINS UNKNOWN, ALTHOUGH APPARENTLY SUBSTANTIAL EXTERNAL FORCE WOULD HAVE BEEN REQUIRED TO BREAK OF THE VALVE FROM THE PIPELINE. PIPELINE 4030 HAS BEEN SINCE DISCONNECTED FROM THE SUBSEA TIE-IN & BLIND FLANGES ARE BEING INSTALLED. ON MAY 14, 1990, EXXON CONTACTED THE NRC FOR THE PURPOSE OF UPDATING REPORT NO. 20677. THE NRC ADVISED THAT THE UPDATE SHOULD BE CALLED TO THE USCG, MORGAN CITY MSO WHICH WAS DONE ON MAY 15,1990. THE MSO INDICATED THAT THE USCG WOULD PROVIDE THIS INFORMATION TO THE DOT OFFICE OFPIPELINE SAFETY.
2017-09-29 08:50 | YES | NO | 19900073 | 1990-05-21 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-04-20 | 17 | AZ | PIMA |  | NO |  | NO | ON RIGHT-OF-WAY BETWEEN I-10 FREEWAY, WESTBOUND FRONTAGE ROAD AND RAILROAD TRACK. ONE MILE SOUTHEAST OF MARANA OFF-RAMP, EXIT 236. | 18081 | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 2444 | 138 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1540 | 1518 | YES | 24 | 2025 | 1 | 55 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS & ENGINEERING | 2134867720 | AT APPROXIMATELY 0017, 4/20/90, OPERATOR AT TUCSON TERMINAL NOTICED A SHARP DROP IN PRESSURE AND REPORTED IT TO SCHEDULER AND THE PIPELINE WAS SHUT DOWN. MARANA POLICE DEPARTMENT REPORTED TO TUCSON TERMINAL AT 0117, 4/20/90, THE SIGHTING OF THE LEAK. FIELD PERSONNEL AND CONTRACT PERSONNEL WERE DISPATCHEDTO THE SCENE IMMEDIATELY. THE LEAK WAS CAUSED BY UNKNOWN PERSONS SCRAPING THE PIPELINE AND NOT REPORTING IT.
2017-09-29 08:50 | YES | NO | 19900074 | 1990-05-21 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-04-21 | 906 | CA | YOLO | SACRAMENTO | NO |  | NO | PLMP 56.99, 80 FEET NORTH OF RAILROAD TRACK. | 18278 | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 2255 | 1405 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 245 | YES | 24 | 1464 | 1 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS & ENGINEERING | 2134867720 | WHILE TRENCHING FOR THE LAYING OF A FIBER OPTIC COMMUNICATION CABLE, TRENCHING MACHINE SCRAPED THE PIPELINE FOR SEVERAL HUNDRED FEET AND THEN GOUGED IT.
2017-09-29 08:50 | YES | NO | 19900075 | 1990-05-14 | 1682 | BP OIL PIPELINE CO | NO | 1990-04-18 | 615 | NJ | BURLINGTON |  | NO |  | NO | APPROX. 50 FEET OFF OF THE EAST EDGE OF THE NORTHBOUND SIDE OF THE NJ TURNPIKE NORTH OF RANCOCAS CREEK AND APPROX. 1,000 YD. SOUTH OF BURLINGTON COUNTY RT 626. | 17771 | LINE PIPE | WELDING FITTING |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1400000 | 1165117.6826 | 2350512.9753 | JET FUEL | 3 | 1400 | 60 | NO | NO | 16 | 0.28 | 52000 | WELDED |  | 1100 | 700 | YES | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | D.K. NEUWERTH, EASTERN REGION SUPERINTENDENT | 2163514777 | A TRUCK OWNED BY DARBY FROCKS LIMITED WAS TRAVELING NORTH ON THE NEW JERSEY TURNPIKE WHEN IT LEFT THE EAST SIDE OF THE ROAD. IT CLIPPED A GUARDRAIL, WENT THROUGH A MARSHY DITCH, KNOCKED DOWN TWO MEDIUM SIZED TREES, KNOCKED DOWN ABLOCK VALVE SECURITY FENCE, AND SMASHED INTO THE HARBOR PIPELINE SYSTEM'S NORTH RANCOCAS CREEK BLOCK VALVE. THE BLOCK VALVE WAS NOT DAMAGED, BUT A 4" BRANCH CONNECTION ADJACENT TO THE ABOVE GROUND BLOCK VALVE WAS SHEARED COMPLETELY OFF OF THE PIPELINE LEAVING A HOLE IN THE PIPE APPROXIMATELY 4" IN DIAMETER. ALARMS WERE RECEIVED IN BP OIL PIPELINE COMPANY'S VANDALIA, OH DISPATCHING CENTER. (RATE OF CHANGE ALARMS ON PRESSURE AND FLOW) THE DISPATCHER SHUTDOWN THE PIPELINE AT 06:15 AND NOTIFIED FIELD OPERATING PERSONNEL. THE NEW JERSEY STATE POLICE CALLED FIELD PERSONNEL AT ABOUT 06:45 AND GAVE THE LOCATION OF THE TRUCK ACCIDENT. FIELD PERSONNEL CLOSED THE SOUTH RANCOCAS CREEK BLOCKVALVE AT 07:10 AND THE NORTH RANCOCAS CREEK BLOCK VALVE AT 07:15. ALL FLOW STOPPED AS SOON AS THE SECOND VALVE WAS CLOSED.
2017-09-29 08:50 | NO | NO | 19900076 | 1990-05-18 | 443 | AMOCO PIPELINE CO | NO | 1990-05-03 | 2000 | IL |  |  | YES | 27 57'20.4"-94 1'37.528" | YES | ON 8" FLANGE AT BOTTOM OF OIL RISER PIPING (SKETCH ATTACHED). |  | LINE PIPE | VALVE |  | 1980 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2 | 0 | NO | NO | 8 | 0.5 | 3506 | FLANGED |  | 2160 | 1300 | YES | 24 | 3200 | 12 | 80 | NO DATA | Null | YES | OTHER | UNKNOWN | OTHER | LINE VIBRATION | Null | NO DATA |  | Null | Null | HOWARD B. SPALDING | 4099483407 | AT 2000 ON MAY 3, 1990, PERSONNEL ON CNG'S H.I.A-571 OBSERVED "BLOSSOMS" ON THE WATER SURFACE NEAR THE 8" OIL RISER. CNG'S NEW ORLEANS OFFICE DEPLOYED CAL DIVE INTERNATIONAL TO BEGIN DEPLOYING DIVERS TO INVESTIGATE. A LEAKING FLANG AT BOTTOM OF THE RISER WAS FOUND MID-MORNING ON MAY 6, 1990. THE FLANGE WAS TIGHTENED AND LEAK CHECKS WERE MADE TO INSURE THAT THE REPAIR WAS SUCCESSFUL.
2017-09-29 08:50 | YES | NO | 19900077 | 1990-05-24 | 19335 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1990-04-23 | 930 | TX | CROCKETT |  | NO |  | NO | SECTION 68, BLOCK 1, I&GN RR CO. SURVEY (SEE ATTACHED). | 18558 | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 38700 | 32207.1817 | 64974.8944 | CRUDE OIL | 3 | 3000 | 1000 | NO | NO | 12.75 | 0.38 | 25000 | COUPLED |  | 850 | 135 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWIN H. GRIPP, DISTRIC MANAGER | 9159497019 | LINE WAS SHUT DOWN 10 DAYS PRIOR TO DISCOVERY OF THE LEAK. LEAK WAS REPORTED BY AIR PATROL AT 0930 ON APRIL 23,1990. BLOCK VALVES WERE CLOSED BY 1020. COMPANY AND CONTRACT EMPLOYEES AT THE SITE WITH BACKHOE, BOAT, BOOMS, PUMPS, AND VACUUM TRUCKS BY 1030. OIL WAS CONTAINED IN A NATURAL DEPRESSION AND THERE WAS NO DANGER TO THE PECOS RIVER (APPROXIMATELY 150' DISTANCE). OIL WAS PICKED UP BY VACUUM TRUCKS. LEAK WAS DUG OUT AND CLAMPED OFF BY 1630. AT THEREQUEST OF LANDOWNER, OILY POCKETS WERE BURNED AFTER OBTAINING PERMISSION FROM THE TEXAS AIR CONTROL BOARD. THE LINE WAS DRAINED, CUT OUT AND A 40' SECTION OF PIPE REPLACED. AS RAINS OCCUR, WATER IS BEING PUMPED OUT OF THE NATURAL BASIN. BACKFILL WILL BE COMPLETED DURING MAY, AND THE AREA WILL BE COVERED WITH DRY DIRT.
2017-09-29 08:50 | YES | NO | 19900078 | 1990-05-21 | 18718 | SUN PIPELINE CO | YES | 1990-04-27 | 1715 | PA | PHILADELPHIA |  | NO |  | YES | FORT MIFFLIN TERMINAL/ PUMPHOUSE MANIFOLD AREA HOG ISLAND ROAD. PHILADELPHIA, PA. 19153. |  | PUMPING STATION | VALVE |  | 1941 | OTHER | VALVE FAILED/METAL FATIGU | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | CRUDE OIL | 1 | 347 | 294 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT, MANAGER, RISK MANAGERMENT | 9185866231 | CRUDE OIL WAS BEING TRANSFERRED FROM FT. MIFFLIN #852 TANK TO THE PHILADELPHIA REFINERY. THIS OPERATION INCLUDED USING #9 SUCTION LINE, #3 AND #4 PUMPS,#6 DISCHARGE LINE AND THE 16" FM-1 LINE. DURING THIS OPERATION, A FAILED VALVE WAS DISCOVERED AND THE TRANSFER PROCEDURE WAS SUBSEQUENTLY STOPPED. CONTAINMENT AND CLEANUP EFFORTS WERE IMMEDIATELY INITIATED.
2017-09-29 08:50 | YES | NO | 19900079 | 1990-05-31 | 26134 | MOBIL PIPELINE CO - MOBIL WEST COAST PIPELINE | NO | 1990-05-08 | 611 | CA | LOS ANGELES |  | NO |  | NO | VALENCIA GOLF COURSE SECTION 1 T4N-R16W. | 6787 | LINE PIPE | PIPE |  | 1972 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | CRUDE OIL | 1 | 240 | 210 | NO | NO | 12 | 0.25 | 2039 | WELDED |  | 1440 | 1043 | YES | 8 | 1831 | 10 | 85 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.D GREGOR, MANAGER OF OPERATIONS, WEST COAST PIPE LINES. | 2132122910 | THE PIPELINE COATING IN THIS AREA WAS DISBONDED, WHICH SHIELDED THE CATHODICPROTECTION CURRENT FROM THE PIPE, ALLOWING EXTERNAL CORROSION TO PENETRATE THE WALL OF THE PIPELINE. THE PIPELINE WAS REPAIRED BY INSTALLING A FULL ENCIRCLEMENT SLEEVE AND HAND WRAPPING THE SECTION OF PIPE WITH POLYKEN TAPE.
2017-09-29 08:50 | YES | NO | 19900080 | 1990-05-31 | 443 | AMOCO PIPELINE CO | YES | 1990-04-24 | 1205 | TX | PARKER | MILLSAP | NO |  | NO | MEMEXIA TO GRAFORD NUMBER 2-8" LINE. MARKER POST 116. APPROX. 3 MI. SOUTH OF HWY 180 AND 1/2 MI. EAST OF FM.113. MAP ATTACHED. | 18843 | LINE PIPE | PIPE |  | 1957 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 100 | 35 | NO | NO | 8 | 0.32 | 0 | WELDED |  | 700 | 0 | YES | 24 | 875 | 5 | 74 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.H. STEPHENS, PIPELINE MAINTENANCE FOREMAN | 8175622381 | LEAK WAS REPORTED BY A PILOT FROM MINERAL WELLS AT 12:05 PM. 4/24/90. CAUSEOF THE LEAK WAS A RUPTURED LINE PIPE. THE LINE WAS BEING EVACUATED WITH NITROGEN TO IDLE THE SYSTEM FROM MEXIA TO GRAFORD. THE LEAK ITSELF WAS NOT IN THE LAKE, BUT WAS A COUPLE OF HUNDRED FEET UP A SLOPE AND THE CRUDE RAN DOWN INTO THE LAKE. THE OIL WAS CONTAINED MAINLY IN THE NORTH WEST CORNER OF THE LAKE WHERE WE IMMEDIATELY STARTED SKIMMING WITH VACUUM TRUCKS. THE IN-COMINGCREEKS WERE BOOMED OFF ALONG WITH THE SPILLWAY AND THE SOUTH END OF THE LAKE. ALSO BOOMED OFF WATER INTAKE. BOOMS ARE STILL IN PLACE.
2017-09-29 08:50 | NO | NO | 19900081 | 1990-05-31 | 12628 | MOBIL PIPELINE CO | YES | 1990-04-26 | 900 | TX | COMANCHE | DE LEON | NO |  | NO | LEAK OCCURED ON MPLCO.'S 12" CRUDE BYPASS LINE WITHIN MPLCO.'S DELEON STATION PROPERTY LOCATED IN COMANCHE COUNTY, 6 MI. NORTHWEST OF DELEON, TX ON HWY. 16. | 19127 | PUMPING STATION | PIPE |  | 1943 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 802 | 295 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582381 | DUE TO RISING FLOOD WATERS CAUSED BY UNUSUALLY HEAVY RAINS, (12"+), MPLCO.BEGAN SHUTDOWN AND BYPASS PROCEDURES ON ITS DELEON PUMP STATION. FOLLOWING STATION SHUTDOWN, STATION PERSONNEL OBSERVED A CRUDE OIL LEAK IN THE STATION YARD, WHICH WAS UNDERWATER, AND PROCEEDED TO ISOLATE THE LEAK BY SHUTTING DOWN THE SYSTEM AND CLOSING UPSTREAM STATION BLOCK VALVES. THE LEAK WAS ISOLATED AND CONTAINED WITH SANDBAGS AND HAY BALES. THE SECTION OF BYPASS LINE CONTAINING INTERNAL CORROSION WAS REPLACED WITH A NEW SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19900082 | 1990-05-31 | 12628 | MOBIL PIPELINE CO | NO | 1990-04-26 | 1115 | TX | EASTLAND | GORMAN | NO |  | NO | LEAK OCCURED ON MPLCO. 12" CRUDE OIL PIPELINE AT MP 203.3, 3/4 MILE SOUTHWEST OF THE TOWN OF GORMAN, TX, NEAR FM 8. | 19155 | LINE PIPE | PIPE |  | 1943 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1260743 | 1049224.2589 | 2116709.1285 | CRUDE OIL | 1 | 2583 | 1732 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 536 | 0 | YES | 2 | 590 | 5 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582381 | DURING THE EMERGENCY SHUTDOWN AND BYPASS OF OUR DOWNSTREAM STATION AT DELEON, THE PIPELINE BETWEEN CLYDE STATION AND DELEON STATION WAS SUBJECT TO HIGHER THAN NORMAL OPERATING PRESSURE, THUS CAUSING A FAILURE AT MP 203.3 IN A CORRODED AREA OF THE PIPE NEAR SHINOAK SPRING BRANCH. EMERGENCY PROCEDURES WEREINITIATED. BOOMS WERE DEPLOYED AT SEVERAL LOCATIONS ALONG SHINOAK BRANCH AND THE SABANA RIVER ABOVE PROCTOR LAKE. PERMANENT REPAIRS WERE MADE BY REPLACING THIS SECTION OF PIPELINE.
2017-09-29 08:50 | YES | NO | 19900083 | 1990-05-31 | 10313 | KOCH PIPELINE INC | YES | 1990-04-26 | 930 | MO | HARRISON |  | NO |  | NO | SEE ATTACHED DRAWING. | 19114 | LINE PIPE | PIPE |  | 1980 | OTHER | INT. CORROSION (UNKNOWN) | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 75 | 60 | NO | NO | 24 | 0.28 | 1405 | WELDED |  | 829 | 202 | YES | 24 | 1151 | 11 | 80 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JEROME H. KLEIN, DIVISION MANAGER | 6124592424 | COTTAGE GROVE WAS NOTIFIED OF A LEAK AT 9:50 AM. APRIL 26, 1990, LOCATED 2 1/4 MILES SOUTH OF BETHANY STATION, MILEPOST 248, SECTION 11-14, 66N, 27W, HARRISON COUNTY, MISSOURI. PUMPS WERE NOT RUNNING AT THE TIME SO BLOCK VALVE NEAR CAINSVILLE STATION WAS CLOSED TO ISOLATE THE LEAK AREA. BLOCK VALVE AT BETHANY STATION WAS LEFT OPEN TO REDUCE PRESSURE ON THE LINE. OUR MAINTENANCE FOREMEN WAS TRANSPORTED BY HELICOPTER, ALONG WITH SOME SORBENT BOOMS, ARRIVING AT BETHANY STATION AT 2:00 PM. AFTER UNLOADING THE HELICOPTER, BOOM DEPLOYMENT BEGAN AT 2:35 PM. PERSONNEL FROM THE STATE OF MISSOURI DNR ARRIVED AT 2:45 PM. TO TAKE WATER SAMPLES AND CHECK THE DEPLOYMENT OF THE BOOMS. DNR OFFICIALSFOUND THE OIL CONTAINMENT TO BE SATISFACTORY. AT 4:00 PM. OUR CONTRACTOR ARRIVED AND CONSTRUCTED AN EARTHEN DIKE WHICH ENCLOSED THE LEAK AREA.
2017-09-29 08:50 | NO | NO | 19900084 | 1990-05-29 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1990-04-25 | 915 | MI | MACKINAC |  | NO |  | YES | 600 FT N OF US HWY 2, ON PRIVATE PROPERTY APPROX. 1/4 MILE W OF HIAWATHA NATIONAL FOREST'S W BOUNDARY IN MACKINAC COUNTY, MI | 19028 | LINE PIPE | LONGITUDINAL WELD |  | 1953 | OTHER | PINHOLE LEAK IN SEAM. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20200 | 16810.9837 | 33914.5444 | CRUDE OIL | 1 | 15 | 5 | NO | NO | 30 | 0.28 | 52000 | WELDED |  | 638 | 342 | YES | 12 | 815 | 1 | 53 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR, GEN. MGR. CORPORATE & TECHNICAL SERVICES | 7153941404 | DURING A ROUTINE LINE INSPECTION BY THE AERIAL PATROL HELICOPTER,A PATCH OF OIL WAS DISCOVERED ON THE GROUND. LINE WAS SHUTDOWN AT 0922 MST. LAKEHEAD EMERGENCY MAINTENANCE PERSONNEL ARRIVED AT THE LEAK SITE AT 1030 MST. AFTER EXCAVATING THE AREA ,A PINHOLE LEAK WAS DISCOVERED IN THE HEAT AFFECTED ZONE OF THE LONGITUDINAL SEAM. THE PINHOLE LEAKED AN ESTIMATED 15 BARRELS WITH 5 BARRELS OF CRUDE OIL RECOVERED. CLEAN-UP ACTIVITIES STARTED IMMEDIATELY. THEOIL SATURATE SANDY SOIL IS TO BE HAULED TO AN APPROVED LANDFILL. THE PINHOLE WAS REPAIRED WITH AN 18" X 30" DIAMETER PLIDCO SPLIT SLEEVE, WELDED AND MAG. PARTICLE TESTED. THE LINE WAS RESTORED TO FULL OPERATING PRESSURE ON APRIL26, 1990.
2017-09-29 08:50 | YES | NO | 19900085 | 1990-06-15 | 18781 | SUN MARINE TERMINALS | NO | 1990-05-16 | 1830 | TX | JEFFERSON | NEDERLAND | NO |  | NO | EAST TEXAS 10" PUMP STATION LOCATED 1/2 MILE NORTH OF HIGHWAY 347 AND 1 MILE SOUTH OF SHIP CHANNEL. |  | PUMPING STATION | VALVE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | CRUDE OIL | 1 | 70 | 70 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT, MANAGER RISK MANAGEMENT | 9185866231 | USING NEW PUMP STATION AT IRC TO DELIVER UP E.T. 10". DURING LINE UP OPERATOR FAILED TO CLOSE SUCTION TO E.T. 10" PUMP STATION CAUSING RELIEF VALVE OR SUCTION SIDE OF #1 PUMP AT E.T. PUMP STATION TO OPEN AND RUN SUMP OVER.
2017-09-29 08:50 | YES | NO | 19900086 | 1990-06-12 | 809 | ARCO PIPE LINE CO | YES | 1990-05-17 | 1900 | TX | ROBERTSON |  | NO |  | NO | OUTBOARD SEAL ON #2 UNIT AT HEARNE STATION, APPROXIMATELY 4 MILES N.E. OF HEARNE, TX. | 22539 | PUMPING STATION | PUMP |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | OUTBOARD SEAL FAILURE | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 25360 | 21105.2746 | 42577.8636 | GASOLINE | 3 | 128 | 115 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.D. HARRIS, MANAGER PRODUCT BUSINESSES | 3163311300 | OUTBOARD SEAL ON #2 UNIT FAILED CAUSING 128 BBLS OF UNLEADED GASOLINE TO SPILL OUT . 115 BBLS WERE RECOVERED FOR A NET LOSS OF 13 BBLS.
2017-09-29 08:50 | YES | NO | 19900087 | 1990-06-13 | 26134 | MOBIL PIPELINE CO - MOBIL WEST COAST PIPELINE | NO | 1990-05-11 | 1650 | CA |  | INGLEWOOD | NO |  | NO | 95TH STREET AND ASH STREET IN THE CITY OF INGLEWOOD. | 90-6845 | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 340000 | 282957.1515 | 570838.8654 | CRUDE OIL | 1 | 25 | 10 | NO | NO | 10 | 0.25 | 52000 | WELDED |  | 1200 | 650 | YES | 8 | 1750 | 10 | 81 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | MR. J.R. JEFFRIES, MANAGER, WCPL | 2132122910 | EXTERNAL CORROSION PENETRATED PIPE WALL DUE TO ISOLATED COATING DAMAGE. THEPIPELINE WAS REPAIRED BY WELDING A FULL ENCIRCLEMENT SLEEVE AND HAND WRAPPING THE SECTION OF PIPE WITH POLYKEN TAPE.
2017-09-29 08:50 | YES | NO | 19900088 | 1990-06-14 | 400 | AMERICAN PETROFINA PIPE LINE CO | YES | 1990-05-09 | 1822 | TX | NUECES | ARANSAS PASS | NO |  | NO | AMERICAN PETROFINA PIPE LINE COMPANY SHIP DOCK ON CORPUS CHRISTI SHIP CHANNEL. | 21243 | TANK FARM | OTHER | OIL TRANSFER HOSE ON SHIP | 1983 | OTHER | FAILED DOCK HOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 13315.6307 | 26863.0054 | CRUDE OIL | 1 | 50 | 32 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.W. BRUTON - TERMINAL SUPERINTENDENT | 5127583571 | EXACT CAUSES NOT KNOWN BUT THEORIZED TO HAVE BEEN CAUSED BY LONG TERM DETERIORATION OR PREVIOUS UNKNOWN DAMAGED TO HOSE. CARGO TRANSFER HOSE FAILED DURING DISHCARGE OF CARGO FROM SHIP CAUSING SPILL. SPILL WAS CLEANED UP AND NEW HOSE WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19900089 | 1990-06-15 | 26086 | SEADRIFT PIPELINE CORP | NO | 1990-05-07 | 1335 | TX | UNKNOWN | TEXAS CITY | NO |  | NO | ADJACENT TO STATE HIGHWAY 146, ONE-HALF MILE NORTH OF LOOP 197. | 20843 | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 58255.8841 | 117525.6488 | L. P. G. | 2 | 450 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1430 | 875 | YES | 24 | 2160 | 1 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | J.L. WYATT, ENVIRONMENTAL ENGINEER | 5127883176 | SHEET PILING WAS BEING INSTALLED BY AN INDEPENDENT CONTRACTOR TO ALLOW WORK ON AN ADJACENT AMOCO PIPELINE. THE SEADRIFT PIPELINE WAS STRUCK BY HE PILINGCAUSING A SMALL PUNCTURE. THE SPECIFIC PIPELINE THAT WAS STRUCK COULD NOT BE IDENTIFIED FOR SEVERAL HOURS BECAUSE OF THE NUMBER OF PIPELINES IN THE AREA AND THE SMALL SIZE OF THE LEAK. THE SEADRIFT PIPELINE WAS LOCATED SEVERAL FEET FROM THE INDICATED POSITION ON THE DRAWING. PROBING FAILED TO PINPOINT THE EXACT LOCATION. NO INJURIES RESULTED FROM THE ACCIDENT. SOUTHBOUND TRAFFIC ON HIGHWAY 146 WAS REROUTED FOR SEVERAL HOURS TO MINIMIZE PUBLIC EXPOSURE.
2017-09-29 08:50 | NO | NO | 19900090 | 1990-06-18 | 22430 | WEST SHORE PIPE LINE CO | YES | 1990-05-15 | 1249 | IL | DU PAGE | OAK BROOK | NO |  | NO | EAST SIDE OF HIGHWAY 83 AND 100 FEET NORTH OF 16TH STREET. | 22060 | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 10 | 2 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1170 | 900 | YES | 24 | 1460 | 1 | 61 | NO DATA | Null | YES | OTHER | UNKNOWN | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KENNETH C. ANDREEN, AREA MANAGER | 7082573740 | A CONTRACTOR WORKING IN THE GENERAL VACINITY OF THE LEAK CALLED AND NOTIFIEDUS OF PRODUCT ON THE GROUND AT 12:49. THE PIPELINE WAS IMMEDIATELY SHUT DOWN. UPON EXCAVATION OF THE PIPELINE, IT WAS FOUND THAT A GUARDRAIL POST HAD BEEN AUGERED INTO THE GROUND AND THE AUGER HAD DENTED OUR PIPELINE IN 2 PLACESABOUT 6 INCHES APART. A CRACK HAD DEVELOPED BETWEEN THE 2 DENTS. INDICATIONS ARE THAT THE GUARDRAIL WAS INSTALLED DURING HIGHWAY 83 RECONSTRUCTION WORKSOMETIME IN THE FALL OF 1989.
2017-09-29 08:50 | YES | NO | 19900091 | 1990-06-18 | 18273 | SHELL PIPE LINE CORP | YES | 1990-05-30 | 1730 | TX | FORT BEND | KATY | NO |  | NO | RANCHO/KATY STATION | 25745 | PUMPING STATION | OTHER | DOPPLER LINE INTEGRITY ME | 1987 | OTHER | PROBE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 13315.6307 | 26863.0054 | CRUDE OIL | 1 | 60 | 59 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. HOLDEN, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | DOPPLER LINE INTREGRITY METER WAS REMOVED - CONNECTION WAS CAPPED AND LINE PUT BACK IN SERVICE.
2017-09-29 08:50 | YES | NO | 19900092 | 1990-06-18 | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-05-23 | 1700 | CO | BACA | UNKNOWN | NO |  | NO | MCCULLOCH-BORGER 6" NGL LINE - MP 125-31+05 SEC. 27, T34S, R37W, 7 MILES WEST, 3 MILES SOUTH AND 1/4 EAST OF CAMPO, CO. |  | LINE PIPE | LONGITUDINAL WELD |  | 1947 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 8800 | 7323.5969 | 14774.653 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1320 | 1020 | YES | 8 | 2088 | 5 | 82 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | LINE FLYER REPORTED DEAD VEGITATION OVER PIPELINE AT 5:00 PM.M ON MAY 23, 1990. LEAK WAS CONFIRMED ON MAY 24, 1990. DENVER MAINTENANCE CREW FOUND AND REPLACED NO SIGNIFICANT INTERNAL OR EXTERNAL CORROSION WAS NOTED.
2017-09-29 08:50 | YES | NO | 19900093 | 1990-06-25 | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1990-05-09 | 710 | TX | MIDLAND | UNKNOWN | NO |  | NO | NW/4 OF THE NE/4 OF SEC. 19, BLOCK 36, T-2-S, T&P RR SURVEY (SEE ATTACHED MAP). | 21076 | LINE PIPE | PIPE |  | 1929 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8322.2692 | 16789.3784 | CRUDE OIL | 1 | 2108 | 2008 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1012 | 12 | YES | 8 | 1266 | 7 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JIMMY MUNN - SR. REGULATORY AFFAIRS REP. | 9152673673 | A BULLDOZER OPERATED BY MACHEM CONTRACTING, INC. (CONTRACTED TO MWJ PRODUCING COMPANY) WAS DIGGING A PIT FOR WORK-OVER OPERATIONS ON THE MWJ FASKIN 19 LEASE WHEN THE BULLDOZER STRUCK THE 10-INCH PIPELINE CAUSING IT TO LEAK. THE BULLDOZER OPERATOR IMMEDIATELY BEGAN TO DIG A SERIES OF PITS IN WHICH TO CONTAIN THE SPILLED CRUDE OIL. VACUUM TRUCKS REMOVED THE CRUDE FROM THE PITS AND TRANSPORTED IT TO TANKAGE.
2017-09-29 08:50 | YES | NO | 19900094 | 1990-06-25 | 4906 | EXXON PIPELINE CO | NO | 1990-05-23 | 1000 | TX | ECTOR |  | NO |  | NO | LEAK OCCURRED ONOUR COMPANY PROPERTY AT OUR ECTOR STATION, APPROXIMATELY 15 MILES NORTHWEST OF ODESSA, TEXAS. | 23487 | PUMPING STATION | PUMP |  | 1988 | OTHER | PUMP CASE BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2200 | 1830.8992 | 3693.6632 | CRUDE OIL | 1 | 170 | 130 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.E. COX, ENVIRONMENTAL AND REGULATORY COMPLIANCE MGR. | 7136565521 | A PIECE OF RUBBER FROM A POLY PIG LODGED IN THE IMPELLER OF A CENTRIFUGAL PUMP, CAUSING THE IMPELLER TO BECOME IMBALANCED. AT 3600 RPM, THIS CAUSED IT TO CRACK THE PUMP CASE ALLOWING OIL TO ESCAPE ON THE GROUND. EXXON PIPELINE COMPANY EMPLOYEES WERE AT THE STATION WHEN THE BREAK OCCURRED. THE PUMP WAS SHUT DOWN AND LINES WERE BLOCKED AS SOON AS POSSIBLE. A VACUUM TRUCK WAS CALLED, AS WELL AS A BACK HOE. THE VACUUM TRUCK PICKED UP 130 BBLS. OF 170 BBLS.SPILLED, LEAVING A NET LOSS OF 40 BBLS. THE BACK HOE AND EXXON REPAIR CREW CLEANED UP THE SPILL AND TURNED THE OIL SOAKED GROUND. BY 3:00 PM OF 5/23/90, OPERATIONS WERE RESUMED.
2017-09-29 08:50 | YES | NO | 19900095 | 1990-06-25 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1990-06-07 | 740 | KS | ELLSWORTH |  | NO |  | NO | THREE(3) MILES NORTH, THREE (3) MILES EAST OF LORRAINE, KANSAS. SECTION 36, TOWNSHIP 16S, RANGE 9W PIPELINE STATION NUMBER: 409+67. | 25678 | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 45772.4804 | 92341.5812 | BUTANE | 2 | 1810 | 0 | NO | NO | 8.63 | 0.22 | 2132 | WELDED |  | 1260 | 522 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | GEORGE A. ROOD, VICE PRESIDENT OPERATIONS | 7138537876 | JOMAX CONSTRUCTION WAS REFURBISHING THE THIRTY INCH (30") "D" LINE FOR NORTHERN NATURAL GAS CO. ENRON'S EIGHT INCH (8") LINE WAS ORIGINALLY FLAGGED AND MARKED ON 5/10/90 BY ENRON LIQUIDS PIPELINE LINE CO. PERSONNEL. THE EIGHT INCH (8") LINE RUNS UNDERNEATH NORTHERN'S THIRTY INCH (30") "D" LINE. NORTHERN'S LINE HAD BEEN REMOVED FROM THE DITCH AND SET-UP ON THE BANK SO JOMAX CONSTRUCTION COULD WORK ON IT. ENRON'S EIGHT INCH (8") LINE WAS FLAGGED AND DEPTH MARKED ON THE FLAGS, THIS WAS EIGHTEEN INCHES (18") BELOW THE BOTTOM OF NORTHERN'S THIRTY INCH (30") "D" LINE. MR. NICK BURTRIM, JOMAX CONSTRUCTION, SAID THAT THEY CAME BACK TO CLEAN OUT OR RE-DITCH AND COVERED OUR FLAGS ON THE RE-DITCH, THEY DID NOT CALL ENRON AND THEY HIT OUR LINE AND PUNCTURED A HOLE INIT APPROXIMATELY 4 INCHES LONG (4") AND THREE EIGHTS OF AN INCH (3/8") WIDE. ONE OPERATOR FOR JOMAX, DUG THE ORIGINAL DITCH AND ANOTHER OPERATOR WAS USED FOR THE RE-DITCH WORK. ONE OF OUR FLAGS WAS RETRIEVED FROM THE BOTTOM OF THE DITCH.
2017-09-29 08:50 | YES | NO | 19900096 | 1990-06-25 | 7349 | HOECHST CELANESE CHEMICAL GROUP INC | NO | 1990-06-08 | 810 | TX | HUTCHINSON | BORGER | NO |  | NO | BLOCK Y SECTION 11 MORRIS & CUMMINGS SURVEY, HUTCHINSON COUNTY, TEXAS. | 25872 | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 9154.4961 | 18468.3162 | BUTANE | 2 | 850 | 0 | NO | NO | 6 | 0.19 | 11514 | WELDED |  | 650 | 55 | YES | 24 | 1100 | 2 | 66 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | SEE BELOW | NO | NO | DANIEL A. LONG , STAFF ENGINEER | 8066657479 | PART J- #3: AERIAL SURVEY FLOWN EVERY 2 WEEKS. PIPELINE WAS INSPECTED 3 DAYS PRIOR TO START OF EXCAVATION & 11 DAYS PRIOR TO ACCIDENT. PIPELINE SIGNS WERE IN PLACE WITHIN 200 FT. OF EACH SIDE OF ACCIDENT LOCATION.OUR 6" PIPELINE WAS STUCK BY A DITCHING MACHINE OPERATED BY D.E. RICE CONSTRUCTION CO. OF BORGER, TEXAS UNDER CONTRACT BY PHILLIPS PIPELINE CO. HOECHST CELANESE PERSONNEL FOLLOWED EMERGENCY PLAN TO BLOCK IN VALVES AND REPORT TO SITE. LINE WAS DEPRESSURED AND REPAIRED. NO FIRES, EXPLOSION, OR INJURIES RESULTED.
2017-09-29 08:50 | YES | NO | 19900097 | 1990-06-27 | 22610 | WILLIAMS PIPELINE CO | YES | 1990-05-19 | 100 | IA | WOODBURY | SIOUX CITY | NO |  | NO | SIOUX CITY TERMINAL # C212 | 22730 | TANK FARM | TANK |  | 1947 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 12500 | 10402.8365 | 20986.723 | TRANSMIX (PART. REFINED PETRO) | 3 | 706 | 468 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | ON THE MORNING OF MAY 19, 1990, A TANK WAS OVERFILED AT OUR SIOUX CITY TERMINAL RESULTING IN A 706 BBL RELEASE OF TRANSMIX (X9). THE OVERFILL OCCURRED AS A RESULT OF A TANK TRANSFER OPERATION INVOLVING THREE SEPARATE PRODUCT TANKS (#753, #752, AND #110). THE TRANSFER WAS INITIATIONG FROM TANK #752 TO TANK #110 (1000 BBL PUP TANK) VIA THE RECEIVE LINE MANIFOLD OF TANK #753. THE TRANSFER WAS NECESSARY TO EMPTY TANK #752 IN PREPARATION FOR A INSPECTION OF THE TANK BOTTOM COATING. TANK #110 IS RARELY USED FOR PRODUCT STORAGE, HENCE IT IS NOT EQUIPPED WITH A HIGH LEVEL ALARM SYSTEM. BEING AWARE OF THIS FACT,TERMINAL PERSONNEL MONITORED THE TRANSFER VIA THE GAUGING ON THE ORIGINATINGTANK #572 AND AS AN ADDITIONAL PRECAUTIONARY MEASURE, SCHEDULED THE TRANSFERDURING DAYLIGHT HOURS. AFTER COMPLETION OF THE TRANSFER EARLY THAT EVENING, HOWEVER, THE OPERATOR FAILED TO PROPERLY ISOLATE TANK #110 FROM THE MANIFOLDING OF TANK #753. THIS ALLOWED PRODUCT FROM #753 TO GRAVITY INTO THE SMALLER TANK #110 AND EVENTUALLY OVERFILLED THE TANK. AT THE TIME, THE LOCATION WAS EXPERIENCING HEAVY THUNDERSTORM ACTIVITY AND HIGH WIND CONDITIONS. THE SITUATION WAS DISCOVERED AROUND 0100 HOURS AFTER A FUEL OIL ODOR WAS DETECTED IN THE AIR. THE RELEASED PRODUCT WAS CONTAINED WITHIN THE DIKED AREA. CLEAN UP ACTIVITY HS BEEN CORRDINATED WITH STATE ENVIRONMENTAL OFFICIALS. A THOROUGH INVESTIGATION OF THE INCIDENT WAS CONDUCTED AND CORRECTIVE MEASURED ARE BEINGINITIATED.
2017-09-29 08:50 | YES | NO | 19900098 | 1990-06-02 | 2552 | COLONIAL PIPELINE CO | YES | 1990-05-20 | 1800 | TN | GRUNDY | MARION | NO |  | NO | SEE ATTACHED SKETCH. | 22888 | LINE PIPE | OTHER | UNKNOWN | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8322.2692 | 16789.3784 | GASOLINE | 2 | 134 | 1 | NO | NO | 10 | 0.22 | 46000 | WELDED |  | 1349 | 875 | YES | 24 | 1795 | 1 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES A. COX, MANAGER-TECHNICAL & REGULATORY | 4048412296 | COLONIAL'S ATLANTA CONTROLER RECEIVED A CALL FROM THE COALMONT TENNESSEE POLICE DEPARTMENT AT 2130 EST ON MAY 20, 1990. A BULLDOZER WORKING IN THE AREA KNOWN AS CLIFTY COVE AT CLIFTY CREEK ON THE MARION COUNTY - GRUNDY COUNTY LINE HAD HIT A PIPELINE AND CAUSED A LEAK. THIS OCCURRED WHERE CLIFTY CREEK FLOWS INTO THE LITTLE SEQUATCHIE RIVER. COLONIAL HAS TWO PIPELINES IN THIS AREAAND BOTH WERE IMMEDIATELY SHUT DOWN BY THE CONTROLLER. CONTRACT AND COLONIAL PERSONNEL WERE DISPATCHED FROM CHATTANOOGA AND NASHVILLE. AT 0230 ON MAY 21, 1990, THE LEAK WAS LOCATED AT THE BOTTOM OF A 1,200 FOOT SLOPE ACCESSIBLE ONLY ON FOOT OR BY TRACT VEHICLE. GASOLINE WAS LEAKING FROM THE PIPELINE THROUGH A GOUGED HOLE. HAND EXCAVATION OF THE LINE BEGAN AT ABOUT 0330 AND A FULL ENCIRCLEMENT REPAIR SLEEVE WAS INSTALLED BY 0900. OHTER PERSONNEL BEGAN INSTALLATION OF CONTAINMENT BOOMS ON THE LITTLE SEQUATCHIE RIVER AT CAMP GLANCZ, ONE MI WEST OF HIGHWAY 28, 5 MILES NORTH OF JASPER, TENNESSEE IN MARION COUNTY, 7 TO 8 MILES DOWNSTREAM FROM THE LEAK SITE. A HELICOPTER SURVEY REVEALED THAT PRODUCT HAD TRAVELED ABOUT TWO MILES DOWNSTREAM. LOCAL GOVERNMENT OFFICIALS WERE NOTIFIED AT APPROXIMATELY 0230 EST AND THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT APPROXIMATELY 1440. THE DEPARTMENT OF TRANSPORTATION, OFFICE OF PIPELINE SAFETY, THE ENVIRONMENTAL PROTECTION AGENCY, TENNESSEE EMERGENCY MANAGEMENT AGENCY AND THE TENNESSEE WATER QUALITY RESPONDED TO THE LEAK. AN EXAMINATION OF THE LEAK SITE REVEALED THAT THE DOZER OPERATOR WAS GRADING AND LOWERING A REMOTE ROAD WHEN HE HIT THE PIPELINE. AN ESTIMATED 134 BARRELS OF PRODUCT ESCAPED FROM THE PIPELINE AND ONLY ABOUT ONE BARREL WAS RECOVERED. THE REST OF THE PRODUCT EITHER EVAPORATED OR WAS TRAPPED IN ROCK FORMATIONS
2017-09-29 08:50 | YES | NO | 19900099 | 1990-06-25 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1990-06-04 | 2218 | IL | MCDONOUGH | GOOD HOPE | NO |  | NO | TOWNSHIP 8 NORTH, RANGE 3 WEST , SECTION 2 5 MILES NORTH AND 2 MILES WEST OF GOOD HOPE, ILLINOIS. |  | LINE PIPE | PIPE |  | 1962 | OTHER | PROPANE VAPORS IGNITED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16.6445 | 33.5788 | L. P. G. | 2 | 1 | 0 | YES | NO | 8.63 | 0.16 | 1881 | WELDED |  | 1354 | 10 | YES | 24 | 1877 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | HWILE DEWATERING THE PIEPLINE, PROPANE VAPORS WERE IGNITED FROM AN UNDETERMINED SOURCE.
2017-09-29 08:50 | YES | NO | 19900100 | 1990-06-25 | 26003 | ARBUCKLE PIPELINE CO | NO | 1990-06-11 | 1715 | OK | MCCLAIN |  | NO |  | NO | W 1/2, SEC.11, T7N-R3W MCCLAIN COUNTY OK. RURAL AREA. | 26406 | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 66578.1533 | 134315.0272 | NATURAL GAS LIQUID | 1 | 4500 | 0 | NO | NO | 8 | 0.16 | 52000 | WELDED |  | 1200 | 530 | YES | 8 | 1554 | 10 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | T.G. LINDSEY , VICE PRESIDENT - OPERATIONS | 4056310496 | THE BULLDOZER OPERATOR WAS IN THE PROCESS OF SETTING A METAL "WHISTLE" (CULVERT/DRAIN PIPE) IN A WASH AND CUTTING THE BANKS DOWN SO VEHICLES COULD CROSS THE WASH. THE LOCATION SELECTED TO BUILD THE CROSSING IS WHERE OUR PIPELINE CROSSES THE WASH. THE WASH RUNS DUE EAST AND WEST AND OUR PIPELINE RUNS DUE NORTH AND SOUTH. THE DOZER HIT OUR PIPELINE ON THE SOUTH BANK OF THE WASH ANDON THE EAST SIDE OF THE PIPE. THE OKLAHOMA ONE-CALL SYSTEM WAS NOT USED ANDWE WERE NOT NOTIFIED IN ANY WAY.
2017-09-29 08:50 | YES | NO | 19900101 | 1990-06-15 | 2731 | CHEVRON PIPELINE CO | NO | 1990-05-13 | 1130 | CA | KINGS | KETTLEMAN | NO |  | NO | CHEVRON U.S.A. - TANK FARM AND KETTLEMAN CITY. | 21854 | TANK FARM | PIPE |  | 1937 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9500 | 7906.1557 | 15949.9095 | CRUDE OIL | 1 | 1150 | 1130 | NO | NO | 12 | 0.38 | 1016 | WELDED |  | 120 | 30 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOE GONZALEZ - OPERATIONS SUPERVISOR | 8057722611 | A LEAK CAUSED BY EXTERNAL CORROSION RELEASED APPROXIMATELY 1150 BBLS OF CRUDE OIL FROM CHEVRON'S 12" PIPING BETWEEN TANK 231 & IT'S KETTLEMAN STATION SWITCHING MANIFOLD. THE RELEASED OIL WAS TOTALLY CONTAINED WITHIN THE EARTHEN TANK BERM OF TANK 231. IT WAS DISCOVERED BY A MEMBER OF CHEVRON'S KETTLEMAN MAINT CREW, WHO HAD NOTICED & INVESTIGATED A CRUDE OIL ODOR. VACUUM TRUCKS WERE USED TOPICK UP AND TRANSFER THE OIL FROM THE LEAK AREA TO ANOTHER STATION. REPAIRS WILL CONSIST OF REPLACING THE CORRODED PIPING WITH APPROX 40' OF NEW 12" PIPE. ALL OIL SOAKED DIRT WILL BE EXCAVATED & REMOVED. THIS MATERIAL WILL BE USED FOR REINFORCING DIVERSION & CONTAINMENT BERMS AT CHEVRON'S KETTLEMAN STA.
2017-09-29 08:50 | YES | NO | 19900102 | 1990-07-06 | 10313 | KOCH PIPELINE INC | YES | 1990-06-17 | 1510 | IA | CLARKE |  | NO |  | NO | SEE ATTACHED DRAWING | 27207 | LINE PIPE | OTHER | UNKNOWN | 1980 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 200 | 125 | NO | NO | 24 | 0.28 | 1405 | WELDED |  | 945 | 495 | YES | 8 | 1313 | 12 | 80 | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JEROME H. KLEIN, DIVISION MANAGER | 6124592424 | COTTAGE GROVE OFFICE WAS NOTIFIED OF A LEAK AT 3:10 P.M. JUNE 17, 1990. IT WAS LOCATED 15 MILES SOUTH OF INDIANOLA, IOWA, MILEPOST 157-158, SE 1/4 OF SECTION 5-73N-24W,LIBERTY TOWNSHIP, CLARKE COUNTY, IOWA. THE LINE PUMPS WERE RUNNING AT THE TIME OF THE ACCIDENT BUT NO ABNORMAL READINGS WERE RECORDED. THE PIPELINE WAS SHUTDOWN AT 3:10 P.M. AT 4:15 PM. THE BLOCK VALVES AT MILEPOST 153 AND 160 WERE CLOSED. ALSO DURING THIS TIME A COFFER DAM WAS BUILT TO CONTAIN THE OIL AT THE LEAK SITE THE TWO CONTAINMENT BOOMS WERE DEPLOYED TO CONTAIN THE FLOW OF OIL IN SKINWAY CREEK. KOCH PERSONNEL AND CONTRACTORES LEFTCOTTAGE GROVE OFFICE AT 8:22 PM. SUNDAY EVENING AND ARRIVED IN DES MOINES, IOWA AT 1:15 AM. MONDAY MORNING. CLEANUP BEGAN MONDAY MORNING AT 6:45 AM. AND AT 1:00 PM PERSONNEL OF THE IOWA DEPARTMENT OF NATURAL RESURCES ARRIVED. AFTER INSPECTING THE LEAK AREA THEY FOUND OUR SPILL CONTAINMENT AND CLEANUP PROCEDURES TO BE SATISFACTORY.
2017-09-29 08:50 | YES | NO | 19900103 | 1990-07-06 | 15774 | PORTAL PIPELINE CO | YES | 1990-06-27 | 900 | ND |  | GLENBURN | NO |  | NO | GLENBURN STATION - SW 1/4, SW1/4 SE1/4 SEC. 1, T158N, R82W. |  | PUMPING STATION | PIPE |  | 1962 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1664.4538 | 3357.8757 | CRUDE OIL | 1 | 150 | 75 | NO | NO | 10 | 0 | 0 | WELDED |  | 20 | 10 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | SULFATE REDUC. BACTERIA | NO DATA |  | Null | NO DATA |  | Null | Null | MARK NICHOLAS, EXECUTIVE VICE PRESIDENT | 7018521087
2017-09-29 08:50 | YES | NO | 19900104 | 1990-07-11 | 5075 | FARMERS UNION CENTRAL EXCHANGE INC - CENEX PIPELIN | YES | 1990-06-18 | 230 | ND | MINOT |  | NO |  | NO | CENEX PIPELINE TERMINAL IS LOCATED AT HIGHWAYS 2 ANS 52 WEST OF MINOT, ND. | 27286 | TANK FARM | OTHER | PROD. SEPARATOR SUMP | 1960 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 590 | 390 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD J. LOHOF, MANAGER, PIPELINES AND TERMINALS | 4062529326 | A DRAIN VALVE WAS MISTAKENLY LEFT OPEN ON A TRUCK LOADING METER CAUSING #2 DIESEL FUEL TO GO TO THE PRODUCTS SEPARATOR SUMP. THE SUMP PUMP HAD BEEN WORKED ON THE PREVIOUS DAY AND THE WATER IN THE WATER LEG WAS NOT REPLACED. WHEN THE SUMP FILLED UP WITH DIESEL FUEL IT WAS AUTOMATICALLY PUMPED TO AN OPEN PITWHERE THE WATER SHOULD GO. THE SPILL WAS DISCOVERED BY A TRUCK DRIVER WHO WAS LOADING. THE SPILL WAS CONTAINED ON OUR PROPERTY, REACHED NO WATERWAY ANDWAS CLEANED UP BY 4:00 PM. JUNE 18, 1990.
2017-09-29 08:50 | YES | NO | 19900105 | 1990-07-10 | 2552 | COLONIAL PIPELINE CO | YES | 1990-06-06 | 1745 | TX | JEFFERSON | NEDERLAND | NO |  | NO | SEE ATTACHED SKETCH. |  | PUMPING STATION | OTHER | 3/8" INSTRUMENT TUBING | 0 | OTHER | BROKING INSTRU. TUBING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 832.2269 | 1678.9378 | FUEL OIL | 3 | 300 | 224 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER-TECHNICAL & REGULATORY | 4048412296 | AT 1745 CDT ON JUNE 6, 1990, COLONIAL'S HEBERT STATION OPERATOR RECEIVED A REPORT OF A POSSIBLE LEAK BEHIND AN ADJACENT TANK FARM FROM A LANDOWNER. AN OPERATOR IMMEDIATELY INVESTIGATED AND FOUND PRODUCT LEAKING FROM INSTRUMENT TUBING THAT WAS CONNECTED TO THE DYNATROL (INTERFACE DETECTOR) ON THE SUCTION SIDE OF HEBERT STATION ON THE NO. 2, 36-INCH DIAMETER PIPELINE. BOTH COLONIAL AND CONTRACT PERSONNEL WERE DISPATCHED TO THE LEAK FROM BEAUMONT AT 1815 AND HAD THE PRODUCT CONTAINED BY APPROXIMATELY 2030. VACUUM TRUCKS ARRIVED AT THE LEAK SITE AT 2230, AND AT 0100 ON JUNE 7, BEGAN TO RECOVER PRODUCT WHICH WAS THEN TRANSFERRED TO COLONIAL'S TANK NO. 4094. THIS OPERATION CONTINUED UNTIL JUNE 11, 1990. A TOTAL OF 224 BARRELS WAS RECOVERED, AND THE REMAINDER EITHER EVAPORATED OR WAS ABSORBED INTO THE GROUND. THE TEXAS WATER COMMISSION, THE NEDERLAND FIRE DEPARTMENT, AND THE JEFFERSON COUNTY SHERIFF'S DEPARTMENT WERE NOTIFIED AT 2100 ON JUNE 6, 1990. AN INSPECTION OF THE DYNATROL UNIT REVEALED THAT ITS PUMP HAD BECOME LOOSE, AND THE RESULTING VIBRATION CAUSED THE INSTRUMENT TUBING TO FAIL. COLONIAL ENVIRONMENTAL PERSONNEL ARE WORKING WITH THE TEXAS WATER QUALITY PERSONNEL TO DETERMINE ANY ADDITIONAL REMEDIATIONTHAT MAY BE NECESSARY.
2017-09-29 08:50 | YES | NO | 19900106 | 1990-07-02 | 10012 | KANEB PIPELINE CO | YES | 1990-06-05 | 600 | KS | CLOUD |  | NO |  | NO | HIGHWAY 24, 2 MILES EAST OF HIGHWAY 81, NORTHWEST 1/4 OF SECTION 14, RANGE 3 WEST, TOWNSHIP 8 SOUTH. |  | TANK FARM | OTHER | GASKET FAILED ON STRAINER | 1962 | OTHER | GASKET FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 3 | 441 | 432 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MACK E. BROWN, V.P. ENGINEERING & OPERATIONS | 3162621408 | THE TOP OPENING GASKET FAILURE OF THE STRAINER OCCURRED WITHIN THE TANK FIREWALLS OF THE TANK THAT WAS RECEIVING THE PRODUCT DURING A RAIN STORM WHICH ACCOUNTED FOR THE HIGH VOLUME RECOVERY OF THE SPILL. THE PRODUCT WAS VACUUMEDOFF THE RAIN WATER AND PLACED IN STORAGE. THE ORIGINAL PAPER TYPE GASKET THAT FAILED WAS REPLACED WITH A METAL REINFORCED RING TYPE GASKET TO PREVENT THE REOCCURRENCE OF THIS TYPE FAILURE.
2017-09-29 08:50 | YES | NO | 19900107 | 1990-07-17 | 809 | ARCO PIPE LINE CO | Null | 1990-06-18 | 1500 | TX | NAVARRO |  | NO |  | NO | 10 MILES EAST OF DAWSON, TEXAS OFF OF FM 642. |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 51 | 41 | NO | NO | 18 | 0.28 | 52000 | WELDED |  | 1169 | 750 | YES | 8 | 1488 | 1 | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. IRISKI - MANAGER, CRUDE BUSINESS UNIT | 3163311300 | COMPANY PATROL PILOT CALLED IN ON HIS WEEKLY FLIGHT THAT THERE WAS A LEAK ONWEAVER RANCH. COMPANY PERSONNEL RESPONDED, CLAMPED LEAK, AND VACUUMED UP THE OIL. PERMANENT REPAIRS WERE MADE THE NEXT DAY.
2017-09-29 08:50 | NO | NO | 19900108 | 1990-07-13 | 443 | AMOCO PIPELINE CO | YES | 1990-06-12 | 1330 | MO | MACON | ELMER | NO |  | Null | NE/4, SECTION 6, TOWNSHIP 59N, RANGE 15W APPROXIMATELY 2 MILES EAST OF ELMER, MISSOURI. | 26559 | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12483.4037 | 25184.0676 | CRUDE OIL | 1 | 5 | 3 | NO | NO | 20 | 0.31 | 947 | WELDED |  | 0 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.B. WEISS, AREA MANAGER | 8168995387 | AN INTERNAL CORROSION PIT ON A SECTION OF EXPOSED 20-INCH PIPE OVER A NORMALLY DRY DITCH RESULTED IN THE RELEASE OF APPROXIMATELY 5 BARRELS OF CRUDE OIL. AS A RESULT OF STORM WATER RUNOFF, TRACES OF CRUDE WERE CARRIED TO SAND CREEK, APPROXIMATELY 1 1/2 MILES AWAY. CONTAINMENT BOOMS, ABSORBENT PADS, AND A STRATEGICALLY PLACED FLUME WERE UTILIZED TO CONTAIN AND RECOVER THE CRUDE OIL. IT SHOULD BE NOTED THE LINE HAS BEEN INACTIVE FOR THE PAST TWO YEARS AND THE RESIDENT CRUDE OIL IS SCHEDULED TO BE DISPLACED WITH NITROGEN DURING 1990. THE PRESSURE ON THE LINE IS BEING MONITORED, BUT IT NEVER VARIED FROM 50 PSI DURING THE TIME THE RELEASE OCCURRED.
2017-09-29 08:50 | NO | NO | 19900109 | 1990-07-13 | 443 | AMOCO PIPELINE CO | YES | 1990-06-15 | 1300 | MO | JACKSON | SUGAR CREEK | NO |  | NO | WITHIN GROUNDS OF FORMER AMOCO REFINERY SITE AT 1000 N. STERLING AVE. IN SUGAR CREEK, MISSOURI. | 27037 | PUMPING STATION | BOLTED FITTING |  | 0 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | DIESEL FUEL | 1 | 38 | 5 | NO | NO | 8 | 0.32 | 1881 | FLANGED |  | 275 | 192 | YES | 8 | 377 | 11 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.B. WEISS, AREA MANAGER | 8168995387 | THE AMOCO PIPELINE PUMPING STATION AT SUGAR CREEK WAS STARTED AT 1216 HRS. ON 6/15/90. THE LEAKING FLANGE WAS OBSERVED AND THE SYSTEM WAS IMMEDIATELY SHUT DOWN AT 1301 HRS. THE SAME DAY. VALVES WERE CLOSED TO ISOLATE THE AFFECTED FLANGE ASSEMBLY. THE SECTION WAS SUBSEQUENTLY DRAINED UP AND THE DEFECTIVEFIBER GASKET WAS REPLACED WITH A FLEXITALLIC UNIT. WITHIN TEN MINUTES OF IDENTIFYING THE OUTAGE, A CONTAINMENT DIKE WAS CONSTRUCTED AND THE DISCHARGE OF PRODUCT TOWARD SUGAR CREEK (WATERWAY) WAS STOPPED. A BOOM WAS PLACED ACROSS THE CREEK AT AN EXISTING WEIR SITE. VACCUM TRUCKS ALREADY ON SITE WERE UTILIZED TO RECOVER ANY FREE HYDROCARBONS. BECAUSE OF THE EXTENSIVE AMOUNT OF RAINFALL PRIOR TO THE SPILL, SUGAR CREEK WAS RUNNING ABOUT FOUR FEET ABOVE ITSNORMAL LEVEL. AS A RESULT, PRODUCT ESCAPED THE PERMANENT WEIR AND REACHED THE RAPIDLY FLOWING CURRENTS OF THE MISSOURI RIVER.
2017-09-29 08:50 | YES | NO | 19900110 | 1990-07-19 | 22610 | WILLIAMS PIPELINE CO | YES | 1990-06-12 | 705 | MN | SCOTT AND HENNIPIN |  | NO |  | NO | BETWEEN MP 13+27 AND 15+20 AT THE MINNESOTA RIVER IN EDEN PRAIRIE, MINNESOTA. | 26381 | LINE PIPE | OTHER | DIA. TUBING ON MAINLINE | 0 | OTHER | DIAMETER TUBING FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 832226.9161 | 1678937.8395 | DIESEL FUEL | 3 | 1826 | 833 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883850 | AT 0705 ON THE MORNING OF JUNE 12,1990, OUR DISPATCHING PERSONNEL DISCOVEREDINDICATIONS OF A LEAK ON THE #6-12" ROSEMOUNT TO WILMAR PIPELINE. THE LINE WAS IMMEDIATELY SHUT DOWN AND CREWS WERE DISPATCHED TO INVESTIGATE. AT 0710,DISPATCHING RECEIVED A CALL FROM A LOCAL MINNESOTA FIRE DEPARTMENT, REPORTING A FUEL ODOR IN THE VICINITY OF THE MINNESOTA RIVER IN EDEN PRAIRIE. FURTHER INVESTIGATION DETERMINED THAT THE RELEASE ORIGINATED FROM A FAILED SECTION OF SMALL DIAMETER TUBING WHICH WAS INSTALLED AS A BYPASS LINE AROUND THE MAINLINE CHECK VALVE AT MILE POST 14. THE BYPASS LINE RELIEVES ANY PRESSURE DIFFERENTIAL ACROSS THE CHECK VALVE DURING STATIC (LOCKED IN) LINE CONDITIONS, WHCIH COULD OTHERWISE CAUSE ERRONEOUS PRESSURE READINGS DURING STATIC MONITORING. APPROXIMATELY 1,826 BBLS. OF FUEL OIL WAS RELEASED, PART OF WHICH MIGRATEDTO THE ADJACENT MINNESOTA RIVER. NAVIGATION ON THE RIVER WAS TEMPORARILY SUSPENDED TO ACCOMMODATE THE CLEAN-UP EFFORTS. 833 BBLS. OF PRODUCT HAVE BEEN RECOVERED TO DATE. CLEAN-UP EFFORTS AT THE LEAK SITE ARE CONTINUING THROUGH THE USE OF ON SITE LAND FARMING TECHNIQUES. ALL RECOVERY EFFORTS WERE COORDINATED WITH STATE AND FEDERAL ENVIRONMENTAL OFFICIALS. THE FAILED TUBING SPECIMEN HAS BEEN SENT TO BATTELLE INSTITUTE FOR FURTHER ANALYSIS.
2017-09-29 08:50 | YES | NO | 19900111 | 1990-07-23 | 12470 | MID - VALLEY PIPELINE CO | YES | 1990-06-25 | 830 | OH | ALLEN | LIMA | NO |  | NO | LEAK IN CASING ON MUMAUGH ROAD IN LIMA, OHIO. (MILEPOST 6.1) | 28319 | LINE PIPE | OTHER | UNKNOWN | 1949 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 127680 | 106258.7326 | 214366.7833 | CRUDE OIL | 1 | 5 | 5 | NO | NO | 22 | 0.38 | 35000 | WELDED |  | 850 | 100 | YES | 24 | 1070 | 4 | 69 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | I.B. NEWMAN - MANAGER OF PIPELINE OPERATIONS | 2147570207 | MAINTENANCE PERSONNEL WERE INSTALLING A NEW CATHODIC TEST SITE AT LOCATION.WHEN THEY EXPOSED THE CASING TO INSTALL NEW WIRE, THEY NOTICED OIL SEEPNG OUT OF THE CASING.HAD VACUUM TRUCK AT SITE WHEN WE OPENED END SEAL, PICKED UP OIL FROM CASING, APPROXIMATELY 5 BBLS. REPLACED THE ENTIRE SECTION OF PIPE WITHIN CASING (195 FT. 8 INCHES). RETURNED LINE TO SERVICE 1103 CDT. SENT FAILEDSECTION OF PIPE TO LAB FOR ANALYSIS, AND VISUALLY INSPECTED REMAINDER OF REMOVED SECTION OF PIPE FOR ANY EVIDENCE OF CORROSION OR DEFECTS - NONE WERE FOUND. LAB ANALYSIS NOT COMPLETE AT THIS TIME. TELEPHONIC MESSAGE GIVEN TO N.R.C. AT 1350 CDT - ON 6/25/90 - CASE #28319. TELEPHONIC MESSAGE CLEARING INCIDENT GIVEN TO N.R.C. AT 1925 C.D.T. ON 6/28/90.
2017-09-29 08:50 | YES | NO | 19900112 | 1990-07-23 | 2552 | COLONIAL PIPELINE CO | YES | 1990-06-22 | 2158 | VA | CHESTERFIELD |  | NO |  | NO | SEE ATTACHED SKETCH. | 28062 | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | FUEL OIL | 3 | 2000 | 1924 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1159 | 1070 | YES | 24 | 1449 | 1 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES A. COX - MANAGER-TECHNICAL & REGULATORY | 4048412296 | AT 2158 EDT ON JUNE 22, 1990, THE PIPELINE WAS SHUTDOWN IMMEDIATELY AFTER THE MITCHELL JUNCTION OPERATOR RECEIVED A LOW SUCTION PRESSURE ALARM AT RICHMOND DELIVERY FACILITY. HE CONCLUDED THAT HE HAD A POSSIBLE LEAK AND ISOLATED THE SEGMENT OF PIPELINE BETWEEN MITCHELL JUNCTION AND RICHMOND DELIVERY TAKE-OFF VALVE TO DRAIN PRODUCT FROM THE LINE. OPERATORS WERE ALSO DISPATCHED TO CLOSE MANUAL ISOLATION VALVES. LOCAL PERSONNEL AND THE MAINTENANCE AND RESPONSE CONTRACTOR WERE MOBILIZED TO INSPECTION ROAD AND WATER CROSSINGS AND DRAINAGE PATHS. THE VIRGINIA DEPARTMENT OF EMERGENCY SERVICES WAS NOTIFIED AT 2323 AND THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 2356. AT 0640 ON JUNE 23,AT DAYLIGHT, AN INSPECTION OF THE RIGHT-OF-WAY, BY HELICOPTER, WAS BEGUN. THE CHESTERFIELD COUNTY POLICE AND FIRE DEPARTMENTS AND THE RICHMOND POLICE AND FIRE DEPARTMENTS ASSISTED COLONIAL PERSONNEL IN THE SEARCH FOR THE LEAK. THE LEAK WAS LOCATED AT 0915 IN CHESTERFIELD COUNTY BY THE COLONIAL'S ENVIRONMENTAL SPECIALIST, AREA MANAGER AND MAINTENANCE SUPERVISOR TO INSPECT THE LEAK SITE. ALL PRODUCT WAS CONTAINED IN A PRIVATELY OWNED POND. THE CHESTERFIELDCOUNTY POLICE AND FIRE DEPARTMENTS WERE IMMEDIATELY NOTIFIED. COLONIAL'S SPILL CONTRACTOR ARRIVED AT THE SPILL SITE AT 1215 AND BEGAN RECOVERY ACTIVITIES AT 1230. AN ESTIMATED 2000 BARRELS OF PRODUCT WERE RELEASED, AND 1924 BARRELS HAVE BEEN RECOVERED. ENVIRONMENTAL CLEAN-UP OPERATIONS ARE STILL IN PROGRESS. THE PORTION OF THE PIPELINE WHICH CONTAINED THE FAILURE WAS UNDER WATER, AND A VISUAL INSPECTION AFTER REMOVAL REVEALED MECHANICAL DAMAGE ADJACENT TO THE FRACTURE. A PORTION OF THE PIPE CONTAINING THE FRACTURE AND DAMAGE WAS SENT TO A METALLURGICAL LABORATORY FOR ANALYSIS. A NEW SECTION OF PRETESTED PIPE AND ONE FITTING WAS INSTALLED,AND THE PIPELINE WAS RETURNED TO SERVICEAT 1700 ON JUNE 24. ALL WELDS WERE VISUALLY INSPECTED AND RADIOGRAPHED.
2017-09-29 08:50 | NO | NO | 19900113 | 1990-07-30 | 12470 | MID - VALLEY PIPELINE CO | YES | 1990-07-08 | 1700 | OH | CYGNET |  | NO |  | NO | CYGNET PUMP STAION, ROCK RIDGE ROAD, CYGNET, OHIO. SEE ATTACHED SKETCH. | 30005 | PUMPING STATION | VALVE |  | 1949 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | GASKET FAILED AT BOLT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8322.2692 | 16789.3784 | CRUDE OIL | 1 | 20 | 5 | NO | NO | 22 | 0.34 | 35000 | FLANGED |  | 780 | 760 | YES | 24 | 1070 | 4 | 69 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | I.B. NEWMAN, MANAGER OF PIPELINE OPERATIONS | 2147570207 | CASE #30005 - THE DISCHARGE CONTROL VALVE AT CYGNET STATION WHILE IN PARTIALDISCHARGE CONTROL, CONTROL VALVE ACTUATOR BROKE, CAUSING VALVE TO CLOSE, PRESSURE BACKED UP CAUSING A GASKET TO FAIL AND SPRAYED OIL. UNITS SHUT DOWN ATCYGNET. CYGNET TERMINAL OPERATOR ISOLATED STATION PIPING UNTIL GASKET COULDBE REPLACED AND VALVE ARM COULD BE REPAIRED.
2017-09-29 08:50 | YES | NO | 19900114 | 1990-08-03 | 2731 | CHEVRON PIPELINE CO | YES | 1990-07-20 | 232 | TX | LIBERTY |  | NO |  | NO | MILE POLE 31.31 WT LPG PIPELINE SYSTEM 11 MILES NORTH OF DAYTON. SEE ATTACHED COUNTY MAP FOR FUTHER INFORMATION ON LOCATION. | 31755 | LINE PIPE | SCRAPER TRAP |  | 0 | OTHER | SEE PART K | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 1 | 100 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH, DIVISION MANAGER | 4098393128 | FOREIGN MATTER WAS LODGED BETWEEN THE VALVE GATE AND VALVE SPRING LOADED SEAL. THE PRESSURE DIFFERENTIAL ALLOWED THE PIPELINE FLUID TO WASH INTO THE DEPRESSURED BARREL, PREVENTING A POSITIVE SEAL FROM THE UPSTREAM PIPELINE PRESSURE. THE PIPE LINE WAS THEN BLOCKED IN. PRESSURE.
2017-09-29 08:50 | YES | NO | 19900115 | 1990-07-27 | 443 | AMOCO PIPELINE CO | YES | 1990-06-25 | 1203 | MO | ST CHARLES | KAMPVILLE | NO |  | NO | S\2 SECTION 2, TOWNSHIP 47 NORTH, RANGE 4 EAST , ST. COUNTY, MISSOURI. (SEE ATTACHED SKETCHES) | 28195 | LINE PIPE | PIPE |  | 1940 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 83222.6916 | 167893.7839 | GASOLINE | 1 | 317 | 205 | NO | NO | 12 | 0.28 | 1111 | WELDED |  | 720 | 200 | YES | 8 | 900 | 6 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | M.B. WEISS, AREA MANAGER | 8168995387 | THE OWNER OF THE PROPERTY, ENGAGED AN EXCAVATOR TO INCREASE THE HEIGHT OF EXISTING LEVIES ALONG THE SOUTH AND WEST SIDES OF AN APPROXIMATELY 50 ACRE TRACT OF LAND TO PROTECT A RECENTLY PLANTED BEAN FIELD FROMTHE RAPIDLY RISING WATERS OFTHE MISSISSIPPI RIVER. NEITHER THE THREE PIPELINE OPERATORS ON THE PROPERTY NOR THE MISSOURI ONE CALL SYSTEM WERE NOTIFIED. AT ABOUT NOON ON SUNDAY, JUNE 24, 1990, THE AMOCO 12-INCH LINE WAS PUNCTURED BY A BULLDOZER OWNED AND OPERATED BY DAVE KOLB GRADING, INC. AT THE TIME OF THE INCIDENT THE PIPELINE WAS NOT IN OPERATION. THROUGH THE COOPERATIVE EFFORTS OF AMOCO, IT'S CONTRACTORS, OTHER AREA PIPELINE COMPANIES, AND LOCAL EMERGENCY RESPONSE ORGANIZATIONS THE GASOLINE WAS CONTAINED WITHIN AND EXISTING DITCH WHICH WAS THE SOURCE OF THE SOIL BEING UTILIZED TO BUILD UP AND REINFORCE THE LEVIES. A PIPELINE MARKER WAS CLEARLY VISIBLE AND WITHIN 72 FEET OF THE LOCATION AT WHICH THE PIPELINE WAS PUNCTURED. THE GASOLINE FLOATED ON THE RISING WATER WITHIN THE DIKED DITCH WHICH FACILITED THE RECOVERY. VACUUM TRUCKS, BOOMS, AND ABSORBENT MATERIALS WERE UTILIZED IN CONTAINING AND RECOVERING THE FREE GASOLINE. THE REMAINING WATER WAS TREATED BY AIR SPARGING TO STRIP OUT DISSOLVED HYDROCARBONS. IT IS ANTICIPATED THE POTENTIAL FOR GROUND WATER CONTAMINATION WILL BE MINIMAL. THE VOLUME OF UNRECOVERED GASOLINE WAS PRIMARILY THE RESULT OF EVAPORATION.
2017-09-29 08:50 | YES | NO | 19900116 | 1990-08-01 | 22610 | WILLIAMS PIPELINE CO | YES | 1990-07-02 | 1600 | IA | WEBSTER |  | NO |  | NO | FORT DODGE TERMINAL #D278. | 29243 | TANK FARM | TANK |  | 1969 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3328.9077 | 6715.7514 | FUEL OIL | 3 | 64 | 60 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT-OPERATIONS | 9185883850 | ON JULY 2, TERMINAL PERSONNEL DISCOVERED PRODUCT AROUND THE OUTSIDE BASE OF TANK #799. SUSPECTING THAT IT ORIGINATED FROM THE UNDERNEATH SIDE OF THE TANK, THEY IMMEDIATELY BEGAN TO TRANSFER THE TANK CONTENTS TO AN ADJACENT STORAGE TANK. EXCAVATION HOLES WERE DUG AROUND THE PERIMETER OF THE TANK TO AID PRODUCT RECOVERY. DUE TO THE HIGH WATER TABLE, THEY WERE ABLE TO RECOVER ALMOST THE ENTIRE RELEASED AMOUNT. THE TANK BOTTOM WAS SAND BLASTED AND INSPECTED FOR DAMAGE. SEVERAL SMALL INTERNAL CORROSION PITS WERE DISCOVERED TO HAVE PENETRATED THE FLOOR PLATE. THE PITS WERE REPAIRED AND THE TANK BOTTOM WAS COATED, CONSISTENT WITH THE SPECIFICATIONS FOR OUR ONGOING TANK BOTTOM RECONDITIONING PROGRAM. ALL CLEAN-UP EFFORTS WERE COORDINATED WITH STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19900118 | 1990-08-09 | 10313 | KOCH PIPELINE INC | NO | 1990-07-10 | 1605 | OK | BEAVER |  | NO |  | NO | SEC. 11, T5N, R24E, BEAVER COUNTY, OKLAHOMA. | 30315 | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 17199 | 14313.4707 | 28876.0519 | L. P. G. | 2 | 758 | 0 | YES | NO | 4.5 | 0.19 | 42 | WELDED |  | 1440 | 0 | YES | 8 | 1810 | 1 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | NO | MARC S. DEVARENNES, DIVISION ENGINEER | 4053952377 | AT APPROXIMATELY 1605 HOURS ON JULY 10, 1990 A DITCHER OWNED BY LON'S WELDING (PERRYTON, TEXAS) STRUCK AND RUPTURED KOCH'S 4.5 INCH PIPELINE RESULTING INA FIRE. THE LINE WAS BLOCKED IN, THE FIRE ALLOWED TO BURN OUT AND REPAIRS WERE MADE TO THE AFFECTED SECTION.
2017-09-29 08:50 | YES | NO | 19900119 | 1990-08-13 | 26103 | TEXAS EASTMAN CO | NO | 1990-07-13 | 1119 | TX | HOUSTON | HARRIS | NO |  | NO | 10111 MILLS ROAD AT TEXAS EASTMAN COMPANY SOUTH BOOSTER PUMP STATION. |  | PUMPING STATION | OTHER | FILTER/ COALESCER | 1978 | OTHER | 0-RING FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 12 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEPHEN J. BUTLER - SUPERVISING ENGINEER, EASTMAN-OWNED P/L | 2142375171 | ON THE MORNING OF JULY 13, 1990, THE FILTER ELEMENTS IN SOUTH BOOSTER FILTER/COALESCER WERE CHANGED PER NORMAL PROCEDURES. THE VESSEL WAS BEING SLOWLY REPRESSURIZED WITH PROPANE WHEN THE 0-RING, WHICH SEALS THE VESSEL OPENING, FAILED RELEASING PROPANE TO THE ATMOSPHERE. THE PIPELINE INSPECTOR WHO WAS REPRESSURIZING THE VESSEL IMMEDIATELY CLOSED THE INLET VALVE WHICH WAS ONLY SLIGHTLY OPEN. THIS ACTION EFFECTIVELY ISOLATED THE VESSEL FROM THE PROPANE SOURCE, BUT THE PROPANE IN THE VESSEL ESCAPED TO THE ATMOSPHERE. THE WIND DISSIPATED THE PROPANE VAPORS ALONG THE NORTH/SOUTH FENCE LINE WITHOUT INCIDENT.
2017-09-29 08:50 | YES | NO | 19900120 | 1990-08-03 | 4487 | ENDICOTT PIPELINE CO | NO | 1990-07-26 | 923 |  |  |  | YES | 70 21'17.6"N,147 57' 20 | NO | ENDICOTT MAIN PRODUCTION ISLAND MODULE 303. |  | PUMPING STATION | OTHER | CONTINUOUS COMP. SAMPLER | 1987 | OTHER | SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | CRUDE OIL | 1 | 2 | 2 | YES | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | F.B. WIESE - OPERATIONS SUPT. ENDICOTT | 9076596566 | TECHNICIAN WAS REMOVING THE COMPOSITE SAMPLER FOR MAINTENANCE WHEN THE HIGH PRESSURE SEAL FAILED. CRUDE OIL LEAKED FROM THE UNIT UNTIL VALVE COULD BE CLOSED. THE CRUDE OIL DRIPPED THROUGH GRATING ONTO A HOT GAS TURBINE EXHAUST TWO FLOORS BELOW CAUSING A SMALL FIRE WHICH WAS IMMEDIATELY EXTINGUISHED BY THE INSTALLED HALON EXTINGUISHING SYSTEM. ALL SPILLED PRODUCT WAS CONTAINED WITHIN THE BUILDING.
2017-09-29 08:50 | YES | NO | 19900121 | 1990-08-20 | 443 | AMOCO PIPELINE CO | NO | 1990-07-16 | 1730 | TX | BRAZORIA | UNKNOWN | NO |  | NO | 1/2 MILE WEST OF HWY 35 1/2 MILE NORTH OF THE INTERSECTION OF FM2351 AND HWY 35. | 31248 | LINE PIPE | PIPE |  | 1938 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1500 | 1320 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 275 | 28 | NO | 0 | 0 |  |  | INTERNAL | Null | NO | OTHER | INTERNAL SALT WATER | NO DATA |  | Null | NO DATA |  | Null | Null | J.P. BLACK | 4099380084 | THE PATROL PILOT NOTIFIED THE AREA OFFICE OF A POSSIBLE LEAK. THE PIPELINE CREW WAS DISPATCHED. THE LEAK WAS CLAMPED. TWO DAYS LATER TWO JOINTS OF PIPE WERE REPLACED. THE SYSTEM WAS THEN PUT BACK INTO SERVICE.
2017-09-29 08:50 | NO | NO | 19900122 | 1990-08-20 | 4906 | EXXON PIPELINE CO | YES | 1990-07-17 | 1200 | LA | JEFFERSON |  | NO |  | NO | THIS LEAK ORIGINATED FROM OUR GRAND ISLE - LITTLE LAKE JUNCTION 12-INCH PIPELINE AT STATION NO. 642+13. THIS POINT IS APPROXIMATELY 12 MILES NORTH OF GRAND ISL | 31411 | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 33000 | 27463.4882 | 55404.9487 | CRUDE OIL | 1 | 2 | 0 | NO | NO | 12 | 0.31 | 52000 | WELDED |  | 1091 | 200 | YES | 0 | 1200 | 1 | 54 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | D.E. COX, ENVIRONMENTAL AND REGULATORY COMPLIANCE MGR. | 7136565521 | AT 1600 HOURS ON JULY 17, 1990 OUR AERIAL PATROL DISCOVERED A SHEEN NEAR OURPIPELINE IN THE BARATARA BAY AREA. AFTER SHUTTING DOWN AND CHECKING, THE SOURCE WAS DETERMINED TO BE A VERY SMALL LEAK ON OUR 12-INCH PIPELINE. THE PIPELINE HAD MECHANICAL DAMAGE ALTHOUGH IT WAS BURIED 4.2 FEET BELOW THE MUDLINE. WATER DEPTH AT THAT POINT WAS ABOUT 5 FEET. THE DAMAGE WAS BELIEVED TO BECAUSED BY MARINE EQUIPMENT, POSSIBLY A SPUD STRIKING THE LINE. REPAIRS WERECOMPLETED AT 0900 HOURS ON JULY 18, 1990. NO FOLLOW-UP CLEANUP WAS NECESSARY BECAUSE THE SHEEN DISSIPATED/EVAPORATED.
2017-09-29 08:50 | NO | NO | 19900123 | 1990-08-20 | 4906 | EXXON PIPELINE CO | YES | 1990-07-17 | 1200 | LA | JEFFERSON |  | NO |  | NO | THIS LEAK ORIGINATED FROM OUR GRAND ISLE - LITTLE LAKE 16-INCH PIPELINE AT STATION NO. 1228+35 IN TURTLE BAY. | 31391 | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 33289.0766 | 67157.5136 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 16 | 0.28 | 52000 | WELDED |  | 1315 | 150 | YES | 0 | 1643 | 1 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.E. COX, ENVIRONMENTAL AND REGULATORY COMPLIANCE MGR. | 7136565521 | AT 1250 HOURS ON JULY 17, 1990 OUR FIELD PERSONNEL DISCOVERED A SHEEN NEAR OUR PIPELINE IN TURTLE BAY. AFTER SHUTTING DOWN AND CHECKING, THE SOURCE WAS DETERMINED TO BE A VERY SMALL LEAK ON OUR 16-INCH PIPELINE. THE PIPELINE HADMECHANICAL DAMAGE ALTHOUGH IT WAS BURIED 5.6 FEET BELOW THE MUDLINE. WATER DEPTH AT THAT POINT WAS ABOUT 6 FEET. THE DAMAGE WAS BELIEVED TO HAVE BEEN CAUSED BY A SPUD STRIKING THE LINE. REPAIRS WERE COMPLETED AT 2300 HOURS ON JULY 18, 1990. NO FOLLOW-UP CLEANUP WAS NECESSARY BECAUSE THE SHEEN DISSIPATED/EVAPORATED.
2017-09-29 08:50 | YES | NO | 19900124 | 1990-07-20 | 22610 | WILLIAMS PIPELINE CO | NO | 1990-06-21 | 1238 | KS | JOHNSON |  | NO |  | NO | MP 189+16 LINE SECTION #B006 SW 1/4, SECTION 4, TOWNSHIP 125, RANGE 24E. | 27875 | LINE PIPE | PIPE |  | 1946 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 46000 | 38282.4381 | 77231.1406 | FUEL OIL | 3 | 398 | 193 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 400 | YES | 8 | 1440 | 1 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9165883850 | AT APPROXIMATELY 1238 HOURS ON JUNE 21, 1990, THE #3-8" BARNSDALL TO KANSAS CITY LINE WAS PUNCTURED BY A FRONT-END LOADER AT M.P. 189+16. THE LOADER WASOWNED AND OPERATED BY HOLLAND CONSTRUCTION COMPANY. HOLLAND WAS UNDER CONTRACT WITH THE CITY OF SHAWNEE, KANSAS, TO CLEAR BRUSH AND TREES IN PREPARATIONFOR SOME PLANNED ROAD CONSTRUCTION, WPL PERSONNEL HAD ATTENDED THE PRE-CONSTUCTION MEETING ON JUNE 5, 1990, WPL CREWS ALSO FLAGGED THE LINE ON JUNE 13, 1990, AND ONCE AGAIN INSTRUCTED THE CONTRACTOR CREW AND FOREMAN NOT TO WORK ORDIG OVER THE PIPELIEN WITHOUT A WPL REPRESENTATIVE PRESENT. WPL WAS NOT NOTIFIED OF THEIR INTENDED ACTIVITY OVER THE LINE UNTIL AFTER THEY HAD STRUCK AND PUNCTURED THE PIPELINE. THE LINE WAS STATIC, HOLDING ABOUT 400 PSI AT THE TIME OF THE FAILURE. DISPATCHING PERSONNEL NOTICED A DROP IN THE LINE PRESSURE AND IMMEDIATELY REQUESTED A FIELD MAINTENANCE CREW TO INVESTIGATE. THE CONTRACTOR CALLED IN SHORTLY THEREAFTER TO REPORT THAT HE HAD HIT THE LINE. ALL APPROPRIATE AGENCIES WERE NOTIFIED. THE RELEASED PRODUCT WAS QUICKLY CONTAINED BY EARTHEN DAMS SET UP BY THE CONTRACTOR'S CREW, CONSEQUENTLY, THE ENVIRONMENTAL IMPACT WAS MINIMAL.
2017-09-29 08:50 | YES | YES | 19900125 | 1990-08-28 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1990-07-25 | 1245 | TX | ECTOR |  | NO |  | NO | SECTION 39, T&P RR CO, BLOCK 44 TS2S, 500 FT WEST OF FM 866 & 1.5 MILES NORTH OF HWY I-20. | 32613 | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 12136 | 10099.9059 | 20375.5896 | L. P. G. | 2 | 886 | 0 | NO | NO | 4.5 | 0.14 | 2632 | WELDED |  | 1895 | 800 | YES | 24 | 2542 | 11 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE WARNING SIGNS | NO | NO | S F ISAACS - PRESIDENT | 9185811800 | THIRD PARTY PUNTURED LINE WITH HOLE AUGER.
2017-09-29 08:50 | YES | NO | 19900126 | 1990-08-29 | 22610 | WILLIAMS PIPELINE CO | YES | 1990-07-30 | 1350 | IA |  | DES MOINES | NO |  | NO | DES MOINES TERMINAL #D201 | 33352 | TANK FARM | BOLTED FITTING |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1664.4538 | 3357.8757 | FUEL OIL | 3 | 71 | 70 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H E JANZEN - VICE PRESIDENT, OPERATIONS | 9185883350 | ON JULY 30, 1990 A LEAK OCCURRED IN THE RACK MANIFOLD AT OUR DES MOINES,IA TERMINAL. MAINTENANCE CREWS WERE REARRANGING JUMPERS IN THE RACK MANIFOLD IN PREPARATION FOR SWITCHING PRODUCT SERVICE ON TWO TANKS. THE PLANNED ACTIVITY WAS REVIEWED WITH THE LOCAL SUPERVISOR AND THE APPROPRIATE LINES WERE ISOLATEDPRIOR TO BEGINNING THE WORK. HOWEVER, WHILE MAKING THE SWITCHES, THEY INADVERTENTLY REMOVED A UNIBOLT CAP FROM AN ADJACENT ACTIVE LINE THAT WAS PUMPING TO THE LOADING RACK. AS A RESULT, 71 BBLS. OF FUEL OIL WAS RELEASED. CREWS QUICKLY ISOLATED THE LINE AND SHUT OFF THE TANK PUMP. CLEAN-UP EFFORTS RECOVERED 70 BBLS. OF THE RELEASE PRODUCT. APPROPRIATE EMPLOYEES WERE SUBJECTED TOPOST ACCIDENT DRUG AND ALCHOL TESTING. A POST ACCIDENT REVIEW MEETING WAS ALSO CONDUCTED WITH THE INVOLVED EMPLOYEES.
2017-09-29 08:50 | YES | NO | 19900127 | 1990-08-27 | 1682 | BP OIL PIPELINE CO | NO | 1990-07-25 | 1200 | OH | MONTGOMERY | MAD RIVER | NO |  | NO | AT REAR OF RESIDENTIAL ADDRESS OF 208 LYNNHAVEN DR, DAYTON, OH | 32664 | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16644.5383 | 33578.7568 | GASOLINE | 3 | 260 | 130 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1200 | 750 | YES | 24 | 1540 | 1 | 70 | EXTERNAL | Null | Null | GALVANIC |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | D K NEUWERTH - EA REG SUPT | 2163514777 | BP OIL PIPELINE CO'S VANDALIA OHIO DISPATCHING CENTER BECAME AWARE OF A GASOLINE SPILL AND EVACUATION THROUGH LOCAL RADIO NEWS BROADCASTS AT ABOUT 13:30 ON 07/25/90. A CHECK WITH THE MAD RIVER TOWNSHIP FIRE DEPARTMENT ATTRIBUTED THE PROBLEM TO A LEAKING TRUCK. A METER-IN-METER-OUIT LINE BALANCE SYSTEM SHOWED NO ABNORMAL VARIATION AND OPERATING PRESSURES WERE ALSO NORMAL, BUT THE PIPELINE ROUTE WAS RIGHT THROUGH THE AFFECTED AREA AND THE PRODUCT IN THE LINE (RED DYED GASOLINE) MATCHED THE DESCRIPTION OF THE SPILLED PRODUCT. TWO PIPELINE SUPERVISORS WERE SENT OUT TO ASSESS THE SITUATION AT 16:00 AND BEFORE THEY ARRIVED THE LINE WAS SHUT DOWN (16:20). A FIELD ASSESSMENT WAS COMPLETED BY ABOUT 17:30. THE MOST LIKELY CAUSE WAS THOUGHT TO BE A PIPELINE LEAK INTO A STROM SEWER WHICH CROSSES THE PIPELINE. BLOCK VALVES WERE CLOSED AND PRESSURE WAS BLED OFF INTO TANKAGE LOCATED AT BP OIL'S DAYTON, OHIO TERMINAL. PRODUCT STOPPED LEAKING INTO THE SEWER, BUT THE PIPELINE LEAK COULD NOT BE LOCATED. THE FIRE DEPARTMENT OFFICIALLY ALLOWED RESIDENTS TO RETURN TO THEIRHOMES AT 01:00 ON 07/26/90. THE STORM SEWER/PIPELINE CROSSING WAS DUG OUT THE MORNING OF 07/26 AND A HERETOFORE UNKNOWN SEWER JUNCTION BOX WAS DISCOVERED TO HAVE BEEN CONSTRUCTED AROUND THE PIPELINE. THE PIPELINE COATING WAS DAMAGED AND ATMOSPHERIC CORROSION WAS PRESENT ON ALL OF THE UNCOATED PIPE. A LEAK CLAMP WAS INSTALLED AND THE LINE WAS TAPPED TO ADMIT AIR AND ALLOW A GRAVITY DRAINDOWN INTO DAYTON TANKAGE. ON 07/27 AN 8' 11.5" SECTION OF PIPE WAS REPLACED WITH NEW PIPE AND THE PIPELINE WAS RESTARTED. THE NEW PIPE WAS PROTECTED WITH EPOXY COATING; HAND APPLIED WRAP AND ROCK SHIELD. THE SEWER JUNCTION BOX WAS REBUILT WITH A MANHOLE TO ALLOW INSPECTION OF THE PIPE.
2017-09-29 08:50 | NO | NO | 19900128 | 1990-08-22 | 15674 | PLANTATION PIPE LINE CO | YES | 1990-07-27 | 800 | AL | SHELBY | HELENA | NO |  | NO | PLANTATION PIPE LINE CO'S HELENA PUMP STATION LOCATED ON SHELBY COUNTY ROAD #52 IN HELENA, AL. (SEE ATTACHED SKETCH A-1528-0) | 33000 | PUMPING STATION | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2496.6807 | 5036.8135 | GASOLINE | 3 | 7 | 7 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VP - OPERATIONS | 4043645916 | ON THURSDAY, 07/26/90, A TIGHTNESS TEST WAS CONDUCTED ON THE BMG STATION PIPING AT PLANTATIONS'S HELENA TANK FARM AND PUMP STATION. PLANTATION'S BMG PIPELINE SYSTEM TRANSPORTS GASOLINE FROM THE HELENA TANK FARM TO BIRMINGHAM TERMINAL VIA A 10" PIPELINE. THREE ATTEMPTS TO HOLD PRESSURE ON THE BMG STATION PIPING FAILED TO OBTAIN A SATISFACTORY TEST. AT MIDNIGHT, THE CONTRACTOR BEGAN TO REMOVE THE CONCRETE FLOOR INSIDE THE PUMP ROOM IN ORDER TO INSPECT THE PIPING UNDER TH FLOOR. AT 08:00 CDST ON 07/27, A PINHOLE LEAK WAS DISCOVERED IN THE BELOW GRADE PIPING FOR THE BMG PUMP. NORMAL OPERATING PRESSURE OF THIS PIPING IS 70 PSI. THE ENTIRE SECTION OF PIPING BETWEEN THE SUCTION VALVE AND THE SUCTION FLANGE OF THE BMG PUMP WAS REMOVED AND REPLACED. IN ACCORDANCE WITH THE ACCIDENT REPORTING REQUIREMENTS UNDER SECTION 195.52(A)(5) OF DOT REGULATIONS, THE NATIONAL RESPONCE CENTER WAS NOTIFIED OF THIS RELEASE ON 07/27 (REPORT #33000). IN THE JUDGEMENT OF PLANTATION, THE INCIDENT IS SIGNIFICANT EVEN THOUGH IT DOES NOT MEET THE NORMAL REPORTING CRITERIA.
2017-09-29 08:50 | YES | NO | 19900129 | 1990-09-05 | 18273 | SHELL PIPE LINE CORP | YES | 1990-08-13 | 1445 | NM | LEA | EUNICE | NO |  | NO | NW 1/4, SE 1/4, SECTION 28, T-21-S, R-37-E HOBBS-HENDRICK 8-INCH AND 10-INCH PIPELINE |  | LINE PIPE | VALVE |  | 1935 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1900 | 1581.2311 | 3189.9819 | CRUDE OIL | 1 | 50 | 35 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 900 | 100 | YES | 8 | 1140 | 7 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | MD HAYS - MGR HEALTH, SAFETY & ENVIRON. | 7132416262 | WHILE DIGGING OUT OLD JUNCTION VALVE ON 8-INCH, A 2-INCH VALVE WAS BUMPED AND BROKEN OFF. AFFECTED AREA IS BEING SOIL FARMED.
2017-09-29 08:50 | YES | NO | 19900130 | 1990-08-31 | 10313 | KOCH PIPELINE INC | YES | 1990-08-13 | 1255 | WI | PORTAGE |  | NO |  | NO | LEGAL DESC IS THE NE1/4 & SE1/4 OF SECTION 16-24N-7E. JUST SOUTH OF MARTIN ISLAND DR, PORTAGE COUNTY, WI. | 35225 | LINE PIPE | PIPE |  | 1988 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 190 | 75 | NO | NO | 10 | 0.19 | 2256 | WELDED |  | 1440 | 44 | YES | 24 | 2050 | 8 | 90 | NO DATA | Null | YES | NO DATA |  | OTHER | WILL BE DETER. AFTER TEST | Null | NO DATA |  | Null | Null | JEROME KLEIN - DIV MGR | 6124592424 | THE LEAK WAS CONFIRED AT 12:55PM ON 08/13/90. KOCH PERSONNEL WERE ON THE SCENE AT THIS TIME FROM OUR JUNCTION CITY TERMINAL. THE CONTRACTOR, MINNESOTA LIMITED, ARRIVED AT THE LEAK SITE AT 6:30PM. SITE CLEANUP BEGAN AT 12:30AM ON TUESDAY, 081490, WITH THE LEAK ON THE PIPELINE EXPOSED AT 8:00AM THAT MORNING. CLEANUP AND REPIAR CONTINUED THROUGHOUT THE DAY. ON WEDNESDAY, 08/15/90, WELDING ON THE PIPELINE STARTED AT 9:50AM, WITH THE REPAIRS BEING COMPLETEDAT 3:20PM. PORTAGE COUNTY EMERGENCY RESPONCE PERSONNEL AND THE WISCONSIN DEPARTMENT OF NATURAL RESOURCES PEOPLE WERE ON THE SCENE TO COORDINATE THE CLEANUP PROCEDURES.
2017-09-29 08:50 | YES | NO | 19900131 | 1990-08-31 | 4805 | EXPLORER PIPELINE CO | YES | 1990-08-01 | 1315 | IL | KANKAKEE |  | NO |  | NO | KANKAKEE COUNTY, BOURBONNAIS TOWNSHIP, SECTION 14, T31N-R11E, SOUTH SIDE OF ROAD N310W APPROXIMATELY ON MILE SOUTH OF HWY 102. | 33644 | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 152000 | 126498.4912 | 255198.5516 | JET FUEL | 3 | 912 | 855 | NO | NO | 24 | 0.28 | 52000 | WELDED |  | 876 | 171 | YES | 24 | 1162 | 10 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | ROD E SANDS - VP - OPERATIONS | 9184935106 | EXPLORER'S 24" MAINLINE WAS PUNCTURED AT MILEPOST 606.1 ON 080190 NEAR BOURBANNAIS, IL BY A THIRD PARTY CONTRACTOR'S TRENCHING MACHINE. THE CONTRACTOR NOTIFIED EXPLORER'S OPERATIONS COORDINATOR IN TULSA, OK AT 13:15 08/01/90 THATHE HAD HIT THE LINE AND FUEL WAS SPILLING. THE OPERATIONS COORDINATOR CONFIRMED AN ABNORMAL PRESSURE LOSS ON THE DAMAGED LINE SEGMENT SIMULTANEOUS WITH THE CALL AND CLOSED REMOTE BLOCK VALVES AT MILE POSTS 563.5 AND 642.3 THE LINE WAS NOT OPERATING AT THE TIME OF DAMAGE AND HAD A STATIC PRESSURE OF 171 PSI AT THE ACCIDENT SITE. EXPLORER'S EMERGENCY RESPONCE TEAM WAS ACTIVATED IMMEDIATELY. THE TRENCHING CONTRACTOR (BASAILLON EXCAVATING CO) CONSTRUCTED EARTHEN DAMS IN THE OPEN TRENCH TO CONTAIN ESCAPING JET FUEL. THE CONTRACTOR, ALONG WITH LOCAL FIRE AND POLICE ODDICIALS WERE REQUESTED TO CLOSE ADJACENT BLOCK VALVES AT MILEPOSTS 605.3 AND 606.8. BOTH VALVES WERE CLOSED BY 14:30.ALL PRODUCT WAS CONTAINED BY THE DITCH IN A 30 FT X 300 FT AREA. EXPLORER PERSONNEL WERE FLOWN BY HELICOPTER FROM OUR WOOD RIVER, IL AND HAMMOND, IND OFFICES. SPILL RESPONCE EQUIPMENT WAS DISPATCHED FROM HAMMOND. THE HAMMOND AREA SUPERVISOR ARRIVED ON THE SITE AT 14:55. VACUUM TRUCKS BEGAN ARRIVING AT THE SITE AT 17:30. BY 24:00 ON 08/01/90 PRODUCT FROM THE DITCH HAD BEEN RECOVERED AND A CONTROLLED DRAINDOWN OF THE PIPELINE SEGMENT INTO TRUCKS WAS STARTED. DRAINDOWN AND REPAIRS TO THE LINE WERE COMPLETED AT 12:00 ON 08/03/90. THE ILLINOIS EPA REQUESTED REMOVAL AND DISPOSAL OF APPROXIMATELY 1500 CUBIC YARDS OF CONTAMINATED SOIL. THE CONTAMINATED SOIL HAS BEEN REMOVED AND REPLACEMENT WITH CLEAN SOIL IS IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19900132 | 1990-09-06 | 443 | AMOCO PIPELINE CO | NO | 1990-08-09 | 1018 | LA |  |  | YES | LAT. 2749.6 LONG.9437.4 | YES | MINOR DRIP LEAK ON CHECK VALVE PACKING ON RISER PIPING DEPARTING PLATFORM. | 34716 | LINE PIPE | VALVE |  | 0 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | CHECK VALVE PACKING FAIL | Null | NO DATA |  | Null | Null | HOWARD B. SPALDING, SUPERVISOR-OPERATIONS | 4099483407
2017-09-29 08:50 | NO | NO | 19900133 | 1990-09-04 | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-08-07 | 834 | TX | ANDREWS |  | NO |  | NO | LINE 80-1 - GOLDSMITH TO DREW - MP 16-47+42 NE/4, SEC. 13, BLOCK 11, UNIVER. LANDS, SW OF GOLDSMITH, TX ON HWY TO 158 TO INTER. OF HWY 158, 181, AND 302; | 34934 | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 33289.0766 | 67157.5136 | NATURAL GAS LIQUID | 2 | 4 | 0 | NO | NO | 12.75 | 0.25 | 45000 | WELDED |  | 1095 | 650 | YES | 24 | 1379 | 4 | 82 | EXTERNAL | Null | YES | OTHER | PIPE CORRODED | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | DURING ROUTINE ROUNDS, PHILLIPS PIPE LINE CRUDE OIL GATHERING EMPLOYEES DISCOVERED LEAK. THE LINE WAS SHUT DOWN, BLOCKED IN, AND 12" X 36" CLAMP WAS INSTALLED. CLAMP WAS WELDED UP AT A LATER DATE (8/16/90).
2017-09-29 08:50 | YES | NO | 19900134 | 1990-09-07 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1990-08-07 | 1300 | CA | LOS ANGELES | WILMINGTON | NO |  | NO | WILMINGTON, COUNTY OF LOS ANGELES, CALIFORNIA THOMAS BROS LOS ANGELES COUNTY REFERENCE P 74, F4. |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | FUEL OIL | 3 | 60 | 60 | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 720 | 100 | YES | 8 | 900 | 1 | 82 | EXTERNAL | Null | YES | OTHER | IMPRESSED CURRENT | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM GREY - MGR. SAFETY, HEALTH & ENV. PROTECTION | 2134289273 | ON AUGUST 7, 1990 AT 1300, CALTRANS WORKERS REPORTED OIL ON THE GROUND. FOUR CORNERS PIPE LINE PERSONNEL RESPONDED AND SUBSEQUENTLY EXCAVATED THE LINE AND REPLACED APPROXIMATELY 300 FEET OF LINE.
2017-09-29 08:50 | YES | NO | 19900135 | 1990-08-31 | 18273 | SHELL PIPE LINE CORP | NO | 1990-08-01 | 246 | CA | KERN | LOST HILLS | NO |  | NO | MID PUMP STATION | 33566 | PUMPING STATION | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12483.4037 | 25184.0676 | CRUDE OIL | 1 | 250 | 250 | NO | NO | 8 | 0.25 | 25000 | WELDED |  | 1170 | 1170 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENTAL | 7132416262
2017-09-29 08:50 | YES | NO | 19900136 | 1990-09-05 | 22442 | WEST TEXAS GULF PIPELINE CO | YES | 1990-08-09 | 1346 | WI | RACINE |  | NO |  | NO | 1/4 MILE EAST OF HWY 45 AND 1/4 MILE SOUTH OF 7 MILE RD. | 34767 | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 1000 | 310 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1170 | 200 | YES | 24 | 1460 | 1 | 61 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KENNETH C. ANDREEN, AREA MANAGER | 7082573740 | A CONTRACTOR WAS INSTALLING 4" DRAIN TILE IN A FIELD FOR A LANDOWNER. THE DRAIN TILE WAS BEING INSTALLED AT A DEPTH OF APROXIMATELY 4.5 FEET BY A RIPPING-TYPE TILING MACHINE. THE TILING MACHINE HIT THE PIPELINE (WHICH WAS AT A DEPTH OF APPROXIMATELY 4.0 FEET) AT ABOUT A 90 DEGREE ANGLE AND PUT A HOLE IN TEH PIPELINE APPROXIMATELY 14" BY 12".
2017-09-29 08:50 | YES | NO | 19900137 | 1990-09-28 | 22610 | WILLIAMS PIPELINE CO | YES | 1990-08-27 | 1530 | NE | OTOE | UNKNOWN | NO |  | NO | LS # C051 MP 133+2400. NW 1/4, SECTION 5, T 7N, R14E. | 37212 | LINE PIPE | VALVE |  | 1950 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 166445.3832 | 335787.5679 | GASOLINE | 3 | 500 | 40 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | WILL BE DETERMINED | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883350 | AT 1530 HOURS ON AUGUST 17, 1990 WHILE CONDUCTING ROUTINE GATE VALVE INSPECTIONS ON THE #5-12" KANSAS CITY TO SIOUX FALLS LINE, A LEAK WAS DISCOVERED IN THE VALVE BOX AT MP 133+2400. DISPATCHING WAS IMMEDIATELY NOTIFIED AND THE LINE WAS SHUT DOWN AND DRAINED. ADDITIONAL MAINTENANCE PERSONNEL WERE DISPATCHED TO THE LEAK SITE TO ASSIST. THE LEAK APPEARS TO HAVE ORIGINATED FROM AN EXTERNAL DRAIN VALVE NEAR THE BOTTOM OF THE VALVE HOUSING. PRELIMINARY VISUAL INVESTIGATION SUGGESTS EVIDENCE OF INTERNAL CORROSION. THE DRAIN VALVE HASBEEN SENT TO A LAB FOR FURTHER METALURGICAL ANALYSIS. THE RELEASED PRODUCT APPARENTLY TRAVELED DOWN GRADIENT ALONG THE SHALLOW WATER TABLE, SURFACED IN NEARBY BAR DITCH THEN FLOWED ABOVE GRADE DOWN TO A NEIGHBORING FARM POND. LIVESTOCK WITHIN THE IMMEDIATE AREA WERE RELOCATED AWAY FROM THE LEAK SITE AND THE POND. A LOCAL VETERINARIAN REPORTED THAT THE LIVESTOCK SHOWED NO ADVERSEAFFECTS FROM THE LEAK. PRODUCT RECOVERY AND SITE REMEDIATION EFFORTS ARE BEING COORDINATED WITH STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19900138 | 1990-09-24 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1990-09-02 | 500 | WY | UINTA | UNKNOWN | NO |  | NO | TWNSHIP 13 NORTH, RANGE 120 WEST SECTION 35. | 37889 | LINE PIPE | PIPE |  | 1980 | OTHER | PIPE FAILED AT PREV DENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 72692 | 60496.239 | 122045.3494 | NATURAL GAS LIQUID | 2 | 4886 | 0 | NO | NO | 6.63 | 0.13 | 2009 | WELDED |  | 1446 | 1180 | YES | 24 | 1884 | 11 | 80 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.F. ISAACS, PRESIDENT | 9185811800 | LINE RUPTURED WELL BELOW MAXIMUM OPERATING PRESSURE. CAUSE UNKNOWN AT THIS TIME. WE ARE WAITING ON RESULTS OF METALLURGY TESTS.UPDATE : THE RUPTURE WAS CAUSED BY A DENT IN THE PIPE. SHALLOW CRACKS DEVELOPEDIN THE COLD-WORKED METAL NEAR THE DENT. THE CRACKS APPARENTLY GREW BY BENDING AND BY FATIGUE UNTIL THEY PENETRATED THE WALL AND CAUSED THE RUPTURE.
2017-09-29 08:50 | YES | NO | 19900139 | 1990-09-27 | 9175 | JAYHAWK PIPELINE CORP | YES | 1990-08-28 | 300 | OK | TEXAS | UNKNOWN | NO |  | NO | SW/4 SEC. 13-T4N-R16E, TX COUNTY, OK 7 1/2 MILES SW CITY OF HOOKER, OK IN RURAL AREA. |  | PUMPING STATION | TANK |  | 1973 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | 3661.7984 | 7387.3265 | CRUDE OIL | 1 | 970 | 860 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DENNIS E. SMITH, PRESIDENT | 3162913254 | A POLICEMAN DISCOVERED AND REPORTED A LEAK AT JAYHAWK'S HOOKER STATION, TEXAS COUNTY, OK DURING A PATROL OF THE OUTLYING RURAL AREA NEAR HOOKER, OKLAHOMA. JAYHAWK PERSONNEL WERE ALTERTED AT 0300 HOURS, AUGUST 28, 1990. THE AREA SUPERVISOR WAS THE FIRST EMPLOYEE AT THE SITE AND FOUND CRUDE OIL SPILLING FROM AN OVERFILLED TANK. ALL INCOMING CRUDE AT THIS LOCATION WAS DIVERTED OR STOPPED BY 0340. STATION PUMPS WERE STARTED AT 0400 AND OIL WAS PUMPED DOWNSTREAM IN ORDER TO LOWER THE CRUDE LEVEL IN THE TANK. THE TOTAL QUANTITY OF CRUDE OIL SPILLED WAS CONTAINED INSIDE THE TANK DIKE. AN ESTIMATED 110 BARRELSOF CRUDE WAS ABSORBED BY THE SOIL WITH THE REMAINING 860 BARRELS BEING RECOVERED. THE OILY DIRT FROM INSIDE THE TANK DIKE WAS REMOVED AND REPLACED. HOOKER STATION OPERATES IN A FLOATING MODE, RECEIVING AND DELIVERING OIL SIMULTANEOUSLY THROUGH THE TANK. AT THE TIME OF THE INCIDENT, JAYHAWK WAS EXPERIENCING A PARTIAL COMMUNICATIONS FAILURE OF ITS SUPERVISORY CONTROL SYSTEM THAT PREVENTED THE DISPATCHER FROM MONITORING CONDITIONS AT HOOKER STATION DIRECTLYAND CONTRIBUTED TO A MISINTERPRETATION OF DATA BEING RECEIVED FROM THE DOWNSTREAM STATION LOCATION. THE PROBLEM WAS ULTIMATELY TRACED TO UNSTABLE SIGNAL LEVELS CAUSED BY A FAULTY TELEPHONE CIRCUIT LEASED FROM SOUTHWESTERN BELL.
2017-09-29 08:50 | YES | NO | 19900140 | 1990-09-14 | 22907 | WYCO PIPE LINE CO | YES | 1990-08-16 | 1130 | CO | ARAPAHOE | AURORA | NO |  | NO |  | 35737 | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 74900.4225 | 151104.4056 | GASOLINE | 3 | 53 | 30 | NO | NO | 6 | 0.22 | 42000 | WELDED |  | 1600 | 675 | YES | 24 | 2000 | 9 | 66 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | DWAINE A. SMROYER, MANAGER - OPERATIONS | 3032866411 | CONTRACTOR WORKING FOR THE CITY OF AURORA, COLORADO PUNCTURED THE PIPELINE WITH A FRONT-END LOADER WHILE EXCAVATING A TEMPORARY DRIVEWAY.
2017-09-29 08:50 | YES | NO | 19900141 | 1990-09-17 | 809 | ARCO PIPE LINE CO | YES | 1990-08-20 | 513 | IN | LAKE | SHERERVILLE | NO |  | NO | 1,200 FT W OF THE INTERSECTION OF KENNEDY AVE & OAK ST, SHERERVILLE, IN NEAR THE INTER OF THE NY CENTRAL & MI CENTRAL RAILROADS. | 36085 | PUMPING STATION | OTHER | SUMP TANK | 1987 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 104000 | 86551.5993 | 174609.5353 | CRUDE OIL | 1 | 125 | 115 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, MANAGER, CRUDE BUSINESS UNIT | 3163311300 | WHILE RECEIVING A SCRAPER THE HIGH-PRESSURE LIMIT SWITCH WAS ACTIVATED CAUSING THE FACILITY TO SHUT DOWN AUTOMATICALLY. ALL SAFETY DEVICES WORKED IN ACCORDANCE WITH THEIR DESIGN. DURING THE RESTART THE OPERATOR UTILIZED A QUICK OPENING VALVE. THE QUICK INCREASE IN PRESSURE ON THE LOWER PRESSUR METER PIPING CAUSED THE PRESSURE RELIEF SYSTEM TO ACTIVATE. THIS SYSTEM CONSIST OF A DANIEL FLOW CONTROL VALVE AND BURSTING HEAD, WHICH IS ATTACHED TO AN 84 BARREL SUMP TANK. WHEN THE RELIEF SYSTEM RELIEVED THE EXCESS PRESSURE INTO THE SUMP TANK THE OPERATOR IMMEDIATELY REACTED BY BLOCKING IN THE ENTIRE LOWER PRESSURE PIPELING SYSTEM. THE ACTION TAKEN BY THE OPERATOR TOOK APPROXIMATELY ONE MINUTE AND FORTY SECONDS. DURING THIS TIME PERIOD THE SUMP TANK FILLED ANDOVERFLOWED.
2017-09-29 08:50 | NO | NO | 19900142 | 1990-10-03 | 10313 | KOCH PIPELINE INC | YES | 1990-09-22 | 1730 | MO | HARRISON | UNKNOWN | NO |  | NO | SEE ATTACHED DRAWING. | 40486 | LINE PIPE | PIPE |  | 1980 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 10 | 10 | NO | NO | 24 | 0.28 | 1405 | WELDED |  | 829 | 27 | YES | 24 | 1151 | 11 | 80 | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JERONE H KLIEN - DIVISION MANAGER | 6124592424 | COTTAGE GROVE WAS NOTIFIED OF THE LEAK AT 5:30 PM. ON 9/22/90. THE LEAK WASLOCATED IN THE SE NW OF SECTION 32-66N-26W, HARRISON COUNTY, MISSOURI. THE LEAK WAS REPORTED TO US BY OUR AIR PATROL. THE PUMPS WERE NOT RUNNING AT THETIME OF THE LEAK. THE BLOCK VALVES AT BETHANY STATION WERE OPENED TO RELIEVE PRESSURE OFF OF THE PIPELINE. KOCH PERSONNEL FROM THE AREA WERE THERE THROUGH THE NIGHT WORKING ON CLEANUP AND REPAIR. ON 9/24/90 THE PIPELINE WAS AGAIN OPERATIONAL. CLEAN UP WAS DONE ON 9/27/90.
2017-09-29 08:50 | YES | NO | 19900143 | 1990-10-15 | 443 | AMOCO PIPELINE CO | YES | 1990-09-23 | 1200 | OK | PAYNE |  | NO |  | NO | PAYNE COUNTY SE1/4, SECTION 13, TOWNSHIP 17N, RANGE 5 EAST | 40547 | LINE PIPE | BOLTED FITTING |  | 0 | OTHER | GAUGE LINE CRACK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 0.5 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. W. CARICO | 9182257271 | A 1/2" PRESSURE TRANSMITTER LINE CRACKED.
2017-09-29 08:50 | YES | NO | 19900144 | 1990-10-15 | 443 | AMOCO PIPELINE CO | YES | 1990-09-09 | 2030 | OK | LINCOLN |  | NO |  | NO | AMOCO TANK FARM, NW1/4, SECTION 24, TOWNSHIP 17N, RANGE 5E | 38732 | TANK FARM | PUMP |  | 0 | OTHER | PUMP CASE CRACKED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 3745.0211 | 7555.2203 | CRUDE OIL | 1 | 500 | 470 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. W. CARICO | 9182257271 | UPON START-UP OF AN OIL TRANSFER BETWEEN TANK FARMS, A 150 ANSI SERIES PUMP CASE (NOT BEING EMPLOYED FOR THE TRANSFER) CRACKED. SYSTEM PRESSURE WAS ABOUT 220 PSI. THE PUMP CASE WILL BE METALLURGICALLY EXAMINED TO DETERMINE THE REASON FOR THE FAILURE
2017-09-29 08:50 | NO | NO | 19900145 | 1990-10-12 | 10250 | KIANTONE PIPELINE CORP | YES | 1990-09-14 | 1800 | NY | ERIE | EDEN | NO |  | NO | 125 SOUTH OF KELLAR ROAD, TOWN OF EDEN, NY |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16644.5383 | 33578.7568 | CRUDE OIL | 1 | 24 | 20 | NO | NO | 12 | 0.22 | 2200 | WELDED |  | 1460 | 880 | YES | 0 | 2200 |  | 71 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RAYMOND E. LOWE, JR., MANAGER KIANTONE PIPELINE | 8147231500 | CRUDE OIL FROM SMALL PINHOLE TRAVELED ALONG PIPE NORTH TO A CULVERT UNDER KELLAR ROAD, FROM THERE INTO A DITCH RUNNING INTO HENDERSON CREEK. PIPELINE INFORMED BY NYS DEC, PUMPS SHUTDOWN WITHIN ONE MINUTE, AREA ISOLATED IN 30 MINUTES. PIPELINE MANAGER ON SCENE WITHIN 2 HOURS, RESPONSE CONTRACTOR - 3 HOURS, EXCAVATION CONTRACTOR - 3 HOURS, PIPELINE CREW - 3 HOURS. PLIDCO CLAMP INSTALLED; PIPELINE STARTED UP; DOWNTIME 20 HOURS; CLEANUP TIME TWO(2) WEEKS. ALL SPILLED OIL CONTAINED WITHIN A ONE-MILE STRETCH OF HENDERSON CREEK.A CLOSE INTERVAL SURVEY WAS COMPLETED ON THE ENTIRE PIPELINE IN 1988. THE AREA OF THE PINHOLE MAY HAVE GIVEN FALSE READINGS DUE TO A GAS PIPELINE ANODE BED ADJACENT. 150 FEET OF PIPELINE WAS STRIPPED OF COATING AND INSPECTED; NOOTHER THINNING OR CORROSION WAS FOUND. THE PIPE WAS WRAPPED AND BACK FILLED.MONITORING WELLS INSTALLED TO CHECK FOR MIGRATION OF OIL IN THE SHALE SUBSTRATTA. WELLS ARE IN THE COMPLETION STAGE AT THIS TIME.AN INSTRUMENT PIGRUN IS PLANNED FOR THIS FALL; REPALCEMENT OF THIS SECTION PLANNED FOR NEXT FALL WHEN THE NEW CRUDE LINE IS PUT INTO SERVICE. THE EXISTING LINE IS SCHEDULED FOR PRODUCT SERVICE.
2017-09-29 08:50 | YES | NO | 19900146 | 1990-10-10 | 4906 | EXXON PIPELINE CO | YES | 1990-08-26 | 300 | TX | HARRIS |  | NO |  | NO | INSIDE THE DIKE AROUND TANK 1997, WEBSTER STATION, 20004 OLD GALVESTON ROAD, WEBSTER, TEXAS |  | TANK FARM | TANK | MIXER ON TANK 1997 | 1959 | OTHER | PIN SHIFTED OUT OF PLACE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3328.9077 | 6715.7514 | CRUDE OIL | 1 | 200 | 195 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D. E. COX - ENVIRONMENTAL AND REG. COMP. MANAGER | 7136565521 | ON 8/26/90 AT 0830, EPC EMPLOYEE CONTACTED EPC SUPERVISOR AND REPORTED OIL IN THE FIREWALL TANK 1997, WEBSTER STATION. THE LEAK WAS CONFIRMED AT 0900 BY EPC SUPERVISOR. THE TANK MIXER ON THE TANK CAME OFF DUE TO THE PIN VIBRATING OUT OF PLACE. THE MIXER PIVOTS ON TWO PINS. THESE PINS ARE HELD IN PLACEWITH A CIRCLIP ON THE TOP AND BOTTOM OF EACH PIN. THE BOTTOM CLIP CAUSED THE PIN TO WORK ITS WAY OUT OF THE HOUSING. THE PIN CAME OUT, ALLOWING THE MIXER TO TILT BACKWARDS; CAUSING OIL TO LEAK FROM THE BALL JOINT. THE OIL WAS PICKED UP BY VACUUM TRUCKS AND THE DIKED AREA CLEANED.CIRCLIP WERE REPLACED WITH FULL ENCIRCLEMENT SNAP RING; NEW PINS ARE BEING BUILT TO REPLACE THE EXISTING PINS.
2017-09-29 08:50 | NO | NO | 19900147 | 1990-10-04 | 15263 | PENNZOIL EXPLORATION & PRODUCTION CO | NO | 1990-09-06 | 630 | TX |  |  | YES | 28 17' 18" - 91 52' 55" | NO | APPROX. 6' ABOVE THE WATER LINE INT HE RISER ON THE NORTHEAST LEG OF "B" PLATFORM, BLOCK 128, SOUTH MARSH ISLAND AREA, GULF OF MEXICO (OCS G-2587) |  | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4993.3615 | 10073.627 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 10 | 0.5 | 35000 | WELDED |  | 1440 | 80 | YES | 24 | 2680 | 8 | 76 | EXTERNAL | Null | YES | OTHER | LOCALIZED CORR. PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | J. GILMORE - DISTRICT CONSTRUCTION MANAGER | 3182694200 | LOCALIZED PITTING BENEATH THE RISER'S VULCANIZED RUBBER COATING RESULTED IN PIN-HOLE FAILURE IN THE WALL OF THE 10" PIPE APPROXIMATELY 6' ABOVE THE WATER.
2017-09-29 08:50 | YES | NO | 19900148 | 1990-10-04 | 2552 | COLONIAL PIPELINE CO | YES | 1990-08-29 | 1930 | VA | CHESAPEAKE |  | NO |  | NO | SEE ATTACHED SKETCH | 37547 | LINE PIPE | LONGITUDINAL WELD |  | 1985 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 3 | 1600 | 1121 | NO | NO | 12.75 | 0.22 | 60000 | WELDED |  | 1293 | 860 | YES | 8 | 1617 | 12 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JAMES A. COX, MANAGER-TECHNICAL AND REGULATORY | 4048412296 | AT 20:00 EDT ON AUGUST 29, 1990, WHILE MAKING A DELIVERY TO CRANEY ISLAND DELIVERY FACILITY, THE MITCHELL JUNCTION OPERATOR DISCOVERED A 1,075 BARREL SHORTAGE. AFTER REVIEWING THE OPERATIONAL DATA, THE OPERATOR TERMINATED THE DELIVERY BY DIVERTING THE FULL STREAM INTO RICHMOND DELIVERY AND BLOCKING THE LINE AT RICHMOND STATION. HE SIMULTANEOUSLY CLOSED THE CRANEY ISLAND JUNCTION TAKEOFF VALVE AND THE CRANEY ISLAND DELIVERY FACILITY BLOCK VALVE AT 20:13.THE NORFOLK DELIVERY FACILITY OPERATOR WAS DISPATCHED TO CRANEY ISLAND DELIVERY AT 20:45 TO VISUALLY INSPECT THE FACILITY. NOTHING ABNORMAL WAS FOUND, AND AT 21:30 THE CHIEF OPERATOR OF THE NORFOLK DELIVERY FACILITY WAS ADVISED OF A POSSIBLE LEAK BETWEEN CRANEY ISLAND JUNCTION AND THE CRANEY ISLAND DELIVERY FACILITY. A SEARCH WAS INITIATED ALONG THE ROUTE OF THE PIPELINE, AND THESPILL WAS DISCOVERED AT 01:15 EDT ON AUGUST 30, 1990.THE COLONIAL GREENSBORO MAINTENANCE TEAM, WHICH WAS IN FREDERICKSBURG, VIRGINIA, AND A LOCAL CONTRACTOR, CENTRAL VIRGINIA MAINTENANCE, INC., WERE DISPATCHED TO THE LEAK SITE AT 01:15. IN ADDITION , INDUSTRIAL MARINE SERVICES, INC., A SPILL RESPONSE CONTRACTOR FROM NORFOLK,WAS REQUESTED TO SEND ASSISTANCE.LOCAL POLICE AND FIRE DEPARTMENTS WERE NOTIFIED BETWEEN 01:20 AND 01:30. THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 02:00, REPORT NO. 37547, AND THE VIRGINIA WATER POLLUTION CONTROL BOARD WAS NOTIFIED AT 02:45.FUEL OIL AT THE LEAK SITE HAD FLOWED DOWN AN UNNAMED TRIBUTARY INTO DRUM POINT CREEK WHICH WAS A MARSH AT THIS LOCATION. BOOMS WERE DEPLOYED ON DRUM POINT CREEK ONE-HALF MILE DOWNSTREAM JUST ABOVE TAYLOR ROAD. MOST PRODUCT WAS RECOVERED AT THE LEAK SITE. AN ESTIMATED 1600 BARRELS ESCAPED FROM THE PIPELINE, AND 1121 BARRELS HAVE BEEN RECOVERED AS OF THIS DATE. ABSORBENT BOOMS AREBEING MAINTAINED AT THE PRESENT TIME.THE PIPELINE WAS EXCAVATED AT THE LEAK SITE AND FOUND TO HAVE RUPTURED IN A BADLY DAMAGED SECTION. THE DAMAGE RESULTED DURING THE RECENT INSTALLATION OFAN ELECTRIC UTILITY'S 30-INCH CASING BENEATH COLONIAL'S PIPELINE BY A THIRD PARTY CONTRACTOR. TWENTY-FIVE FEET OF 12.750-INCH O.D., 0.219-INCH W.T., X60PIPE WERE REMOVED AND REPLACED WITH 12.750-INCH O.D., 0.250-INCH W.T., X60, HYDROSTATICALLY TESTED PIPE. ALL TIE-IN WELDS WERE RADIOGRAPHED.
2017-09-29 08:50 | YES | NO | 19900149 | 1990-10-04 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1990-09-01 | 2230 | NY | CAYUGA |  | NO |  | NO | BUCKEYE PIPE LINE COMPANY'S AUBURN STATION GATES ROAD ROUTE 6 BOX 83, AUBURN, NY 13021--SEE ATTACHED DRAWING | 37877 | TANK FARM | TANK |  | 1959 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 2014 | 1315 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER, REGULATORY COMPLIANCE COORDINATOR | 2158208300 | TANK 312 AT AUBURN STATION WAS OVERFILLED. INCORRECT SELECTION OF TANK FILLMANIFOLD VALVE BY OPERATOR RESULTED IN THIS GASOLINE PRODUCT OVERFLOW. THE PRODUCT WAS CONTAINED IN TANK 312 DIKE AREA.
2017-09-29 08:50 | NO | NO | 19900150 | 1990-10-11 | 809 | ARCO PIPE LINE CO | YES | 1990-09-06 | 1920 | TX | FREESTONE |  | NO |  | NO | TWO MILES SOUTH OF TEAGUE, TEXAS ON HIGHWAY #80 | 38559 | TANK FARM | PIPE |  | 1957 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 166.4454 | 335.7876 | CRUDE OIL | 1 | 40 | 30 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | NANCY LODER FOR V.P. DUSKI-MGR. CRUDE BUSINESS UNIT | 3163311300 | EMPLOYEE FOUND LEAK. COMPANY PERSONNEL RESPONDED, CLAMPED LEAK AND VACUUMEDTHE SPILLED OIL.NOTE: TELEPHONIC NOTICE TO THE NATIONAL RESPONSE CENTER WAS MADE PRIOR TO ACCURATELY DETERMINING THE QUANTITY OF SPILLED OIL. AFTER FURTHER INVESTIGATION, IT WAS FOUND THAT THE INCIDENT DID NOT REQUIRE DOT REPORTING. HOWEVER, THIS REPORT IS BEING SUBMITTED AS A FOLLOW-UP TO THE TELEPHONIC NOTICE.
2017-09-29 08:50 | YES | NO | 19900151 | 1990-10-16 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-06-23 | 459 | CA | CONTRA COSTA | RICHMOND | NO |  | NO | IN RICHMOND STATION, AT 520 CASTRO STREET, RICHMOND, CALIFORNIA | 28081 | PUMPING STATION | VALVE |  | 1984 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 66578.1533 | 134315.0272 | JET FUEL | 3 | 180 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. M. ABBOUD, SR. V.P., OPERATIONS AND ENGINEERING | 2134867720 | 1. AT START OF A DELIVERY TO POINT MOLATE, A NAVY SUPPLY DEPOT, THE RICHMOND STATION IN-STATION HIGH-PRESSURE RELIEF VALVE ACTUATED, BUT DID NOT RESEAT PROPERLY.2. THE HIGH-SUMP ALARM FAILED TO GIVE AN INDICATION AND PRODUCT OVERFLOWED THE SUMP CAUSING PRODUCT ESCAPE.
2017-09-29 08:50 | YES | NO | 19900152 | 1990-10-16 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-07-06 | 1300 | CA | CONTRA COSTA | BRENTWOOD | NO |  | NO | THIRTY FEET SOUTH OF INTERSECTION OF FAIRVIEW AND BALFOUR ON BALFOUR IN THE CITY OF BRENTWOOD |  | LINE PIPE | PIPE |  | 1957 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 832226.9161 | 1678937.8395 | GASOLINE | 3 | 60 | 0 | NO | NO | 10 | 0.25 | 46000 | WELDED |  | 1390 | 1050 | YES | 24 | 1820 | 0 | 57 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. M. ABBOUD, SR. V.P., OPERATIONS AND ENGINEERING | 2134867720 | PIN-HOLE LEAK DEVELOPED ALONG SEAM, PIPE WAS WET BUT NO LIQUID IN SOIL. PIPE FAILURE PROBABLE CAUSE.
2017-09-29 08:50 | YES | NO | 19900153 | 1990-10-30 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-09-21 | 745 | AZ | MARICOPA | CHANDLER | NO |  | NO | 1/3 MILE EAST OF 56TH STREET ON GILA RIVER INDIAN RESERVATION | 40266 | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 332890.7664 | 671575.1358 | DIESEL FUEL | 3 | 30 | 0 | NO | NO | 6 | 0.22 | 42000 | WELDED |  | 0 | 0 | YES | 24 | 1800 | 0 | 56 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | Null | Null | J.M. ABBOUD, SR. V.P. OPERATIONS AND ENGINEERING | 2134867720 | THERE WAS ACTIVITY BETWEEN 1964 AND 1969 WHEN A WATER LINE (10") WAS INSTALLED ACROSS SFPP'S PIPELINE. THERE IS EVIDENCE OF SEVERAL SCRAPES WHERE THE COATING WAS KNOCKED OFF AND A LITTLE METAL. IT WAS NOT REPORTED BY THE CONTRACTOR. A SMALL LEAK DEVELOPED AND A 7-FOOT SLEEVE WAS WELDED INTO PLACE TO PROTECT ALL AREA SCRAPED BY OUTSIDE FORCE.
2017-09-29 08:50 | NO | NO | 19900154 | 1990-09-14 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1990-10-09 | 600 | ND | PEMBINA |  | NO |  | NO | M.P 795.4, APPROXIMATELY 4 MILES WEST OF THE RED RIVER OF THE NORTH IN PEMBINA COUNTY, NORTH DAKOTA. |  | LINE PIPE | LONGITUDINAL WELD |  | 1965 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9986.723 | 20147.2541 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 835 | 198 | YES | 10 | 780 | 6 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR, SEC. AND G.M., CORPORATE TECH. SERVICES | 7153941404 | PINHOLE DEFECT IN LONGITUDINAL SEAM OF FLASH-WELD SEAM PIPE MANUFACTURED BY A.O. SMITH. NO EXTERNAL CORROSION ON PIPE OR SEAM EVIDENT. PLIDCO SLEEVE WELDED AND LINE RETURNED TO SERVICE 1100 MST, OCTOBER 10, 1990.
2017-09-29 08:50 | YES | NO | 19900155 | 1990-11-06 | 26085 | SCURLOCK OIL CO | NO | 1990-09-18 | 1900 | TX | RUSK | LEVETT CHAPEL | NO |  | NO | HWY 42 SOUTH, TURN WEST AT THE CHAPEL SCHOOL, GO 2-1/2 MILES, TURN NORTH ON SCURLOCK ROAD, GO 1 MILE TO 1ST TRAILER HOUSE ON RIGHT, TURN INTO DRIVEWAY TO LEAK S | 39837 | LINE PIPE | OTHER | UNKNOWN | 1979 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2496.6807 | 5036.8135 | CRUDE OIL | 1 | 100 | 80 | NO | NO | 10.75 | 0.25 | 24000 | WELDED |  | 550 | 300 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | NO | THOMAS. HRUCIR, DIVISION SUPERINTENDENT | 2149845252 | LANDOWNER WAS DIGGING ON OUR ROW TO BURY STUMPS. WHEN HE GOT TOO CLOSE TO OUR LINE AND HIT IT WITH HIS CABLE LINK BELTH TRACK HOE. THE ROW WAS CLEAR AND HE DID NOT CONTACT US BEFOR HE BEGAN TO DIG.
2017-09-29 08:50 | NO | NO | 19900156 | 1990-11-19 | 443 | AMOCO PIPELINE CO | NO | 1990-11-07 | 1100 | TX | WOOD |  | NO |  | NO | APP. 1 MILE NORTH OF QUITMAN STATION ON HW 2225, QUITMAN, TEXAS. | 46742 | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 4 | 0.28 | 100 | WELDED |  | 100 | 100 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | ONE CALL |  | NO | NO | PAT M. CLANCY/PIPELINE MAINTENANCE FOREMAN | 9037597131
2017-09-29 08:50 | NO | NO | 19900157 | 1990-11-19 | 26085 | SCURLOCK OIL CO | NO | 1990-11-03 | 1030 | TX | GREGG | LONGVIEW | NO |  | NO | ONE MILE WEST OF HWY. 42 ON SOUTH SIDE OF SABINE RIVER, OFF RIVER ROAD. | 46230 | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 30 | 30 | NO | NO | 6.63 | 0.25 | 24000 | NO DATA |  | 702 | 50 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | UNKNOWN | DAMAGE BY NATURAL FORCES |  | Null | OTHER | UNKNOWN | NO | NO | THOMAS G. HRNCIR, DIVISION SUPERINTENDENT | 9039845252 | SCURLOCK WAS NOTIFIED BY THE GREGG COUNTY SHERIFF'S DEPT. @ 10:30 AM. ON 11/3/90 OF A LEAK IN SABINE RIVER. COMPANY PERSONNEL VERIFIED LEAK BEING IN OURTWIN 6" PIPELINE LOCATED IN THE WEST LINE ON THE NORTH BANK. THE LEAK WAS DUE TO EXTERNAL CORROSION IN APPROXIMATELY THE 8:00 POSITION FROM TOP OF PIPE. THIS PORTION OF PIPE WAS EXPOSED TO ATMOSPHERE. A CLAMP WAS IMMEDIATELY INSTALLLED APPROXIMATELY 2" FROM WHERE THE PIPE WENT INTO THE NORTH BANK, THEREFORE SHUTTING OFF THE SOURCE. COMPANY PERSONNEL BLOCKED IN THE VALVES ON THE WEST LINE ISOLATING THAT SECTION CROSSING THE RIVER. A CONTRACTOR WAS CONTACTED & THREE BOOMS WERE IN PLACE WITHIN ONE HOUR AND FIFTEEN MINUTES AFTER SCURLOCK WAS NOTIFIED. CONTRACT AND COMPANY CREWS BEGAN CLEANUP IMMEDIATELY USING BOATS, VACUUM TRUCKS NAD OTHER NECESSARY EQUIPMENT. CLEANUP EFFORTS HAD 98% OF THE OIL RECOVERED BY MIDNIGHT 11/3/90.
2017-09-29 08:50 | YES | NO | 19900158 | 1990-11-15 | 10012 | KANEB PIPELINE CO | YES | 1990-10-11 | 543 | NE | FILLMORE |  | NO |  | NO | NW 1/4 SECTION 29, TOWNSHIP 6 NORTH, RANGE 4 WEST FILLMORE COUNTY, NEBRASKA. |  | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12567 | 10458.5957 | 21099.2118 | GASOLINE | 3 | 351 | 10 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1235 | 755 | YES | 24 | 1625 | 7 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | OPERATOR | NO | NO | MACK E. BROWN, VICE PRESIDENT OF ENGINEERING AND OPERATIONS | 3162621408 | THE RUPTURE OCCURRED APPROXIMATELY 2 MILES WEST OF KANEB'S SHICKLEY JUNCTIONAND AFFECTED THE LINE THAT GOES TO PHILLIPSBURG, KS. SHICKLEY JUNCTION IS THE FACILITY THAT KANEB BUILT AFTER THE CHAMPLIN PIPELINE ACQUISITION. WE PUMP PRODUCT FROM GENEVA TERMINAL TO SHICKLEY JUNCTION, WHERE THE FLOW CAN BE DIVERTED NORTH OR SOUTH INTO THE FORMER CHAMPLIN LINE OR WEST INTO THE PHILLIPSBURG LINE. OUR INVESTIGATION REVEALED THAT THE RUPTURE OCCURRED IN A SECTION OF LINE PIPE THAT HAD BEEN HIT SEVERAL TIMES BY A SUB SOIL CHISEL FARM IMPLEMENT. FURTHER INVESTIGATION CONFIRMED THAT THE GROUND HAD BEEN WORKED WITH A SUB SOIL CHISEL ONLY 2 OR 3 DAYS BEFORE THE RUPTURE. PRIOR TO THE RUPTURE, OUR OPERATION WAS SPLITTING THE STREAM BETWEEN THE PHILLIPSBURG LINE AND THE NORTH LEG OF THE CHAMPLIN LINE AT SHICKLEY JUNCTION. THE PHILLIPSBURG LINE DURING THE OPERATION WITHHELD THE PRESSURE OF THE SPLIT STREAM, BUT WHEN THE FLOW WAS DIVERTED INTO ONLY THE PHILLIPSBURG LINE, THE WEAKENED AREA STRUCK BY THE CHISEL RUPTURED.
2017-09-29 08:50 | YES | NO | 19900159 | 1990-11-21 | 13131 | CONOCO INC | YES | 1990-10-23 | 1334 | WY | PLATTE |  | NO |  | NO | NW 1/4, NW 1/4, S1, T22N, R66W. | 45178 | LINE PIPE | WELDING FITTING |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8322.2692 | 16789.3784 | CRUDE OIL | 1 | 210 | 171 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1440 | 275 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | YES | DWIGHT D. JACKSON, MGR. OEPRATIONS ENGINNERING | 7132932130 | AN INTERNAL SURVEY OF THIS LINE SEGMENT HAD REVEALED AN "ANOMALY" AT THIS LOCATION WHICH TURNED OUT TO BE A 2-INCH DIAMETER NIPPLE WELDED ON THE LINE. DURING EXCAVATION THE NIPPLE WAS STRUCK BY THE BACKHOE CAUSING THE PIPELINE TOFAIL.SOME OF THE CRUDE SPRAYED FROM THE PIPELINE TEAR INTO THE AIR AND ONTO LAND JUST DOWNWIND OF THE LEAK SITE. THE REMAINDER FLOWED INTOTHE BELLHOLE WHERE IT WAS REMOVED VIA VACUUM TRUCK.
2017-09-29 08:50 | YES | NO | 19900160 | 1990-12-04 | 2731 | CHEVRON PIPELINE CO | YES | 1990-11-21 | 730 | TX | POLK | ONALASKA | NO |  | NO | ATTACHED COUNTY MAP. | 48482 | PUMPING STATION | OTHER | DENSITOMETER SUCTION LINE | 1990 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 190 | 180 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | UNKNOWN | 4098393100 | 1/4" SUCTION LINE TO DENSITOMETER FAILED. CRUDE OIL SPRAYED ONTO MAIFOLD AREA. THE MAJORITY OF THE CRUDE OIL WAS CONTAINED INSIDE THE CONCRETE CONTAINMENT BERM. REMAINDER WAS CONTAINED BY NEWLY CONTRUCTED BERM. ALL FREE CRUDEOIL WAS RETURNED TO STORAGE. THE PRELIMINARY CAUSE OF THE TUBING APPEARS TOBE VIBRATION.
2017-09-29 08:50 | YES | NO | 19900161 | 1990-12-04 | 18273 | SHELL PIPE LINE CORP | YES | 1990-10-30 | 1120 | IL | WILLIAMSON | MARION | NO |  | NO | CAPLINE 40-INCH PIPELINE. SW 1/4, SW 1/4, SECTION 3, T-9-S, R-2-E ONE MILE NORTH OF HIGHWAY 13 ON SKYLINE ROAD. | 45731 | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 499336.1497 | 1007362.7037 | CRUDE OIL | 1 | 1470 | 1444 | NO | NO | 40 | 0.31 | 52000 | WELDED |  | 576 | 330 | YES | 24 | 800 | 1 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | A 3 TO 4-INCH HOLE WAS DRILLED IN THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19900162 | 1990-11-27 | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-10-26 | 1643 | TX | HUTCHINSON | UNKNOWN | NO |  | NO | BORGER-E. CHICAGO 12" BLUE LINE. MP 1-43+30. MIDDLE OF LEASE ROAD, SEC. 63, BLK. 46, HT&CH SURVEY. | 45187 | LINE PIPE | PIPE |  | 1956 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20805.6729 | 41973.446 | L. P. G. | 2 | 10 | 0 | NO | NO | 12.75 | 0.38 | 46000 | WELDED |  | 960 | 580 | YES | 24 | 1470 | 7 | 80 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B. L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | LEAK WAS DISCOVERED BY INDIVIDUAL WHO OBSERVED FROZEN AREA ON THE SURFACE OFTHE GROUND AND REPORTED IT TO PHILLIPS PIPE LINE COMPANY'S BORGER AREA OFFICE. THE LEAK WAS THROUGH A 3/8" LONG SPLIT IN THE LONGITUDINAL SEAM OF THE PIPE RIGHT UNDER AN ARC BURN.
2017-09-29 08:50 | YES | NO | 19900163 | 1990-04-03 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1990-11-07 | 2001 | AR | UNION |  | NO |  | NO | SECTION 7, T17S, R13W, UNION COUNTY, ARKANSAS. | 46883 | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 83222.6916 | 167893.7839 | ANHYDROUS AMMONIA | 2 | 2622 | 0 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1340 | 1214 | YES | 24 | 1953 | 8 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | RAY O. MORAN, JR., DIVISION MANAGER | 3144865488 | PRESSURE DROP WAS DETECTED BY OUR PRODUCT MOVEMENT COORDINATOR, IN WICHITA, KANSAS, AT 20:01 HOURS AT OUR M-4 PUMP STATION THAT IS LOCATED APPROXIMATELY 19.5 MILES FROM THE LEAK SITE. HE IMMEDIATELY SHUT-IN OUR REMOTELY OPERATED BLOCK VALVE AT M-4 AND SHUT-DOWN THE PUMP STATION. THIS WAS DONE AT 20:02 HOURS. THE COORDINATOR THEN CALLED OUR PERSONNEL IN THE AREA AND BLOCK VALVES NEARER THE LEAK WERE CLOSED IN ORDER TO ISOLATE IT FURTHER. IT APPEARED THAT THE LINE HAD BLOWN A HOLE IN IT ABOUT 12 TO 14 INCHES LONG. THERE WERE SEVERAL GOUGES IN THE LINE WHERE IT HAD BEEN STRUCK BY MACHINERY. AT THIS TIME IT IS NOT KNOWN WHO STRUCK THE LINE, BUT THERE WERE SEVERAL LOGGING COMPANIES THAT WERE OPERATING IN THE AREA THIS PAST SPRING. IT IS BELIEVED THAT THE LINEMAY HAVE BEEN STRUCK SOMETIME IN THE SPRING AND FINALLY GAVE WAY THE NIGHT OF NOVEMBER 7TH, 1990. A SEVEN FOOT SECTION WAS REMOVED AND REPLACED WITH TESTED PIPE. THERE WERE NO SIGNS OF CORROSION OR OTHER REASONS FOR THE FAILURE OF THE PIPE.
2017-09-29 08:50 | YES | NO | 19900164 | 1990-12-13 | 12628 | MOBIL PIPELINE CO | YES | 1990-11-10 | 615 | NY | ERIE | SENECA | NO |  | NO | HARLEM ROAD AND MINERAL SPRINGS ROAD, BLOCK 700. |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 249668.0748 | 503681.3518 | GASOLINE | 3 | 186 | 130 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 1440 | 30 | YES | 8 | 1900 | 1 | 81 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.L. DENNARD, VICE PRESIDENT, OPERATIONS | 2146582226 | LEAK WAS DISCOVERED AT 0615 HRS. AND THE LINE WAS COMPLETELY SHUT DOWN BY 0617 HRS. MOBIL PIPE LINE COMPANY (MPLCO.) MAINTENANCE CREWS WERE IMMEDIATELY DISPATCHED AND RECOVERY AND CLEANUP PROCEDURES WERE INITIATED. REFINED PETROLEUM PRODUCT ENTERED A STORM SEWER THAT DRAINED INTO THE BUFFALO RIVER. SPILL CONTAINMENT BOOMS WERE INSTALLED IN THE BUFFALO RIVER. CLEANUP AND RECOVERY OF FREE PRODUCT HAS BEEN SUCCESSFULLY COMPLETED. A SITE ASSESSMENT AND SITE REMEDIATION PLAN IS BEING DEVELOPED FOR THE SOIL AND GROUNDWATER WITH THE APROVAL OF DEC FOR THE FINAL SITE RESTROATION. LEAK WAS CAUSED BY EXTERNAL CORROSION RESULTING FROM DIRECT CONTACT WITH A 4 INCH UNPROTECTED WATER LINE. THIS WATER LINE WAS INSTALLED IN THE 1950'S BY AN UNKNOWN CONTRACTOR AND OUR RECORDS REFLECT 12 INCHES OF CLEARANCE. ACTIVITIES SINCE THE 1950'S.WHICH RESULTED IN THE DIRECT CONTACT,ARE BEING RESEARCHED. PERMAMENT REPAIR WAS MADEBY REPLACING DAMAGED SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19900165 | 1990-12-11 | 4906 | EXXON PIPELINE CO | NO | 1990-11-13 | 1200 | LA | CADDO |  | NO |  | NO | LEAK OCCURRED IN T20N, R14W, SEC 5 ON THE RODESSA - RED CHUTE JCT. 8-INCH TRUNK LINE, STATION NO. 1013+21. THE LOCATION IS ADJACENT TO LA HWY. 71. |  | LINE PIPE | PIPE |  | 1943 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 582.5588 | 1175.2565 | CRUDE OIL | 1 | 75 | 70 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 315 | 25 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.E. COX, ENVIRONMENTAL & REGULATORY COMPLIANCE MANAGER | 7136565521 | ON NOVEMBER 8, 1990, APPROXIMATELY 1400 HOURS, THE LANDOWNER WAS PLOWING HISFIELD WHEN HE STRUCK EXXON PIPELINE COMPANY'S 8-INCH PIPELINE. HE REPORTED THE OCCURRENCE TO EXXON PIPELINE COMPANY ON NOVEMBER 13, 1990 AT 1145 HOURS WHEN HE NOTICED CRUDE OIL AT THE LOCATION WHERE HE STRUCK THE PIPELINE. UPON KNOWLEDGE OF THE LEAK, THE LINE WAS SHUT IN ON 11/13/90 AT 1200 HOURS. THE CRUDE OIL WAS CONTAINED BY NATURAL SURROUNDING. EXXON PIPELINE COMPANY PERSONNEL, CONTRACTED EQUIPMENT AND VACUUM TRUCKS WERE DISPATCHED TO THE LEAK SITE AT 1330 HOURS. THE LINE WAS TEMPORARILY REPAIRED BY PLACING A CLAMP OVER THEDAMAGED SECTION OF THE PIPE. THE LINE WAS RESTORED TO SERVICE AT 1600 HOURSON 11/13/90. THE LINE WAS SHUT IN ON NOVEMBER 15, 1990 AT 0900 HOURS TO PERMANENTLY REPAIR THE LINE BY REPLACING THE DAMAGED SECTION OF PIPE. THE LINE WAS PLACED BACK INTO PERMANENT SERVICE ON NOVEMBER 15, 1990 15 1600 HOURS.
2017-09-29 08:50 | YES | YES | 19900166 | 1990-12-11 | 22610 | WILLIAMS PIPELINE CO | YES | 1990-11-08 | 945 | IL | WHITESIDE |  | NO |  | NO | LS # D039, NW 1/4, R63, T20N, SECTION 18. APPROXIMATELY 150 FEET WEST OF ILLINOIS - MISSISSIPPI CANAL, TWO MILES WEST OF HIGHWAY 88. |  | LINE PIPE | OTHER | DRAIN VALVE LEAK | 1954 | OTHER | DRAIN VALVE LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 1 | 0 | 1 | 1 | 0 | 1 | 20000 | 16644.5383 | 33578.7568 | L. P. G. | 2 | 668 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATION | 9185883850 | ON NOVEMBER 8, 1990, WHILE WORKING IN A BURIED GATE VALVE BOX A CONTRACTOR'S(PRAIRIE CONTRACTORS) EMPLOYEE WAS OVERCOME WITH PROPANE FUMES & WAS ASPHYXIATED. CONTRACT CREWS HAD JUST COMPLETED A HYDROSTATIC TEST ON THE LINE AND WERE IN THE PROCESS OF DRAINING REMANENT WATER FROM THE BOTTOM OF ALL THE MAINLINE GATE VALVES. WHILE IN THE PROCESS OF DRAINING WATER FROM THE VALVE AT MP 203+02 ONE OF THE TWO CONTRATORS EMPLOYEES IN THE BOX WAS OVERCOME WITH PROPANE VAPORS. THE OTHER PERSON WAS ABLE TO GET OUT OF THE BOX AND SUMMON HELP. THE RESPONDING LOCAL RESCUE TEAM (FIRE DEPARTMENT) WAS ABLE TO RETRIEVE THE VICTIM FROM THE GATE VALVE BOX, HOWEVER, THEY WERE UNABLE TO REVIVE HIM. IN THE PROCESS, ONE FIREMAN WAS OVERCOME AND WAS HOSPITLIZED OVERNIGHT. THE DRAIN VALVE HAS BEEN SENT TO A METALLURGIST FOR FURTHER ANALYSIS. THE CENTRAL REGION OPS HAS BEEN INVOLVED IN THE ACCIDENT INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19900167 | 1990-12-11 | 22610 | WILLIAMS PIPELINE CO | YES | 1990-11-07 | 2031 | MO | VERNON |  | NO |  | NO | SW 1/4, SECTION 36, T35N, R30W, VERNON COUNTY MISSOURI. THE SPILL OCCURRED AT A LOCATION APPROXIMATELY SIX MI E. OF THE INTERSECTION OF MO STATE HWY E US HWY71 |  | LINE PIPE | PIPE |  | 1945 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 88000 | 73235.9686 | 147746.5299 | GASOLINE | 3 | 3000 | 500 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 700 | 680 | YES | 8 | 880 | 1 | 83 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN, VICE PRESIDENT - OPERATIONS | 9185883350 | AT APPROXIMATELY 20:31 HOURS ON 11/7/90 THE WPL DISPATCHING DEPARTMENT OBSERVED A PRESSURE DROP AT SHELDON STATION. THE UNIT AT SHELDON AUTOMATICALLY SHUT DOWN. THE DISPATCHER IMMEDIATELY SHUT DOWN THE OPERATION AND DRAINED INTO THE COLUMBIA TERMINAL TANK FARM. THE DISPATCHER CONTACTED FIELD PERSONNEL AND APPRISED THEM OF THE SITUATION. EMERGENCY RESPONSE CREWS WERE DISPATCHEDIMMEDIATELY TO SHUT MAINLINE VALVES AND THE SEARCH FOR THE SITE OF THE LEAK. AT APPROXIMATELY 22:45 HOURS ON 11/7/90 THE LEAK WAS FOUND AND EMERGENCY RESPONSE CREWS WERE DIRECTED TO THE AREA. THE CAUSE OF THE SPILL WAS DETERMINED TO BE A CORRODED AREA IN THE PIPE WHERE THE TOP OF THE PIPE WAS EXPOSED IN THE BOTTOM OF A DRY CREEK BED. THE PIPELINE WAS REPAIRED BY REPLACING THE CORRODED AREA OF PIPE. APPROXIMATELY 3,000 BARRELS OF PREMIUM UNLEADED GASOLINE WERE SPILLED WITH 500 BARRELS RECOVERED. ALL CLEANUP EFFORTS WERE COORDINATE WITH THE MISSOURI DEPARTMENT OF NATURAL RESOURCES (MDNR). APPROVAL WAS OBTAINED FROM THE MDNR TO BURN THE REMANENT PRODUCT TO AID IN SITE REMEDIATION.
2017-09-29 08:50 | NO | NO | 19900168 | 1990-12-12 | 26085 | SCURLOCK OIL CO | NO | 1990-12-01 | 115 | TX | GREGG |  | NO |  | NO | 300' NORTH OF GOFORTH ROAD AND 300' WEST OF MAGNOLIA ROAD L.B. OUTLAW SURVEY. |  | LINE PIPE | PIPE |  | 1933 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 10 | 8 | NO | NO | 6.63 | 0.25 | 24000 | OTHER |  | 702 | 50 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | OTHER | UNKNOWN | Null | Null | TOM HRNCIR, DIVISION SUPERINTENDENT | 9039845252 | LEAK OCCURRED IN 6 5/8" P.L. MOBIL P.L. REPRESENTATIVE, CHARLIE PALMER, NOTIFIED SCURLOCK OF LEAK. WE RESPONDED BY DEPLOYING CONTRACT CREW TO DIG OUT AND CLAMP LEAK. VACUUM TRUCKS AND MEN WITH WASH TRUCK WERE USED TO WASHTHE OIL DOWN AND PICK IT UP.
2017-09-29 08:50 | YES | NO | 19900169 | 1990-12-04 | 443 | AMOCO PIPELINE CO | YES | 1990-11-05 | 1320 | MO | MACON | ETHEL | NO |  | NO | MISSOURI: SW/4 SECTION 31 TOWNSHIP 59 NORTH RANGE 16 WEST E OF "AT&SF" RAILROAD; NEAR TURKEY CREEK. SEE ATTACHMENT A. |  | LINE PIPE | PIPE |  | 1923 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 3000000 | 2496680.7483 | 5036813.5184 | CRUDE OIL | 1 | 2400 | 2000 | NO | NO | 12 | 0.38 | 28000 | THREADED |  | 695 | 540 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.A. NEWMAN - MANAGER, PIPELINE ADMINISTRATION | 7089906108 | AMOCO PIPELINE PERSONNEL WERE PURGING THE PIPELINE IN QUESTION WITH NITROGENWHEN THE LEAK OCCURRED. HERE IS A SUMMARY OF EVENTS: CONSISTENT WITH APL'S ON-GOING EFFORT TO ELIMINATE POSSIBLE PROBLEMS FROM IDLE LINES, APL DECIDED TO PURGE ITS #2 CRUDE SYSTEM BETWEEN LAPLATA AND FREEMAN, MISSOURI, WITH NITROGEN AND DECOMMISSION IT. APL CONTRACTED WITH UCISCO, A NITROGEN SERVICE COMPANY, TO SUPPLY NITROGEN FOR THE CRUDE OIL OUT OF THE LINE INTO A TANK AT FREEMAN. UCISCO'S TWO NITROGEN TRUCKS WERE CONNECTED TO THE PIPELINE, AND THE PUMPING OF NITROGEN INTO THE PIPELINE COMMENCED ON MONDAY, NOVEMBER 5, 1990, ATABOUT 13:20 AND CONTINUED THROUGHOUT THE AFTERNOON. LATE IN THE AFTERNOON, ONE OF THE NITROGEN TRUCKS BEGAN DEVELOPING OPERATIONAL PROBLEMS AND, SHORTLYAFTER 18:00 HAD TO BE SHUT DOWN BY UCISCO. AT ABOUT THE SAME TIME, PRESSUREMEASUREMENT DEVICES INDICATED A PRESSURE DROP WHICH WAS LOGICALLY ASSOCIATEDWITH A REDUCTION IN PUMPING CAPACITY. THE REMAINING PUMP TRUCK CONTINUED OPERATING AND THE TANK AT FREEMAN CONTINUED RECEIVING OIL FROM THE LINE AT A REDUCED RATE. THE DISABLED PUMP TRUCK WAS REPAIRED AND PUT BACK ON LINE ABOUT 19:00. THE MAXIMUM PRESSURE AT THE LOCATION OF THE NITROGEN TRUCKS UP UNTIL THE SHUT DOWN OF THE FIRST TRUCK WAS 570 PSI. AFTER SHUT DOWN OF THE FIRST TRUCK PRESSURE DROPPED BELOW 300 PSI. FOLLOWING THE RETURN OF THE SECOND PUMP TRUCK, PRESSURE STAYED LOW LONGER THAN EXPECTED, WHICH APPEARED TO INDICATE THE LINE WAS AGAIN BEING PACKED. COMMUNICATIONS WITH APL'S TULSA CONTROL CENTER WERE HEIGHTENED IN A EFFORT TO MORE COMPLETELY UNDERSTAND THE REASONS WHY PURGE LINE PRESSURE WAS FAILING TO RETURN TO PRE-SHUTDOWN LEVELS. FLOW RATE AND PRESSURE INFORMATION WAS REQUESTED FROM THE TULSA CONTROL CENTER AT APPROXIMATELY 20:00. APL WAS IN THE PROCESS OF EVALUATING THIS DATA WHEN A CALL WAS RECEIVED AT 20:15 FROM A THIRD PARTY, NOTIFYING APL OF A POSSIBLE LEAK. APL IMMEDIATELY DIRECTED THE CESSATION OF NITORGEN PUMPING, AND AT ABOUT 20:20. APL PERSONNEL LEFT LAPLATA TO LOCATE THE SUSPECTED LEAK. APL PERSONNEL ARRIVED IN ELMER, CONFIRMED THE ODOR, BUT COULD FIND NO LEAK. AT ABOUT 21:30, AFTER SEARCHING THE AREA, APL PERSONNEL ACTUALLY FOUND THE LEAK NEAR ETHEL INA FARM FIELD 1/2 MILE AWAY FROM THE NEAREST ROAD. APL PERSONNEL PROCEEDED TO ANSPACH JUNCTION TO CLOSE THE NEAREST UPSTREAM VALVE. THE ACTUAL CAUSE OF THIS PIPE FAILURE IS UNDER INVESTIGATION. THE ACTUAL TIME OF RUPTURE IS NOT KNOWN, BUT IS BELEIVED TO HAVE BEEN BETWEEN 18:00 AND 20:00, NOVEMBER 5, 1990.
2017-09-29 08:50 | YES | NO | 19900170 | 1990-12-05 | 2731 | CHEVRON PIPELINE CO | YES | 1990-11-18 | 1210 | TX | WINKLER | WINK | NO |  | NO | APPROX. 2 MILES N.E. OF WINK, TEXAS /// SEC. 32, BLK.5, SURVEY: PSL. |  | TANK FARM | VALVE |  | 1980 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 250 | 200 | NO | NO | 0 | 0 | 0 | THREADED |  | 10 | 7 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.D. DIMMITT- COMPLIANCE COORDIANTOR | 9156877559 | 2" BLEEDER VALVE LEFT OPEN BY MISTAKE CAUSING THE SUMP TO OVER-FILL AND SPILL TO THE GROUND.
2017-09-29 08:50 | YES | NO | 19900171 | 1990-12-19 | 3370 | DIAMOND SHAMROCK REFINING & MARKETING CO | NO | 1990-11-16 | 2202 | TX | POTTER | AMARILLO | NO |  | NO | 3 MILES NORTH OF CITY LIMITS OF AMARILLO AT WESTERN STREET AND ST. FRANCIS STREET SECTION 14, BLOCK 9, BS&F SURVEY, POTTER COUNTY, TX. |  | TANK FARM | OTHER | UNKNOWN | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 6100 | 5076.5842 | 10241.5208 | GASOLINE | 3 | 297 | 41 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS, MANAGER, PIPELINE SAFETY & REGULATIONS | 8063783583 | AT 2202 HOURS ON NOVEMBER 16, 1990, THE PUMPER ON DUTY AT OUR AMARILLO PRODUCTS STORAGE AND LOADING TERMINAL FAILED TO OPEN THE FILL LINE VALVE TO THE PREMIUM UNLEAD TANK. UPON ATTEMPTING TO "STRIP-OFF" INTO THE TANK, A 1/2" RELIEF VALVE OPENED AND ALLOWED 297 BARRELS OF PREMIUM UNLEADED GASOLINE TO ESCAPE, ALL OF WHICH WAS CONTAINED WITHIN THE DIKED AREA. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED.
2017-09-29 08:50 | YES | NO | 19900172 | 1990-12-18 | 3370 | DIAMOND SHAMROCK REFINING & MARKETING CO | NO | 1990-11-26 | 1300 | NM | QUAY | TUCUMCARI | NO |  | NO | 3 MILES EAST OF THE CITY LIMITS OF TUCUMCARI ON HIGHWAY 54 SECTION 4, TOWNSHIP 11 NORTH, RANGE 31 EAST, QUAY COUNTY, NEW MEXICO. |  | TANK FARM | OTHER | UNKNOWN | 0 | OTHER | INCORRECT PROCEDURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12483.4037 | 25184.0676 | GASOLINE | 3 | 645 | 645 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS, MANAGER, PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APPROXIMATELY 1300 HOURS ON NOVEMBER 26, 1990, WHILE ATTEMPTING TO TRANSFER FUEL BETWEEN TANKS IN A STORAGE TERMINAL PREVIOUSLY OWNED BY ANOTHER OPERATOR, A DRAIN LINE FROM THE PUMP TO AN UNDERGROUND TANK BEGAN LEAKING ALLOWING645 BARRELS OF UNLEADED GASOLINE TO ESCAPE. SUBSEQUENT INVESTIGATION REVEALED THE UNDERGROUND TANK HAD BEEN REMOVED BY THE PREVIOUS OPERATOR AND THE DRAIN LINE STILL BURIED IN PLACE HAD NOT BEEN BLINDED OR CAPPED. THE PRODUCT, WHICH WAS CONTAINED ON OUR PROPERTY, DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE DRAIN LINE HAS SINCE BEEN REMOVED AND BLINDED AT THE PUMP TO PREVENT FURTHER ACCIDENTAL RELEASES.
2017-09-29 08:50 | YES | NO | 19900173 | 1990-12-17 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1990-12-10 | 2330 | IL | WHITE |  | NO |  | NO | NORRIS CITY STATION, HIGHWAY 1 NORTH |  | PUMPING STATION | OTHER | FLANGE GASKET | 1959 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 124834.0374 | 251840.6759 | L. P. G. | 2 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM U. HANNIGAN, EXECUTIVE VICE PRESIDENT | 7137593605 | AT 2330 HOURS C.S.T. ON DECEMBER 10, 1990, THE GAS DETECTOR AT THE NORRIS CITY PUMP STATION SHUT DOWN THE TEPPCO 20" MAINLINE DUE TO A LEAKING FLANGE GASKET. AT 2331 HOURS, THE OPERATOR ALSO SHUT DOWN THE PUMP ON THE 16" PARALLELPIPELINE SYSTEM. THE UPSTREAM STATIONS OF THE 20" PIPELINE SYSTEM WERE SHUTDOWN AT 2332 HOURS. AT APPROXIMATELY 2335 HOURS THE NORRIS CITY POLICE DEPARTMENT AND THE ILLINOIS STATE POLICE WERE NOTIFIED OF THE SITUATION. THE UPSTREAM BLOCK VALVE WAS CLOSED. THE DOWNSTREAM STATIONS WERE ALLOWED TO RUN TOREDUCE THE PRESSURE AT THE LEAK SITE. THE BLOCK VALVE DOWNSTEAM WAS THEN CLOSED AND THE LEAK SITE WAS BLOCKED IN. THE ESCAPING VAPORS FROM THE LEAK WERE NOT IGNITED. A TEMPORARY FLARE AND THE STATION FLARE WERE USED TO BLEED DOWN THE PIPELINE. THE LEAK SITE WAS EXCAVATED AND THE LEAKING FLANGE GASKET WHICH WAS THE SOURCE OF THE RELEASE WAS UNCOVERED. A TEMPORARY REPAIR WAS ACCOMPLISHED USING A PLIDCO FLANGE CLAMP TO SEAL OFF THE LEAK. THE LINE WAS REPRESSURIZED AND THE FLANGES WERE CHECKED TO DETERMINE THERE WAS NO LEAKAGE. THE SYSTEM WAS RESTARTED AT 0440 HOURS, DECEMBER 13, 1990 AND WAS OPERATED ATA REDUCED PRESSURE UNTIL 0555 HOURS, DECEMBER 14,1990. PERMANENT REPAIRS WERE THEN INITIATED AND ARE SCHEDULED FOR COMPLETION BY DECEMBER 14, 1990.
2017-09-29 08:50 | NO | NO | 19900174 | 1990-12-03 | 26138 | POWERINE OIL CO | NO | 1990-12-01 | 1150 | CA | LOS ANGELES | LONG BEACH | NO |  | NO | NEAR THE INTERSECTION WILLOW ST / GOLDEN AVE CITY OF LONG BEACH |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1664.4538 | 3357.8757 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 6 | 0 | 0 | WELDED |  | 720 | 500 | YES | 4 | 900 | 1 | 88 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWIN J. SATO - PIPELINE ENGINEER | 2139446111 | ON DEC 1, 1990 A PIPELINE SPILLED OCCURRED UNDER NORMAL OPERATING CONDITIONSIN A PUBLIC ROAD. DAMAGE TO THE COATING OCCURRED PRIOR TO THE ONE CAL UNDERGROUND SERVICE ALERT SYSTEM.
2017-09-29 08:50 | NO | NO | 19900175 | 1990-12-19 | 26138 | POWERINE OIL CO | NO | 1990-11-12 | 450 | CA | LOS ANGELES | HAWAIIAN GARDENS | NO |  | NO | INTERSECTION OF BLOOMFIELD AVE/ CARSON STREET CITY OF HAWAIIAN GARDENS. |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12483.4037 | 25184.0676 | CRUDE OIL | 1 | 4 | 4 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 720 | 250 | YES | 4 | 900 | 1 | 88 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWIN J. SATO, PIPELINE ENGINEER | 2139446111 | 0445 HRS-RECEIVED CALL FROM LOS ANGELES CO. FIRE DEPT REGARDING CRUDE OIL SPILL @ BLOOMFIELD AVE/CARSON STREET IN THE CITY OF HAWAIIAN GARDENS. POWERINEPIPELINE WAS NOT IN USE @ THIS TIME.0450 HRS- INSTITUTED EMERGENCY REPSONSE PLAN. OIL WAS CONTAINED BY LOSS ANGELES CO. PUBLIC WORKS DEPT.
2017-09-29 08:50 | NO | NO | 19900176 | 1990-12-19 | 26138 | POWERINE OIL CO | NO | 1990-11-11 | 910 | CA | LOS ANGELES | CERRITOS | NO |  | NO | INTERSECTION OF BLOOMFIELD AVE/SOUTHEAST CITY OF CERRITOS. |  | LINE PIPE | PIPE |  | 1970 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2 | 2 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 720 | 250 | YES | 4 | 900 |  |  | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWIN J. SATO - PIPELINE ENGINEER | 2137446111 | ON NOV. 11, 1990 A PIPELINE SPILL OCCURRED UNDER NORMAL OPERATING CONDITINS IN A PUBLIC ROAD. CLEANUP HAS BEEN COMPOUNDED BY CRUDE OIL FOLLOWING THE BASE MATERIAL UNDER A STORM DRAIN NEXT TO POWERINES PIPELINE.
2017-09-29 08:50 | NO | NO | 19900177 | 1990-12-19 | 26138 | POWERINE OIL CO | NO | 1990-11-07 | 445 | CA | LOS ANGELES | CERRITOS | NO |  | NO | BLOOMFIELD AVE 950' N/O DEL AMO BLVD CITY OF CERRITOS. |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 20 | 20 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 720 | 250 | YES | 4 | 900 |  | 88 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | KEITH DARNEY - PIPELINE OPERATOR | 2137446111 | ON NOV. 7, 1990 A PIPELINE SPILLED OCCURRED UNDER NORMAL OPERATING CONDITIONS IN A PUBLIC ROAD. CRUDE OIL ENTERED COYOTE CREEK FLOOD CONTROL (CONCRETE LINED) WHERE IT WAS CONTAINED AND REMOVED. NO SIGNIFICANT IMPACT TO WILDLIFE OCCURRED PER CALIFORNIA'S STATES LANDS COMMISSION AND FISH & GAME DEPT.
2017-09-29 08:50 | YES | NO | 19900178 | 1990-12-26 | 26149 | ALYESKA PIPELINE SERVICE CO | NO | 1990-11-23 | 1500 | AK | NORTH SLOPE BOROUGH | PRUDHOE BAY | NO |  | NO | PUMP STATION NO. 1 TANK 111 (SEE ATTACHMENTS). |  | PUMPING STATION | TANK |  | 1976 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 270 | 270 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | T.L. POLASEK - VICE PRESIDEN, OPERATIONS | 9072658923 | A WATER LEAK FROM UNDER TANK 111 WAS DISCOVERED BY AN OPERATING TECHNICIAN MAKING NORMAL ROUNDS AT ABOUT 1500 HOURS ON FRIDAY, NOVEMBER 23, 1990. SHORTLYTHEREAFTER IT WAS DECIDED THAT THE TANK WOULD BE TAKEN OUT OF SERVICE AND INSPECTED. BY 1628 HOURS OIL HAD BEGUN TO LEAK FROM THE TANK INTO THE TANK VAULT, BUT OPERATIONS PERSONNEL HAD ALREADY CONSTRUCTED DIKES AND BEGAN PICKING UP THE LEAKAGE WITH A VACUUM TRUCK. THE LEAK FIRST APPEARED FLOWING INTO THECONCRETE VAULT FORM THE 48-INCH BOTTOM FILL NOZZLE ON THE WEST SIDE OF THE TANK. INITIALLY, THE LEAKAGE RATE WAS ESTIMATED AT ABOUT FIVE GALLONS PER MINUTE, BUT WAS REDUCED TO A TRICKLE WHEN THE OIL HEAD IN THE TANK HAD BEEN LOWERED TO THE MINIMUM PUMPING LEVEL. THE ORIGINAL TANK LEVEL OF 8 FEET WAS REDUCED TO .39 FEET BY 1830 HOURS. AT THE PRESENT TIME, THE 48-INCH VALVES TO THETANK ARE CLOSED, THE TANK IS PARTIALLY INERTED WITH NITROGEN AND THE EXTERNAL LEAKAGE FROM THE TANK HAS ESSENTAILLY STOPPED. THE TOTAL QUANTITY OF WATER AND OIL REMOVED FROM THE TANK VAULT IS ESTIMATED TO BE 270 BARRELS. THE RECOVERED OIL AND WATER WAS INJECTED BACK INTO THE SYSTEM, RESULTING IN NO KNOWN MEASUREABLE LOSS. PLANS HAVE BEEN MADE TO COMPLETELY INERT THE TANK ATMOSPHERE WITH NITROGEN AS AN EXTRA SAFETY PRECAUTION AND TO ARRANGE FOR CLEANING ANDTOTAL ISOLATION (BLINDING) OF THE TANK CONNECTIONS. WE ANTICIPATE HAVING ENOUGH LIQUID NITROGEN ON SITE BY DECEMBER 29, 1990 TO FINISH THE NITROGEN PURGE, WHICH WILL TAKE ABOUT TWO FULL DAYS. AFTER THE NITROGEN PURGE THE TANK WILL BE VENTILATED WITH AIR AND BLINDS WILL BE PLACED IN ALL OF THE TANK NOZZLE. THIS WILL PROBABLY TAKE AN ADDITIONAL TWO TO THREE DAYS. IF THIS EFFORT GOES SMOOTHLY, IN SPITE OF THE EXTREME COLD WEATHER WORKING CONDITIONS, WE SHOULD HAVE ACCESS TO THE INTERIOR OF THE TANK BY ABOUT DECEMBER 29 OR 30, 1990.AT THAT TIME, WE WILL START THE CLEANING OF THE TANK SO THAT IT CAN BE INSPECTED AND THE CAUSE OF THE LEAK DETERMINED. THE NATURE OF THE NECESSARY REPAIR CAN NOT BE ASSESSED UNTIL AFTER THE CLEANING IS WELL UNDERWAY.
2017-09-29 08:50 | YES | NO | 19900179 | 1990-12-26 | 18718 | SUN PIPELINE CO | YES | 1990-12-03 | 1835 | OK | OKLAHOMA | DEL CITY | NO |  | NO | THE SPILL OCCURRED AT OUR DEL CITY TERMINAL AT RENO AND SUNNYLAND IN DEL CITY, OK. THE SPILL WAS FRORM TANK #23 OVERFLOWING WHICH WAS CONFINED TO THE DIKE AREA |  | TANK FARM | TANK |  | 1986 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1664.4538 | 3357.8757 | GASOLINE | 2 | 60 | 58 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT | 9185866231 | AT APPROXIMATELY 18:35 TANK #23 AT OUR DEL CITY TERMINAL IN DEL CITY, OK. BEGAN TO OVERFLOW BECAUSE IT REACHED ITS FULL CAPACITY. THE PRODUCT (UNLEADEDPREMIUM GASOLINE) SPILLED WAS CONFINED TO THE DIKE AREA FOR TANK #23 .THE PRODUCT FILLING TANK #23 WAS SWITCHED TO ANOTHER TANK WHEN THE SPILL WAS DISCOVERED (18:35 - 18:39). AT 19:02 A CALL WAS PLACED TO VACUUM TRUCK CONTRACTOR TO COLLECT THE PRODUCT. SPILL WAS COLLECTED AND PLACED IN TERMINAL'S OIL/WATER SEPARATOR. CLEAN-UP WAS COMPLETED 2:00 12/4/90.
2017-09-29 08:50 | YES | NO | 19910001 | 1991-01-07 | 15774 | PORTAL PIPELINE CO | YES | 1990-12-04 | 700 | ND | GRENORA |  | NO |  | NO | GRENORA STATION NE 1/4 SECTION 14, T159N, 4103W, WILLAIMS COUNTY. |  | PUMPING STATION | PUMP |  | 1979 | OTHER | NUT ON PUMP BACKED OFF | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 305 | 300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD JOHNSON, FIELD SUPERINTENDENT | 7018521087 | PART D - PACKING NUT ON PUMP BACKED OFF CAUSING PACKING TO BLOW OUT SPILLINGOIL IN STATION. PART K - THE PUMPING UNIT AT THE ABOVE MENTIONED LOCATION IS AMODEL 1755 GASO DUPLEX PISTON PUMP WITH ROD PACKING WHICH IS HELD IN PLACE BYA THREADED PACKING GLAND. THIS GLAND BACKED OFF THE STUFFING BOX AREA WHICHALLOWED THE PACKING TO COME OUT THUS LETTING A PRODUCT RELEASE ALONG THE ROD.REPAIRS WERE MADE BY REPLACING PACKING, THREADING GLAND BACK IN PLACE ANDINSTALLING A GLAND LOCKING DEVICE TO PREVENT ANY FUTURE OCCURRENCES.
2017-09-29 08:50 | YES | NO | 19910003 | 1991-01-10 | 3445 | DIXIE PIPELINE | YES | 1990-12-13 | 600 | AL | OPELIKA |  | NO |  | NO | OUTGOING MAINLINE SCRAPER TRAP, OPELIKA STATION 3-1/2 M. SOUTH OF I-85 ON SR 51 OPELIKA, AL 36801. |  | PUMPING STATION | SCRAPER TRAP |  | 1987 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | O-RING FAILURE | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1930 | 1606.1979 | 3240.35 | L. P. G. | 2 | 92 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.F. PHILLIPS, GENERAL MANAGER, DIXIE PIPELINE COMPANY | 4043962995 | O-RING FAILURE IN SCRAPER TRAP CLOSURE RESULTED IN RELEASE OF ROUGHLY 92 BARRELS OF PROPANE. PROPANE VAPORIZED AND FLOWED INTO A SMALL, SHALLOW RAVINE DOWNWIND OF TRAP. PUMP STATION WAS SHUT DOWN, AND LOCAL EMERGENCY OFFICIALS NOTIFIED AS A PRECAUTION. THE SCRAPER TRAP WAS ISOLATED, BLOWN-DOWN AND O-RING REPLACED WITHOUT INCIDENT. VAPORS DISSIPATED WITHIN 30 MINUTES AND NORMAL OEATIONS RESUMED.
2017-09-29 08:50 | NO | NO | 19910004 | 1990-01-09 | 18273 | SHELL PIPE LINE CORP | YES | 1990-12-05 | 830 | TX | UPTON | MCCAMEY | NO |  | NO | SW 1/4, NW 1/4, SECTION 37, BLOCK 35 THREE MILES NORTH OF MCCAMEY BARNSLEY-MCCAMEY NO.2 - 6-INCH. |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 4577.248 | 9234.1581 | CRUDE OIL | 1 | 40 | 35 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 850 | 100 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19910005 | 1991-01-08 | 2731 | CHEVRON PIPELINE CO | YES | 1990-12-16 | 1145 | TX | EASTLAND |  | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 832.2269 | 1678.9378 | L. P. G. | 2 | 50 | 0 | NO | NO | 10.75 | 0.37 | 35000 | WELDED |  | 1048 | 800 | YES | 24 | 1311 |  | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH - DIVISION MANAGER | 4098393100 | PASSER BY, NOTICED FROST OR ICE ON TOP OF THE GROUND IN THE MIDDLE OF OUR RIGHT-OF-WAY. THEY CALLED A NEAR BY GAS PLANT (ENSEARCH 108) WHICH CONTACTED OUR CONTROL CENTER WHICH IN TURNED SHUT DOWN THE SYSTEM. THE AFFECTED AREA WAS LIMITED TO A 15' SQUARE AREA. NITROGEN WAS INJECTED INTO THE PIPELINE TO DISPLACE THE LPG. THE CORRODED SECTION OF PIPE WAS CUT OUT AND REPLACED.
2017-09-29 08:50 | YES | NO | 19910006 | 1991-01-08 | 13131 | CONOCO INC | YES | 1990-12-12 | 1404 | OK | OKLAHOMA |  | NO |  | NO | SECTION 34 AND 27, TOWNSHIP 14 NORTH, RANGE 2 WEST OKLAHOMA COUNTY, OKLAHOMA. 1.0 MILE EAST OF I-35 ON HIGHWAY 66. |  | LINE PIPE | PIPE |  | 1990 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | CRUDE OIL | 1 | 1345 | 1125 | NO | NO | 12.75 | 0.25 | 52000 | WELDED |  | 1468 | 650 | YES | 4 | 1870 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | JIM M. LAHEY - MARYLAND DISTRICT MANAGER | 4057672357 | CONOCO PIPELINE COMPANY'S 12 INCH CRUDE OIL PIPELINE WAS HIT BY A STATE CONTRACTOR'S TRACKHOE ALONG HIGHWAY 66 ON DECEMBER 12, 1990 AT 14:04 HOURS. THE PUNCTURED LINE HAD PREVIOUSLY BEEN LOWERED IN MAY OF 1990 TO ACCOMODATE ROAD WORK BEING DONE BY THE STATE. THE LINE WAS LOWERED TO SPECIFICATIONS PROVIDED BY THE STATE. NO "ONE-CALL" NOTIFICATION WAS MADE BY THE STATE PRIOR TO THE INCIDENT; HOWEVER, PIPELINE WAS PROPERLY MARKED.
2017-09-29 08:50 | NO | NO | 19910007 | 1991-01-11 | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-12-13 | 1330 | OK | ROGER MILLS |  | NO |  | NO | BUXTON-BORGER (LINE 0) - MP 102-34+73 NW/4 SEC. 10, T11N,R23W. 1.5 MILES SE OF BERLIN,OK FROM HWY. 283/HWY. 6. GO 3 MILES N, 2 MILES E, AND 3/8 MILES SOUTH. |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 8400 | 6990.7061 | 14103.0779 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 10.75 | 0.2 | 42000 | WELDED |  | 1140 | 840 | YES | 24 | 1450 | 8 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | PHILLIPS PIPE LINE COMPANY EMPLOYEE DISCOVERED AN OILY SPOT WHILE LOCATING THE LINE FOR A FOREIGN CROSSING AS REQUESTED BY OKIE ONE-CALL. WHEN THE LINEWAS EXCAVATED, IT WAS DISCOVERED THAT THE PIPELINE HAD BEEN DAMAGED BY HEAVYEQUIPMENT. DISCOLORATION OF THE PIPE INDICATED THAT THE DAMAGE HAD OCCURREDEARLIER. DATE OF DAMAGED IS UNKNOWN.
2017-09-29 08:50 | YES | NO | 19910008 | 1991-01-16 | 26085 | SCURLOCK OIL CO | NO | 1990-12-27 | 915 | TX | RUSK | LAIRD HILL | NO |  | NO | TAKE HWY 42 S OF LAIRD HILL APPROXIMATELY 3 MILES GO W ON REID SWITCH RD. APPROXIMATELY 2 MILES THEN S 100 YARDS ON PIPELINE ROW TO LEAK SITE. |  | LINE PIPE | OTHER | UNKNOWN | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 416.1135 | 839.4689 | CRUDE OIL | 1 | 100 | 60 | NO | NO | 10.75 | 0.22 | 24000 | WELDED |  | 550 | 290 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | THOMAS G. HRNCIR - DIVISION SUPERINTENDENT | 9039845252 | SCURLOCK HOUSTON (PIPELINE CONTROL CENTER) NOTIFIED KILGORE OPERATIONS AT 5:30 AM. 12/27/90 OF A LOSS IN METER COUNTS RECEIVED AT LAGLORIA DELIVERY. IT WAS ASSUMED THAT THE LINE HAD A LEAK. THE LINE WAS SHUT DOWN IMMEDIATELY. AT DAY BREAK COMPANY & CONTRACT PERSONELL WERE DIRECTED TO SEVERAL LOCATIONS ALONG THE 30 MILE STRETCH OF PIPE TO BEGIN WALKING TO DETERMINE IF & WHERE THE LEAK WAS LOCATED. AT 9:15 AM. A WALKER SPOTTED THE LEAK SITE APPROXIMATELY 300' SOUTH OF REID SWITCH ROAD, STATION 3762+00. CREWS DUG OUT PIPE & INSTALLED A 10" CLAMP. A VACUUM TRUCK & CLEAN UP CREW WERE DISPATCHED TO PICK UP THE OIL AND SQUEEZE DOWN AND WASH THE GRASS. IT WAS DETERMINED THAT APPROXIMATELY 85 BARRELS WAS LOST AND APPROXIMATELY 60 BARRELS WERE RECOVERED.
2017-09-29 08:50 | YES | NO | 19910009 | 1991-01-08 | 2731 | CHEVRON PIPELINE CO | NO | 1990-12-19 | 1500 | TX | SCURRY | SNYDER | NO |  | NO | SEC 125, BLK.23,SURVEY: H&TC R.R.CO., FIELD NAME: SHARON RIDGE, TAKE STATE HWY.180 W OUT OF SNYDER, TX. |  | PUMPING STATION | PUMP |  | 1980 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | OTHER | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 175 | 175 | NO | NO | 0 | 0 | 0 | NO DATA |  | 1050 | 1050 | Null | 0 | 0 |  |  | NO DATA | Null | YES | OTHER | IMPRESSED CURRENT | OTHER | PUMP PACKING GLAND | Null | ONE CALL |  | Null | Null | D.D. DIMMITT, COMPLIANCE COORDINATOR | 9156877559 | TWO BOLTS HOLDING THE PACKING GLAND ON A P.D. PUMP BROKE CAUSING THE SPILL. THE CRUDE RELEASED FROM THE PUMP ONTO COMPANY PROPERTY AND INTO A CONTAINED AREA. THE CRUDE OIL WAS PICKED-UP BY VACUUM TRUCKS AND PUMPED BACK INTO THE SYSTEM.
2017-09-29 08:50 | NO | NO | 19910010 | 1991-01-15 | 2371 | CINIZA PIPELINE INC | NO | 1991-01-08 | 1245 | NM | MCKINLEY |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 25 | 0 | NO | NO | 0 | 0.25 | 1760 | WELDED |  | 620 | 380 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | OTHER | AIR PATROL | Null | Null | ROBERT ULLO - GENERAL MANAGER OF PIPELINE OPERATIONS | 5056328006 | TOTAL COST OF DAMAGE HAS NOT BEEN DETERMINED AS OF THIS DATE. A REVIESED REPORT WILL BE SUBMITTED WHEN A COST CAN BE ESTIMATED.
2017-09-29 08:50 | YES | NO | 19910011 | 1991-01-15 | 809 | ARCO PIPE LINE CO | YES | 1990-12-12 | 1000 | TX | GAINES |  | NO |  | NO | SW/4 OF SECTION 500, BLOCK G, CCSD & RGNG SURVEY, GAINES COUNTY, TEXAS 17 MILES SOUTHWEST OF DENVER CITY, TEXAS. |  | LINE PIPE | PIPE |  | 1939 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 11651.1768 | 23505.1298 | CRUDE OIL | 1 | 1107 | 625 | NO | NO | 6.63 | 0.2 | 35000 | WELDED |  | 910 | 714 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI | 3163311300 | A RUPTURE OCCURRED ON A 6' SECTION OF LAPWELD PIPE. A METALLURGICAL ANALYSIS IS BEING CONDUCTED.
2017-09-29 08:50 | NO | NO | 19910013 | 1991-01-18 | 18718 | SUN PIPELINE CO | YES | 1990-12-22 | 100 | PA | CHESTER | UPPER UWCHLAN | NO |  | NO | THE PIPELINE IN THIS AREA IS PARALLEL AND ADJACENT TO THE PENNSYLVANIA TURNPIKE, I-76, APPROXIMATELY 2 MILES WEST OF THE DOWNINGTOWN INTERCHANGE EXIT 23. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8322.2692 | 16789.3784 | FUEL OIL | 3 | 5 | 0 | NO | NO | 8 | 0.31 | 2530 | WELDED |  | 1100 | 70 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT, MANAGER, RISK MANAGEMENT | 9185866231 | REPORTED TO PIPELINE CONTROL CENTER BY CHESTER COUNTY FIRE RADIO DISPATCHER AS PRODUCT ON WATER AT MARSH CREEK LAKE. AT TIME OF REPORT, 8" LINE WAS NOT BEING OPERATED, BUT WAS LAID DOWN UNDER MINIMAL PRESSURE. INVESTIGATION INDICATED MINOR AMOUNT OF FUEL OIL ENTERING BLACK HORSE CREEK FROM RIGHT-OF-WAY OF SPL 8" PIPELINE. EXCAVATION OF PIPE APPROXIMATELY 20 FEET NORTH OF CREEK EXPOSED A FINE MIST COMING FROM PIPE. LEAK WAS CLAMPED. AFTER EXCAVATION WASCLEANED UP, PATCH WAS WELDED ON PIPELINE. TIME OF ACTUAL FAILURE IS UNKNOWN.
2017-09-29 08:50 | YES | NO | 19910014 | 1991-01-18 | 4906 | EXXON PIPELINE CO | YES | 1990-12-24 | 700 | MT | YELLOWSTONE | BILLINGS | NO |  | NO | AT THE BILLINGS METER STATION ON THE SILVERTIP TO EXXON REFINERY 12-INCH PIPELINE. |  | LINE PIPE | VALVE |  | 1970 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8322.2692 | 16789.3784 | CRUDE OIL | 1 | 250 | 240 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.E. COX, ENVIRONMENTAL & REGULATORY AFFAIRS MANAGER | 7136565521 | EPC EMPLOYEE HAD BEEN CLEANING THE STRAINER ON THE 21ST OF DECEMBER AND THE DRAIN LINES WERE FROZEN AT THE TIME. THE DRAIN VALVE WAS ACCIDENTLY LEFT OPEN WHEN THE WORK WAS COMPLETED. WHEN THE TEMPERATURE MODERATED, THE DRAIN LINE THAWED OUT AND THE CRUDE OIL DRAINED FROM THE METER TO THE SUMP. THE SUMP RAN OVER AND FLOODED THE METER STATION. THE DIKE AROUND THE METER STATION CONFINED THE OIL TO THE METER STATION ONLY.
2017-09-29 08:50 | YES | NO | 19910015 | 1991-01-18 | 12127 | MARATHON PIPE LINE CO | YES | 1990-12-19 | 827 | IL | EFFINGHAM | UNKNOWN | NO |  | NO | 10 YARDS EAST OF COUNTY ROADS 1610E AND 1000N, EFFINGHAM COUNTY, WATSON TOWNSHIP, SECTION 14, T7N, R63, STATE OF ILLINOIS. |  | PUMPING STATION | PUMP |  | 1968 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | FAILURE OF MR ELECTRICAL | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 83222.6916 | 167893.7839 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE PRESIDENT | 4194214002 | DURING NORMAL OPERATIONS AN ELECTRICAL COMMAND WAS ISSUED FROM THE OPERATIONS CENTER TO STOP THE #1 PUMPING UNIT AT EFFINGHAM STATION. THE MOTOR FOR THIS UNIT DID NOT SHUT DOWN ON COMMAND BECAUSE AN ELECTRICAL RELAY THAT CONTROLSSTART-UP AND SHUTDOWN FAILED TO PROPERLY ACCUATE. AS PART OF THE PRE-PROGRAMMED SHUTDOWN PROCEDURE, THE SUCTION AND DISCHARGE VALVES TO UNIT #1 CLOSED IN RESPONSE TO THE SHUT DOWN COMMAND. THE CLOSURE OF THESE VALVES CAUSED THE PUMP AND MOTOR TO OVERHEAT AND VIBRATE LOOSE. BEFORE THE UNIT COULD BE MANUALLY SHUT DOWN, BEARING AND SEAL FAILURES ALLOWED A SMALL QUANTITY OF OIL TO ESCAPE. THE PUMP AND MOTOR SUSTAINED SUBSTANTIAL DAMAGE.
2017-09-29 08:50 | NO | NO | 19910016 | 1991-01-08 | 12624 | MOBIL OIL CORP | NO | 1990-12-15 | 1445 | CA | LOS ANGELES | UNKNOWN | NO |  | NO | EAST OF OLD 99 HIGHWAY, 1 MILE SOUTH OF PYRAMID DAM. SEC. 11 T6 R18W. |  | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20805.6729 | 41973.446 | CRUDE OIL | 1 | 5 | 5 | NO | NO | 10 | 0.25 | 1953 | WELDED |  | 1376 | 500 | YES | 8 | 1720 | 9 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null |  | 0 | RECEIVED TELEPHONE CALL FROM DISPATCHER THAT A LEAK HAD BEEN REPORTED ON OLDHIGHWAY 99 BELOW PYRAMID LAKE. RESPONDED WITH MEN AND EQUIPMENT. DALLAS CONTROLLERS SHUT THE PIPELINE DOWN. WE EXCAVATED THE PIPELINE AND REPAIRED BY WELDING A 1' FULL ENCIRCLEMENT WRAP. WE STEAMED CLEANED THE STREETS AND REMOVED CONTAMINATED SOIL. RECOATED BARE PIPE WITH POLYKEN TAPE.
2017-09-29 08:50 | YES | NO | 19910017 | 1991-01-28 | 2731 | CHEVRON PIPELINE CO | NO | 1990-12-26 | 730 | TX | HARRIS | UNKNOWN | NO |  | NO | SEE ATTACHED MAP. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 166445.3832 | 335787.5679 | CRUDE OIL | 1 | 340 | 178 | NO | NO | 2 | 0.19 | 0 | OTHER |  | 150 | 70 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | A.E. SMITH - DIVISION MANAGER | 4098393100 | GOOSE CREEK GAUGER, (CPL) WAS ALERTED BY CHEVRON USA PERSONNEL. GAUGER CONFIRMED LEAK, SECURED PUMPING ACTIVITIES, AND CALL DISTRICT OFFICE FOR ASSTISTANCE. OIL HAD ENTERED GOOSE GREEK BAY FROM NEARBY PIPELINE LEAK. BOOMS WEREDEPLOYED, AS SWEEPS, ABSORBENT PADS, AND VACUUM TRUCKS WERE USED TO CONTAIN AND COLLECT THE OIL. ADDITIONAL ASSISTANCE FROM GARNER ENVIRONMENTAL WAS SECURED. A NEW SECTION OF HEAVY WALL PIPE HAS BEEN INSTALLED.CAUSE: WE BELIEVE A PASSED AUTO ACCIDENT AT THIS LOCATION MAY HAVE WEAKEN THE LINE JUST AS IT ENTERS THE ROAD XING CASING, AND WITH THE RECENT HARD FREEZES IN THE AREA HAD STRESSED THE LINE TO FAILURE.
2017-09-29 08:50 | YES | NO | 19910018 | 1991-01-28 | 13131 | CONOCO INC | YES | 1990-12-24 | 110 | WY | PLATTE | UNKNOWN | NO |  | NO | SE 1/4, SE 1/4, SEC 17, T26N, R65W. |  | TANK FARM | PIPE |  | 1955 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4161.1346 | 8394.6892 | CRUDE OIL | 1 | 2140 | 2110 | NO | NO | 12.75 | 0.1 | 24000 | WELDED |  | 90 | 80 | YES | 2 | 200 | 6 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWIGHT D. JACKSON - MGR, OPERATIONS ENGINEERING | 7132932130 | ON DECEMBER 24, 1990, AT APPROXIMATELY 1:10 AM, A 12-INCH TANK SUCTION LINERUPTURED WHILE A DELIVERY WAS BEING INITIATED OUT OF TANKAGE. CAUSE OF THE RUPTURE IS UNDER INVESTIGATION. APPROXIMATELY 2,140 BARRELS OF CRUDE OIL WASRELEASED INTO THE TANK DIKE AREA. AS THE GROUND WAS FROZEN TO A DEPTH OF APPROXIMATELY TWO FEET, VACUUM TRUCKS WERE ABLE TO RECOVER 2,110 BARRELS.
2017-09-29 08:50 | YES | NO | 19910019 | 1991-01-30 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1990-12-30 | 1042 | AR | CLEVELAND | UNKNOWN | NO |  | NO |  |  | PUMPING STATION | PUMP | ELECTRIC DRIVER | 1990 | OTHER | DRIVER SHAFT TORQUE TWIST | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 37450.2112 | 75552.2028 | L. P. G. | 2 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O. HORTON CUNNINGHAM - VICE PRESIDENT - OPERATIONS | 7137593615 | THE FORDYCE PUMP STATION'S 200" MAINLINE PUMP WAS SHUT DOWN BY SUPERVISORY CONTROLS AT 1041 HOURS C.S.T. ON DEC. 30, 1990. THIS WAS DUE TO A MOTOR DRIVESHAFT FAILURE. THE MOTOR FAILURE DAMAGED THE PUMP, CAUSING A RELEASE OF ISOBUTANE WHICH IGNITED. THE FIRE WAS LIMITED TO THE AREA AROUND THE PUMP. EXPERTS HAVE CLASSIFIED THE FAILURE AS A DRIVE SHAFT TORQUE SHEAR TWIST, HOWEVERTHE EXACT CAUSE IS STILL UNDER INVESTIGATION. IMMEDIATE ACTION WAS TAKEN TOBRING THE 20" SYSTEM DOWN. THE DOWNSTREAM STATIONS WERE ALLOWED TO RUN, REDUCING PRESSURE AT THE FORDYCE STATION. PERSONNEL WHICH WERE DISPATCHED TO THELOCATION CLOSED THE SOUTH STATION BLOCK VALVE AT 1225 HOURS AND THE NORTH BLOCK VALVE AT 1255 HOURS. THE FIRE WAS ALLOWED TO BURN ITSELF OUT AND DAMAGE WAS LIMITED TO THE 20" MAINLINE PUMP, MOTOR AND CONTROLS. THERE WERE NO PERSONNEL INJURIES OF ANY KIND.
2017-09-29 08:50 | YES | NO | 19910020 | 1991-01-30 | 443 | AMOCO PIPELINE CO | YES | 1990-12-25 | 400 | OK | CREEK | UNKNOWN | NO |  | NO | AMOCO PUMP STA, EAST EDGE OF DRUMRIGHT, OK., NE CORNER OF HWY 99 AND 33 INTERSECTION, SW 1/4 SECTION 33, TOWNSHIP 18 NORTH, RANGE 7 EAST. |  | LINE PIPE | VALVE |  | 0 | OTHER | VALVE BODY CRACKED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 83222.6916 | 167893.7839 | CRUDE OIL | 1 | 1000 | 975 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. CARICO | 9182257271 | A CAST IRON VALVE BODY CRACKED DURING SUB ZERO TEMPERATURES. RESIDUAL WATER FROM A PREVIOUSLY CONDUCTED HYDROSTATIC TEST MAY HAVE CONTRIBUTED TO THE FAILURE.
2017-09-29 08:50 | NO | NO | 19910021 | 1991-01-28 | 12628 | MOBIL PIPELINE CO | YES | 1990-12-16 | 645 | NJ | GLENCESTER | PAULSBORO | NO |  | NO | MOBIL OIL REFINERY ON BILLINGSPORT ROAD. |  | PUMPING STATION | VALVE | 12" CHECK VALVE | 1942 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | TOP FLANGE GASKET FAILED | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24966.8075 | 50368.1352 | FUEL OIL | 3 | 10 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD, VICE PRESIDENT, OEPRATIONS. | 2146582226 | ON DECEMBER 16, 1990, A GASKET FAILURE OCCURRED IN THE FLANGE OF A CHECK VALVE AT MPLCO'S PAULSBORO PUMP STATION NEAR PAULSBORO, NJ, RESULTING IN A SPILLOF APPROXIMATELY 10 BARRELS OF NO.2 FUEL OIL. A PORTION OF THIS VOLUME REACHED THE DELAWARE RIVER. THE PIPELINE WAS IMMEDIATELY SHUT DOWN, AND CONTAINMENT, RECVOERY, & CLEAN-UP OF THE AFFECTED SITE, AND THE RIVER, WAS BEGUN AT ONCE. APPROXIMATELY 5 BARRELS OF PRODUCT WERE RECOVERED WITH THE REMAINDER ABSORBED IN SORBENT PADS AND SOIL, OR LOSS DUE TO EVAPORATION. ALL RECOVERABLE OIL WAS REMOVED USING VACUUM TRUCKS BY DECEMBER 17, 1990. OIL CONTAMINATED SOIL WAS EXCAVATED AND WILL BE DISPOSED OF IN COMPLIANCE WITH STATE REGULATIONS. THE GASKET WAS REPLACED ON DECEMBER 16, 1990, AND THE INTERSTATE PIPELINE
2017-09-29 08:50 | YES | NO | 19910022 | 1991-01-30 | 15490 | PHILLIPS PIPE LINE CO | YES | 1990-12-30 | 1045 | MO | COLE | UNKNOWN | NO |  | NO | BORGER-E. CHICAGO "BLUE" LINE - MP 571-19+36. SEC. 26, T44N, R11W. APPROXIMATELY 100' EAST OF THE MOREAU RIVER AND 100' SOUTH OF HIGHWAY 50. |  | LINE PIPE | GIRTH |  | 1942 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | L. P. G. | 2 | 1200 | 0 | NO | NO | 8.63 | 0.19 | 40000 | WELDED |  | 1080 | 300 | YES | 24 | 1470 | 10 | 72 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | BASED ON AN UNEXPECTED PRESSURE DROP WHILE THE JEFFERSON CITY TO ROSEBUD SECTION OF THE BLUE LINE WAS SHUT DOWN AND BLOCKED, FIELD PERSONNEL INVESTIGATEDAND DISCOVERED THE LEAK AT 10:45 AM. ON DECEMBER 30. THE LEAK RESULTED FROMA 2" CRACK IN THE CENTER OF A GIRTH WELD. THE LINE WAS REPAIRED AND PUT BACK INTO SERVICE.
2017-09-29 08:50 | YES | NO | 19910023 | 1991-01-24 | 19226 | TEXACO PIPELINE INC | NO | 1990-12-26 | 630 | IL | CLAY | CLAY | NO |  | NO | FROM CLAY CITY FLASHING LIGHT ON U.S. ROUTE 50 GO E 1.4 MI. TO RD #2000E THEN S 6/10 MI. TO RD. #515N THEN E 1/2 MI TO RD #2050E THEN S APX 3/4MI TO BOOSTER STA |  | PUMPING STATION | VALVE |  | 1967 | OTHER | CRACK IN BODY OF VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 23000 | 19141.2191 | 38615.5703 | CRUDE OIL | 1 | 500 | 490 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L. BARRETT, AREA SUPERINTENDENT | 6185486068 | WHILE AT THE CLAY CITY STATION, A CONTRACT EMPLOYEE HEARD A LOUD "POPPING"SOUND AND NOTICED OIL ESCAPING FROM THE VICINITY OF THE DOWNSTREAM VALVE. HE IMMEDIATELY NOTIFIED LAWRENCEVILLE STATION OPERATOR AND THE UPSTREAM STATION AT PATOKA WAS SHUT DOWN. CLAY CITY STATION WAS NOT RUNNING AT THE TIME. OPEATING PRESSURE AT THE STATION WAS 580 LBS. AT THE TIME OF THE VALVE FAILURE. MAXIMUM ALLOWABLE OPERATING PRESSURE IS 1060 LBS. VALVE AND COMPANION FLANGES WERE CUT OUT. SEVEN FEET OF NEW 12" 0.375 WALL THICKNESS PRE-TESTED PIPE WAS INSTALLED. BOTH WELDS PASSED X-RAY.
2017-09-29 08:50 | NO | NO | 19910024 | 1991-01-25 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-12-18 | 645 | CA | IMPERIAL | NILAND | NO |  | NO | INSIDE SFPP'S NILAND STATION. |  | LINE PIPE | VALVE | MAINLINE CHECK VALVE | 1988 | OTHER | O-RING ON CHECK VALVE LID | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 41611.3458 | 83946.892 | OIL AND GASOLINE | 3 | 2 | 1 | NO | NO | 20 | 0.38 | 60000 | WELDED |  | 1440 | 1090 | YES | 8 | 2125 | 12 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUND, SENIOR VICE PRESIDENT, OPER & ENGINEERING | 2134867720 | O-RING ON MAINLINE CHECK VALVE BETWEEN SFPP'S NILAND STATION INCOMING AND OUTGOING BLOCK VALVES DAMAGED CAUSING A SMALL REFINED PETROLEUM PRODUCT LEAK.
2017-09-29 08:50 | YES | NO | 19910025 | 1991-01-25 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1990-12-17 | 1415 | CA | SAN BERNARDINO | RIALTO | NO |  | NO | INSIDE SFPP'S COLTON STATION |  | PUMPING STATION | OTHER | COLTON STATION SURGE TANK | 1955 | OTHER | MANIFOLD VALVE MALFUNC. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 83222.6916 | 167893.7839 | TURBINE FUEL | 3 | 20 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPER & ENGINEERING | 2134867720 | WHILE FLUSHING SURGE SYSTEM, THE MANIFOLD VALVE MALFUNCTIONED.
2017-09-29 08:50 | NO | NO | 19910026 | 1991-02-05 | 809 | ARCO PIPE LINE CO | YES | 1990-12-31 | 1305 | TX | HARRIS | GALENA PARK | NO |  | Null | NORTH SIDE OF HOUSTON SHIP CHANNEL, 1/2 MILE SOUTH OF CLINTON DRIVE, GALENA PARK, TX. EZEKIAL THOMAS SURVEY, A-73. |  | LINE PIPE | SCRAPER TRAP |  | 1990 | OTHER | FAULTY "O" RING SEAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1664.4538 | 3357.8757 | CRUDE OIL | 1 | 4 | 4 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | V.P. DRISKI, CRUDE BUSINESS MANAGER | 3163311300 | SCRAPER CRAP CLOSURE WAS FOUND TO BE LEAKING BY COMPANY EMPLOYEE DURING ROUTINE INSPECTION OF FACILITIES.
2017-09-29 08:50 | YES | NO | 19910027 | 1990-01-31 | 19335 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1991-01-06 | 1400 | TX | UPTON | UNKNOWN | NO |  | NO | SECTION 52, BLOCK 35, H&TC RR CO. SURVEY 1 1/2 MILES NORTH OF MCCAMEY, TEXAS. |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2009.3254 | 4053.6209 | CRUDE OIL | 3 | 140 | 100 | NO | NO | 12.75 | 0.38 | 25000 | COUPLED |  | 850 | 85 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWIN H. GRIPP - DISTRICT MANAGER | 9159497019 | THE LEAK WAS REPORTED AT 1400 ON JANUARY 6, 1991. THE LINE WAS NOT OPERATING AT THE TIME OF THE LEAK. LEAK WAS DUG OUT AND CLAMPED OFF BY 1600. RECOVERED OIL WAS TAKEN TO CRANE STATION. TEMPORARY REPAIRS MADE WITH HALF-SOLE AND GASO CLAMPS. OIL SOAKED AREA COVERED WITH FRESH DIRT. PERMANENT REPAIRS WILL BE MADE AT A LATER DATE.
2017-09-29 08:50 | YES | NO | 19910028 | 1991-02-12 | 13131 | CONOCO INC | YES | 1991-01-11 | 147 | OK | DELAWARE | UNKNOWN | NO |  | NO | TWO MILES SOUTH OF AFTON, OKLAHOMA. |  | PUMPING STATION | PUMP |  | 1955 | OTHER | MECHANICAL SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1400 | 1125.2222 | 2270.0277 | L. P. G. | 2 | 2023 | 0 | YES | NO | 10 | 0.37 | 35000 | WELDED |  | 890 | 210 | YES | 8 | 1160 | 1 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.G. HUBBARD - MANAGER, SUPPLY AND TRANS ENVIR AFFAIRS | 7132932032 | AT 01:47 ON JANUARY 11,1991, A SEAL FAILURE ALARM ALERTED CONOCO'S OIL MOVEMENT DEPARTMENT IN HOUSTON, TEXAS OF A POTENTIAL PROBLEM AT CONOCO PIPE LINE COMPANY'S AFTON PUMP STATION. UPON HIS ARRIVAL, THAT STATION WAS FOUND TO BE ON FIRE. BLOCK VALVES IMMEDIATELY UPSTREAM AND DOWNSTREAM ON THE TWO 10-INCHPIPELIENS WERE CLOSED TO STOP THE FLOW OF PROPANE TO THE FIRE. LOCAL FIRE DEPARTMENT, CONTRACTORS, AND ADDITIONAL CONOCO PERSONNEL WERE SUMMONED. THE FIRE WAS MONITORED AND ALLOWED TO BURN ITSELF OUT.
2017-09-29 08:50 | YES | YES | 19910029 | 1991-02-11 | 26099 | TAMPA BAY PIPELINE CO | NO | 1991-01-17 | 1500 | FL | HILLSBOROUGH | TAMPA | NO |  | NO | IMC TERMINAL, PORT SUTTON ROAD. TAMPA, FL 33619. |  | PUMPING STATION | OTHER | 1/2" NIPPLE | 1981 | OTHER | SEE REMARKS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 6 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GLENN D. HOWELL - GENERAL MANAGER | 8136232431 | DURING NORMAL MAINTENANCE (CALIBRATION) OF SUCTION/DISCHARGE PRESSURE TRANSMITTERS AT INJECTION STATIONS, ONE TRANSMITTER (SUCTION) WAS FOUND WITH A STUCK CAP. EMPLOYEE WAS USING AN 18" PIPE WRENCH (FOR PURPOSE OF HAVING JAWS TO OPEN LARGE ENOUGH TO GO AROUND CAP) TO TRY TO GET CAP REMOVED FROM TRANSMITTER. THE EXTRA LEVERAGE FROM THE LENGTH OF THE PIPE WRENCH ALONG WITH THE FORCE EXERTED BY THE EMPLOYEE BROKE THE NIPPLE CONNECTING THE TRANSMITTER TO THE PIPELINE. THE ANGLE OF THE BREAK FORCED THE RELEASED AMMONIA TOWARD THE EMPLOYEE.
2017-09-29 08:50 | YES | NO | 19910030 | 1991-02-11 | 15156 | SINCLAIR PIPELINE CO | YES | 1990-12-24 | 1100 | WY | CARBON |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 83.2227 | 167.8938 | CRUDE OIL | 1 | 325 | 315 | NO | NO | 10 | 0.22 | 56000 | WELDED |  | 1440 | 60 | YES | 24 | 2000 | 1 | 74 | EXTERNAL | Null | YES | OTHER | IMPRESS CURRENT RECTIFIER | NO DATA |  | Null | NO DATA |  | Null | Null | J. CAMPBELL - MAINTENANCE SUPERVISOR | 3073242636 | AT APPROX. 11:00 AM ON DECEMBER 24, 1990 A LEAK WAS FOUND AT THE FORMER GETTY OIL TERMINAL. APPROXIMATELY 3/4 OF A MILE NORTH OF THE TOWN OF SINCLAIR, AT THE SW 1/4 OF SECTION 4, T 21 N, R 86 W IN CARBON COUNTY. SINCLAIR PIPELINE EMPLOYEES WERE SENT TO THE SCENE AND THE LINE WAS SHUT DOWN WHILE A CLAMP WAS PLACED ON THE LINE. THE SPILL OCCURRED INSIDE THE FIRE WALL OF THE TERMINAL AND DID NOT REACH ANY WATER SOURCE. 325 BARRELS OF CRUDE REPORTED OUT OF WHICH 315 BARRELS WERE RETRIEVED VIA BAC TRUCK. THE LINE WAS DOWN UNTIL 2:00 PM AND CLEAN-UP OPERATIONS IS STILL UNDERWAY. IF ANY OTHER INFORMATION IS REQUIRED, PLEASE CONTACT THE WRITER AT 307-324-2636.
2017-09-29 08:50 | NO | NO | 19910031 | 1991-02-26 | 443 | AMOCO PIPELINE CO | YES | 1991-02-01 | 1530 | TX |  | GREENVILLE | NO |  | NO | APPROXIMATELY 4 MILES N/E OF GREENVILLE, TEXAS. VANTIS - HEALDTON LINE - M.M. 30. |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | CRUDE OIL | 1 | 20 | 15 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 1440 | 500 | YES | 8 | 1800 | 9 | 89 | EXTERNAL | Null | YES | OTHER | DISBONDED COATING | NO DATA |  | Null | ONE CALL |  | Null | Null | PAT M. CLANCY - PIPELINE MAINTENANCE FOREMAN | 9037597131 | LEAK WAS 450' EAST SIDE OF FM 118 COMMUNITY OF JACOBIE IN HUNT COUNTY.
2017-09-29 08:50 | YES | NO | 19910032 | 1991-02-26 | 12624 | MOBIL OIL CORP | NO | 1991-01-31 | 2332 | CA | LOS ANGELES |  | NO |  | NO | M-70 PIPELINE, 1/2 MILE SOUTH OF HEWHALL STATION, INSIDE OF THE VALENCIA GOLF COURSE. |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1777 | 1200 | NO | NO | 12 | 0.25 | 2039 | WELDED |  | 1440 | 1380 | YES | 8 | 1825 | 10 | 85 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.R. JEFFRIES - MANAGER WEST COAST PIPE LINES. | 2134937224 | AT 2332 HRS. JANUARY 31, 1991, THE OPERATIONS CONTROL CENTER DETECTED A DROPIN PRESSURE AT NEWHALL STATION. THE FLOW WAS IMMEDIATELY STOPPED IN THIS SECTION OF THE PIPELINE AND THE VALVES WERE CLOSED AT NEWHALL STATION. PIPELINEPERSONNEL WERE DISPATCHED TO INVESTIGATE. A LEAK WAS DISCOVERED ON THE VALENCIA GOLF COURSE APPROXIMATELY 1/2 MILE SOUTH OF NEWHALL STATION. THE SPILL WAS A RESULT OF EXTERNAL CORROSION WHICH HAD PENETRATED THE WALL OF THE PIPE. THE DAMAGED 12" PIPE WAS REMOVED AND A 31 FT. SECTION OF NEW TESTED PIPE WAS INSTALLED. THE SPILLED OIL RAN FROM THE GOLF COURSE INTO A WATER RUNOFF DITCH AND INTO THE SANTA CLARA RIVER. CLEAN-UP IS CURRENTLY ONGOING AND BEING OVERSEEN BY THE CALIFORNIA DEPARTMENT OF FISH AND GAME. THE ESTIMATED PROPERTY DAMAGE IS EXTREMELY HIGH DUE TO THE COST OF HAND CLEANING OF PLANT LIFE ONTHE SANTA CLARA RIVER AND DISPOSAL OF CONTAMINATED MATERIAL AND SOIL.
2017-09-29 08:50 | YES | NO | 19910033 | 1991-02-25 | 400 | AMERICAN PETROFINA PIPE LINE CO | NO | 1991-01-18 | 1507 | TX | GLASSCOCK | GARDEN CITY | NO |  | NO | APPROXIMATELY 5.72 MI. NORTH OF GARDEN CITY, AND 2.4 MI. EAST OF HWY. 33. |  | LINE PIPE | PIPE |  | 1929 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 7500000 | 6027976.1037 | 12160862.5965 | CRUDE OIL | 1 | 690 | 490 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1039 | 860 | YES | 8 | 1266 | 7 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED - REGULATORY COMPLIANCE SUPV. | 9152645414 | D BY NATURAL DRAINAGE FEATURES IN THE AREA. CLEAN-UP AND LINE REPAIR WAS IMDIATELY BEGUN, WITH ALMOST ALL ACTIVITY COMPLETED ON SUNDAY, JANUARY 20TH.
2017-09-29 08:50 | YES | NO | 19910034 | 1991-02-20 | 12127 | MARATHON PIPE LINE CO | YES | 1991-01-17 | 450 | MI | MONROE | SAMARIA | NO |  | NO | MARATHON PIPE LINE COMPANY, SAMARIA STATION, 2185 SAMARIA ROAD. SAMARIA MICHIGAN, 48177, MONROE CO. SECT. 9, T8S, R8E. |  | TANK FARM | OTHER | UNKNOWN | 1939 | CORROSION | TANK BOTTOM CORROSION | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1205.5952 | 2432.1725 | CRUDE OIL | 1 | 547 | 477 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE PRESIDENT | 4194214002 | ON JANUARY 17, 1991 OPERATIONS CENTER ADVISED THE AREA GAUGER THAT THE CRUDEOIL LEVEL IN THE TANK 707 STARTED TO FALL. INVESTIGATION BY GAUGER SHOWED CRUDE OIL OUT INSIDE THE TANK DIKE. THE TANK HAS BEEN ISOLATED FROM THE PIPING SYSTEM AND DRAINED IN PREPARATION FOR A COMPLETE INTERNAL INSPECTION. CLEAN-UP OF THE CRUDE OIL FROM THE TANK DIKE IS ESTIMATED OVER $5,000.00.
2017-09-29 08:50 | YES | NO | 19910035 | 1991-02-14 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1991-01-14 | 200 | OK | PAYNE | CUSHING | NO |  | NO | 1 BLOCK NORTH, 1/2 BLOCK EAST OF INTERSECTION OF HWY 33 AND LINDWOD STREET IN CUSHING, OKLAHOMA. |  | LINE PIPE | OTHER | UNKNOWN | 1989 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | CRUDE OIL | 1 | 300 | 280 | NO | NO | 30 | 0.31 | 65000 | WELDED |  | 0 | 5 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT (MANAGER, RISK MANAGEMENT) | 9185866231 | WELD ACROSS TOP OF 30" PIPE FAILED WHILE RECEIVING CRUDE OIL. CAUSE OF FAILURE WAS PROBABLY STRESS. OIL RAN OFF PROPERTY INTO A BAR DITCH BY A MOTEL AND THEN INTO A SMALL STREAM. OIL WAS CONTAINED AND PICKED UP BY VACUUM TRUCKS. THE RESIDUAL OIL WAS BURNED BY THE CUSHING FIRE DEPARTMENT. MID-CONTENENTPIPE LINE COMPANY DISPATHCERS NOTED A SHORTAGE ON THE SYSTEM AND SHUT THE LINE DOWN.
2017-09-29 08:50 | YES | NO | 19910036 | 1991-02-21 | 14295 | OLYMPIC PIPE LINE CO | YES | 1991-01-17 | 825 | WA | PIERCE | SPANAWAY | NO |  | NO | 4420 - 180TH ST. E., SPANAWAY, WA 98387 - OLYMPIC PIPE LINE COMPANY FEE OWNED PUMP STATION FACILITY. REMOTE-NON RESIDENTIAL, RURAL AREA. |  | PUMPING STATION | OTHER | ELECTRIC MOTOR & PUMP | 1973 | OTHER | FIRE AND EXPLOSION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 241119.0441 | 486434.5039 | DIESEL FUEL | 2 | 2 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM A. MULKEY - REGULATORY / ENVIRONMENTAL COMPLIANCE | 2062357745 | JAN. 17, 1991 - OLYMPIC'S OPERATIONS CONTROL CENTER. AT APPROXIMATELY 08:23PST, CONTROLLER RECEIVED REMOTE INDICATION OF A PUMP MOTOR SHUTDOWN ON A 2500 HP UNIT (NO. 2) LOCATED AT THE SPANAWAY PUMP STATION, 35 MILES SOUTH OF THERENTON CONTROL CENTER. THIS SHUTDOWN FOLLOWED A HIGH CONTROL INDICATION AT THE PUMP STATION. AT 08:25, A 1500 HP UNIT (NO. 1) WAS INITIATED TO START ATSPANAWAY AND REMOTE INDICATIONS SHOWED THE ELECTRIC MOTOR STARTED AND ALL STATION PRESSURES ADJUSTED TO NORMAL FLOW CONDITIONS WITH THIS ONE MOTOR/PUMP UNIT ON. 20 MINUTES LATER (08:35) SPANAWAY PUMP STATION INDICATED A LOCK OUT CONDITION, THE RUNNING PUMP UNIT STOPPED AND A RESTART FEATURE WAS INHIBITED. WHILE TECHNICIANS DISPATCHED TO THE FACILITY WERE IN ROUTE, OLYMPIC'S CONTROLLER RECEIVED A CALL FROM THE SPANAWAY FIRE DISTRICT #2 OFFICE THAT THEY WERE RESPONDING TO A FIRE REPORTED AT OLYMPIC'S SPANAWAY FACILITY. APPARENTLY, THOUGH SUCTION AND DISCHARGE VALVES CLOSED ON UNIT NO. 2, A SHUTDOWN WAS NEVER EFFECTED. THIS INVESTIGATION IS ONGOING.
2017-09-29 08:50 | YES | NO | 19910037 | 1991-02-15 | 19536 | TOTAL PIPELINE CORP | YES | 1991-01-18 | 1545 | OK | KAY | BLACKWELL | NO |  | NO | NE/4 SECTION 25, T27N - R1W, KAY CITY., OKLAHOMA. |  | LINE PIPE | PIPE |  | 1930 | OTHER | CORROSION PIT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2600 | 2089.6984 | 4215.7657 | CRUDE OIL | 1 | 60 | 50 | NO | NO | 8.63 | 0.32 | 25069 | WELDED |  | 720 | 240 | YES | 8 | 1000 | 5 | 85 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GARY A STRACK - DOT-COORDINATOR | 3164425100 | EVIDENTLY REPORTED BY LANDOWNER, MAINT. DEPT. RESPONDED IMMEDIATELY AND INSTALLED A CLAMP. 42' OF NEW HYDROTESTED PIPE WAS IINSTALLED ON 1/24/91. NO ACTIVE CORROSION VISIBLE, CONFIRMED BY CLOSE INTERNAL CATHODIC PROTECTION SURVEY, COPY ATTACHED. SPECIMEN RETAINED FOR FURTHER INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19910038 | 1991-02-14 | 2731 | CHEVRON PIPELINE CO | NO | 1991-01-17 | 1050 | CA | CONTRA COSTA | PINOLE | NO |  | NO | 890 SAN PABLO BLVD., PINOLE CA. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 500 | 500 | NO | NO | 0 | 0.38 | 0 | WELDED |  | 0 | 50 | YES | 8 | 0 |  | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | K.D. BILLETER - DISTRIC SUPERVISOR | 4154327590 | AN OPERATOR ON A 977 CAT LOADER HIT THE PIPELINE WHILE CLEANING TRASH AND CUTTING TOE OF SLOPE WHERE PIPELINES ARE BURIES IN A HILLSIDE. CRUDE OIL SPRAYED FROM PIPELINE & SPRAY WAS BLOWN BY WIND IN A NORTHERN DIRECTION.
2017-09-29 08:50 | YES | NO | 19910039 | 1991-02-20 | 12127 | MARATHON PIPE LINE CO | NO | 1991-01-14 | 1415 | IL | MADISON | WOOD RIVER | NO |  | NO | MARATHON PIPE LINE COMPANY, WOOD RIVER STATION, SOUTH 6TH STREET WOOD RIVER, ILLINOIS 62095, MADISON COUNTY, WOD RIVER TWP. SEC 27, T5N, R9W. |  | PUMPING STATION | BOLTED FITTING |  | 1990 | OTHER | OPERATOR ERROR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | NATURAL GAS LIQUID | 2 | 40 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER, VICE PRESIDENT | 4194214001 | DURING NORMAL OPERATING PROCEDURE TO TRANSFER BUTANE FROM PHILLIPS PIPE LINECO., MARATHON PIPE LINE EAST SAINT LOUIS 8" LINE, THROUGH WOOD RIVER STATIONMANIFOLD TO CLARK REFINERY, WOOD RIVER. AFTER DELIVERING 900 BBLS OF NO LEAD GASOLINE (BUFFER) AND 340 BBLS OF BUTANE WAS METERED THROUGH WOOD RIVER STATION THE RATE STARTED TO FALL OFF. CLARK REFINERY OPERATOR IMPROPERLY ALINGED A 8 INCH VALVE AT THE CLARK REFINERY. THE FLOW OF BUTANE STOPPED, OVER-PRESSURING THE 8 INCH LINE RESULTING IN GASKET FAILURE AT VALVE S4, WOOD RIVER STATION. APPROXIMATELY 40 BBLS OF BUTANE WAS RELEASED.
2017-09-29 08:50 | YES | NO | 19910040 | 1991-02-21 | 18273 | SHELL PIPE LINE CORP | YES | 1991-01-29 | 1030 | LA | CALCASIEU | IOWA | NO |  | NO | SECTION 24, T-10-S, R-7-W, SIX MILES SOUTH OF IOWA. IOWA PUMP STATION. |  | PUMPING STATION | OTHER | FLARE | 1990 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1205.5952 | 2432.1725 | NATURAL GAS LIQUID | 2 | 45 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH , SAFETY & ENVIRONMENT | 7132416262 | FLARE FAILED TO IGNITE - REASON UNKNOWN.
2017-09-29 08:50 | YES | NO | 19910041 | 1991-03-05 | 15851 | PRIDE REFINING INC | NO | 1991-02-03 | 1130 | TX | COMANCHE | COMYN | NO |  | NO | APPROX 4 MILES E. OF DELEON, TX OH HWY 6, TURN S. ON TO FM RD. 1496 TO TOWN OF COMYN, TX CROSS OVER RR TRACKS TURN TO RHGT THEN BACK TO LEFT WHERE LINE CROSSES. |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | CRUDE OIL | 1 | 325 | 112 | NO | NO | 8.63 | 0.32 | 25000 | WELDED |  | 40 | 12 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DAVE CADDELL - VICE PRESIDENT | 9156748304 | THE OPERATOR OF A TREE TRANSPLANTING MACHINE WHILE ATTEMPTING TO RELOCATE A PECAN TREE STRUCK AND PUNCTURED THE PIPELINE. THE TREE TRANSPLANTING MACHINEIS OF A DESIGN THAT SURROUNDS THE TREE AND DIGS UP THE TREE COMPLETE WITH AROOT BALL FOR RELOCATION. THE PIPELINE WAS WELL-MARKED ACROSS THE PECAN ORCHARD WITH APPROXIMATELY 27 INCHES OF COVER AT THE ACCIDENT SITE. THE PIPELINE WAS TEMPORARILY REPAIRED USING A PIPELINE LEAK REPAIR CLAMP. ON 2/13/91, PERMANENT REPAIRS WERE MADE BY REPLACING THE DAMAGED PORTION OF THE PIPELINE WITH PRE-TESTED PIPE. LEAK #57797 AND 7B-91-10.
2017-09-29 08:50 | YES | NO | 19910042 | 1991-03-07 | 443 | AMOCO PIPELINE CO | YES | 1991-02-07 | 1310 | TX | HOCKLEY | UNKNOWN | NO |  | NO | GO SOUTH OF SUNDOWN, TX ON HWY 303 FOR 5 MILES, SLAUGHTER STATION IS NORTH OF HWY ON HWY FM-41. |  | TANK FARM | PIPE |  | 1944 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | CRUDE OIL | 1 | 3115 | 2115 | NO | NO | 16 | 0 | 0 | WELDED |  | 275 | 0 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | NOT KNOWN AT THIS TIME. | NO DATA |  | Null | NO DATA |  | Null | Null | P.L. RHYNE - AREA MANAGER/ LEVELLAND, TEXAS | 8068944200 | LEAK OCCURRED IN AT 16" FILL LINE OF TANK 6687 AT SLAUGHTER STATION. LEAK WAS CAUSED BY INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19910043 | 1991-03-08 | 19226 | TEXACO PIPELINE INC | YES | 1991-02-05 | 1400 | KS | FRANKLIN | UNKNOWN | NO |  | NO | NW/4 SECTION 11-T19S-R17E, FRANKLIN COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1988 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 40186.5074 | 81072.4173 | FUEL OIL | 1 | 60 | 50 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 913 | 596 | YES | 8 | 1805 | 5 | 88 | EXTERNAL | Null | YES | OTHER | INTERFERENCE FOREIGN P/L | NO DATA |  | Null | NO DATA |  | Null | Null | J.E. ZANG - DISTRICT MANAGER | 3163214645 | AT APPROXIMATELY 10:30 AM ON FEBRUARY 5, 1991, THE PUBLIC REPORTED AN ODOR NEAR THE KANSAS CITY PIPELINE ROUTE. COMPANY PERSONNEL ARRIVED AT THE LOCATION TO INVESTIGATE THE REPORT AT APPROXIMATELY 13:45. AT 14:12 THE PIPELINE WAS SHUT DOWN AND CONTAINMENT AND CLEANUP EQUIPMENT WAS ORDERED. LOCATION OF LEAK WAS AT INTERSECTION OF COMPANY'S PIPELINE WITH A FOREIGN LINE. INVESTIGATION REVEALED INTERFERENCE FROM THE FOREIGN PIPELINE'S CATHODIC PROTECTION HAD CAUSED THE LEAK. PERMANENT REPAIRS HAVE BEEN COMPLETED AND BOND MADE WITHTHE FOREIGN PIPELINE TO PREVENT RECURRENCE OF INTERFERENCE.
2017-09-29 08:50 | YES | NO | 19910044 | 1991-03-03 | 13131 | CONOCO INC | YES | 1991-02-02 | 2237 | KS | SEDGWICK | WICHITA | NO |  | NO | TOWNSHIP 28 SOUTH, RANGE 2 EAST, SECTION 11, SEDGWICK COUNTY, KANSAS INTERSECTION OF 127TH AND 13ST STREET. |  | LINE PIPE | PIPE |  | 1920 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | GASOLINE | 1 | 1092 | 63 | NO | NO | 6 | 0.28 | 30000 | WELDED |  | 1200 | 490 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY F. CLYNCH, DIVISION MANAGER | 4057676352 | AT APPROXIMATELY 22:37 CST ON FEBRUARY 2, 1991, CONOCO PIPE LINE COMPANY'S 6"WICHITA, KANSAS PETROLEUM PRODUCTS PIPELINE EXPERIENCED A LEAK. THE INCIDENT OCCURRED WHEN AN ACETYLENE WELD ON THE LINE CRACKED DUE TO BEING SUBJECTED ATO A HYDRAULIC SHOCK. CONOCO PIPE LINE COMPANY IS REPLACING THE 1920 VINTAGE 6" PIPELINE WITH 87 MILES OF NEW 10" AND 8" PIPE.
2017-09-29 08:50 | YES | NO | 19910045 | 1991-03-15 | 443 | AMOCO PIPELINE CO | YES | 1991-02-26 | 3 | UT | SUMMIT |  | NO |  | NO | NW 1/4, NW 1/4 SEC. 20 T6N - R8E SUMMIT COUNTY, UTAH. |  | TANK FARM | OTHER | TANK MIXER-ON TANK #48398 | 1989 | OTHER | PIN LOOSEN ON MIXER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 401.8651 | 810.7242 | CRUDE OIL | 1 | 3800 | 3796 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. PETERSON - AREA MANAGER | 3072662119 | LEAK OCCURRED ON A JENSEN TANK MIXER MODEL #620-VA-25. TOP LOCATING PIN DISLODGED ALLOWING MIXER ASSEMBLY TO "FALL" OUT OF PLACE, PUTTING A STRAIN ON PACKING RING CAUSING PACKING TO LEAK. ONCE LEAK WAS DISCOVERED, MIXER WAS REPOSITIONED BACK INTO PLACE AND PIN REPLACED, WHICH STOPPED THE FLOW OF OIL. LEAK OCCURED INSIDE TANK CONTAINMENT FIRE WALL,NO PRODUCT ESCAPED.ALSO GROUND WASFROZEN, SEEPAGE INTO SOIL WAS MINIMAL AND ALL BUT 3-4 BARRELS OF PRODUCT WERE RECOVERED AND RECLAIMED ON SITE.
2017-09-29 08:50 | NO | NO | 19910046 | 1991-03-12 | 18718 | SUN PIPELINE CO | YES | 1990-03-17 | 918 | PA | CHESTER | HONEYBROOK | NO |  | NO | NEAR THE INTERSECTION FO CHESTNUT TREE ROAD AND LIPPETT ROAD STA NO. 1/2292 CHESTER COUNTY, STA NO. 75+72, LIPPETT ROAD, HONEYBROOK, PA. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7139 | 5941.268 | 11985.9372 | FUEL OIL | 1 | 1 | 1 | NO | NO | 6 | 0.28 | 30000 | WELDED |  | 1200 | 1200 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT (MANAGER , RISK MANAGEMENT) | 9185866231 | AT 9:18 AM. ON MARCH 17, 1990, MR. STOLTZFUSS CALLED SPL DISPATCHING IN GLENHARDIE AND REPORTED A STAIN ON THE GROUND OVER THE PIPELINES NEAR THE INTERSECTION OF CHESTNUT TREE ROAD AND LIPPETT ROAD. BOTH THE 6" NORTH AND 8" ELVERSON LINES WERE IMMEDIATELY SHUT DOWN. GLEN AMMONS WAS NOTIFIED AND HE PROCEEDED TO THE SITE. HE BELIEVED THAT FUEL OIL HAD LEAKED FROM ONE OF THE LINES. TOM CROSS AND GLENN NOTIFIED D. CHALSON, H. HIESTER, R. ARNET AND R. NOTT. HE THEN CALLED OUT THE ICEDALE CREW. EXCAVATION OF THE 6" NORTH LINE STARTED AT 10:20 AM. AFTER THE LINES WERE BLOCKED IN AND THE LEAK WAS FOUND AT 10:45 AM. ON MARCH 17. THE LEAK WAS DUE TO A CORROSION PIT LOCATED AT THE 6:00O' CLOCK POSITION. A PLIDCO TEMPORARY REPAIR SLEEVE WAS IN PLACE AT 11:50 AM. VALVES WERE OPENED AND THE LINE RESTARTED AT 12:20 PM. EXCAVATION OF THECONTAMINATED SOIL WAS COMPLETED AT 2:30 PM. ALL SOIL WAS PLACED ON PLASTIC AND COVERED WITH PLASTIC. PADER WAS NOTIFIED BUT DID NOT COME TO THE SITE. CONSTRUCTION FENCE WAS PLACED AROUND THE EXCAVATION AND NO SMOKING SIGNS WEREPOSTED. WORK WAS SUSPENDED AT 3:30 PM. UNTIL MONDAY, MARCH 19, 1990.
2017-09-29 08:50 | NO | NO | 19910047 | 1991-03-12 | 18718 | SUN PIPELINE CO | YES | 1990-07-25 | 1100 | MI | WAYNE | HAMTRAMCK | NO |  | NO | NEAR THE INTERSECTION OF CARPENTER AND MCCOUGALL STREETS IN HAMTRAMCK, MI. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 14304 | 11904.1738 | 24015.5269 | FUEL OIL | 1 | 5 | 1 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 1000 | 720 | YES | 8 | 1269 | 12 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | AT 11:00 AM. ON WEDNESDAY, JULY 25, 1990, SUN PIPE LINE COMPANY RECEIVED NOTIFICATION FROM HAMTRAMCK WATER COMPANY THAT SEVERAL RESIDENTS HAD COMPLAINED OF HYDROCARBON ODORS IN THEIR HOMES. RESPONDERS FROM INKSTER ARRIVED AT THE SITE BY 11:30 AM. AND DETECTED FUEL OIL IN A STORM/SANITARY SEWER MANHOLE. PROBING OF THE LINE REVEALED OIL SATURATED SOIL AT EITHER SIDE OF MCDOUGALL STREET. EXCAVATION REVEALED AN AREA OF ACTIVE LOCALIZED CORROSION INSIDE A CASING UNDER MCDOUGALL STREET. CONTAMINATED SOIL WAS REMOVED AND TAKEN TO A NEARBY SUN TERMINAL FOR TEMPORARY STORAGE, AND LATER DISPOSED OF. HOMES IN THE AREA WERE MONITORED FOR THE PRESENCE OF VAPORS BUT NONE WERE NOTICED. PERMANENT REPAIRS INCLUDED REPLACEMENT OF THE ROAD CROSSING WITH PRETESTED PIPE.
2017-09-29 08:50 | NO | NO | 19910048 | 1991-03-12 | 18718 | SUN PIPELINE CO | YES | 1990-08-28 | 1730 | PA | BERKS | SINKING SPRING | NO |  | NO | FRETZTOWN ROAD, SPRING TOWNSHIP. |  | PUMPING STATION | OTHER | UNDERGROUND SUMP TANK | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 37452 | 31168.5625 | 62879.58 | GASOLINE | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | NO | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | AS PART OF A PROGRAM TO LOCATE A "MYSTERY" SPILL OF PRODUCTS THAT WERE LEACHING INTO A CONTAINMENT POND, VARIOUS SUMPS IN THE MONTELLO STATION WERE TESTED FOR LEAKS. THE FIRST SUMP TESTED DID NOT HOLD PRESSURE, WAS EXCAVATED AND FOUND TO HAVE 20 TO 30 PITS AND HOLES IN THE SHELL OF THE TANK. THIS TANK WAS REMOVED FROM SERVICE, AND LEACHING CEASED. THE COST OF TESTING OF THE TANK, REMOVAL AND CLEANUP WAS APPROXIMATELY $1,000; COST OF OTHER RELATED WORK ELEVATED THE TOTAL COST OF THIS PROJECT IN 1990 TO $37,452.
2017-09-29 08:50 | YES | NO | 19910049 | 1991-03-12 | 18718 | SUN PIPELINE CO | YES | 1990-06-15 | 1100 | PA | SCHUYLKILL | TAMAQUA | NO |  | NO | ONE FOURTH (1/4) MILE WEST OF STATE HWY 309 ON THE NORTH EDGE OF TAMAQUA. STATION IS ADJACENT TO THE LITTLE SCHUYKILL RIVER. |  | PUMPING STATION | SCRAPER TRAP |  | 0 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 118425 | 98556.4725 | 198828.2136 | GASOLINE | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | SPILLAGE FROM LEAKING PLUG OCCURRED BETWEEN 06/10/90 AND 6/15/90 AT THE TAMAQUA STATION (UNATTENDED). PRODUCT SATURAGED GROUND AND APPARENTLY LEACHED INTO LITTLE SCHUYKILL RIVER. THE SPILL WAS CONTAINED AND THE PLUG TIGHTENED. SATURATED SOIL WAS DUG OUT AND REPLACED. RECOVERY WELLS WERE INSTALLED TO SKIM OFF PRODUCT INTO A SERIES OF SEPARATORS, A COMBINATION CARBON FILTRATION AND AIR STRIPPER, BEFORE WATER WAS RETURNED TO RIVER. ACTURAL CLEANUP EXTENDED OVER A PERIOD OF MONTHS WITH NEGLIGIBLE RECOVERY.
2017-09-29 08:50 | NO | NO | 19910050 | 1991-03-12 | 18718 | SUN PIPELINE CO | YES | 1990-03-22 | 1255 | OH | LUCAS | OREGON | NO |  | NO | SOUTH SIDE OF PICKLE STREET. 2200' WEST OF THE INTERSECTION OF PICKLE STREET AND WHEELING STREET. |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18265 | 15200.6246 | 30665.7996 | NATURAL GAS LIQUID | 2 | 4 | 2 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1200 | 1100 | YES | 24 | 1500 | 10 | 58 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | AT 12:55 EST ON THURSDAY, MARCH 22, 1990, SUN PIPE LINE COMPANY RECEIVED A CALL AT THEIR TOLEDO STATION (IN OREGON, OH.) FROM SUN REFINERY REPORTING SPORADIC EMISSION OF LPG VAPORS FROM THE GROUND NEAR THE REFINERY'S PICKLE STREETGATE. THE PIPELINE WAS NOT IN OPERATION AT THE TIME OF THE REPORT AND WAS UNDER 1100 PSI PRESSURE. PRESSURE WAS BLED OFF BACK INTO THE REFINERY. AUTHORITIES WERE NOTIFIED. PICKLE STREET WAS BARRICADED AND CONTINUAL ATMOSPHERIC MONITORING OF THE RELEASE AREA AND LOCAL HOMES WAS CONDUCTED. SUN PIPE LINE COMPANY ISOLATED THE PIPELINE, DISPLACED THE BUTANE WITH #2 FUEL OIL AND EXCAVATED AND EXPOSED THE SUSPECTED LINE SECTION. INVESTIGATION REVEALED THREE AREAS OF ACTIVE CORROSION PITTING ON A CASED SECTION OF PIPELINE. ONE PITTEDAREA HAD THREE AREAS; THE LINE WAS PRESSURED, INSPECTED AND TEMPORARILY BACKFILLED UNTIL PERMANENT REPAIRS WERE MADE. PERMANENT REPAIR INCLUDED REPLACEMENT OF APPROXIMATELY 120 FEET OF PRETESTED PIPE, AND LOWERING TO ELIMINATE CASED CROSSING.
2017-09-29 08:50 | YES | NO | 19910051 | 1991-03-13 | 10012 | KANEB PIPELINE CO | YES | 1991-02-04 | 1204 | KS | COWLEY | UNKNOWN | NO |  | NO | SE 1/4, SECTIO 18, T-34-S, R-4-E. |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 32149.2059 | 64857.9338 | GASOLINE | 3 | 424 | 25 | NO | NO | 8.63 | 0.25 | 35000 | WELDED |  | 1324 | 283 | YES | 24 | 1665 | 4 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | NO | NO | L.L. ANDERSON, MANAGER REGULATORY AFFAIRS | 3162621408 | JOMAX CONSTRUCTION COMPANY OF GREAT BEND, KANSAS, GAVE NOTICE TO THE KANSAS ONE CALL SYSTEM APPROXIMATELY ONE MONTH BEFORE THIS ACCIDENT OCCURRED. APPROXIMATELY TWO WEEKS BEFORE THE ACCIDENT, JOMAX HAD A PRECONSTRUCTION MEETING.KANEB ATTENDED THIS MEETING, AND REQUESTED THAT A REPRESENTATIVE FROM JOMAX A BE PROPERLY MARKED. KANEB WAS ADVISED THAT JOMAX WOULD CONTACT KANEB PRIOR TO DITCHING ACTIVITY COMMENCING IN THE ARKANSAS CITY, KANSAS AREA, AND THAT IT WAS NOT NECESSARY TO MARK THE PIPELINE AT THAT TIME SINCE ALL CONSTRUCTION ACTIVITY WAS OUT OF THE AFFECTED AREA. KANEB HAS A POLICY THAT REQUIRES THE LINE TO BE LOCATED AND MARKED JUST PRIOR TO ANY ACTIVITY. IN ADDITION, KANEB REQUIRES THAT AN EMPLOYEE BE PRESENT DURING ANY ACTIVITY IN CLOSE PROXIMITY TO THE PIPELINE. UNFORTUNATELY, KANEB WAS NOT CONTACTED BY JOMAX, AND AS A RESULT, THE PIPELINE WAS RUPTURED BY THEIR DITCHING MACHINE.
2017-09-29 08:50 | YES | NO | 19910052 | 1991-03-13 | 22907 | WYCO PIPE LINE CO | YES | 1991-02-20 | 1300 | WY | NATRONA | EVANSVILLE | NO |  | NO |  |  | PUMPING STATION | OTHER | PROVER BARREL | 1968 | OTHER | O RING FAILURE/DOOR CLOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | DIESEL FUEL | 2 | 100 | 60 | NO | NO | 20 | 0.38 | 0 | OTHER |  | 800 | 300 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWANE A. SHROYER | 3032866400 | THERE WAS A FAILURE OF THE "O" RING IN A 16" PROVER DOOR CLOSURE.
2017-09-29 08:50 | YES | NO | 19910053 | 1991-03-14 | 22430 | WEST SHORE PIPE LINE CO | YES | 1991-02-15 | 515 | WI | MILWAUKEE | MILWAUKEE | NO |  | NO | INCIDENT OCCURRED ON THE GROUNDS OF WEST SHORE'S GRANVILLE PUMP STATION FACILITY, ADDRESS: 11115 COUNTY LINE ROAD, MILWAUKEE, WISCONSIN 53224. |  | PUMPING STATION | OTHER | STRAINER | 1981 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 34153 | 27449.7957 | 55377.3254 | FUEL OIL | 1 | 277 | 166 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD E. SCHAU - AREA MANAGER | 7082573740 | AT APPROXIMATELY 0515 HOURS ON FEBRUARY 15, 1991, A SECURITY GUARD FROM THE CLARK OIL TERMINAL CONTACTED THE CONTROL CENTER TO ADVISE THAT PRODUCT WAS SPRAYING FROM WEST SHORE'S GRANVILLE FACILITY. SHUTDOWN PROCEDURES WERE IMMEDIATELY INITIATED. THE INCOMING LINE (FROM SOUTH) WAS SHUT AND THE TERMINAL CLOSED OUT AT 0530 HOURS AND THE OUTBOUND SYSTEM WAS SHUTDOWN AT 0536 HOURS. MAINTENANCE PERSONNEL WERE DISPATCHED. THE SOURCE OF THE SPRAY WAS A METER STRAINER ON THE OUTGOING SYSTEM. THE LID GASKET ON THE STRAINER HAD FAILED. CONTRACT PERSONNEL WERE CALLED IN TO BEGIN CLEAN-UP ACTIVITIES. THE FAILED GASKET WAS REPLACED AND ALL FREE PRODUCT WAS PICKED-UP BY 2230 HOURS.
2017-09-29 08:50 | YES | NO | 19910054 | 1991-03-14 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1991-02-13 | 1300 | OK | LINCOLN |  | NO |  | NO | SW 1-15N-3E LINCOLN COUNTY, OKLAHOMA. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12500 | 10046.6268 | 20268.1043 | CRUDE OIL | 1 | 360 | 310 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 1000 | 100 | YES | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | INADEQUATE PROTECTION | NO DATA |  | Null | NO DATA |  | Null | Null | THURMAN SMITH - AREA FOREMAN | 4052758280 | EXTERNAL CORROSION: TEST STATIONS ON EACH SIDE OF LEAK SITE INDICATED ADEQUAE PROTECTION; HOWEVER, THE RESULTS OF A CLOSE-INTERVAL SURVEY SHOWED POTENTIALS TO BE LOW IN THE AREA OF LEAK.
2017-09-29 08:50 | YES | NO | 19910055 | 1991-04-01 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1991-03-18 | 1310 | IA | FRANKLIN | UNKNOWN | NO |  | NO | NW 1/4 OF SECTION 15 T93N R22W FRANKLIN COUNTY, IOWA. |  | PUMPING STATION | VALVE |  | 1970 | OTHER | VALVE PACKING BLEW OUT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1205.5952 | 2432.1725 | ANHYDROUS AMMONIA | 2 | 41 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RAY O. MORAN, JR., DIVISION MANAGER | 3144865488 | VAPOR CLOUD WAS SPOTTED BY PIPELINE AIR PATROL AT 1310 HOURS ON MARCH 18TH AND PRODUCT MOVEMENT COORDINATOR WAS NOTIFIED. GULF CENTRAL DISPATCHED PERSONNEL TO SITE. PMC CLOSED REMOTELY OPERATED BLOCK VALVE NEAREST LEAK SITE ON UPSTREAM SIDE AT 1310 HOURS, AND CONTINUED TO PUMP AWAY FROM LEAK SITE. GULF CENTRAL PERSONNEL ARRIVED AT SITE ABOUT 1358 HOURS AND FURTHER ISOLATED AREA BY CLOSING BLOCK VALVES NEARER LEAK SITE. NEAREST RESIDENT WAS ABOUT 1/2 MILE AWAY AND WAS NOTIFIED BY COMPANY PERSONNEL, AS WERE RESIDENTS WITHIN ONE MILE OF SITE, BUT NONE WAS EVACUATED. THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 1445 HOURS AND THE IOWA DEPARTMENT OF NATURAL RESOURSES AND THE AREA DOTOFFICE IN KANSAS CITY WERE NOTIFIED IMMEDIATELY AFTER THE NCR. ESCAPING AMMONIA WAS BURNED-OFF USING PROPANE BURNERS UNTIL LINE PRESSURE WAS DOWN LOW ENOUGH TO WORK ON IT. A 1" BALL VALVE ON A BY-PASS LINE HAD BLOWN THE PACKING OUT AND PRODUCT WAS LEAKING FROM THIS VALVE. THERE WERE NO SIGNS OF CORROSION. SECTION OF LINE WAS REMOVED, INCLUDING BY-PASS, AND REPLACED WITHOUT BY-PASS. CAUSE OF VALVE FAILURE IS UNKNOWN AT THIS TIME.
2017-09-29 08:50 | YES | NO | 19910056 | 1991-04-02 | 19585 | TRANS - MOUNTAIN OIL PIPELINE CO | YES | 1991-01-15 | 1145 | WA | WHATCOM |  | NO |  | NO | LAUREL PUMP STATION - 1009 EAST SMITH ROAD, WHATCOM COUNTY. |  | PUMPING STATION | PIPE |  | 1956 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 180839.2831 | 364825.8779 | CONDENSATE - WATER | 1 | 75 | 10 | NO | NO | 1 | 0.13 | 0 | THREADED |  | 4369 | 1055 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GLENN A. IRVING - VICE PRES. SECRETARY AND GENERAL COUNSEL | 6048766711 | AT APPROXIMATELY 11:45 PST ON JANUARY 15, 1991 THE COMPANY RECEIVED A REPORTOF AN APPARENT LEAK FROM THE LAUREL PUMP STATION LOCATED AT 1009 EAST SMITH ROAD IN WHATCOM COUNTRY, APPROXIMATELY 10 MILES NORTHEAST OF BELLINGHAM, WASHINGTON. THE REPORT WAS RECEIVED FROM THE BELLINGHAM PUBLIC HEALTH DEPARTMENTWHO HAD RECEIVED A REPORT FROM AN ANONYMOUS SOURCE. COMPANY PERSONNEL WERE IMMEDIATELY DISPATHCED TO THE LAUREL STATION, WHICH IS IN INTERMITTENT USE AND NOT REGULARLY MANNED, AND ISOLATED THE LEAK AT APPROXIMATELY 12:05 PST. STEPS WERE INITIATED IMMEDIATELY TO CONTAIN THE ESCAPED MATERIAL. CONTAINMENT FACILITIES REMAIN IN PLACE AND CLEANUP ACTIVITIES ARE ONGOING. THE LEAK ORIGINATED FROM A ONE INCH NOMINAL DIAMETER INSTRUMENTATION LINE. THE APPARENT CAUSE OF FAILURE OF THE INSTRUMENTATION LINE WAS TENSILE STRESS ON THE PIPE. THE MOST PROBABLE CAUSE OF THE TENSILE STRESS IS FROSTHEAVING OF THE GROUND AROUND THE PIPE. THE FAILED SECTION OF PIPE HAS BEEN SUBJECTED TO A METALLURGICAL ANALYSIS; A COPY OF THE ANALYSIS REPORT IS ATTACHED HERETO. THIS INCIDENT WAS REPORTED TELEPHONICALLY TO THE NATIONAL RESPONSE CENTRE ON JANUARY 16,1991. IT HAS BEEN ASSIGNED CASE NO. 55255.
2017-09-29 08:50 | YES | NO | 19910057 | 1991-04-01 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1991-03-03 | 1231 | MN | ITASCA | UNKNOWN | NO |  | NO | APPROX. 1/4 MI. W. OF THE ITASCA COMMUNITY COLLEGE CAMPUS AND 1/4 MI. NORTH OF HWY 169, JUST E. OF GRAND RAPIDS, MN CITY LIMITS. LAKEHEAD MILE POST 1009.90. |  | LINE PIPE | LONGITUDINAL WELD |  | 1967 | OTHER | SPLIT IN HEAT AFFECT ZONE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 14400000 | 11573714.1192 | 23348856.1853 | CRUDE OIL | 1 | 40500 | 39800 | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 611 | 473 | YES | 8 | 764 |  | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR - GENERAL MANAGE CORPORATE & TECH. SERVICES | 7153941404 | ON MARCH 3, 1991, THE PIPELINE OPERATOR DETECTED AN UNEXPLAINED DROP IN DISHCARGE RPESSURE AND SHUTDOWN LINE 3 AT 12:31 MST. AT 13:43 MST, LAKEHEAD'S SUPERIOR CONTROL CENTER RECEIVED CONFIRMATION OF THE LEAK AND AS A PRECAUTION, LAKEHEAD'S LINES 1 AND 2 WERE SHUTDOWN AT 14:02 MST. THE OIL WAS PRIMARILY COLLECTING IN A FIELD ADJACENT TO THE ITASCA COMMUNITY COLLEGE, BUT ALSO MIGRATED 3/4 MILE DOWN A STORM DRAIN LINE WHICH EMPTIED INTO THE PRAIRIE RIVER. NEARBY RESIDENTS WERE EVACUATED FROM 14:45 TO 20:00 MST. IN ADDITION, A ROADBLOCK WAS CONSTRUCTED ON THE HIGHWAY 169 CROSSING OVER THE PRAIRIE RIVER UNTIL THE SITE WAS SECURED. CONTAINMENT AND CLEAN-UP EFFORTS BEGAN BY LATE AFTERNOON WITH 3 LAKEHEAD CREWS AND SEVERAL CONTRACTORS ON-SITE . ONCE ACCESS TO THE LEAK SITE WAS ESTABLISHED, THE LINE WAS EXPOSED AND DRAINED, REVEALING A60" X 6" SPLIT IN THE HEAT AFFECTED ZONE OF THE LONGITUDINAL SEAM. THE PIPELINE WAS REPAIRED BY REMOVING THE FAILED SECTION AND REPLACING IT WITH A SECTION OF PRE-TESTED PIPE. LINE 3 WAS RETURNED TO SERVICE AT A REDUCED RATE AT 02:54 MST 03/07/91.
2017-09-29 08:50 | YES | NO | 19910058 | 1991-04-01 | 443 | AMOCO PIPELINE CO | YES | 1991-03-05 | 1615 | IL | WILL | MANHATTAN | NO |  | NO | AMOCO PIPELINE COMPANY TANK FARM LOCATED AT 15600 GALLAGHER ROAD, MANHATTAN, ILLINOIS. |  | TANK FARM | VALVE |  | 1981 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | DAMAGED VALVE FAILED | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2009.3254 | 4053.6209 | CRUDE OIL | 1 | 100 | 99 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.A. STAHL - AREA MANAGER | 2197382384 | WHILE SAMPLING TANK #6973 A SLIGHT LEAK AT THE ROOF DRAIN VALVE WAS NOTICED. WHILE TRYING TO STOP THE LEAK THE VALVE FAILED AND A STREAM OF OIL WAS RELEASED WITHIN THE TANK DIKE WALL. A NEW VALVE WAS INSTALLED AND THE CONTAINED SPILL WAS CLEANED UP AND THE CRUDE OIL RECOVERED. IT APPEARS THAT WATER GOT INTO THE VALVE AND FROZE, THUS BREAKING COMPONENTS OF THE VALVE AND BODY. WHILE TRYING TO TIGHTEN THE VALVE IT FAILED.
2017-09-29 08:50 | NO | NO | 19910059 | 1991-04-01 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1991-02-19 | 1945 | CA | CONTRA COSTA | RICHMOND | NO |  | NO | SANTA FE PACIFIC PIPELINES' RICHMOND STATION. |  | PUMPING STATION | OTHER | SUMP OVERFLOWED | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1607.4603 | 3242.8967 | GASOLINE | 3 | 10 | 9 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT, OPER. & ENGINEERING | 2134867720 | FULL-FLOW RELIEF VALVE ACTIVATED AND BECAUSE OF THE HIGH PRESSURE DID NOT RESET UNTIL 10 BARRELS OF PRODUCT HAD ESCAPED INTO THE BERMED CONTAINMENT AREA. RECOVERY WAS IMMEDIATELY INITIATED AND APPROXIMATELY 9 OF THE 10 BARRELS THAT HAD ESCAPED WERE RECOVERED.
2017-09-29 08:50 | NO | NO | 19910060 | 1991-04-01 | 26085 | SCURLOCK OIL CO | NO | 1991-03-06 | 1200 | TX | RUSK | UNKNOWN | NO |  | NO | TAKE HWY 42 TO REID SWITCH - HEAD WEST TURN RIGHT ON AMERICAN PLANT ROAD - GO TO EAST TEXAS SALT WATER DISPOSAL. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | CRUDE OIL | 1 | 15 | 5 | NO | NO | 8.63 | 0.22 | 702 | NO DATA |  | 260 | 100 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | THOMAS G. HRNCIR - DIVISION SUPERINTENDENT | 9039845252 | LEAK OCCURRED DUE TO EXTERNAL CORROSION IN AN 8" PIPELINE. EAST TEXAS SALT WATER NOTIFIED SCURLOCK OF THE LEAK. SCURLOCK DISPATCHED A CREW TO SITE TO DIG OUT AND CLAMP OFF LEAK. CONTRACT CREW SET OUT BOOM IN CREEK AND VACUUM TRUCK WAS USED TO PICK THE OIL AS CREWS WASHED DOWN CREEK.
2017-09-29 08:50 | NO | NO | 19910062 | 1991-03-19 | 443 | AMOCO PIPELINE CO | YES | 1990-04-25 | 1600 | TX | GALVESTON | TEXAS CITY | NO |  | NO | NORTH OF TEXAS CITY, TEXAS, 1/2 MILE NORTH AT THE INTERSECTION OF TEXAS LOOP 197 AND TEXAS 146, ON THE WEST SIDE OF TEXAS 146. |  | LINE PIPE | WELDING FITTING |  | 1987 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 83.2227 | 167.8938 | TRANSMIX (PART. REFINED PETRO) | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | N.J. MCNAIR FOR J.P. BLACK | 4099380084 | COMPANY PERSONNEL WERE PERFORMING SURVEY WORK ON AMOCO'S 18-INCH PRODUCT LINE. WHEN PROBING THE PIPELINE ASSOCIATED WITH THE SURVEY WORK, THEY NOTICED A PETROLEUM ODOR WHEN THE PROBE BAR WAS REMOVED. AS A RESULT AT THE SURVEY CREW'S FINDINGS, THE PIPELINE WAS ESCAVATED AND A PRODUCT SEEP WAS DISCOVERED FROM A MECHANICAL SLEEVE. THE MECHANICAL SLEEVE WAS THEN RE-WELDED.
2017-09-29 08:50 | YES | NO | 19910063 | 1991-03-25 | 3445 | DIXIE PIPELINE | YES | 1991-03-02 | 1350 | SC | RICHLAND | UNKNOWN | NO |  | NO | 3/4 MILE SW OF COUNTY ROAD 955 CROSSING AND BOMBING RANGE ROAD. |  | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 28130.5552 | 56750.6921 | L. P. G. | 2 | 2000 | 0 | NO | NO | 8 | 0.19 | 0 | WELDED |  | 1024 | 566 | YES | 24 | 1600 |  | 61 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R.F. PHILLIPS - GENERAL MANAGER | 4043962995 | AT APPROXIMATEY 1350 HOURS, SATURDAY, MARCH 2, 1991, A FRONT END LOADER WAS GRADING AND EXCAVATING WITHIN TEN FEET OF A PERMANENT PIPELINE MARKER WHEN THEBUCKET PUNCTURED DIXIE'S PROPANE PIPELINE. THE PIPELINE WAS LATER DETERMINED TO BE AT LEAST 36" DEEP AT THE LOCATION OF THE ACCIDENT. THERE WAS NO "ONECALL" NOTIFICATION NOR ANY OTHER NOTICE OF EXCAVATION RECEIVED FROM THE PROPERTY OWNER OR CONTRACTOR. THE DISPATCHER ON DUTY AT DIXIE'S ATLANTA CONTROL CENTER IMMEDIATELY RECOGNIZED THE LOSS OF PRESSURE AT THE UPSTREAM AND DOWNSTREAM PUMP STATIONS AND AN EXCESSIVE FLOWRATE AT THE UPSTREAM STATION. THE UPSTREAM STATION WAS SHUTDOWN AND REMOTELY OPERATED STATION VALVES CLOSED. THEDOWNSTREAM STATION WAS ALLOWED TO SHUTDOWN ON LOW SUCTION PRESSURE TO PULL AS MUCH PRESSURE AS POSSIBLE AWAY FROM THE LEAK SITE. DIXIE FIELD PERSONNEL WERE NOTIFIED AND INSTRUCTED TO CLOSE MAINLINE BLOCK VALVES BETWEEN THE TWO PUMP STATIONS. AT APPROXIMATELY THE SAME TIME, A RESIDENT NEAR THE LEAK SITE CALLED DIXIE'S DISPATCHER ON THE EMERGENCY LINE TO REPORT THE INCIDENT AND PROVIDED THE GENERAL LOCATION. THE DISPATCHER ALSO NOTIFIED THE RICH LAND COUNTY SHERIFF AND EMERGENCY COORDINATOR AND APPRAISED THEM OF THE SITUATION. ALLTHESE ACTIONS BY THE DISPATCHER TOOK PLACE IN A MATTER OF A FEW MINUTES. THE LEAK WAS ISOLATED IN A FIVE MILE SECTION OF PIPELINE. SEVERAL SUBDIVISIONSARE WITHIN ONE MILE OF THE LEAK SITE AND RICHLAND COUNTY EMERGENCY PERSONNELHANDLED EVACUATION OF RESIDENTS. DIXIE MAINTENANCE PERSONNEL USED AN EXISTING 2" THREAD-O-RING (TOR) FITTING AT ONE OF THE BLOCK VALVES AND INSTALLED ANADDITIONAL 2" TOR FITTING FOR TEMPORARY FLARE CONNECTIONS. THE TEMPORARY FLARES WERE SET AT A SAFE DISTANCE FROM THE LEAK AND USED TO MINIMIZE THE LEAKAGE AT THE SITE. AS SOON AS THE PIPELINE PRESSURE WAS SUFFICIENTLY LOW AND THELEAK AREA WAS SAFE TO ENTER, A BOLT-ON PLIDCO CLAMP WAS INSTALLED AND SUBSEQUENTLY WELDED IN PLACE. THE LINE WAS RETURNED TO OPERATION ON MONDAY, MARCH4. THIS SECTION OF PIPELINE WILL BE INCLUDED IN AN EXTENSIVE HYDROSTATIC TEST PROGRAM THAT IS SCHEDULED FOR JUNE OF THIS YEAR. AT THAT TIME, A NEW JOINT OF PIPE WILL BE INSTALLED TO REPLACE THE JOINT CONTAINING THE CLAMP.
2017-09-29 08:50 | NO | NO | 19910064 | 1991-03-22 | 19231 | TEXACO PRODUCTION & EXPLORATION INC | NO | 1991-03-02 | 1630 | LA | VERMILION | UNKNOWN | NO |  | NO | THE INCIDENT OCCURRED 5.5 MILES SOUTH FO ERATH, LA ON HWY #331 AND PARISH ROAD 2-9. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 48223.8088 | 97286.9008 | NATURAL GAS LIQUID | 2 | 2 | 0 | NO | NO | 6.63 | 0.22 | 46 | WELDED |  | 2160 | 1100 | YES | 8 | 2800 | 4 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | MICHAEL A. BURGESS - SAFETY & INDUSTRIAL HYGIENE SUPERVISOR | 9185606432 | LIGHTNING STRUCK A POWER LINE AND THE POWER LINE FELL ON THE ROAD CROSSING CONDUIT VENT. THE ELECTRICAL CURRENT BURNED A PIN HOLE IN THE PRODUCT PIPE LINE. THE LEAK WAS INSIDE THE ROADCROSSING CONDUIT.
2017-09-29 08:50 | YES | NO | 19910065 | 1991-04-22 | 12628 | MOBIL PIPELINE CO | YES | 1991-03-23 | 1830 | TX | GAINES | SEMINOLE | NO |  | NO | 7 MILES SOUTH OF SEMINOLE, TX, @MOBILE PIPE LINE COMPANY MILEPOST 57.01. |  | LINE PIPE | VALVE |  | 1942 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | 4" CAST IRON GATE VALVE | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | CRUDE OIL | 2 | 740 | 40 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD - VICE PRESIDENT, OPERATIONS | 2146582226 | ON SATRUDAY, MARCH 23, 1991, AT 1500 HRS., THE DALLAS OPERATIONS CONTROL CENTER NOTED A SHORTAGE ON THE SEMINOLE-ANDREWS MAINLINE. MIDLAND AND SEMINOLE EACH WERE INSTRUCTED TO PROVE METERS. WHEN NO METERING PROBLEMS WERE DISCOVERED, THE LINE WAS IMMEDIATELY SHUT DOWN AT 1717 HRS. TO INVESTIGATE. AT 1845 HRS., AERIAL PATROL REPORTED A LEAK AT MP 57.08. MAINTENANCE CREWS WERE DISPATCHED AND DISCOVERED THAT A CAST IRON GATE VALVE HAD SEPARATED. RECOVERY AND CLEAN-UP PRODECURES WERE INITIATED. PERMANENT REPAIRS WERE MADE BY REPLACING 15' OF LINE PIPE.
2017-09-29 08:50 | YES | NO | 19910066 | 1991-04-22 | 1682 | BP OIL PIPELINE CO | NO | 1991-03-05 | 1204 | OH | TRUMBULL | LORDSTOWN | NO |  | NO | APPROXIMATELY 50 FEET SOUTHEAST OF THE INTERSECTION OF MUTH ROAD AND LYNTZ ROAD, VILLAGE OF LORDSTOWN, OHIO. |  | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 160746.0294 | 324289.6692 | DIESEL FUEL | 3 | 691 | 559 | NO | NO | 8.63 | 0.25 | 35000 | WELDED |  | 650 | 150 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | D.K. NEUWERTH, EASTERN REGION SUPERINTENDENT | 2163514777 | A SEWER INSTALLATION CONTRACTOR WORKING FOR THE VILLAGE OF LORDSTOWN, OHIO STRUCK BP OIL PIPELINE'S PIPE WHILE EXCAVATING TO INSTALL A LATERAL LINE ON ANEIGHT (8) INCH PVC SANITARY SEWER LINE. THE BP PIPELINE HAD BEEN STAKED ABOUT ONE MONTH PREVIOUSLY AND BP OIL PERSONNEL HAD BEEN ON SITE TWICE SINCE THEORIGINAL STAKING. ONCE TO WITNESS THE BORING OF THE MUTH ROAD AND ONCE TO OBSERVE SEISMORGRAPH READINGS OVER THE PIPELINE DURING BLASTING OPERATIONS. THE CONTRACTOR HAD BEEN WORKING PARALLEL TO BP'S PIPELINE DURING MOST OF SEWER PROJECT AND HAD OBLITERATED ALL OF THE STAKES DURING EXCAVATION (PILED SOIL ON THEM) AND BACKFILLING OPERATIONS. THE CONTRACTOR ELECTED TO DIG TO INSTALL THE LATERAL (WHICH WAS SHOWN ON THE SEWER PLANS AS CROSSING BP'S PIPELINE) WITHOUT CALLING FOR THE LINE TO BE RESTAKED. A LARGE HYDRAULIC TRACKED BACKHOE WITH A ROCK BUCKET STRUCK AND RUPTURED THE PIPELINE. THE CONTRACTOR PUT A MESSAGE ON THE ONE CALL SYSTEM REQUESTING THE LINE BE STAKED APPROXIMATELY 10 MINUTES AFTER THE RUPTURE.
2017-09-29 08:50 | YES | NO | 19910067 | 1991-04-22 | 19226 | TEXACO PIPELINE INC | YES | 1991-03-27 | 600 | MT | DAWSON | UNKNOWN | NO |  | NO | S10 - T21N - R53E (SEE ATTACHED DRAWING). |  | PUMPING STATION | PUMP |  | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | STUDS ON PUMP FAILED. | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 5626.111 | 11350.1384 | CRUDE OIL | 1 | 250 | 249 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAN DOBSON | 4066873304 | THE STUDS HOLDING A PLUNGER CAP ON THE PUMP FAILED. STUDS HAVE BEEN SENT INFOR ANALYSIS TO DETERMINE WHAT CAUSED THEIR FAILURE. THE PRESSURE AT THE TIME OF FAILURE WAS MUCH LESS THAN THE PUMPS PRESSURE RATING. AS THE OIL ACCUMULATED ON THE WEST END OF THE STATION PROPERTY AT OUR OIL DYKE, OIL CUT A PATHALONG OUR DRAIN PIPE AND PROCEEDED WEST ALONG THE COUNTY ROAD IN THE BARROW DITCH FOR ABOUT 1550'.
2017-09-29 08:50 | NO | NO | 19910068 | 1991-04-10 | 12127 | MARATHON PIPE LINE CO | YES | 1991-03-08 | 845 | IN | LAKE | GRIFFITH | NO |  | NO | 1200 READER ROAD - SEC. 1, T35N, R9W. |  | PUMPING STATION | OTHER | PIPE NIPPLE | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | FUEL OIL | 1 | 30 | 30 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | C.A. RYSENGA, PRESIDENT | 4194214000 | WHILE EXCAVATING AROUND A SCRAPER TRAP AT LOTTAVILLE STATION IN FROZEN EARTH, A 3/8 INCH TUBING LINE WAS CAUGHT BY A BACKHOE BUCKET. THE TUBING LINE WASPULLED CAUSING A 1/2 INCH NIPPLE CONNECTED TO A 10" PIPELINE TO MUSKEGON, MI, TO TEAR IN THE THREADS ALLOWING APPROXIMATELY 30 BBLS. OF #2 FUEL OIL OT ESCAPE FROM THE LINE. A CONTAINMENT HOLE WAS DUG TO COLLECT THE LEAKING PRODUCT UNTIL A VACUUM TRUCK COULD BE PROCURRED TO RECOVER THE 30 BBLS. OF PRODUCT CONTAMINATED AND ALL OTHER AFFECTED SOIL WAS REMOVED FROM THE CONTAINMENT HOLE. ALL CONTAMINATED SOIL WILL BE REMOVED AND DISPOSED OF ACCORDING TO STATE ENVIRONMENTAL REGULATIONS.
2017-09-29 08:50 | NO | NO | 19910069 | 1991-04-10 | 809 | ARCO PIPE LINE CO | YES | 1991-03-19 | 2200 | MO | AUDRAIN | UNKNOWN | NO |  | NO | AT DAVIS CREEK, NORTHWEST OF MEXICO, MO. SEC. 23, T51N, R9W, AUDRAIN COUNTY. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 2 | 2 | 0 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 630 | 171 | YES | 24 | 885 | 8 | 70 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | F.L. NEELEY, MANAGER PRODUCT BUSINESSES | 3163311300 | LEAK WAS CUSED BY EXTERNAL CORROSION ON A SPAN CROSSING OF DAVIS CREEK
2017-09-29 08:50 | YES | NO | 19910070 | 1991-04-10 | 18273 | SHELL PIPELINE CORP | YES | 1991-04-07 | 810 | WY | NIOBRARA | LUSK | NO |  | NO | SW 1/4, SE 1/4 SECTION 22, T-18-N, R-62-W, 35 MILES NORTH OF LUSK, BUTTE 16-INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1955 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 325000 | 261212.2978 | 526970.7125 | CRUDE OIL | 1 | 8150 | 1400 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1170 | 1160 | YES | 12 | 1308 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | CAUSE OF PIPE FAILURE IS UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE FILED AT A LATER DATE TO SHOW TOTAL PROPERTY DAMAGE COST AND CAUSE OF PIPE FAIRLURE.
2017-09-29 08:50 | YES | NO | 19910071 | 1991-04-12 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1991-04-08 | 1300 | WY | UINTA |  | NO |  | NO | TOWNSHIP 12 NORTH, RANGE 121 WEST, SECTION 12. |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 8818 | 7087.2924 | 14297.9315 | NATURAL GAS LIQUID | 2 | 700 | 0 | NO | NO | 6.63 | 0.13 | 2009 | WELDED |  | 1447 | 1118 | YES | 24 | 1871 | 10 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | PIPELINE WARNING SIGNS | NO | YES | S.F. ISAACS, PRESIDENT | 9185811800 | LINE WAS DAMAGED BY CONTRACTOR WHILE EXCAVATING FOR NEW PIPELINE.
2017-09-29 08:50 | YES | NO | 19910072 | 1991-04-12 | 13131 | CONOCO INC | NO | 1991-03-23 | 1630 | LA | CALCASIEU | UNKNOWN | NO |  | NO |  |  | TANK FARM | VALVE |  | 1944 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | VALVE BODY CRACKED | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 6500 | 5224.246 | 10539.4143 | CRUDE OIL | 1 | 3082 | 3082 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN W. WRIGHT, DISTRICT MANAGER | 3184754050 | THE 8-INCH VALVE AT TANK 80013 CRACKED. CRUDE OIL WAS CONTAINED WITHIN DIKED AREA. DURATION OF THE LEAK WAS APPROXIMATELY 10 1/2 HOURS DURING WHICH TIME THE CRUDE OIL STORED IN TANK 80013 WAS TRANSFERRED TO OTHER STORAGE TANKS.NOTIFICATIONS INCLUDED THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY. CAUSE OF LEAK HAS BEEN THOROUGHLY INVESTIGATED AND CORRECTIVE ACTIONS TO PREVENT SIMILIAR RELEASES HAVE BEEN TAKEN.
2017-09-29 08:50 | YES | NO | 19910073 | 1991-04-22 | 12628 | MOBIL PIPELINE CO | YES | 1991-03-21 | 1717 | TX | MITCHELL | WESTBROOK | NO |  | NO | 5 MILES OSUTH WEST OF CITY OF WESTBROOK, SOUTH OF INTERSTATE 20, AND WEST OF FM 670, MOBIL PIPELINE OMPANY MILEPOST 61.5. |  | LINE PIPE | OTHER | UNKNOWN | 1943 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 48223.8088 | 97286.9008 | CRUDE OIL | 1 | 5359 | 3784 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 665 | 607 | YES | 8 | 917 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD - VICE PRESIDENT, OPERATIONS | 2146582226 | THE DALLAS OPERATIONS CONTROL CENTER NOTED A PRESSURE DROP AT IATAN STATION ON THE 12"/8" MIDLAND TO CORSICANA PIPELINE SYSTEM AT 1717 HOURS ON MARCH 21,1991. THE LINE WAS IMMEDIATELY SHUT DOWN AND MAINTENANCE CREWS WERE DISPATCHED TO ISOLATE THE SECTION OF LINE AND INVESTIGATE. A SPLIT SEAM IN THE PIPELINE WAS DISCOVERED AT 2230 HOURS AT MILEPOST 61.5. RECOVERY AND CLEAN-UP PROCEDURES WERE INITIATED IMMEDIATLEY. PERMANENT REPAIRS WERE MADE BY REPLACINGTHE COMPLETE JOINT OF PIPE WITH 45 FT. OF NEW TESTED LINE PIPE. THE FAILEDSECTION OF THE PIPELINE IS PRESENTLY AT A METALLURGICAL LABORATORY FOR ANALYSIS. A COPY OF THE REPORT WILL BE FURNISHED TO THE OFFICE OF PIPELINE SAFETY, SOUTHWEST REGION OFFICE IN HOUSTON, WHEN COMPLETED.
2017-09-29 08:50 | YES | YES | 19910074 | 1991-04-22 | 22610 | WILLIAMS PIPELINE CO | YES | 1991-03-20 | 1600 | IA | JASPER |  | NO |  | NO | NEWTON STATION #D591, SE 1/2, S21, T79N, R19W. |  | LINE PIPE | OTHER | LINE PACKER | 0 | OTHER | PRESSURE SENSING LINE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 200 | 160.746 | 324.2897 | L. P. G. | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN - VICE PRESIDENT - OPERATIONS | 9185882204 | WHILE WORKING ON SOME MANIFOLD PIPING IN THE NEWTON PUMP STATION, A MAINTENANCE EMPLOYEE RECEIVED MILD FREEZE BURNS ON THE BACK OF HIS LEG. THE MAINTENANCE CREW HAD INSTALLED AN 8" LINE PACKER AS A VAPOR BARRIER TO ACCOMMODATE BEVEL PREPARATIONS FOR A WELD TIE-IN. THE PACKER IS EQUIPPED WITH A VENT HOSE (END OF HOSE IS OUTSIDE THE DITCH) AND A PRESSURE GAUGE TO RELIEVE AND MONITOR PRESSURE CONDITIONS UPSTREAM OF THE PACKER ASSEMBLY. A SMALL AMOUNT OF VAPOR WAS SLOWLY VENTING THROUGH THE HOSE DURING THE PIPE BEVELING PROCESS. WHILE LOOSENING THE PACKER TO ALLOW FOR THE PIPING TO BE MOVED IN AND FIT UP, THE PACKER STARTED TO PUSH OUT. PERSONNEL IMMEDIATELY BEGAN TO EVACUATE THE AREA, HOWEVER, ONE OF THE CREW MEMBERS CLOSEST TO THE PIPE OPENING RECEIVED MILD FREEZE BURNS FROM THE RELEASED PROPANE AS THE PACKER PUSHED OUT OF THE PIPE. THE AFFECTED EMPLOYEE WAS TREATED AT SKIFF MEDICAL CENTER AND RELEASED. FURTHER INVESTIGATION REVEALED THAT THE PACKER VENT TUBE HAD BECOME PARTIALLY OBSTRUCTED WITH ROUGE, ACCOUNTING FOR THE SMALL AMOUNT OF VAPOR FLOW THROUGH THE VENT AND THE ABSENCE OF A RECORDABLE PRESSURE READING.
2017-09-29 08:50 | YES | NO | 19910075 | 1991-04-18 | 18718 | SUN PIPELINE CO | YES | 1991-02-15 | 1430 | PA | BERKS | UNKNOWN | NO |  | NO | APPROXIMATELY 400 FEET SOUTH OF MOUNTAIN ROAD AT ITS INTERSECTION WITH MOUNTAIN VIEW ROAD IN BERKS COUNTY, PENNSYLVANIA. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 80373.0147 | 162144.8346 | GASOLINE | 1 | 25 | 0 | NO | NO | 6.63 | 0.26 | 35000 | WELDED |  | 1970 | 700 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | AT APPROXIMATELY 1430 HOURS ON FRIDAY, FEBRUARY 15, 1991, THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL RESOURCES CONTACTED SUN PIPE LINE ABOUT A POSSIBLELEAK NEAR MOUNTAIN ROAD IN NORTH BERKS COUNTY. UPON INVESTIGATION AT 1500, WE FOUND AN AREA OF SOIL ABOUT 140' X 60' SATURATED WITH GASOLINE ON OUR R.O.W. HASSLER RUN CREEK ALSO HAD A SHEEN OF PRODUCT ON IT. THE LINE WAS ALREADY SHUT DOWN; THE AREA WAS THEN EXCAVATED AND A PINHOLE LEAK WAS FOUND AT APPROXIMATELY 4 O'CLOCK ON THE BOTTOM OF THE PIPE. A TEMPORARY LEAK CLAMP WAS INSTALLED, CONTAMINATED SOILS REMOVED, BOOMS AND PADS USED TO REMOVE CONTAMINANTS FROM THE WATER. PERMANENT REPAIRS ARE SCHEDULED TO OCCUR ON 3/20/91.
2017-09-29 08:50 | YES | NO | 19910076 | 1991-04-03 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1991-03-05 | 2100 | PA | LEHIGH | UNKNOWN | NO |  | NO |  |  | TANK FARM | OTHER | UNKNOWN | 1953 | OTHER | CORROSION, EXTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | FUEL OIL | 3 | 157 | 62 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | NO | OTHER | CRACK IN TANK FLOOR PLATE | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER, REGULATORY COMPLIANCE COORDINATOR | 2158208300 | ABOUT 2100 HOURS (EST) ON MARCH 5, 1991, NUMBER 2 FUEL OIL WAS OBSERVED IN DRAINAGE DITCH AND SPILL DIKE AT TANK 207. UPON DETERMINATION OF LEAKAGE, THECONTENTS OF TANK 207 WAS PUMPED TO THE PIPELINE AND TANK 207 WAS EMPTY AT 0239, STOPPING FURTHER RELEASE OF NUMBER 2 FUEL OIL.
2017-09-29 08:50 | NO | NO | 19910077 | 1991-04-08 | 4906 | EXXON PIPELINE CO | YES | 1991-03-04 | 1214 | LA | JEFFERSON | UNKNOWN | NO |  | NO | THIS SPILL ORIGINATED FROM OUR GRAND ISLE-LITTLE LAKE 12-INCH PIPELINE AT STATION NO. 1339+82 (LONGITUDE - 90 DEGREE 09.4'W, LATITUDE - 29 DEGREE 32.7'N). |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 48223.8088 | 97286.9008 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 1091 | 40 | YES | 8 | 1200 |  | 54 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC TIDE ZONE EFF | NO DATA |  | Null | NO DATA |  | Null | Null | J.B. HOLT, MANAGER - ENVIRONMENTAL & REGULATORY COMPLIANCE | 7136565521 | AT 1414 HOURS ON 3/4/91 AN OIL SHEEN WAS REPORTED IN THE VICINITY OF OUR PIPELINE AT LITTLE LAKE JUNCTION. OUR GRAND ISLE TO LITTLE LAKE PIPELINE WAS SHUTDOWN AND SUBJECTED TO OUR AERIAL INSPECTION. THE SOURCE OF THE LEAK WAS DETERMINED TO BE OUR PIPELINE. THE LEAK OCCURRED IN A MARSHY AREA AND WAS DUE TOATMOSPHERIC CORROSION WHERE THE PIPELINE RISER EXITED THE GROUND. TEMPORARYREPAIRS WERE MADE BY 1700 HOURS. CLEANUP WAS INITIATED IMMEDIATELY. PERMANENT REPAIRS WERE MADE 3/10/91 BY REPLACING 30 FEET OF 12-INCH PIPE.
2017-09-29 08:50 | YES | NO | 19910078 | 1991-05-09 | 22907 | WYCO PIPE LINE CO | YES | 1991-04-12 | 2300 | CO | DUPONT |  | NO |  | NO |  |  | TANK FARM | OTHER | UNKNOWN | 1947 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 32149.2059 | 64857.9338 | KEROSENE | 3 | 1700 | 1010 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWAINE A. SHOYN - AREA MANAGER | 3032866400 | MANUAL TRANSFER BETWEEN TANKS INADVERTANTLY LEAD TO THE OVERFLOW OF THE RECEIVING TANK.
2017-09-29 08:50 | YES | NO | 19910079 | 1991-05-09 | 22610 | WILLIAMS PIPELINE CO | YES | 1991-04-08 | 1700 | SD | UNION |  | NO |  | NO | LS # E120, MP 389+2950, SEC. 10, T95N, R482. |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 100466.2684 | 202681.0433 | L. P. G. | 2 | 2881 | 0 | NO | NO | 6 | 0.22 | 35000 | WELDED |  | 1450 | 300 | YES | 8 | 1912 |  | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | LINE MARKERS | NO | NO | H.E. JANZEN - VICE PRESIDENT-OPERATIONS | 9185883850 | ON APRIL 8, 1991 A SCRAPER TRACTOR OPERATOR STRUCK AND SEVERED OUR #2-6" PIPELINE BETWEEN MP 289 AND 290, APPROXIMATELY ONE HALF MILE NORTH OF THE BIG SIOUX RIVER. ADJACENT VALVES WERE CLOSED ISOLATING A 13 MILE SECTION OF LINE. STOPPLE EQUIPMENT WAS BROUGHT ON SITE, HOWEVER, BY THE TIME PREPARATIONS COULD BE MADE, THE LINE FILL WAS VIRTUALLY GONE SO THE REMAINDER WAS ALLOWED TO BLOW DOWN. A NEARBY RAILROAD AND HIGHWAY WERE SHUTDOWN TEMPORARILY UNTIL THE VAPOR CLOUD TOTALLY DISPERED. THE LINE WAS REPAIRED BY INSTALLING A NEW JOINT OF PIPE. THE CONTRACTOR, VAN BUSKIRK CONSTRUCTION, WAS WORKING UNDER A JOINTCONTRACT WITH THE SOUTH DAKOTA AND IOWA DEPARTMENTS OF TRANSPORTATION TO BUILD DIRT BERMS FOR THE CONSTRUCTION OF A NEW INTERSTATE BRIDGE ACROSS THE BIG SIOUX RIVER. THE CONTRACTOR CALLED THE IOWA ONE-CALL (COPY OF THE NOTICE ATTACHED), HOWEVER, THE REPORTED "EXTENT OF WORK" IN THE NOTICE WAS LIMITED TO EITHER SIDE OF THE BRIDGE. THE NOTICE ALSO GAVE SPECIFIC WORK LOCATION REFERENCE TO SECTION 15 IN SIOUX COUNTY, IOWA, HOWEVER, THE PIPELINE WAS STRUCK IN SECTION 10 IN UNION COUNTY, SOUTH DAKOTA. WHEN WE RECEIVED THE ONE-CALL NOTICE WE CALLED THE COTNRACTOR TO VERIFY THE EXTENT TO THE WORK ACTIVITY. THE CONTRACTOR MADE MENTION ONLY OF THE WORK AT THE BRIDGE SITE, AND SINCE OUR LINE WAS APPROXIMATELY 1000 FEET TO THE WEST OF THE CONSTRUCTION (SEE ATTACHED MAPS), THE NOTICE WAS CLEARED. HOWEVER, THE CONTRACTOR FAILED TO INFORM US THAT HE WAS TAKING DIRT FROM A BORROW PIT APPROXIMATELY 1/2 MILE NORTH WHICH WAS LOCATED ON TOP OF OUR PIPELINE. THE ENGINEERING PLANS FOR THE BORROW PIT EXCAVATION SPECIFICALLY INSTRUCTED THE CONTRACTOR TO CALL THE PIPELINE COMPANIES IN THE AREA BEFORE BEGINNING ANY EXCAVATION ACTIVITY. WE WERE NOT GIVEN ACOPY OF THESE PLANS NOR WERE WE INFORMED OF THE PRE-CONSTRUCTION MEETING WERETHEY WERE DISCUSSED. THE NEAREST PIPELINE MARKER WAS APPROXIMATELY 100 FEET AWAY FROM THE LEAK SITE, AND CLEARLY VISIBLE. BOTH THE CONTRACTOR AND THE LANDOWNER ACKNOWLEDGED THAT THEY KNEW OF THE PIPELINES PRESENCE AND HAD SEEN THE PIPELINE MARKERS. THE LANDOWNER HAD ALSO BEEN SENT A COPY OF OUR PUBLIC EDUCATION BROCHURE IN 1989.
2017-09-29 08:50 | NO | NO | 19910080 | 1991-05-09 | 22610 | WILLIAMS PIPELINE CO | YES | 1991-04-02 | 1235 | MN | UNKNOWN | MINNEAPOLIS | NO |  | NO | LS #FO43 - MP 260+3000 NE 1/4, SEC. 8, T29N, R23W. |  | LINE PIPE | PIPE |  | 1979 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16074.6029 | 32428.9669 | FUEL OIL | 3 | 2 | 0 | NO | NO | 12 | 0.28 | 42000 | WELDED |  | 950 | 900 | YES | 8 | 1200 |  | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. JANZEN - VICE PRESIDENT - OPERATIONS | 9185883850 | ON APRIL 2, 1991, A LEAK WAS DISCOVERED BY LOCATION PERSONNEL ON THE #4-12" PIPELINE NEAR OUR MINNEAPOLIS TERMINAL. WHEN THE LINE WAS UNCOVERED, THE LEAK WAS FOUND TO BE ORIGINATING FROM A SMALL CRACK ON THE OUTSIDE RADIUS OF A 45 DEGREE PIPE BEND. METALLURGICAL ANALYSIS IDENTIFIED THE FAILURE AS AN EXTERNAL QUENCH CRACK WHICH HAD APPARENTLY ORIGINATED AT THE FACTORY AND WAS THERESULT OF IMPROPER TEMPERING DURING THE "HOT" BENDING PROCESS. HIGH HARDNESS VALUES FURTHER SUPPORTED THIS CONCLUSION. THERE WAS NO EVIDENCE OF ANY CORROSION OR FATUGUE. THE BEND HAD BEEN SUCCESSFULLY TESTED TO 1500 PSI PRIOR TO INSTALLATION IN 1979. A NEW "COLD" BEND REPLACEMENT WAS INSTALLED. ENVIRONMENTAL INVESTIGATION AND REMEDIATION ACTIVITIES CONTINUE IN COOPERATION WITHSTATE AGENCIES.
2017-09-29 08:50 | NO | NO | 19910081 | 1991-05-07 | 18273 | SHELL PIPELINE CORP | YES | 1991-03-26 | 1030 | IL | GROVE BOND | MULBUERY | NO |  | NO | SECTION 2, T-6-N, 5 MILES NORTH OF MULBERY EAST LINE 8-INCH. |  | LINE PIPE | PIPE |  | 1937 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9350 | 7514.8769 | 15160.542 | JET FUEL | 3 | 2 | 0 | NO | NO | 8 | 0.32 | 36000 | WELDED |  | 1350 | 837 | YES | 0 | 0 |  | 37 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | THE PIPE WAS DEACTIVATED ON JANUARY 28, 1991. THE PIPELINE HAD BEEN SHUT DOWN WITH VALVES CLOSED IN PREPARATION FOR DISPLACEMENT OF THE PRODUCT AND DEACTIVATION. GROUND TEMPERATURE INCREASES CAUSED THE PRESSURE IN THE SECTION OFTHE PIPELINE TO INCREASE TO 837 PSI CAUSING A PIN HOLE LEAK IN A CORROSION PIT.
2017-09-29 08:50 | YES | NO | 19910082 | 1991-05-07 | 809 | ARCO PIPE LINE CO | YES | 1991-04-20 | 200 | TX | MIDLAND | MIDLAND | NO |  | NO | 2 1/2 MILES EAST OF MIDLAND ON HGIHWAY 80. |  | TANK FARM | OTHER | UNKNOWN | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | CRUDE OIL | 1 | 339 | 110 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.L. THOMAS, INTERIM CRUDE BUSINESS MANAGER | 3163311300 | STATION OPERATOR REMOVED SCRAPER FROM LINE AND FAILED TO CLOSE DRAIN VALVE PRIOR TO START UP, CAUSING SUMP TO OVERFLOW.
2017-09-29 08:50 | YES | NO | 19910083 | 1991-05-06 | 2731 | CHEVRON PIPELINE CO | YES | 1991-04-19 | 230 | UT | DAVIS | UNKNOWN | NO |  | NO | STATE ROAD SR-68 AT ABOUT 1500 WEST. CHEVRON PIPE LINE LOCATION NEAR MP-4. |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 375000 | 301398.8052 | 608043.1298 | DIESEL FUEL | 3 | 200 | 180 | NO | NO | 8.63 | 0.25 | 45000 | WELDED |  | 1870 | 1760 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN R. MOON - AREA SUPERVISOR | 8015397293 | THE SPILL WAS DUE TO EXTERNAL CORROSION IN A BEND, UNDER A STATE HI-WAY SHOULDER. THE PRODUCT LEAKING FROM THE PIPE CONTAMINATED A OPEN FLOOD DRAIN CANAL. IT WAS TURNED INTO DAVIS COUNTY ENVIRONMENTAL AGENCY BY A NEARBY PROPERTYOWNER THAT SMELLED THE PRODUCT.
2017-09-29 08:50 | NO | NO | 19910084 | 1991-05-06 | 15490 | PHILLIPS PIPE LINE CO | YES | 1991-04-07 | 1340 | NM | LEA | UNKNOWN | NO |  | NO | LINE 80-1-5-1-1 - JAL 4 TO TEXACO EUNICE - STA. 00+80. SEC. 5, R37E. T24S. NORTH OF JAL, NM, ON HWY. 18 APPROXIMATELY 9 TO 10 MILES, THEN WEST APPROX. 1/2 MILE. |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 6027.9761 | 12160.8626 | NATURAL GAS LIQUID | 2 | 4 | 0 | NO | NO | 4.5 | 0.16 | 42000 | WELDED |  | 1440 | 840 | YES | 24 | 1900 | 8 | 69 | EXTERNAL | Null | YES | OTHER | COATING WAS LOOSE. | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J. SCHMITZ, TECHNICAL SERVICES COORDINATOR | 9186614814 | AN EMPLOYEE WITH SID RICHARDSON DISCOVERED THE LEAK ON HIS DAILY ROUNDS. THE LEAK WAS REPORTED TO THE CONTROL CENTER. THE LINE WAS SHUT DOWN, BLOCKED IN, AND THE SECTION OF PIPE REPLACED.
2017-09-29 08:50 | NO | NO | 19910085 | 1991-05-06 | 15490 | PHILLIPS PIPE LINE CO | YES | 1991-04-09 | 1635 | TX | MIDLAND | MIDLAND | NO |  | NO | LINE 80-1-6 - GOLDSMITH TO BENEDUM - MP62-16+63. SEC 40,BLOCK 37, T4S, T&P SURVEY. APPROX. 5 MILES NORTH OF MIDKIFF, TS,ON HWY. 3095, THEN APROX 2 M EAST ON RD |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | NATURAL GAS LIQUID | 2 | 3 | 0 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 1100 | 580 | YES | 24 | 1412 | 9 | 76 | EXTERNAL | Null | YES | OTHER | PIPE GRADUALLY CORRODED. | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J. SCHMITZ, TECHNICAL SERVICES COORDINATOR | 9186614814 | THE CONTRACT LINE FLYER, ON HIS WEEKLY FLIGHT, DISCOVERED THE LEAK AND REPORTED IT TO THE CONTROL CENTER. THE LINE WAS SHUT DOWN, BLOCKED IN, AND THE SECTION OF PIPE REPLACED.
2017-09-29 08:50 | YES | YES | 19910086 | 1991-04-09 | 18718 | SUN PIPELINE CO | YES | 1991-03-29 | 1030 | PA | BERKS | SHOEMAKERSVILLE | NO |  | NO | PA, BERKS COUNTY, PERRY TOWNSHIP, SHOEMAKERSVILLE, APPROX. 1.2 MILES W OF SR 61, BETWEEN US I-78 AND PA RT 662, ON FARM PROPERTY OWNED BY LEROY AND JOYCE ZWEIZI |  | LINE PIPE | PIPE |  | 1931 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 333000 | 267642.139 | 539942.2993 | GASOLINE | 3 | 130 | 117 | NO | NO | 6 | 0.28 | 3000 | WELDED |  | 1826 | 1020 | YES | 8 | 1400 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ROBERT A. ARNET, ACTING MANAGER , RISK MANAGEMENT | 9185866231 | ON GOOD FRIDAY, MARCH 29, 1991, AT APRPOXIMATELY 1030, LARRY ZWIEZIG (SON) WAS OPERATING A RENTAL TRACTED FRONT-END-LOADER TO WIDEN SWALE IN ZWEIZIG FARMFIELD. A TOOTH ON THE LOADER BUCKET PUNCTRURED SUN PIPE LINE COMPANY'S (SPL) 6" NORTH LINE. THIS LINE IS IN THE SPL EASTERN REGION II, MONTELLO AREA. UNLEADED GASLOINE WAS BEING PUMPED THROUGHT THE LINE AT APPROXIMATELY 1020 PSIG. LEROY ZWEIZIG (OWNER) CALLED 911 AT 1042; THE SHOEMAKERSVILLE FIRE DEPARTMENT WAS DISPATCHED. MR. ZWEIZIG CONTACTED THE EASTERN AREA CONTROL CENTER AT 1045. THE CONTROL CENTER CONTACTED THE MONTELLO AREA SUPERVISOR; HE ORDERED THE PUMPS DOWN. ALL THREE LINE PUMPS ON LINES THROUGH THE GENERAL AREA OF THE LEAK WERE SHUT DOWN AT 1047. THE MONTELLO AREA SUPERVISOR TELEPHONED MR. ZWEIZIG AND LEARNED THE LINE WAS RUPTURED (LATER DETERMINED THE LINE HAD BEENSLIGHTLY DENTED AND PENETRATED WITH A 2" X 1/2" HOLE), THAT PRODUCT WAS SHOOTING 25-30 FEET INTO THE AIR AND THE NO "ONE-CALL" HAD BEEN MADE. THE SUPERVISOR CALLED THE EASTERN REGION II SUPERINTENDENT TO ARRANGE FOR ADDITONAL ASSISTANCE. THE SHOEMAKERSVILLE FIREMEN, AFTER REACHING THE SITE, CALLED OUT THE BERKS COUNTY HAZMAT TEAM AT 1055. HAZMAT SET UP A LEVEL III CONTROLLED HAZARDOUS MATERIALS SITE WITH RESTRICTED ACCESS AND CHECKPOINTS AND BEGAN EVACUATION OF A ONE-HALF MILE REDIUS (20-25 HOMES). THEY ALSO SET UP A HAY-BALE DAM TO BLOCK THE FLOW OF GASOLINE IN THE DRAINAGE SWALE TOWARD THE FARM POND EAST OF THE LEAK. NRC/EPA WAS CONTACTED AT 1130 (# 65762). THE AREA SUPERVISOR ARRIVED AT THE SITE AT 1150. HE WAS INFORMED BY THE HAZMAT LEADER THAT NO ONECOULD ENTER THE HOT ZONE WITHOUT SELF-CONTAINED BREATHING APPARATUS (SCBA).THE HOT ZONE WAS BEING MONITORED WITH FLAMMABLE VAPOR DETECTORS. THE PA DER WAS NOTIFIED AT ABOUT 1230 (KERRY LEIB). DER WAS ALREADY AWARE OF THE INCIDENT. SPL SUPERVISION, CREW AND EQUIPMENT ARRIVED ON SITE AT VARIOUS TIMES AFTER 1300, AND VALVES AT BERKS PUMP STATION AND BERNE JUNCTION (NEAREST MAINLINEVALVES ABOVE AND BELOW THE LEAK) WERE CLOSED AT THAT TIME. A PA DER RESPONSETEAM, EPA AND FISH & GAME COMMISSION PERSONNEL ALSO RESPONDED TO THE SCENE AT VARIOUS TIMES THEREAFTER. THE LEAK WAS EXCAVATED AND TEMPORARILY REPAIRED WITH A 6" PLIDCO SLEEVE AT APPROXIMATELY 1730. THE LINE VALVES WERE REOPENEDAT 1800. AT 1840 THE LINE WAS REPRESSURED TO 1140 PSIG AND HELD PRESSURE.SUPPLEMENTAL 6/3/93: OWNER, LEROY ZWEIZIG, EXPERIENCED CHEST PAINS AND WASTAKEN BY AMBULANCE TO A HOSPITAL. HE WAS IN THE HOSPITAL FOR 4 DAYS. IT WASLEARNED THAT 3 BLOOD VESSELS WERE 50% BLOCKED, AND WERE SURIGICALLY CLEARED.
2017-09-29 08:50 | YES | NO | 19910087 | 1991-04-30 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1991-03-28 | 1710 | OK | OKFUSKEE | UNKNOWN | NO |  | NO | 1 1/4 MILES WEST OF PHAROAH, OKLAHOMA. 1/8 MILE NORTH INTO LOCATION. |  | TANK FARM | TANK |  | 1922 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3214.9206 | 6485.7934 | CRUDE OIL | 1 | 1395 | 1390 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT ( MANAGER, RISK MANAGER) | 9185866231 | POLYESTER TANK BOTTOM LINER FAILED ALLOWNG CRUDE OIL BETWEEN THE LINER AND THE STEEL TANK SHELL. THIS ALLOWED THE CRUDE OIL TO MIGRATE TO THE MISSING RIVET AT THE EXTERNAL STEEL SHELL, ALLOWING THE CRUDE OIL TO LEAK FROM THE TANK. ALL THE OIL WAS CONTAINED IN THE TANK DIKE.
2017-09-29 08:50 | YES | NO | 19910088 | 1991-05-01 | 19536 | TOTAL PIPELINE CORP | YES | 1991-03-12 | 1200 | OK | PAYNE | UNKNOWN | NO |  | NO | NW/4 SEC. 1, T19N-R3E, FROM NW CORNER OF SECTION, APPROXIMATELY 1/8 MILE SOUTH AND ON ROAD EDGE 15 EAST SIDE OF ROAD. |  | LINE PIPE | PIPE |  | 1920 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3740 | 3005.9508 | 6064.2168 | CRUDE OIL | 1 | 200 | 83 | NO | NO | 6.63 | 0.32 | 24110 | WELDED |  | 880 | 200 | YES | 8 | 1100 | 7 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GARY A. STRACK - CO-ORDINATOR | 3164425100 | PIPELINE WAS INSTALLED IN THE 1920'S. THIS ROAD CROSSING WAS BURIED BUT SHALLOW. OPERATOR HIT LINE WHILE DOING SOME ROUTINE GRADING. PERMANENT LINE MARKERS LOCATED ON EACH SIDE OF ROAD. PIPELINE WAS IMMEDIATELY SHUT DOWN AND AREPAIR WAS MADE.
2017-09-29 08:50 | YES | NO | 19910089 | 1991-05-01 | 12628 | MOBIL PIPELINE CO | NO | 1991-03-24 | 2341 | TX | GRIMES | UNKNOWN | NO |  | NO | MILEPOST 145.07, APPROXIMATELY 12 MILES DOWNSTREAM NAVASOTA STATION, IN GRIMES COUNTY, TX. APPROXIMATELY 14 MILES SE OF COLLEGE STATION, TX. |  | LINE PIPE | LONGITUDINAL WELD |  | 1947 | FAILED WELD | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 268000 | 215399.6794 | 434548.1568 | DIESEL FUEL | 2 | 1459 | 900 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 1000 | 846 | YES | 8 | 1318 | 4 | 87 | EXTERNAL | Null | YES | GALVANIC | GROOVING CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD - VICE PRESIDENT , OPERATIONS | 2146582226 | THE DALLAS OPERATIONS CONTROL CENTER NOTED A PRESSURE DROP AT NAVASOTA STATION ON THE 12" HEBERT TO HEARNE PRODUCTS PIPELINE SYSTEM AT 2341 HRS. ON MARCH 24, 1991. THE LINE WAS IMMEDIATELY SHUT DOWN. MAINTENANCE CREWS WERE DISPATCHED TO ISOLATE THE SECTION OF LINE AND INVESTIGATE. A SPLIT SEAM IN THE PIPELINE AT MP 145.07 WAS DISCOVERED AT 0430 HRS. ON MARCH 25, 1991. RECOVERY AND CLEAN-UP PROCEDURES WERE INITIATED IMMEDIATELY. PERMANENT REPAIRS WERE MADE BY REPLACING 83' OF PIPE WITH NEW TESTED LINE PIPE. THE FAILED SECTION OF THE PIPELINE IS PRESENTLY AT A METALLURGICAL LABORATORY FOR ANALYSIS. A COPYOF THE REPORT WILL BE FURNISHED TO THE TEXAS RAILROAD COMMISSION, PIPELINE SAFETY SECTION, HOUSTON REGION, WHEN COMPLETED.
2017-09-29 08:50 | NO | NO | 19910090 | 1991-05-01 | 443 | AMOCO PIPELINE CO | YES | 1991-04-15 | 1115 | TX | GREENVILLE |  | NO |  | NO | APPROXIMATELY 5 MILES N.E. OF GREENVILLE, TX. YANTIS/HEALDTON LINE - M.M. 30.5 |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CONDENSATE | 1 | 2 | 0 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 1440 | 500 | YES | 8 | 1800 | 9 | 89 | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | PAT M. CLANCY- PIPELINE MAINTENANCE FOREMAN | 9037597131
2017-09-29 08:50 | NO | NO | 19910091 | 1991-05-09 | 737 | ASHLAND PIPELINE CO | NO | 1991-04-09 | 2315 | KY | BULLITT | UNKNOWN | NO |  | NO | HWY 61, 2 MILES NORTH OF LEBANON JUNCTION, KY. |  | PUMPING STATION | OTHER | SUMP TANK | 1973 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | CRUDE OIL | 1 | 25 | 25 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LOUIS B. MORGAN - ENGINEERING SECTION SUPERVISOR | 5026832485 | A ONE INCH RELIEF VALVE MALFUNCTIONED CAUSING A FLOW OF CRUDE OIL TO THE SUMP. THE RELIEF VALVE WAS TESTED DECEMBER 6, 1991. THE RESULTING SPILL OCCURREDBECAUSE THE SUMP TANK HIGH ALARM DID NOT SHUT THE STATION DOWN BECAUSE OF A BS BUILD UP ON THE FLOAT. A MAINTENANCE CREW WAS DISPATCHED IMMEDIATELY AFTER WE WERE NOTIFIED. VACUUM AND TANK TRUCKS WERE DISPATCHED FROM OWENSBORO. THE MIGRATION OF THE SPILL WAS STOPPED APPROXIMATELY 1900 FEET FROM THE STATION IN A ROAD DITCH. A DAM AND SIPHON WERE INSTALLED AND SORBENT BOOMS WERE INSTALLED BELOW THE SIPHON. CLEANUP CONTINUED AROUND THE CLOCK FOR 6 DAYS. A TOTAL OF 873 MAN HOURS WERE USED IN THE CLEANUP EFFORT. CLEANUP CONSISTEDOF REMOVING THE OIL WITH VACUUM TRUCKS. CONTAMINATED SOIL AND DEBRIS WERE REMOVED AND WILL BE DISPOSED OF WHEN ANALYSIS IS RECEIVED AND PERMITS APPROVED
2017-09-29 08:50 | YES | NO | 19910092 | 1991-05-13 | 13131 | CONOCO INC | YES | 1991-04-10 | 1300 | OK | TULSA | TULSA | NO |  | NO | NORTHWEST SECTIONOF 29, TOWNSHIP 20 NORTH, RANGE 14 EAST, TULSA COUNTY, OKLAHOMA. |  | LINE PIPE | PIPE |  | 1970 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | JET FUEL | 1 | 186 | 164 | NO | NO | 4 | 0.13 | 35000 | WELDED |  | 725 | 100 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | D.M. COBB, DISTRICT MANAGER | 4057672367 | AT APPROXIMATELY 13:00 ON APRIL 10, 1991 CONOCO PIPE LINE COMPANY'S 4 INCH COMMERCIAL JET FUEL (JFA) PIPELINE THAT SERVICES THE TULSA, OKLAHOMA INTERNATIONAL AIRPORT WAS SEVERED BY A BACKHOE OPERATED BY MCGUIRE BROTHER CONSTRUCTION COMPANY. THE 4 INCH PIPELINE WAS PROPERLY MARKED FOR THE CONSTRUCTION AND MCGUIRES WAS INSTRUCTED TO CONTACT CONOCO PRIOR TO DOING ANY EXCAVATION NEAR THE LINE. MCGUIRES FAILED TO CONTACT CONOCO AND DID NOT YIELD TO OUR LINE LOCATION MARKERS.MCGUIRES HAS ADMITTED GUILT TO NOT CONTACTING CONOCO AND NOT YIELDING TO THELINE MARKERS.
2017-09-29 08:50 | NO | NO | 19910093 | 1991-06-03 | 1682 | BP OIL PIPELINE CO | NO | 1991-05-07 | 1615 | LA | PLAQUEMINES |  | NO |  | NO | BAY ADAM LORAN C 29200/89372. |  | LINE PIPE | GIRTH | LACK OF PENETRATION | 1955 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | CRUDE OIL | 3 | 1 | 0 | NO | NO | 12 | 0.31 | 35000 | WELDED |  | 1100 | 900 | YES | 8 | 1375 | 3 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.L. OWEN - REGION SUPT. | 5043926601 | A LIGHT INTERMITTENT SHEEN WAS SIGHTED BY SHELL PIPE LINE COMPANY PERSONNEL AT APPROXIMATELY 1600 HOURS CDT ON MAY 7, 1991. SIZE INVESTIGATION BY BP OIL PIPELINE COMPANY EMPLOYEES CONFIRMED A LIGHT SHEEN WAS FROM THE VICINITY OF BP'S 12 INCH CRUDE PIPELINE. THE LINE WAS IMMEDIATELY SHUTDOWN AND BLOCKED IN.WORK BEGAN ON MAY 10 TO UNCOVER THE PIPELINE AND LIFT IT TO THE SURFACE FOR INSPECTION. THE LINE WAS LOCATED IN 5 FEET OF WATER, UNDER 2.5 FOOT OF COVER. INSPECTION OF THE PIPE REVEALED A SMALL HOLE RESULTING FROM A LACK OF PENETRATION IN THE BOTTOM OF A GIRTH WELD. A 2 FOOT FULL ENCIRCLEMENT PRESSURE CONTAINMENT SLEEVE WAS INSTALLED. THE LINE WAS PLACED ON THE BOTTOM AND JETTED TO A DEPTH OF 2.5 FOOT OF COVER. DAMAGE TO PROPERTY AND PIPELINE WAS MINOR.THE COST TO HIRE CONTRACTORS TO ACCESS THE PIPELINE WILL CAUSE THE TOTAL REPAIR TO EXCEED $5,000.00.
2017-09-29 08:50 | YES | NO | 19910094 | 1991-05-29 | 18718 | SUN PIPELINE CO | YES | 1991-04-29 | 850 | TX | RUSK | UNKNOWN | NO |  | NO | SUN PIPE LINE COMPANY, EAST TEXAS 10" TRUNK SYSTEM, GRISSOM PUMP STATION. |  | TANK FARM | OTHER | UNKNOWN | 1931 | OUTSIDE FORCE DAMAGE | HIGH WIND CAUSE TANK FLEX | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16074.6029 | 32428.9669 | CRUDE OIL | 1 | 215 | 200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB ARNET, ACTING MANAGER, RISK MANAGEMENT | 9185866231 | CRUDE OIL RELEASED FROM BOTTOM OF 82,000 BARREL TANK DURING INCLEMENT WEATHER. ALL SPILLED CRUDE IS CONTAINED INSIDE FIREWALL AREA. CLEANUP OPERATIONS WERE BEGUN ON APRIL 29, 1991. REMAINING CRUDE IN TANK IS BEING TRANSFERRED TOANOTHER TANK BY PUMP. A TORNADO PASSED NEAR GRISSOM STATION ON APRIL 29, 1991. ALTHOUGH IT DID NOT ACTUALLY HIT THE TANK, STRONG WINDS APPARENTLY SHOOKTHE PREVIOUSLY DAMAGED OUT OF SERVICE TANK, OPENING A HOLE IN THE BOTTOM ANDRELEASING THE OIL. ONLY A SMALL QUANTITY OF OIL AND WATER WERE IN THE 82,000BARREL TANK AT THE TIME OF THE INCIDENT. THE OIL WAS PICKED UP BY VACUUM TRUCK. OIL REMAINING IN THE TANK HAS BEEN TRANSFERRED TO ANOTHER TANK. THE UNRECOVERED OIL IS BEING TREATED BY BIOREMEDIATION.
2017-09-29 08:50 | YES | NO | 19910095 | 1991-06-03 | 22461 | WESTERN FUEL OIL CO | NO | 1991-04-23 | 50 | CA | LOS ANGELES | SAN PEDRO | NO |  | NO | EAST SIDE OF HARBOR FREEWAY #110 EMBANKMENT, JUST WEST OF HOHN S GIBSON BLVD, WHICH IS WEST OF THE LOS ANGELES HARBOR DEPARTMENT WEST BASIN. |  | LINE PIPE | OTHER | GASKET LEAK IN FLANGES | 1971 | OTHER | FAILED GASKET IN FLANGES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 530000 | 425976.978 | 859367.6235 | GASOLINE | 1 | 269 | 45 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILIAM H. LOUIS III FOR LARRY SULLIVAN - GENERAL MANAGER | 2134994465 | SEE ATTACHED US COAST GUARD POLLUTION INCIDENT STATEMENT
2017-09-29 08:50 | YES | NO | 19910096 | 1991-06-04 | 18718 | SUN PIPELINE CO | YES | 1991-04-15 | 1640 | PA | BERKS | UNKNOWN | NO |  | NO | MONTELLO WAREHOUSE AND PUMP STATION FACILITY LOCATED ON FRITZTOWN ROAD, SINKING SPRING TOWNSHIP, BERKS COUNTY, PENNSYLVANIA. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | FUEL OIL | 1 | 178 | 12 | NO | NO | 6.63 | 0.26 | 35000 | WELDED |  | 2130 | 942 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB ARNET, ACTING MANAGER, RISK MANAGEMENT | 9185866231 | AFTER EXPERIENCING PRESSURE DROP, SHUTTING DOWN THE LINE, AND CHECKING METERS, ETC., CONTROL CENTER NOTIFIED SUPERINTENDENT OF PROBLEM. THE LINE HAD BEEN OPERATING AT 952 PSI. THE GENERAL LOCATION OF THE LEAK WAS IDENTIFIED AS BEING INSIDE A CASING UNDER THE CONRAIL RR R/W THROUGH THE PIPELINE PROPERTY. SUN PIPE LINE SUPERVISION AND EMPLOYEES WERE ABLE TO RESPOND TO THE SITE IMMEDIATELY BECAUSE THE LEAK OCCURRED AT THE MONTELLO REGIONAL OFFICE LOCATION, WHICH INCLUDES PIPELINE MAINTENANCE, PUMP STATION AND TANK FARM FACILITIES, WITH ALL NORMAL EQUIPMENT AND PERSONNEL ON SITE. VACUUM TRUCK CONTRACTOR WAS CALLED TO SITE. RESPONSE CONTINUED, INCLUDING: EXCAVATION ON BOTH SIDES OF CASING IN ATTEMPT TO LOCATE LEAK, RECOVERY OF PRODUCT ABOVE AND BELOW GROUND USING AIR-DRIVEN PUMPS AND VACUUM TRUCK, MONITORING OF NEARBY CACOOSING CREEK TOVERIFY PRODUCT NOT REACHING WATER, MONITORING OF WORK AREA TO VERIFY NON-FLAMMABLE ATMOSPHERE, AND DRAINING OF PRODUCT REMAINING IN PIPELINE USING AIR PUMPS AND VACUUM TRUCK. CITIZEN'S UTILITIES WATER CO. NOTIFIED, AND ENGINEER, STEVE GIBBS, LATER RESPONDED TO SITE. WATER COMPANY WILL MONITOR THEIR ACTIVE WELL ABOUT ONE-QUARTER MILE EAST OF THE SITE. RESPONSE CONTINUED THROUGHOUTTHE NIGHT, DRAINING LINE AND RECOVERING PRODUCT. RESPONSE CONTINUED. TEST PITS WERE DUG AND CHECKED FOR PRODUCT; ALL WERE NEGATIVE AND REFILLED EXCEPT ONE ON EAST SIDE OF RR ABOUT 10 FEET FROM PIPELINE. THIS PIT WAS FITTED W/ A PERFORATED PVC PIPE (BOTTOM CAPPED) AND VACUUMED. ACCIDENT DISCUSSED W/ DOT OPS, PHILLIP NGUYEN. CONRAIL NOTIFIED; ENGINEER, JOHN GOSHERT, RESPONDED TO SITE AND APPROVED ACTIONS RE RR R/W. RESPONSE CONTINUED. TRENCH EXCAVATEDTO PERMIT EXTRACTION OF PIPE FROM CASING UNDER RR. 162 FT. OF PIPE REMOVED FROM CASING. TWO 1/32" HOLES WERE FOUND AT APPROX. 71 FT. AND 76 FT. FROM THE EAST END OF THE REMOVED PIPE. WORK IN PREPARATION FOR REPLACEMENT OF THE PIPE CONTINUED THROUGHOUT THE NIGHT. REPLACEMENT PIPE SECTIONS IN PLACE AND WELDED. WELD X-RAYS APPROVED. LINE THEN REPRESSURED AND WORKING.
2017-09-29 08:50 | YES | YES | 19910097 | 1991-06-10 | 15490 | PHILLIPS PIPE LINE CO | YES | 1991-05-11 | 1000 | TX | BLANCO | UNKNOWN | NO |  | NO | 3600 FT. EAST OF FM 1320, ONE MILE SOUTH OF SANDY, TEXAS. SECTION 543; H.M. DOWNMAN SURVEY (LINE EZ PIPELINE MP 221-52+00). |  | LINE PIPE | OTHER | TD WILLIAMSON COMP. PLUG | 1991 | OTHER | BALL CHECK ASSEMPLY LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN - ENGINEERING MANAGER | 9186614721 | MEDICAL TREATMENT WAS PROVIDED FOR A MAINTENANCE CREW EMPLOYEE WHO RECEIVED A FIRST DEGREE NGL FREEZE BURN ON HIS RIGHT FOREARM DURING THE INSTALLATION OF THE BLIND FLANGE ON A T D WILLIAMSON STOPPLE FITTING. A SMALL AMOUNT OF LIQUID NGL SUDDENLY ESCAPED FROM THE CHECKBALL IN THE COMPLETION PLUG. COMPLETION OF THE BLIND FLANGE INSTALLATION HALTED THE LEAK. THE EMPLOYEE RETURNED TO HIS NORMAL WORK SCHEDULE FOLLOWING THE EMERGENCY ROOM TREATMENT.
2017-09-29 08:50 | NO | NO | 19910098 | 1991-06-10 | 18718 | SUN PIPELINE CO | YES | 1991-04-29 | 1415 | PA | LUZERNE | UNKNOWN | NO |  | NO | LUZERNE COUNTY, SALEM TOWNSHIP, APPROXIMATELY 2 MILES WEST OF TOWN OF SHICKSHINNY, 1431 FEET NORTH OF SAW MILL ROAD. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | GASOLINE | 3 | 11 | 1 | NO | NO | 6 | 0.26 | 35000 | WELDED |  | 1970 | 685 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB ARNET, ACTING MANAGER, RISK MANAGEMENT | 9185866231 | PIPELINE CONTROL CENTER AT WAYNE, PA. (CHESTER COUNTY) RECEIVED TELEPHONE CALL FROM RESIDENT (JAMES BACH) NEAR 6" NORTH LINE, LUZERNE COUNTY, SALEM TOWNSHIP, WHO HAD SMELLED PETROLEUM ODOR NEAR RIGHT-OF-WAY (R/W) ABOVE SAW MILL ROAD, APPROXMATELY 2 MILES WEST OF SHICKSHINNY, PENNSYLVANIA AND OBSERVED A SMALL STAINED AREA. THE MONTELLO MAINTENANCE (BERKS COUNTY, SPRING TOWNSHIP) FOREMAN (MMF) WAS NOTIFIED AND ORDERED THE LINE SHUT DOWN. HE ALSO SENT A PIPELINER TO THE SCENE TO INVESTIGATE. THE LINE WAS UNDER PRESSURE (668 PSIG) AND WAS BLOCKED IN AT OPERATING PRESSURE. THE PRODUCT WAS UNLEADED GAS. THE LINE IS NOT COATED IN THIS AREA. THE PIPELINER WALKED THE AREA AND HAND-EXCAVATED THREE TEST PITS ON THE R/W. ONE OF THE PITS DID HAVE AN ODOR BUT IT DIDNOT APPEAR TO HAVE A PETROLEUM ODOR. THE LINE PRESSURE HAD HELD STEADY FOR NEARLY 4 HOURS. THE MONTELLO DISTRICT SUPERVISOR RELEASED THE LINE FOR START-UP AND INSTRUCTED THE MMF TO FOLLOW-UP THE NEXT DAY WITH A CREW AND HEAVY EQUIPMENT FOR A MORE THOROUGH INVESTIGATION. 6" NORTH LINE WAS SHUT DOWN AT ENDOF GASOLINE CYCLE. THE MMF AND A CREW WITH EQUIPMENT LEFT FOR THE SITE TO FOLLOW UP WITH ADDITIONAL TEST PITS. MMF REPORTED POSSIBLE EVIDENCE OF A LEAK, AND CONTINUED WITH EXCAVATIONS. NOTIFICATION OF SUSPECTED LEAK TO NRC; #70023. NOTIFICATION OF SUSPECTED LEAK TO PA DER (ANSWERING SERVICE - REPR. TO CALL BACK). CALL BACK FROM PA DER REPR., KEVIN AUGUSTINE. STATED DER WOULD NOT RESPOND IMMEDIATELY, BUT ASKED TO BE NOTIFIED IF LEAK PROVED TO BE A MAJOR LEAK. LEAK FOUND; WAS AN ISOLATED CORROSION PIT ABOUT 1/4" IN DIAMETER LOCATED AT APPROXIMATELY THE FIVE-THIRTY POSITION ON THE PIPE WHEN FACING NORTH. BELLHOLE EXCAVATED AROUND PIPELINE. EMERGENCY LEAK CLAMP INSTALLED OVER HOLE IN PIPE TO STOP ESCAPE OF PRODUCT WHILE LINE WAS DRAINED DOWNHILL AS MUCH AS POSSIBLE. LITTLE PRODUCT WAS SEEN; IT WAS BELIEVED THAT VERY LITTLE HAD ESCAPED. ABOUT 15 GALLONS OF PRODUCT WERE COLLECTED FROM THE HOLE IN THE PIPEBEFORE CLAMP WAS INSTALLED. PRODUCT WAS ALSO COLLECTED IN ABSORBENT MATERIALS. TEMPORARY REPAIR SLEEVE (PLIDCO) INSTALLED. LINE WILL NOT BE RE-PRESSURED UNTIL 05-02-91 AT 0115. PIPELINERS WILL BE ON-SITE TO MONITOR TEMPORARY REPAIR DURING START UP. NOTIFIED PA DER OF SITUATION. ROBERT GADINSKI, HYDROGEOLOGIST, RESPONDED TO SITE, INSPECTED AREA AND DISCUSSED FUTURE ACTIONS.
2017-09-29 08:50 | YES | NO | 19910099 | 1991-06-10 | 2731 | CHEVRON PIPELINE CO | YES | 1991-05-28 | 1900 | TX | WINKLER | KERMIT | NO |  | NO | APPROX. 4 MILES N OF KERMIT ON HWY 8, & APPROX. 4 MILES NE ON 874. SEC. 10, BLK B-3, SURVEY PSL, KEYSTONE FIELD. |  | TANK FARM | TANK |  | 1953 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 250 | 230 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.D. DIMMITT - COMPLIANCE COORDINATOR | 9156877559 | VAREC GAUGING SYSTEM MALFUNCTIONED, CAUSING TANK TO OVERFLOW.
2017-09-29 08:50 | YES | NO | 19910100 | 1991-06-03 | 13131 | CONOCO INC | YES | 1991-05-21 | 1115 | OK | PAYNE | UNKNOWN | NO |  | NO | SW/4 SE/4 SEC. 15, T17N, R53 (3 MILES SW OF CUSHING, OKLAHOMA) PAYNE COUNTY, OKLAHOMA. |  | LINE PIPE | PIPE |  | 1977 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8841.0316 | 17835.9318 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 1186 | 50 | YES | 4 | 1483 |  | 77 | INTERNAL | Null | YES | OTHER | INTERNAL CHEM IONIZATION | NO DATA |  | Null | NO DATA |  | Null | Null | VANCE WEBB, ENVIRONMENTAL COORDINATOR | 4057674845 | ON MAY 21, 1991, AS A RESULT OF INTERNAL CORROSION, CRUDE OIL LEAKED FROM THE12" LINE LOCATED INSIDE CONOCO PIPE LINE'S CUSHING STATION FACILITY. THE OIL TRAVELED DOWN GRADIENT AND ONTO THE ADJACENT TEXACO FACILITY, WHERE IT CONTACTED A FIRE WATER POND. THE OIL WAS CONTAINED AT THIS POINT WITH ABSORBENTBOOMS. RECOVERY CONSISTED OF USING ABOSRBENT BOOMS, A VACUUM TRUCK AND ABSORBENT PADS. THE REMAINING RESIDUE WAS BURNED. THE DAMAGED PIPE WAS REPAIREDWITH A 28" SECTION OF HALF SOLE, AND NORMAL OPERATIONS HAVE RESUMED. AS SOON AS OPERATIONS PERMIT, THE DAMAGED JOINT OF PIPE WILL BE REPLACED. THIS LINE OPERATES AT LESS THAN 20% SMYS AND IS NOT CONSIDERED TO BE OPERATING UNDER DOT JURISDICTION, HENCE, THIS REPORT IS BEING SUPPLIED FOR INFORMATIONAL PURPOSES ONLY.
2017-09-29 08:50 | YES | NO | 19910101 | 1991-06-05 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1991-05-02 | 1315 | CA | CONTRA COSTA | RICHMOND | NO |  | NO | APPROXIMATELY 60 FT FROM CARLSON BLVD AND APPROXIMATELY 15 FEET FROM SOUTHERN PACIFIC RAILROAD MAIN LINE TRACKS. |  | LINE PIPE | PIPE |  | 1963 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 80373.0147 | 162144.8346 | DIESEL FUEL | 3 | 85 | 80 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1440 | 1380 | YES | 24 | 1800 | 4 | 63 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS & ENGINEERING | 2134867720 | PIPE EXPERIENCED A SEAM SPLIT AND APPROXIMATELY 85 BARRELS OF NO. 2 DIESELFUEL ESCAPED OF WHICH 80 BARRELS WERE RECOVERED.
2017-09-29 08:50 | YES | NO | 19910102 | 1991-06-04 | 22610 | WILLIAMS PIPELINE CO | YES | 1991-05-06 | 1730 | KS | MONTGOMERY | UNKNOWN | NO |  | NO | LINE SECTION A058, MP 5+1663 SE 1/4, NE 1/4, SECTION 31, T34S, R16E. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1607.4603 | 3242.8967 | FUEL OIL | 3 | 210 | 170 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 600 | 587 | YES | 8 | 845 |  | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E.JAZEN-VICE PRESIDENT OPERATION | 9185883850 | ON 5/6/91 THE #2-8" COFFEYVILLE-CANEY JUNCTION LINE WAS SHUT DOWN BECAUSE OFA SUSPECTED LEAK CONDITION. CREWS WERE DISPATCHED TO CONFIRM AND LOCATE THELEAK. THE LEAK WAS DISCOVERED IN A CASING UNDER THE UNION PACIFIC RAILROAD.EXTERNAL CORROSION WAS THE CAUSE. THE OLD PIPE WAS PULLED FROM THE 162' CASING AND NEW PIPE WAS INSTALLED. APPROXIMATELY 170 BBLS OF FREE PRODUCT WERE RECOVERED. THE REMAINING PRODUCT IS EXPECTED TO BE RECOVERED VIA SOIL EXCAVATION. ALL CLEANUP EFFORTS HAVE BEEN COORDINATED WITH STATE ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19910103 | 1991-06-25 | 2552 | COLONIAL PIPELINE CO | YES | 1991-05-24 | 745 | AL | SHELBY | PELHAM | NO |  | NO | COLONIAL PIPELINE COMPANY'S PELHAM JUNCTION COUNTY ROAD - 52 EAST. P.O. BOX 248 PELHAM, AL 35124. |  | TANK FARM | OTHER | UNKNOWN | 1980 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2411.1904 | 4864.345 | GASOLINE | 3 | 65 | 65 | NO | NO | 3 | 0.22 | 0 | WELDED |  | 720 | 300 | YES | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | WAITING ON METALLURG REP. | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER - TECHNICAL & REGULATORY | 4048412296 | AT 7:45 AM EST ON MAY 24, A991, THE PELHAM OPERATOR DISCOVERED A SHEEN OF REFINED PRODUCT ON THE RETENTION POND WITHIN COLONIAL'S PELHAM JUNCTION TANK FARM. THE ALABAMA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT WAS NOTIFIED AT 9:30AM. EST. PRODUCT APEARED TO BE COMING FROM THE DRAIN LINE FROM THE OIL/WATERSEPARATOR ON THE NO. 1 STATION, AND WAS ESTIMATED TO BE SMALL IN QUANTITY. AN INSPECTION WAS IMMEDIATELY BEGUN AND CONSISTED OF UNCOVERING THE PIPING FROM THE OIL/WATER SEPARATOR AND DIGGING TEST PITS. THE LEAK WAS LOCATED ON JUNE 4, 1991, AT 11:17 AM EST IN A 3 INCH O.D. DRAIN LINE ON THE PIPING WHICH WAS LOCATED BETWEEN THE BOOSTER PUMP AND OUTGOING TRAP OF A 16-INCH DELIVERY STUB LINE. THE DRAIN LINE WAS EMPTIED AND THE LEAKING PIPING REPLACED. EXAMINATION REVEALED INTERNAL CORROSION HAD OCCURRED ADJACENT TO A GIRTH WELD. OTHER DRAIN LINES ARE BEING EXPOSED, DRAINED AND REDIOGRAPHED. RECOVERY EFFORTS ARE CONTINUING. NINE MONITORING WELLS HAVE BEEN DRILLED AND INSTALLED. APPROXIMATELY 65 BARRELS HAVE BEEN RECOVERED.
2017-09-29 08:50 | NO | NO | 19910104 | 1991-06-25 | 737 | ASHLAND PIPELINE CO | YES | 1991-05-24 | 2000 | OH | MORROW | UNKNOWN | NO |  | NO | BLOOMING GROVE PUMP STATION APPROX. 1/4 MILE SOUTH OF ST. RT. 288 ON CO.RD. 20, N. BLOOMFIELD TWP., MORROW CO., NE QUARTER OF SEC. 14-519N,R20W. |  | PUMPING STATION | OTHER | THREADED FITTING | 1968 | OTHER | 1/2" PIPE NIPPLE CRACKED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10500 | 8439.1665 | 17025.2076 | CRUDE OIL | 1 | 12 | 10 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A. BAKER - DIVISION SUPERINTENDENT | 4198840800 | AT 7:12 PM., MAY 24, 1991 THE OPERATOR AT THE COMPANY'S PIPELINE CONTROL CENTER IN ASHLAND, KY RECEIVED A CALL FROM A LANDOWNER THAT OIL WAS RUNNING FROMA FIELD TILE INTO A ROAD DITCH NEAR THE COMPANY'S BLOOMING GROVE CRUDE OIL PUMP STATION. A RESPONSE CREW WAS IMMEDIATELY DISPATCHED TO THE SCENE, AND AT7:15 PM., MAY 24, 1991 THE LINE WAS SHUT DOWN. AT APPROXIMATELY 1:30 AM. ONMAY 25, 1991 IT WAS DETERMINED THAT THE CAUSE OF THE SPILL WAS A CRACK IN A 1/2" PIPE NIPPLE ATTACHED TO THE MANIFOLD PIPING IN THE PUMP STATION. THE DEFECTIVE PIPE NIPPLE WAS REMOVED AND REPLACED WITH A 1/2" STEEL PIPE PLUG, ANDTHE LINE WAS RESTARTED AT ABOUT 1:45 AM. ON MAY 25, 1991 THE OIL RAN APPROXIMATELY 100 FT DOWN A ROAD DITCH INTO A SMALL UNNAMED WATERWAY. SIPHON DAMS WERE INSTALLED IN THE STREAM AND ROAD DITCH TO HALT THE FLOW OF OIL AND VACUUMTRUCKS AND SORBENT MATERIALS WERE USED TO PICK UP THE FREE OIL. APPROXIMATELY 10 BARRELS OF FREE OIL WERE RECOVERED AND RETURNED TO THE SYSTEM. THE OILY WASTE AND RESIDUE WAS COLLECTED IN A SPECIAL CONTAINER TO BE DISPOSED OF ATA LICENSED LANDFILL. AS OF THIS WRITING, CLEAN-UP IS APPROXIMATELY 90% COMPLETE.
2017-09-29 08:50 | NO | NO | 19910105 | 1991-06-24 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1991-05-31 | 1600 | IA | IOWA | UNKNOWN | NO |  | NO | SEC. 33 T79N.R11W IOWA COUNTY, IA. |  | LINE PIPE | OTHER | 3RD PARTY DAMAGE | 1970 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 8 | 0.2 | 42000 | WELDED |  | 1420 | 875 | YES | 24 | 1969 |  | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PUBLIC AWARENESS/MARKERS | NO | NO | KENNETH D. COLLINS, GOVERNMENT REGULATIONS COORDINATOR | 3144865488 | APPEARS THAT A TILTING MACHINE HAS STRUCK THE LINE SOME TIME AGO. AMMONIA VAPORS WERE REPORTED BY A FARMER WORKING IN THE FIELD. PERSONNNEL WERE DISPATCHED AND LINE WAS REPAIRED ACCORDING TO DOT SPECIFICATIONS. THERE WERE NO INJURIES, NO EVACUATION, NO CONTAIMINATION OF WATERWAYS, AND NO PERSONAL PROPERTYDAMAGE. NATIONAL RESPONSE CENTER REPORT NUMBER 73992. ALSO REPORTED LEAK TO IOWA DEPARTMENT OF NATURAL RESOURCES, REFERENCE NUMBER 05311 WPW.
2017-09-29 08:50 | NO | NO | 19910106 | 1991-06-24 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1991-06-03 | 1740 | IA | PALO ALTO | UNKNOWN | NO |  | NO | PALO ALTO COUNTY SEC. 22 T96N R34W IOWA. |  | LINE PIPE | OTHER | UNKNOWN | 1970 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1205.5952 | 2432.1725 | ANHYDROUS AMMONIA | 2 | 3 | 0 | NO | NO | 8 | 0.2 | 42000 | WELDED |  | 1420 | 680 | YES | 24 | 1969 |  | 70 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH D. COLLINS, GOVERNMENT REGULATIONS COORDINATOR | 3144865488 | GROUND DISCOLORATION WAS NOTICED BY FARMER AND CALLED IN TO OUR PIPELINE CONTROL CENTER. COMPANY PERSONNEL WERE DISPATCHED TO LOCATION. LINE WAS DUG-UPAND A SMALL PIN HOLE WAS FOUND IN A GIRTH WELD. REPAIR WAS MADE ACCORDING TODOT SPECTIFICATIONS. THERE WERE NO INJURIES, NO EVACUATION, NO CONTAMINATION OF WATERWAYS, AND ONLY SLIGHT PERSONAL PROPERTY DAMAGE TO CROPS. NATIONAL REPSONSE CENTER REPORT NUMBER 74297. ALSO REPORTED TO IOWA DEPARTMENT OF NATURAL REESOURCES, REFERENCE NUMBE 06051 WPW.
2017-09-29 08:50 | NO | NO | 19910107 | 1991-06-27 | 15490 | PHILLIPS PIPE LINE CO | YES | 1991-05-28 | 1430 | TX | SCHLEICHER | UNKNOWN | NO |  | NO | BENEDUM-SWEENY LINE - WP 67-30+67. SECTION 24, BLOCK 57, UNIVERSITY LAND 20.5 MILES WEST OF ELDORADO, TX, ON HWY. 190, THEN 3 MILES NORTH. |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 14467.1426 | 29186.0702 | NATURAL GAS LIQUID | 2 | 1 | 0 | NO | NO | 10.75 | 0.39 | 30000 | WELDED |  | 990 | 390 | YES | 24 | 1280 | 8 | 75 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | A LEAK WAS REPORTED BY A SURVEY CREW LAYING OUT ROUTE FOR REPLACEMENT PIPELINE. ONSITE INSPECTION INDICATED THAT THE PINHOLE LEAK APPEARED TO HAVE BEEN CAUSED BY EXTERNAL CORROSION. PITTING WAS NOTED NEAR THE LEAK. PIPE IN THE AFFECTED AREA WAS REPLACED.
2017-09-29 08:50 | NO | NO | 19910108 | 1991-06-25 | 22610 | WILLIAMS PIPELINE CO | YES | 1991-05-22 | 1345 | NE | DOUGLAS | UNKNOWN | NO |  | NO | LS #C116, MP 162+2640, 15N, R12E, SECTION 7. |  | LINE PIPE | WELDING FITTING |  | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | L. P. G. | 2 | 1 | 0 | NO | NO | 6 | 0.22 | 35000 | WELDED |  | 1450 | 0 | YES | 8 | 1975 | 9 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - VICE PRESIDENT - OPERATIONS | 9185883850 | WHILE ON A ROUTINE LEAK PATROL, AN OMAHA METROPOLITAN UTILITY DIVISION EMPLOYEE DETECTED SOME GAS VAPORS ALONG THE SIDE OF WEST MAPLE ST. NEAR THE NORTH EDGEOF EAGLE RUN GOLF COURSE IN OMAHA, NEBRASKA. THE INDIVIDUAL NOTICED OUR PIPELINE MARKERS NEARBY AND CALLED OUR EMERGENCY NUMBER TO REPORT A POSSIBLE LEAK. THE LINE WAS SHUT DOWN AND CREWS WERE DISPATCHED TO INVESTIAGE. FURTHER INVESTIGATION IDENTIFIED A SMALL AMOUNT OF VAPOR (BARELY DETECTIBLE) EMMINATING OUT OF THE CASING VENT. EXCAVATION OF THE SITE WAS VERY DIFFICULT BECAUSETHE LINE WAS 20-25 FEET DEEP UNDER THE ROAD CROSSING. THE ORIGIN OF THE LEAK WAS FINALLY TRACED TO AN INCOMPLETE FILLET WELD ON TWO OLD WELD-PLUS-END REPAIRS MADE BY THE PREVIOUS OWNER (WPL PURCHASED LINE IN 1983); ONE JUST OUTSIDE THE END OF THE CASING AND THE OTHER INSIDE THE CASING. THE OLD REPAIRS WERE CUT OUT AND THE ENTIRE LENGTH OF PIPE INSIDE THE CASING WAS REPLACED WITH N
2017-09-29 08:50 | YES | NO | 19910109 | 1991-06-25 | 4906 | EXXON PIPELINE CO | NO | 1991-05-21 | 1340 | TX | HARRIS | UNKNOWN | NO |  | NO | LEAK OCCURRED AT GATE PLANT "R" ON SATSUMA-WEBSTER SYSTEM. [APPROXIMATELY STATION 1182 + 20] |  | LINE PIPE | OTHER | STUB CONNEC. OFF 8" PIPE. | 1920 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1607.4603 | 3242.8967 | CRUDE OIL | 1 | 90 | 89 | NO | NO | 8 | 0.32 | 25000 | FLANGED |  | 600 | 300 | YES | 8 | 750 |  | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | YES | J.B. HOLT, ENVIRONMENTAL & REGULATORY COMPLIANCE MANAGER | 7136565521 | AT ABOUT 1343 HOURS ON MAY 21, 1991, WHILE BACKFILLING AN AREA WHICH HAD BEEN PREVIOUSLY EXCAVATED AT A GATE PLANT FOR HYDROSTATIC TEST PURPOSES, A BACKHOE ACCIDENTALLY STRUCK AND DAMAGED A "BLINDED" STUB CONNECTION ON AN ACTIVE 8-INCH PIPELINE. OUR OIL TRAFFIC CONTROL CENTER WAS IMMEDIATELY NOTIFIED OF THE RESULTANT LEAK AND THE AFFECTED LINE WAS SHUTDOWN. ALL OF THE ESTIMATED 90 BARRELS OF OIL WAS CONTAINED IN THE PREVIOUSLY EXCAVATED BELL HOLE. VACUUM TRUCKS RECOVERED 89 BARRELS. PERMANENT REPAIRS WERE COMPLETED THE SAME DAY BY INSTALLING A 31-FOOT SECTION OF 8-INCH PIPE.
2017-09-29 08:50 | YES | NO | 19910110 | 1991-06-25 | 9175 | JAYHAWK PIPELINE CORP | YES | 1991-05-22 | 1645 | KS | SEWARD | UNKNOWN | NO |  | NO | NW/4 SECTION 5-T34S-R32W SEWARD COUNTY, KANSAS APPROXIMATELY 6 MILES EAST AND 1 1/4 MILES NORTH OF LIBERAL, KANSAS IN RURAL AREA. |  | LINE PIPE | OTHER | UNKNOWN | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6500 | 5224.246 | 10539.4143 | CRUDE OIL | 1 | 125 | 0 | NO | NO | 6.63 | 0.19 | 35000 | WELDED |  | 1000 | 850 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | NO | MARK E. MOORE, PRESIDENT | 3162913254 | JAYHAWK PIPELINE WAS NOTIFIED BY TELEPHONE AT 1700 MAY 22, 1991 BY LANDOWNERTHAT HE HAD PUNCTURED OUR PIPE LINE WHILE OPERATING A ROAD MAINTAINER IN THEDITCH AREA OF HIS RANCH ROAD. TIME OF THE LEAK WAS APPROX. 1645. THE LEAK LOCATION WAS IN A RURAL AREA IN SEWARD COUNTY, 6 MI. EAST AND 1 1/4 MI. NORTH OF LIBERAL, KS. PIPELINE "WARNING" MARKERS WITH THE OPERATOR IDENTIFICATION AND EMERGENCY TELEPHONE NUMBER WERE ON EACH SIDE OF THE ROAD AT THE ACCIDENT LOCATION. THE LINE WAS SHUT DOWN BY 1730. BLOCK VALVES EAST AND WEST OF THE LEAK LOCATION WERE CLOSED BY 1900. DRAIN UP OF THE ISOLATED SECTION OF PIPELINE AND EXCAVATION OF THE DAMAGED PIPE WERE COMPLETED BY 0600 MAY 23. THE DAMAGED PIPE WAS REMOVED AND A REPLACEMENT JOINT, 4' 6", OF PRETESTED 6" PIPE WAS INSTALLED. THE TWO TIE-IN WELDS WERE X-RAYED AND OKAYED AT 1130. LINE WASBACK IN SERVICE AT 1145 MAY 23, 1991. THE PUNCTURE WAS ON THE TOPSIDE OF THE PIPE. THE INITIAL UPWARD SPRAY OF CRUDE OIL STAINED A 150' X 1150' AREA NORTH OF THE LEAK DUE TO A GUSTY SOUTH WIND. AN ESTIMATED 100 BARRELS OF CRUDEWAS ABSORBED BY THE SANDY SOIL IN THIS AREA. TWENTY-FIVE BARRELS OF CRUDE RAN DOWN THE HILLSIDE TO TWO SMALL STOCK PONDS. THE LEAK WAS REPORTED TO THE KANSAS DEPARTMENT OF HEALTH & ENVIRONMENT, GARDEN CITY, KS OFFICE THE MORNINGOF MAY 23 AND PERMISSION WAS OBTAINED TO BURN THE CRUDE ON THE PONDS AFTER THE LINE REPAIRS HAD BEEN COMPLETED. INTERNAL AND EXTERNAL INSPECTION OF PIPE AT LEAK SHOWED NO EVIDENCE OF CORROSION. REPLACEMENT AND EXPOSED PIPE WERE COATED WITH ROSCOTE AND GLASFAB.
2017-09-29 08:50 | NO | NO | 19910111 | 1991-06-25 | 18718 | SUN PIPELINE CO | YES | 1991-05-14 | 1200 | OH | LUCAS | TOLEDO | NO |  | NO | 2500' FEET NORTH OF YORK STREET CROSSING AND 30' NORTH OF DUCK CREEK INT HE CITY OF TOLEDO, OHIO; TOLEDO TO INKSTER 6" LINE. |  | LINE PIPE | WELDING FITTING |  | 1963 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16074.6029 | 32428.9669 | L. P. G. | 2 | 1 | 0 | NO | NO | 6.63 | 0.28 | 0 | WELDED |  | 1100 | 900 | YES | 8 | 1600 | 11 | 85 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | LEAK WAS REPORTED BY A NEIGHBOR WHO SPOTTED BUBBLING IN A DRAIN DITCH EMPTYING INTO DUCK CREEK. HE THEN CALLED THE TOLEDO REFINERY AND TALKED TO BILL RENNIE. BILL CHECKED LEAK SITE AND NOTIFIED FLOYD PAYTON WHO INVESTIGATED AND FOUND IT BELONGED TO SUN PIPE LINE. SUN PERSONNEL THEN PURGED THE LINE WITH NITROGEN AND REMOVED LEAKING SMITH COUPLING.
2017-09-29 08:50 | NO | NO | 19910112 | 1991-06-18 | 809 | ARCO PIPE LINE CO | YES | 1991-05-24 | 1230 | KS | MONTGOMERY | UNKNOWN | NO |  | NO | SEC. 3. T34S, R14E, MONTGOMERY COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 6429.8412 | 12971.5868 | FUEL OIL | 3 | 5 | 0 | NO | NO | 8.63 | 0.32 | 25000 | WELDED |  | 490 | 155 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | F.L. NEELEY, MANAGER PRODUCTS BUSINESS UNIT | 3163311300 | EVIDENCE OF PRODUCT ON SMALL FARM POND WAS REPORTED BY LANDOWNER TO CONTROL CENTER. LINE WAS SHUT DOWN AND INVESTIGATION BY COMPANY PERSONNEL REVEALED SMALL LEAK CAUSED BY EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19910113 | 1991-07-10 | 15851 | PRIDE REFINING INC | NO | 1991-06-12 | 830 | TX | JONES | HAWLEY | NO |  | NO | PRIDE PIPELINE COMPANY'S HAWLEY TANK FARM. |  | TANK FARM | TANK |  | 1952 | OTHER | FAILURE IN TANK BOTTOM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | FUEL OIL | 3 | 620 | 611 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON, PIPELINE MANAGER | 9156748231 | LEAK OCCURRED IN THE FLOOR OF A 55,000 BBL STORAGE TANK. THE REMAINING VAPOR GAS OIL (VGO) WAS TRANSFERRED FROM THE TANK WHILE THE VGO WHICH HAD LEAKED FROM THE TANK WAS VACUUMED UP AND TRANSPORTED BACK TO THE REFINERY.
2017-09-29 08:50 | YES | NO | 19910115 | 1991-07-08 | 19226 | TEXACO PIPELINE CO | YES | 1991-06-14 | 1515 | OK | NOBLE | UNKNOWN | NO |  | NO | THE INTERSEC. OF HWY 64 & 86 IN NOBLE CTY, OK. GO 4 MILES S. THE WHY 86, 2 MI. EAST, 1 MI. S. AND 1/4 E. LEAK OCCURRED IN THE SW 1/4, SEC. 7, T20N, R1E NOBLE. |  | LINE PIPE | PIPE |  | 1918 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | CRUDE OIL | 1 | 300 | 150 | NO | NO | 8 | 0.32 | 35000 | THREADED |  | 490 | 60 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B.C. VRATIL - OKLAHOMA AREA OPERATIONS MANAGER | 9182253469
2017-09-29 08:50 | NO | NO | 19910116 | 1991-07-08 | 19536 | TOTAL PIPELINE CORP | YES | 1991-06-05 | 1100 | OK | GARFIELD | UNKNOWN | NO |  | YES | NE/4 & SE/4 SEC. 16, T22N - R3W. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8841.0316 | 17835.9318 | CRUDE OIL | 1 | 20 | 5 | NO | NO | 6 | 0.25 | 26627 | THREADED |  | 792 | 500 | YES | 8 | 990 | 10 | 85 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GARY A. STRACK - DOT CO-ORDINATOR | 3164425100 | NOTIFIED BY OWNER, LINE CLAMPED & PUT BACK IN SERVICE. OIL TRAVELED DOWNPASTURE DRAW AND BARELY REACHED A POND IN SE/4 SEC. 16. PICKED UP SOME OIL &BURNED PER PERMISSION FROM AIR QUALITY SERVICE. OKLA. CORP. COMMISSIONSATISFIED WITH CLEAN UP. UPDATE: PERMANENT REPAIR MADE TO PIPELINE ON6/26/91. ONLY A SHORT SECTION OF PIPE WAS REPLACED AS PIPELINE WAS INEXCELLENT CONDITION EXCEPT FOR THE ONE PIT THAT FAILED. SAMPLE BEING RETAINEDFOR TESTING. SUPPLEMENTAL REPORT 8/26/94 INDICATES PIPE TO SOIL POTENTIAL WELLOVER -.850 WITH IR DROP CONSIDERED.
2017-09-29 08:50 | YES | NO | 19910117 | 1991-07-15 | 443 | AMOCO PIPELINE CO | YES | 1991-06-30 | 2300 | TX | YOAKUM |  | NO |  | NO | ONE MILE NORTH AND THREE MILES EAST OF DENVER CITY, YOAKUM COUNTY, TEXAS. |  | LINE PIPE | PIPE |  | 1944 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | CRUDE OIL | 1 | 28200 | 26900 | NO | NO | 20 | 0.38 | 0 | WELDED |  | 275 | 0 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES L. HOMER - PIPELINE MAINTENANCE FMN. | 5053962817 | SPILL WAS DISCOVERED 2300 HOURS ON 6/30/91. IT IS UNKNOWN WHAT TIME IT ACTUALLY OCCURRED. TOTAL OUTAGE WAS 28,200 BBLS. LEAK WAS TEMPORARILY REPAIRED AND TANK AND LINE WERE TAKEN OUT OF SERVICE UNTIL PERMANENT REPAIRS CAN BE MAD
2017-09-29 08:50 | YES | NO | 19910118 | 1991-07-15 | 443 | AMOCO PIPELINE CO | YES | 1991-06-19 | 1100 | TX | TERRY | UNKNOWN | NO |  | NO | GO NORTH OF TOKIS, TEXAS 5 MILES ON BLACK TOP ROAD, TURN EAST 1/2 MILE BETWEEN FARMS' TURN ROLL. |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | CRUDE OIL | 1 | 1000 | 15 | NO | NO | 16 | 0.25 | 38250 | WELDED |  | 788 | 300 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ALBERT L. WOOD, JR. - PIPELINE MAINT. FOREMAN | 8068946187 | PIPELINE ACCIDENTAL PUNCTURE BY TELEPHONE COMPANY, PLOWING IN TELEPHONE CABLE
2017-09-29 08:50 | YES | NO | 19910119 | 1991-07-16 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1991-06-20 | 845 | TX | CHAMBERS | MT. BELVIEU | NO |  | NO | NEAR FM 1942 OFF STATE HWY. 146. |  | TANK FARM | TANK |  | 1954 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 15 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JESSE L. MITCHELL - MANAGER DOT COMPLIANCE DEPT. | 7137593784 | ON THE MORNING OF JUNE 20, 1991 TEPPCO'S TERMINAL OPERATOR BEGAN FILLING THEISOBUTANE TANK FOR TRUCK DELIVERY LOAD-OUTS. AN UNEXPECTED INCREASE IN THE FILLING FLOW RATE OCCURRED AND OVERFILLED THE TANK. THE OVER-PRESSURE SAFETYVALVE FUNCTIONED PROPERLY RELEASING PRODUCT TO THE ATMOSPHERE TO PREVENT OVERPRESSURING THE TANK. THE OPERATOR IMMEDIATELY SHUT DOWN THE FLOW TO THE TANK. WHEN THE PRESSURE IN THE TANK RETURNED TO NORMAL THE OVER PRESSURE SAFETYVALVE CLOSED STOPPING THE RELEASE OF PRODUCT.
2017-09-29 08:50 | YES | NO | 19910120 | 1991-07-16 | 2731 | CHEVRON PIPELINE CO | YES | 1991-06-28 | 1530 | TX | HUDSPETH | DELL CITY | NO |  | NO | S ON HWY 1437 FROM DELL CITY APPRX 8 MI: W ON 180: SEC: 2 BLK: L, SURVEY UNIV LANDS MP 73. |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 120.5595 | 243.2173 | CRUDE OIL | 1 | 150 | 145 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 700 | 600 | YES | 8 | 1000 |  | 83 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D,D, DIMMITT - COMPLIANCE COORDINATOR | 9156877559 | LEAK DUE TO EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19910121 | 1991-07-16 | 25140 | UNOCAL CORP | NO | 1991-06-17 | 1530 | CA |  |  | YES | 33 35'14"118 08'26.07" | YES |  |  | LINE PIPE | PIPE |  | 1983 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 522424.5957 | 1053941.425 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | SHIP ANCHOR |  | Null | OTHER | UNKNOWN | NO | NO | DAVID L. SAYLOR, DISTRICT PRODUCTION ENGINEER | 2139466246 | ON JUNE 17, 1991 AT APPROXIMATELY 3:30 PM AN OIL SHEEN WAS SPOTTED IN THE VICINITY OF THE SOUTHWEST CORNER OF PLATFORM EDITH LOCATED IN OCS P-0296. INVESTIGATION AND TESTING OF THE 6-INCH OIL PIPELINE SERVING THE PLATFORM COMFIRMED IT TO BE THE SOURCE OF THE SPILL. SPILL RESPONSE EFFORTS WERE SUBSEQUENTLY MOBILIZED AND THE PIPELINE WAS SECURED. A DETAILED SUBSEA INVESTIGATION WAS MOBILIZED BEGINNING AT 6:00 PM LATER ON JUNE 17, 1991. VESSELS WITH EQUIPMENT AND DIVERS ARRIVED ON THE SCENE IN THE AFTERNOON ON JUNE 18, 1991 AND INITIATED PRELIMINARY INVESTIGATION EFFORTS. LATE IN THE EVENING ON JUNE 18, 1991 THE SOURCE OF THE SPILL WAS LOCATED. THE PIPELINE HAD BEEN SNAGGED BY A SHIP'S ANCHOR (OR GRAPPLING DEVICE) AND SEVERELY BUCKLED. THE PIPELINE HAD FAILED AT THE TOP OF THE BUCKLE WHERE THE PIPE WALL HAD THINNED. THE FAILURE WAS A SMALL CRACK AND WAS NOT LEAKING WHEN OBSERVED. PRELIMINARY INVESTIGATION EFFORTS WERE CURTAILED AND REVISED EQUIPMENT WAS MOBILIZED TO PATCH THE CRACK AND INSPECT THE ENITRE LENGTH OF THE PIPELINE. THIS WORK WAS ACCOMPLISHEDBETWEEN JUNE 20 TO 24, 1991. DISPLACEMENT OPERATIONS TO FLUSH ALL MOVEABLE OIL FROM THE PIPELINE WERE SUCCESSFULLY COMPLETED ON JUNE 25. THE PIPELINE IS CURRENTLY SECURED AND STANDING FULL OF PRODUCED WATER. SUBSEQUENT INVESTIGATIONS HAVE INDENTIFIED THE VESSEL AND ACTIVITIES WHICH CAUSED THE MECHANICALDAMAGES. THE DAMAGE OCCURRED LATE ON THE EVENING OF JUNE 11, 1991 AND INFORMATION ON THE INCIDENT WAS WITHHELD FROM UNOCAL UNTIL THE SUBSEQUENT FAILURE INVESTIGATION. BETWEEN JUNE 11 AND JUNE 17, 1991 THE PIPELINE SYSTEM CONTINUED TO OPERATE WITH NORMAL PRESSURE RANGES UNTIL PROGRESSIVE PIGGING OPERATIONS TO PREPARE FOR AN INTERNAL INSPECTION CREATED A PRESSURE SURGE TO 1,640 PSIG (PIPELINE MAOP IS 2,160 PSIG). THIS SURGE RESULTED IN A FAILURE AT THE BUCKLE WHERE PIPE WALL THINNING HAD OCCURRED. REPAIR PROGRAM PREPARATIONS ARE NOW IN PROGRESS WITH THE LOCAL REGIONAL SUPERVISORS OFFICE OF THE MMS.
2017-09-29 08:50 | YES | NO | 19910122 | 1991-07-20 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1991-06-14 | 600 | OK | KINGFISHER | UNKNOWN | NO |  | NO | NE 1/4 SEC. 23-15N-5W KINGFISHER COUNTY. |  | PUMPING STATION | OTHER | UNKNOWN | 1962 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10929 | 8783.9668 | 17720.809 | CRUDE OIL | 1 | 5290 | 5275 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | THURMAN SMITH, AREA FOREMAN | 4052758280 | LIGHTNING HIT CONTROL PANEL, KNOCKING DOWN THE DISCHARGE PUMP AND AS A DIRECT RESULT CAUSING THE ALARM SYSTEM TO FAIL.
2017-09-29 08:50 | YES | NO | 19910123 | 1991-07-22 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1991-06-27 | 843 | CA | STANISLAUS | UNKNOWN | NO |  | NO |  |  | PUMPING STATION | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 32149.2059 | 64857.9338 | CRUDE OIL | 1 | 634 | 605 | NO | NO | 2 | 0.25 | 35000 | WELDED |  | 40 | 40 | NO | 0 | 0 |  |  | NO DATA | Null | NO | OTHER | NONE | OTHER | UNKNOWN | Null | NO DATA |  | Null | Null | R.E. KELLEY - NORTHERN DISTRICT MANAGER | 8053270110 | PIPELINE HEATER FUEL CIRCULATING LINE CRACKED DUE TO BROKEN BRACKET HOLDING PIPE. PIPE CRACKED UNDER STRAIN WHEN PIPE BRACKET BROKE.
2017-09-29 08:50 | YES | NO | 19910124 | 1991-07-22 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1991-07-12 | 945 | CA | FRESNO |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1910 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | CRUDE OIL | 1 | 800 | 750 | NO | NO | 10 | 0.38 | 35000 | WELDED |  | 90 | 90 | YES | 5 | 300 | 9 | 85 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. KELLEY, NORTHER DISTRICT MANAGER | 8053270110 | CORROSION PIT LEAK.
2017-09-29 08:50 | YES | NO | 19910125 | 1991-07-23 | 2552 | COLONIAL PIPELINE CO | YES | 1991-06-22 | 800 | MS | PIKE | MAGNOLIA | NO |  | NO | COLONIAL PIPELINE COMPANY'S MCCOMB STATION. OLD HIGHWAY 51. MAGNOLIA, MS 39652. |  | PUMPING STATION | OTHER | UNKNOWN | 1978 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 80373.0147 | 162144.8346 | FUEL OIL | 3 | 55 | 51 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX - MANAGER-TECHNICAL & REGULATORY | 4048412296 | AT 8:00 AM. ON JUNE 22, 1991, A SENIOR OPERATOR, DURING A ROUTINE STATION CHECK, FOUND FUEL OIL IN THE GRAVEL ON THE STATION YARD AT COLONIAL'S MCCOMB PUMP STATION. THE MISSISSIPPI DEPARTMENT OF NATURAL RESOURCES WAS NOTIFIED AT 9:30 AM. AT 1:30 PM. ON JUNE 24, 191, IT WAS DETERMINED THAT THE PRODUCT WASLEAKING FROM A 1 1/2" DIAMETER BLOW DOWN LINE ON THE BOTTOM OF THE 30" AUXILIARY DISCHARGE VALVE OF THE PUMP STATION ON COLONIAL'S NO. 2 MAINLINE. EXAMINATION REVEALED THAT INTERNAL CORROSION HAD OCCURRED IN THE PIPING. THE DRAINLINE WAS EMPTIED, REMOVED, AND PERMANENTLY REPLACED WITH A WELD CAP ON JUNE 26, 1991. TO DATE 50.5 BARRELS OF FUEL OIL AND KEROSINE HAVE BEEN RECOVERED FROM THE STATION GROUNDS AND RETENTION POND. CLEAN-UP ACTIVITIES ARE CONTINUING.
2017-09-29 08:50 | YES | NO | 19910126 | 1991-07-26 | 22610 | WILLIAMS PIPELINE CO | YES | 1991-06-26 | 1215 | NE | OTOE | UNKNOWN | NO |  | NO | NW 1/4 SECTION 25 AND NE 1/4 SECTION 36, T9N, R13E, OTOE COUNTY, NE (#C241). |  | TANK FARM | OTHER | UNKNOWN | 1966 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 64500 | 51840.5945 | 104583.4183 | FUEL OIL | 1 | 170 | 134 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 275 | 30 | YES | 9 | 375 | 6 | 87 | INTERNAL | Null | YES | OTHER | INTERNAL PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - VICE PRESIDENT - OPERATIONS | 9185883850 | ON WEDNESDAY, JUNE 26, 15 12:15 PM., NEBRASKA CITY TERMINAL PERSONNEL DISCOVERED THAT APPROXIMATELY 170 BARRELS OF 32 FUEL OIL HAD LEAKED FROM A BURIED RECEIVE LINE. THE PRODUCT ENTERED THE LOCATION'S STORM WATER DRAIN SYSTEM ANDEXITED THE EAST END OF THE FACILITY. THE FUEL THEN FLOWED THROUGH A CULVERT UNDER RAILROAD TRACKS AND INTO A TRIBUTARY OF WALNUT CREEK. THE PRODUCT THENSPREAD OUT ALONG A ONE MILE STRETCH OF THE TRIBUTARY. NO PRODUCT ENTERED WALNUT CREEK. DAMS WERE ERECTED AT VARIOUS POINTS ALONG THE TRIBUTARY TO CONTAIN THE SPILL. AS PRODUCT ACCUMULATED AT THE DAM SITES, IT WAS VACUUMED AND RETURNED TO OUR NEBRASKA CITY FACILITY. TO AID IN THE RECOVERY, WATER WAS TRANSPORTED TO THE TRIBUTARY AND USED TO FLUSH PRODUCT DOWNSTREAM TO THE DAM SITES. THE REMAINING PRODUCT WAS COLLECTED WITH SORBENT PADS. OF THE 170 BARRELS RELEASED, 133.5 BARRELS OF FREE PRODUCT WERE RECOVERED. AT THE TERMINAL, APPROXIMATELY 500 CUBIC YARDS OF SOIL CONTAINING APPROXIMATELY 36.5 BARRELS OF OIL WAS CONTAMINATED. WPL PLANS TO EXCAVATE AND LAND FARM ALL CONTAMINATEDSOIL. ALL CLEAN UP ACTIVITY IS BEING COORDINATED WITH STATE ENVIRONMENTAL OFFICIALS. THE LINE WAS REPAIRED AND HYDROSTATICALLY TESTED PRIOR TO RETURNING IT TO SERVICE.
2017-09-29 08:50 | YES | NO | 19910127 | 1991-07-26 | 10012 | KANEB PIPELINE CO | YES | 1991-06-25 | 257 | KS | SEDGWICK | UNKNOWN | NO |  | NO | SOUTHEAST 1/4, SEC. 2T, TOWNSHIP 26 S, RANGE 1 EAST, INSIDE PHILLIPS PIPELINE TERMIANL PROPERTY LOCATED AT 2400 E. 37TH ST N., JUST OUTSIDE OF WICHITA CITY LIM. |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | GASOLINE | 2 | 5 | 1 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 679 | 163 | YES | 24 | 902 | 4 | 72 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | L. LEROY ANDERSON - MANAGER PURCHASING & REGULATORY AFFAIRS | 3162621408 | THIS IS THE SUPPLEMENTAL REPORT REQUIRED BY CFR TITLE 49 PART 195.54(2). TELEPHONIC NOTICE OF THIS INCIDENT WAS GIVEN THE NATIONAL RESPONSE CENTER AT 05:00 JUNE 25, 1991. EVEN THOUGH THIS INCIDENT DID NOT MEET ANY OF THE CRITERIA LISTED IN 195.50 OR 195.52, IT WAS DETERMINED THAT NOTIFICATION WAS IN ORDER BECAUSE OF THE CLOSE PROXIMITY TO THE CITY OF WICHITA. ALTHOUGH PROPANE WAS IN THIS LINE SECTION INITIALLY, IT WAS DISPLACED WITH GASOLINE SHORTLY AFTER THE LEAK WAS DISCOVERED. THE LOCATION OF THE LEAK WAS APPROXIMATELY 1/4 MILE FROM THE PHILLIPS PUMPING MANIFOLD, WHERE THE PROPANE WAS SHUT OFF AND THE GASOLINE DIVERTED TO THE LINE SECTION. OUR INVESTIGATION HAS DETERMINED THAT LESS THAN 5 BARRELS OF PROPANE OR 5 BARRELS OF GASOLINE ESCAPED THROUGH THE LEAK. IMMEDIATELY AFTER THE PROPANE WAS DISPLACED, EXCAVATION OF THE LEAK SITE BEGAN AND LESS THAN 5 GALLONS OF GASOLINE WAS RECOVERED DUE TO THE SMALLAMOUNT OF CONTAMINATION. A SMALL LOCALIZED CORROSION PIT WAS DISCOVERED AS THE CAUSE OF THE LEAK. ONE OTHER LOCALIZED PIT WAS ALSO FOUND AND REPAIRED.THERE WERE A NUMBER OF DISCARDED WELDING ROD BUTTS IN THE IMMEDIATE AREA OF THE PITS AND THEY ARE SUSPECTED AS THE CAUSE OF THE CORROSION. THE LINE WAS EXPOSED AND CHECKED 25 FEET MINIMUM EITHER SIDE OF THE LEAK AND IT WAS STILL IN "LIKE NEW" CONDITION AS PERSONNEL WERE ABLE TO READ THE ORIGINAL MILL STENCILS. THE LINE WAS REPAIRED AND PLACED BACK INTO OPERATION.
2017-09-29 08:50 | YES | NO | 19910128 | 1991-07-29 | 18718 | SUN PIPELINE CO | YES | 1991-06-24 | 1415 | PA | BERKS | UNKNOWN | NO |  | NO | SUN PIPELINE MONTELLO 600 TANK FARM, FRITZTOWN ROAD, NEAR SINKING SPRING, PA. |  | TANK FARM | WELDING FITTING |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 104484.9191 | 210788.285 | GASOLINE | 3 | 307 | 76 | NO | NO | 12 | 0.38 | 35000 | WELDED |  | 150 | 38 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | CHARLES W. DURRETT - MANAGER, RISK MANAGEMET | 9185866231 | A SUN PIPE LINE CONTRACTOR EMPLOYEE WAS OPERATING A WHEELED FRONT-END-LOADERTO BACKFILL A PREVIOUS EXCAVATION AT THE 600 TANK FARM MANIFOLD, WORKING IN A VERY TIGHT AND CONGESTED AREA. AFTER DUMPING SEVERAL LOADS INTO THE EXCAVATION, HE STATED HE WAS DISTRACTED BY A TRUCK AND BACKED INTO A 4" ABOVEGROUNDRISER WELDED TO THE 12" UNDERGROUND DISTRIBUTION LINE BETWEEN TANK #601 AND THE 600 FARM MANIFOLD SYSTEM. THE RISER BROKE LOOSE AT THE WELD LINE. THE 12" LINE WAS IN OPERATION, AND ALSO WAS PRESSURED AFTER THE PUMPS WERE SHUT DOWN BY 32.25 FT. OF PRODUCT IN TANK #601, UNITL THE TANK VALVE WAS CLOSED.
2017-09-29 08:50 | YES | NO | 19910129 | 1991-07-16 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1991-05-18 | 1400 | OK | CREEK | DRUMRIGHT | NO |  | NO | 3/4 MILE EAST OF STATE HIGHWAY 33 & 16 INTERSECTION - SOUTH INTO LOCATION (J. RICHARDS TANK FARM). |  | TANK FARM | OTHER | UNKNOWN | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL | OPERATOR ERROR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | CRUDE OIL | 1 | 1540 | 1530 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | OPERATOR UTILIZED INCORRECT TANK TABLE AND INCORRECT FLOW RATE TO CALCULATE AVAILABLE ROOM IN RECEIPT TANK.
2017-09-29 08:50 | YES | NO | 19910130 | 1991-07-16 | 443 | AMOCO PIPELINE CO | YES | 1991-05-07 | 900 | OK | JACKSON | UNKNOWN | NO |  | NO | NORTHWEST QUARTER, SECTION 4, TOWNSHIP 3 NORTH, RANGE 20 WEST. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1200 | 1200 | NO | NO | 16 | 0.25 | 42000 | WELDED |  | 945 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOHN W. CARICO, AREA MANAGER | 9182257271 | A JACKSON COUNTY ROAD COMMISSION MAINTAINER STRUCK ONE OF AMOCO PIPELINE'S 16" CRUDE LINES WHILE CLEANING OUT A DITCH. OIL BEGAN SPRAYING INTO THE AIR, CARRIED BY MODERATE WINDS. THE COMMISSION OFFICE WAS RADIOED, WHICH CONTACTEDTHE CONTROL CENTER. AFTER SHUTTING DOWN THE LINE SEGMENT, RESPONSE PERSONNEL WERE DISPATCHED TO EFFECT CONTAINMENT AND CLEAN UP. THE COUNTY ASSISTED COMPANY AND CONTRACT CREWS TO PREVENT THE SPILLED OIL FROM REACHING ANY WATERWAY. IN ADDITION TO THE NATIONAL RESPONSE CENTER, NOTIFICATION WAS ALSO MADE TOOKLAHOMA STATE POLLUTION CONTROL, OKLAHOMA STATE CORPORATION COMMISSION AND THE DEPARTMENT OF TRANSPORTATION, OFFICE OF PIPELINE SAFETY IN HOUSTON.
2017-09-29 08:50 | YES | NO | 19910131 | 1991-07-25 | 2731 | CHEVRON PIPELINE CO | YES | 1991-06-27 | 1545 | UT | SUMMIT | UNKNOWN | NO |  | NO | RELEASE IS NORTH OF HWY US-189, EAST OF ABANDONED UNION PACIFIC RAILROAD SPUR TO PARK CITY. |  | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 57750 | 46415.416 | 93638.642 | CRUDE OIL | 1 | 3000 | 2800 | NO | NO | 10.75 | 0.25 | 35000 | WELDED |  | 1165 | 575 | YES | 8 | 1455 | 9 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOHN R. MOON - SALT LAKE AREA SUPERVISOR | 8015397293 | THE PROPERTY OWNER WAS CLEARING BRUSH FOR A NEW FENCE LINE. THE BULLDOZER USED FOR THE BRUSH CLEARING PUNCTURED THE PIPELINE. THE CRUDE OIL RAN DOWN A HILLSIDE AND INTO A SMALL STREAM OF WATER. THE WATER CARRIED THE OIL FOR ABOUT 2 MILES BEFORE CHEVRON PIPE LINE COMPANY PERSONNEL WERE ABLE TO CONTAIN THE
2017-09-29 08:50 | NO | NO | 19910132 | 1991-08-02 | 13131 | CONOCO INC | YES | 1991-07-14 | 1900 | WY | PARK | UNKNOWN | NO |  | NO | N/E 1/4, NE 1/4, S36, T58N, R98W. |  | PUMPING STATION | OTHER | NIPPLE FAILED ON DISCHARG | 1984 | OTHER | METAL FATIGUE (VIBRATION) | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | CRUDE OIL | 1 | 15 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SWIGHT D. JACKSON - MANAGER OPERATIONS ENGINEERING | 7132932130 | A 1/2" X 2" SCHEDULE 80 SCREWED NIPPLE WITH A 1/2" SCREWED GATE VALVE AND PRESSURE GAUGE FAILED RESULTING IN A CRACKED NIPPLE. THIS NIPPLE WAS LOCATED ON THE DOWNSTREAM SIDE OF VALVE #12 WHICH IS THE DISCHARGE VALVE OF UNIT ONE AT FRANNIE STATION.
2017-09-29 08:50 | YES | NO | 19910133 | 1991-08-09 | 18273 | SHELL PIPELINE CORP | NO | 1991-07-18 | 800 | TX | CRANE | CRANE | NO | N/A | NO | SE 1/4, NW 1/4, SECTION 12, BLOCK 27 HENDRICK-BARNSLEY NO.1 - 6-INCH. |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 723.3571 | 1459.3035 | CRUDE OIL | 1 | 55 | 35 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 800 | 250 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19910134 | 1991-08-09 | 18273 | SHELL PIPELINE CORP | NO | 1991-07-16 | 930 | TX | CRANE | CRANE | NO | N/A | NO | NW 1/4, NW 1/4, SECTION 42, BLOCK 32 FOURTEEN MILES WEST OF CRANE BARNSLEY STATION (DISCHARGE UNIT) |  | PUMPING STATION | VALVE |  | 1927 | OTHER | VALVE OPEN RELEASE OIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4900 | 3938.2777 | 7945.0969 | CRUDE OIL | 1 | 800 | 730 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19910135 | 1991-08-05 | 18273 | SHELL PIPELINE CORP | NO | 1991-07-01 | 1620 | TX | MENARD | FORT MCKAVETT | NO | N/A | NO | SE 1/4, SE 1/4, SECTION 7, BLOCK 16 TEN MILES SOUTH OF FT. MCKAVETT ON HIGHWAY 1674 RANCHO 24-INCH PIPELINE |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16074.6029 | 32428.9669 | CRUDE OIL | 1 | 400 | 215 | NO | NO | 24 | 0.31 | 52000 | WELDED |  | 910 | 485 | YES | 12 | 1050 |  | 52 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | OUTSIDE COMPANY HIT OUR PIPELINE WHILE USING AN AUGER TO DRILL HOLES TO SET 'H' BRACES IN FENCE LINE.
2017-09-29 08:50 | YES | NO | 19910136 | 1991-08-05 | 18273 | SHELL PIPELINE CORP | NO | 1991-07-01 | 1712 | TX | YOAKUM | DENVER CITY | NO | N/A | NO | SW 1/4, SE 1/4, SECTION 826, BLOCK D TWO MILES NORTH OF DENVER CITY ON HIGHWAY 214 WASSON STATION. |  | TANK FARM | TANK |  | 1939 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2411.1904 | 4864.345 | CRUDE OIL | 1 | 55 | 50 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | TRANSFER PUMP FAILED TO OPERATE CAUSING TANK TO OVERFLOW. RELAY PROBLEM IN PUMP'S CONTROL PANEL WAS CORRECTED.
2017-09-29 08:50 | NO | NO | 19910137 | 1991-08-05 | 2552 | COLONIAL PIPELINE CO | YES | 1991-07-04 | 930 | SC | ANDERSON | BELTON | NO | N/A | NO | COLONIAL PIPELINE COMPANY'S BELTON JUNCTION 1916 CAMELOT FOREST BELTON, S.C. 29627. |  | TANK FARM | TANK |  | 1963 | OTHER | CORROSION, INTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 13663.4125 | 27564.6219 | GASOLINE | 3 | 30 | 15 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | NO | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER TECHNICAL & REGULATORY | 4048412296 | WHILE MAKING AN INSPECTION OF COLONIAL'S BELTON JUNCTION TANK FARM AT APPROXIMATELY 9:30 AM., EASTERN STANDARD TIME, ON JULY 4, 1991, AN OPERATOR SMELLEDGASOLINE. AN INVESTIGATION REVEALED PRODUCT IN THE DIKE CONTAINING TANK 515. THE SOURCE OF THE LEAK WAS THEN DETERMINED TO BE A FAILED ROOF DRAIN ON ADJACENT TANK 531. UNDER NORMAL CIRCUMSTANCES, THE DIKE DRAIN AT TANK 531 IS OPEN TO THE DIKE OF TANK 515. A ROOF DRAIN VALVE WAS CLOSED TO STOP THE LEAK,AND THE DIKE DRAIN VALVE WAS CLOSED TO CONTAIN THE PRODUCT. ONCE IT WAS DETERMINED THAT THE ROOF DRAIN WAS THE SOURCE OF THE LEAK, IT BECAME APPARENT THAT THE COST OF THE ACCIDENT WOULD EXCEED $5000.00, AND THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 12:02 PM. ON THE SAME DAY, REPORT NUMBER 78034. THE AREAS WITHIN THE DIKES WERE FILLED WITH WATER TO PREVENT THE SOIL'S ABSORPTIONOF GASOLINE. APPROXIMATELY 30 BARRELS OF PRODUCT ESCAPED, AND 15 BARRELS WERE RECOVERED. EXAMINATION OF THE ROOF DRAIN REVEALED THAT CORROSION WAS THE CAUSE OF FAILURE.
2017-09-29 08:50 | YES | NO | 19910138 | 1991-08-16 | 2552 | COLONIAL PIPELINE CO | YES | 1991-07-15 | 1545 | NJ | GLOUCESTER | WEST DEPTFORD TOWNSHIP | NO | N/A | NO | COLONIAL PIPELINE COMPANY'S WOODBURY JUNCTION MANTUA GROVE ROAD, WOODBURY, NJ 08096. |  | TANK FARM | WELDING FITTING |  | 1964 | OTHER | CORROSION, INTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 64298.4118 | 129715.8677 | GASOLINE | 3 | 8 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MANAGER TECHNICAL & REGULATORY | 4048412296
2017-09-29 08:50 | NO | NO | 19910139 | 1991-08-19 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1991-08-05 | 750 | AR | CALHOUN | UNKNOWN | NO | N/A | NO | SECTION 10 T15S R13W CALHOUN COUNTY BLOCK VAVLE 3-6. |  | LINE PIPE | VALVE |  | 1969 | OTHER | FAULTY CAST ON CHECK VALV | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 401.8651 | 810.7242 | ANHYDROUS AMMONIA | 2 | 2 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH D. COLLINS, GOVERNMENT REGULATIONS COORDINATOR | 3144865488 | ON JULY 15, 1991, AT 3:45 PM. EDT THE OPERATOR AT WOODBURY JUNCTION IN WEST DEPTFORD TOWNSHIP, NEW JERSEY, DETECTED GASOLINE IN THE DELIVERY FACILITY YARD NEAR THE INCOMING STRAINER. AT 5:20 PM. EDT ON JULY 15, THE NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION WAS NOTIFIED. EXCAVATION AT THE STRAINERREVEALED A LEAK IN A 24" BOLTED FLANGE CONNECTION ON THE DISCHARGE HEADER OFTHE INCOMING STRAINER PIPING. THE BOLTS IN THIS FLANGE WERE TIGHTENED AND THE HEADER WAS PRESSURED WITH PRODUCT AND OBSERVED TO ENSURE THAT THE REPAIR WAS SECESSFUL. AS A PRECAUTIONARY MEASURE TO ENSURE THAT NO OTHER LEAKS EXISTED, EXCAVATION AND INSPECTION CONTINUED. ON JULY 17, 1991, A SECOND LEAK WASDISCOVERED IN A 1", 90 DEGREE THREADED ELBOW ON THE CONTROL VALVE DRAIN PIPING. THIS SECOND LEAK WAS A RESULT OF INTERNAL CORROSION. AFTER REVIEW BY COLONIAL'S ENVIRONMENTAL PERSONNEL, IT WAS DETERMINED THAT THE COST OF EXCAVATION, SOIL DISPOSAL AND REPAIR WOULD EXCEED $5,000.00, AND AT 9:20 AM. EDT ON JULY 19, 1991, THE NATIONAL RESPONSE CENTER WAS NOTIFIED OF THE LEAK, REPORT NUMBER 80079. APPROXIMATELY 8 BARRELS OF GASOLINE WAS RELEASED. TO DATE, 5 BARRELS HAVE BEEN RECOVERED; THE REMAINING 3 BARRELS WERE LOST TO EVAPORATION AND ABSORPTION.
2017-09-29 08:50 | NO | NO | 19910140 | 1991-08-09 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1991-07-16 | 1750 | IA | KOSSUTH | UNKNOWN | NO | N/A | NO | SECTION 26 T90N R30W KOSSUTH COUNTY, IA. |  | LINE PIPE | GIRTH |  | 1970 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3214.9206 | 6485.7934 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 8 | 0.2 | 42000 | WELDED |  | 1420 | 358 | YES | 24 | 1969 |  | 70 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH D. COLLINS, GOVERNMENT REGULATIONS COORDINATOR | 3144865488 | PIPELINER WAS DRIVING ALONG RIGHT-OF-WAY AND NOTICED DEAD SPOT IN FARMER'S BEAN FIELD. LEAK SITE WAS EXCAVATED AND A SMALL PIN-HOLE WAS DISCOVERED IN THE GIRTH WELD. WELD WAS REPAIRED USING FULL-ENCIRCLEMENT SLEEVE. REPAIR WAS X-RAYED AND PLACED BACK IN SERVICE. THERE WERE NO INJURIES, NO EVACUATION, NO CONTAMINATION OF WATERWAYS, AND ONLY SLIGHT PERSONAL PROPERTY DAMAGE TO CROPS. NATIONAL RESPONSE CENTER REPORT NUMBER: 79702. ALSO REPORTED TO IOWA DEPARTMENT OF NATURAL RESOURCES, REFERENCE NUMBER 07161WPW.
2017-09-29 08:50 | YES | NO | 19910141 | 1991-08-05 | 15681 | PLATTE PIPE LINE CO | YES | 1991-07-02 | 1400 | MO | CHARITON | UNKNOWN | NO | N/A | NO | SALISBURY STATION, SECTION 8 T53H R17W CHARLTON COUNTY, MO. |  | TANK FARM | PIPE |  | 1953 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 60279.761 | 121608.626 | CRUDE OIL | 1 | 200 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.B. LARSEN - VICE PRESIDENT | 4194212802 | INTERNAL CORROSION CAUSED A PINHOLE TO FORM ON THE 26" UNDERGROUND TANK LINETO TANK 803. AN ESTIMATED 200 BBLS OF CRUDE OIL WERE RELEASED. STATION TANK LINES WERE EXCAVATED TO THE EXTENT NECESSARY TO LOCATE AND REPAIR THE LEAK.REPAIR WAS AFFECTED BY WELDING AN 18" X 24" PATCH TO THE LINE. FREE OIL WASRECOVERED TO THE EXTENT FEASIBLE. WE ARE WORKING WITH THE MISSOURI DNR TO DETERMINE THE FINAL DISPOSITION OF THE CONTAMINATED SOIL.
2017-09-29 08:50 | YES | NO | 19910142 | 1991-08-05 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1991-07-09 | 2000 | OK | CREEK | DRUMRIGHT | NO | N/A | NO | FROMTHE INTERSECTION OF HWY. 33 AND HWY. 99 IN DRUMRIGHT, OK. 3/4 MILES EAST AND THEN SOUTH INTO LOCATION (J. RICHARDS TANK FARM). |  | TANK FARM | TANK |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2009.3254 | 4053.6209 | CRUDE OIL | 1 | 1300 | 1285 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | OVERFLOW OF TANK 250 WAS DUE TO GAUGER INCORRECTLY CALCULATING AVAILABLE ROOM IN TANK.
2017-09-29 08:50 | YES | NO | 19910143 | 1991-08-08 | 7349 | HOECHST CELANESE CHEMICAL GROUP INC | NO | 1991-07-11 | 300 | TX | CARSON | BORGER | NO | N/A | NO | I & GN RR SURVEY BLOCK 4 SECTION 120 CARSON COUNTY, TEXAS. |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 24220 | 19466.3442 | 39271.4789 | NATURAL GAS LIQUID | 2 | 1500 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 650 | 500 | YES | 24 | 1100 | 2 | 66 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DANIEL A. LONG - STAFF ENGINEER | 8066651801 | AERIAL SURVEY FLOWN EVERY WEEK. PIPELINE WAS INSPECTED 1 DAY PRIOR TO ACCIDENT. PIPELINE SIGNS WERE IN PLACE WITHIN 60 YRDS & 110 YRDS OF EACH SIDE OF ACCIDENT LOCATION. OUR 6" PIPELINE WAS STRUCK BY A BULLDOZER OPERATED BY HAINING DOZER SERVICE OF BORGER, TEXAS. THE DOZER WAS STOCK PILING CALICHE IN A PIT NEAR OUR LINE. HOECHST CELANESE PERSONNEL FOLLOWED THE EMERGENCY PLAN TOBLOCK IN VALVES AND REPORT TO SITE. LINE WAS DEPRESSURED AND REPAIRED. NO FIRES, EXPLOSIONS, OR INJURIES OCCURRED.
2017-09-29 08:50 | YES | NO | 19910144 | 1991-08-08 | 10313 | KOCH PIPELINE INC | YES | 1991-06-29 | 1640 | WI | PORTAGE | UNKNOWN | NO | N/A | NO | NE SE 1/4 SEC. 22, T24N, R7E, 1/4 MILE NORTH OF COUNTY ROAD "M" NEAR MP 175, CARSON TOWNSHIP, PORTAGE COUNTY, WISCONSIN. |  | LINE PIPE | PIPE |  | 1988 | OTHER | SENDING PIPE FOR TESTING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 160746.0294 | 324289.6692 | GASOLINE | 3 | 1291 | 979 | NO | NO | 10 | 0.19 | 2256 | WELDED |  | 1440 | 1085 | YES | 24 | 2050 | 8 | 88 | NO DATA | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JEROME H. KLEIN - DIVISION MANAGER |  | THE LEAK WAS CONFIRMED AT 4:40 PM. JUNE 29, 1991. IT OCCURRED ON THE RAYMOND RAMCHECK PROPERTY, APPROXIMATELY 6 MILES SOUTHEAST OF OUR JUNCTION CITY TERMINAL.
2017-09-29 08:50 | YES | NO | 19910145 | 1991-08-21 | 15490 | PHILLIPS PIPE LINE CO | YES | 1991-07-09 | 1705 | TX | AUSTIN | UNKNOWN | NO | N/A | NO | BENEDUM-SWEENY LINE-MP 353-42+73, BLOCK A-299, S. SWEARINGER SURVEY, AUSTIN CO. 4 MI W OF INTERS. OF FM 1094 AND FM 949 ON FM 1094 AND THEN 1 3/4 MI N ON FM1094 |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 38000 | 30541.7456 | 61615.0372 | NATURAL GAS LIQUID | 2 | 600 | 0 | NO | NO | 10.77 | 0.28 | 50000 | WELDED |  | 1100 | 554 | YES | 24 | 1535 | 10 | 78 | EXTERNAL | Null | YES | OTHER | LOCALIZED PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | EXTERNAL PITTING ON THE PIPELINE RESULTED IN ALEAK THAT WAS REPORTED BY A LINE FLYER.
2017-09-29 08:50 | YES | NO | 19910146 | 1991-08-15 | 2731 | CHEVRON PIPELINE CO | YES | 1991-07-27 | 1400 | TX | MIDLAND | MIDLAND | NO | N/A | NO | 3400 E. HWY 80, MIDLAND LPG STATION, SEC: 41; BLK: 38, SURVEY: T&P. |  | PUMPING STATION | OTHER | MECHANICAL PUMP SEAL | 1990 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | MECHANICAL PUMP SEAL | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 35 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.D. DIMMITT - COMPLIANCE COORDINATOR | 9156877559 | A POWER FAILURE CAUSED BY A LIGHTNING STORM SHUT DOWN ALL OF THE PUMPING UNITS. THE LPG UNIT WULD NOT RE-START AND WHEN THE OPERATOR CHECKED THE UNIT, HE FOUND THAT THE OUTBOARD PUMP SEAL HAD FAILED AND LPG WAS LEAKING.
2017-09-29 08:50 | YES | NO | 19910147 | 1991-08-19 | 2371 | CINIZA PIPELINE INC | NO | 1991-08-05 | 809 | NM | SANDOVAL | UNKNOWN | NO | N/A | NO | ON PIPELINE RIGHT-OF-WAY 1 1/2 MI. SOUTH OF LYBROOK, NEW MEXICO. SEC. 23, T23N, R7W SANDOVAL COUNTY, NEW MEXICO. |  | LINE PIPE | OTHER | UNKNOWN | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 11137 | 8951.1426 | 18058.0702 | CRUDE OIL | 3 | 323 | 126 | NO | NO | 4 | 0.16 | 1760 | WELDED |  | 620 | 540 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AIR PATROL | Null | Null | ROBERT ULLO - GENERAL MANAGER OF PIPELINE OPERATIONS | 5056328006 | 4" LINE RUPTURE WAS DUE TO PREVIOUS DAMAGE CAUSED BY EQUIPMENT. IT ISUNKNOWN WHEN THE PIPE WAS DAMAGED. SUPPLEMENTAL REPORT 10/13/94 CHANGED CAUSEOF ACCIDENT FROM "OTHER" TO "OUTSIDE FORCE DAMAGE".
2017-09-29 08:50 | YES | NO | 19910148 | 1991-08-19 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1991-07-30 | 1720 | TX | JEFFERSON | BEAUMONT | NO | N/A | NO | APPRX 3 MI. SE OF BEAUMONT (TX) CITY-LMT AND 3 1/2 MI. SE OF HWY 69/96 & W. PT. ARTHUR RD. INTERS. AND APPROX. 3,536' E. OF W. PT. ARTHUR RD., ON TX. |  | LINE PIPE | PIPE |  | 1929 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | CRUDE OIL | 1 | 80 | 60 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1050 | 200 | YES | 8 | 1329 | 3 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | BOB REED, REGULATORY COMPLIANCE SUPV. | 9152645414 | DAMAGE WAS CAUSED BY EQPT. (BULLDOZER) OWNED/OPERATED BY WEIR EXCAVATING, WHILE IN THE (APPARENT) PROCESS OF SITE PREPARATION (CLEARING) FOR NEW TDC PRISON. WEIR EXCAVATING IS OWNED BY, AND IS AN AFFILIATE COMPANY OF, ENVIRO CONTRACTORS, INC (ECI) OF BEAUMONT. APPARENTLY, THE PRIME CONTRACTOR ON-SITE WASMANHATTAN CONST., WHO HAD NOTIFIED THE TESS (ONE-CALL) CENTER ON 7/29. INFORMATION AS TO THIS CONTACT HAD BEEN PASSED ON TO FINA REPRESENTATIVE IN AREA DURING THE DAY. FINA'S REPRESENTATIVE HAD MADE CONTACT WITH MANHATTAN EARLY THE NEXT DAY, 7/30, AND ADVISED THEM THAT NO WORK WAS TO BE DONE UNTIL HE WASON SITE. THE WORK FOR WHICH MANHATTAN HAD MADE THE ONE-CALL NOTIFICATION WAS "BUILDING A ROAD" THE WORK IN WHICH THE BULLDOZER WAS ENGAGED WHEN THE PIPELINE WAS HIT WAS: (1) NOT APPARENTLY RELATED TO ROAD WORK, AND (2) WAS NOT WITHIN THE AREA IDENTIFIED IN THE NOTIFICATION. IT APPEARS THAT THERE WAS A COMMUNICATION BREAKDOWN WITHIN THE CONTRACTOR/SUB-CONTRACTOR RELATIONSHIP. THEBULLDOZER OEPRATOR STRUCK THE PIPELINE WHILE APPARENTLY DIGGING A DITCH, EVEN THOUGH A PROMINENT SIGN ANDMARKER POST WAS ONLY ABOUT 15' FROM THE SITE ANDSTAKES MARKING THE PIPELINE ROUTE (POSSIBLY INSTALLED BY ONE OF THE CONTRATORS) WERE IN EVIDENCE. FINA RECEIVED NOTICE OF THE RUPTURE WITHIN APPROXIMATELY 23 MINUTES OF THE OCCURRENCE OF THE ACCIDENT. THE OIL FLOWED FROM THE PIPELINE INTO A NEARBY DEPRESSION INTHE SOIL.
2017-09-29 08:50 | YES | NO | 19910149 | 1991-09-17 | 19226 | TEXACO PIPELINE INC | NO | 1991-08-02 | 904 | TX |  | MCCLENNAN | NO | N/A | NO | 2559' SOUTH OF HWY 2114, APM 74.5 LOCATED ON NORTH SIDE OF HWY APPROXIMATELY 1.9 MILES EAST OF WEST, TEXAS. |  | LINE PIPE | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | DIESEL FUEL | 3 | 2401 | 200 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1050 | 900 | YES | 24 | 1000 |  | 48 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. MINER, DISTRICT MANAGER | 7139534260 | WHILE PUMPIING FROM HEARNE TO DALLAS UNDER NORMAL OPERATING CONDITIONS, AT 9:04 AM THE WACO BOOSTER STATION LOW SUCTION ALARM ENERGIZED ALERTING THE DENVER CONTROLLER. THE CONTROLLER IMMEDIATELY SHUT DOWN THE MAIN LINE AT 9:05 AM. MAIN LINE BLOCK VALVES WERE CLOSED AT ALL LOCATIONS. AIR PATROL WAS CONTACTED AT 9:45 AM AND ROUTED TO SUSPECT AREA. COMPANY PERSONNEL AND CONTRACT CREW WERE DISPATCHED TO THE SCENE AT 10:00 AM. LINE FLYER LOCATED LEAK AT MP 74.5 AT 12:45 PM. LINE WAS UNCOVERED AND REPAIRED BY REPLACING 55'8" OF PIPE. THE PIPE REPLACED CONTAINED A SECTION OF SPLIT SEAM APPROXIMATELY 31" LONG, THE SPLIT ORIGINATING FROM AN AREA OF EXTERNAL CORROSION. PERMANENT REPAIRS WERE COMPLETED AND THE LINE WAS RESTARTED AT 2:45 PM ON AUGUST 3, 1991.
2017-09-29 08:50 | NO | NO | 19910150 | 1991-09-17 | 2552 | COLONIAL PIPELINE CO | YES | 1991-08-14 | 830 | SC | SPARTANBURG |  | NO | N/A | NO | COLONIAL PIPELINE COMPANY'S SPARTANBURG DELIVERY FACILITY CAMP CROFT, 180 KELTNER ROAD SPARTANBURG, SC 29301. |  | TANK FARM | TANK | TANK ROOF DRAIN | 1976 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 14467.1426 | 29186.0702 | GASOLINE | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | NO | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX - MANAGER TECHNICAL & REGULATORY | 4048412296 | WHILE MAKING A ROUTINE INSPECTION OF COLONIAL'S SPARTANBURG DELIVERY TANK FARM ON AUGUST 14, 1991, AN OPERATOR NOTICED A GASOLINE ODOR IN THE VICINITY OFTANK 613. AT 8:30 AM., EST, AFTER A THOROUGH INVESTIGATION, IT WAS DETERMINED THAT APPROXIMATELY 1/2 BARREL OF GASOLINE HAD ESCAPED FROM A FAULTY ROOF DRAIN. ONCE IT WAS DETERMINED THAT THE COST OF THE CLEAN UP AND REPAIRS TO THE ROOF DRAIN WOULD EXCEED $5000.00, THE NATIONAL RESPONSE CENTER WAS NOTIFIEDAT 9:50 AM., EST, ON AUGUST 14 (REPORT NUMBER 83748). THE SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL (SCDHEC) AND THE LOCAL DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL OFFICE WERE ALSO NOTIFIED OF THE LEAK.BECAUSE OF THE SMALL AMOUNT INVOLVED, NONE OF THE SPILLED GASOLINE COULD BE RECOVERED. THE AFFECTED SOIL AND GRAVEL IS BEING EXCAVATED FOR REMEDIATION. EXAMINATION OF THE ROOF DRAIN REVEALED THAT CORROSION WAS THE CAUSE OF THE FAILURE.
2017-09-29 08:50 | YES | NO | 19910151 | 1991-09-11 | 15674 | PLANTATION PIPE LINE CO | YES | 1991-08-08 | 850 | TN | BRADLEY | COLLEGEDALE | NO | N/A | NO | 650 FEET NORTHEAST OF PINE HILL ROAD. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 42000 | 33756.6662 | 68100.8305 | DIESEL FUEL | 3 | 367 | 63 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1480 | 600 | YES | 13 | 2107 | 5 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ROY M. CROOK - VICE PRESIDENT-OPERATIONS | 4043645916 | PLANTATION OWNS AND OPERATES AN 8-INCH DIAMETER PIPELINE WHICH CARRIES REFINED PETROLEUM PRODUCTS FROM BREMEN, GEORGIA TO KNOXVILLE, TENNESSEE. ON AUGUST 8, 1991, AT APPROXIMATELY 0850 EDST, THE VULCAN MATERIALS COMPANY PUNCTUREDTHE LINE WITH A 6-INCH DIAMETER ROCK BIT WHILE DRILLING IN A SPARSELY POPULATED AREA TO DETERMINE THE EXTENT OF A LIMESTONE VEIN FOR A POTENTIAL QUARRY LOCATION. THE DRILL STRUCK AND PUNCTURED THE PIPELINE WHICH WAS THREE FEET BELOW GRADE. DIESEL FUEL WAS BEING TRANSPORTED IN THE PIPELINE AT THE TIME OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19910152 | 1991-09-04 | 2731 | CHEVRON PIPELINE CO | YES | 1991-07-25 | 1015 | TX | POLK | ONALASKA | NO | N/A | NO | SEE ATTACHED COUNTY MAP. |  | PUMPING STATION | PIPE |  | 1952 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 300 | 285 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.E. SMITH - DIVISION MANAGER | 4098393103 | INTERNAL CORROSION OF 4 INCH INCOMING STRAINER DISHCARGE LINE.
2017-09-29 08:50 | YES | NO | 19910153 | 1991-09-12 | 2731 | CHEVRON PIPELINE CO | YES | 1991-08-29 | 848 | TX | NOLAN |  | NO | N/A | NO | 8 MILES EAST OF SWEETWATER, TEXAS AND 1 MILE SOUTH OF I-20 ON THE H.E. GRAHAM RANCH. |  | LINE PIPE | PIPE |  | 1945 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 5840 | 0 | NO | NO | 10.75 | 0.37 | 35000 | WELDED |  | 704 | 700 | YES | 24 | 1250 | 9 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | UNKNOWN | NO | NO | W.M. (MAC) GILLILAND | 9156877560 | CONTRACTOR EQUIPMENT OPERATOR, REGGIE PEARL, OPERATING A BULLDOZER FOR THREE-WAY CONSTRUCTION COMPANY, WAS RE-BUILDING A WATER BREAK AND WAS BACK-DRAGGING DURING THE CLEAN UP PROCESS ON A CHEVRON CONSTRUCTION PROJECT WHEN THE #1-10" LPG PIPELINE WAS HIT AND RUPTURED. ROGER ROBERTS, CPL INSPECTOR, WAS APPROXIMATELY 500' WEST OF SITE ON CPL PIPELINE RIGHT-OF-WAY AND REPORTED THE MISHAP IMMEDIATELY. EDDIE PEAR, BROTHER OF REGGIE, ALSO AN EQUIPMENT OPERATOR, AND THEIR HELPER, MONTY HALL, WERE APPROXIMATELY 300' EAST OF RUPTURE SITE. REGGIE PEARL JUMPED FROM BULLDOZER WHEN RUPTURE OCCURRED AND RAN SOUTH. REGGIE PEARL STATED THAT THE BACK OF THE DOZER BLADE PROBABLY HIT AND RUPTURED THE PIPELINE WHEN THE DOZER SHIFTED AND BROKE OVER A RISE ON THE ROW DURING THEBACK-DRAGGING CLEAN-UP PROCESS.
2017-09-29 08:50 | YES | NO | 19910154 | 1991-09-13 | 22610 | WILLIAMS PIPELINE CO | YES | 1991-08-11 | 2100 | KS | WYANDOTTE | KANSAS CITY | NO | N/A | NO | KANSAS CITY STATION (B550), 401 EAST DONOVAN ROAD, KANSAS CITY, KANSAS NW 1/4 OF SECTION 35, TOWNSHIP 10 SOUTH, RANGE 25 EAST. |  | PUMPING STATION | VALVE |  | 1950 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3214.9206 | 6485.7934 | GASOLINE | 1 | 1 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - VICE PRESIDENT OPERATIONS | 9185883850 | AT APRPOXIMATELY 2100 HOURS ON 8/11/91, THE CONTROL VALVE ON THE #7 MAINLINEPUMPING UNIT DEVELOPED A LEAK. THE LEAKING PRODUCT IGNITED AND CAUGHT FIRE.THE INVESTIGATION POINTS TO THE FAILURE OF THE CONNECTING LINKAGE BETWEEN THECONTROL VALVE SHAFT AND THE CONTROL VALVE ACTUATOR SHAFT. IT IS BELIEVEDTHAT THE LINKAGE PIN FAILED ALLOWING THE CONTROL VALVE SHAFT TO BEGIN TOSPIN. THIS MOTION CAUSED THE VALVE PACKING TO FAIL ALLOWING PRODUCT TO ESCAPEFROM THE VALVE. THE SPINNING CONTROL VALVE SHAFT DEVELOPED FRICTION BETWEENTHE SHAFT AND THE SPLIT NUT COUPLER. IT IS BELIEVED THAT THIS FRICTIONHEATED THE SHAFT AND COUPLER TO THE POINT THAT THE LEAKING PRODUCT IGNITED.THE OPERATORS ON DUTY NOTICED AN ABNORMAL NOISE AND WERE INVESTIGATING THESOURCE WHEN THEY SAW THE FLAME. SIMULTANEOUSLY, THE STATION FIRE ALARMSACTUATED SHUTTING DOWN ALL UNITS AND PROVIDING AN AUDIBLE ALARM. THEOPERATORS ASSESSED THE SITUATION AND UTILIZED THE STATION FIRE EXTINGUISHERSTO PUT OUT THE FIRE. DAMAGE FROM THE ACCIDENT WAS LIMITED TO THE CONTROLVALVE SHAFT AND LINKAGE WHICH WAS CAUSED BY THE KINETICS OF THE CONTROL VALVESHAFT AT THE TIME OF FAILURE. SUPPLEMENTAL REPORT 9/26/94 INDICATES A CHANGEIN PART D/CAUSE OF ACCIDENT, FROM "OTHER - FAILED PIN IN VALVE SHAFT" TO"MALFUNCTION OF CONTROL/RELIEF EQUIPMENT." AN ERROR IN CITY NAME WAS ALSONOTED AND CHANGED 1/17/95.
2017-09-29 08:50 | YES | NO | 19910155 | 1991-09-12 | 13131 | CONOCO INC | YES | 1991-08-15 | 1630 | OK | GARFIELD | UNKNOWN | NO | N/A | NO | FROM ENID, EAST ON HWY 15/64, 4 MILES. NORTH 1/2 MILE ON WEST SIDE OF ROAD. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | L. P. G. | 2 | 732 | 0 | NO | NO | 4 | 0.13 | 42000 | WELDED |  | 1152 | 230 | YES | 8 | 1440 |  | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | LARY CLYNCH - DIVISION MANAGER | 4057676352 | ON AUGUST 9, 1991 AN INITIAL ONE CALL NOTIFICATION WAS MADE BY C & F PIPELINESERVICES (LOCATE REQUEST NUMBER 91080910240287). CONOCO PIPELINE (CPL) RESPONDED TO THE REQUEST AND MET WITH C & F REPRESENTATIVES AT THE REPORTED CONSTRUCTION LOCATION ON AUGUST 12, 1991. AT THAT TIME C & F INFORMED CPL OF THEIR INTENTION TO CROSS THE HENNESSEY 4" PBC LINE WITH A 3" PLASTIC LINE BEING LAID FOR MUSTANG FUEL. CPL HAD NO OBJECTION TO THIS CROSSING, BUT REQUESTED THAT A CONOCO REPRESENTATIVE BE PRESENT DURING EXCAVATION AROUND THE CPL 4". THE LINE WAS THEN MARKED AND C & F AGREED TO NOTIFY CPL WHEN THEY WERE READY TO CROSS THE 4" LINE. ON AUGUST 15, 1991 C & F PIPELINE SERVICES ATTEMPTED TOEXCAVATE ACROSS THE CONONCO 4" LINE WITHOUT CONTACTING CPL. THIS ACTION RESULTED IN DAMAGE TO THE 4" PBC LINE RELEASING PRODUCT INTO THE ATMOSPHERE.
2017-09-29 08:50 | YES | NO | 19910156 | 1991-09-30 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1991-08-30 | 5 | CA | LOS ANGELES | UNKNOWN | NO | N/A | NO | GLENOAKS AND COHASSET BOULEVARD |  | PUMPING STATION | OTHER | 3/4" INSTR. LINE REMOVED | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 52242.4596 | 105394.1425 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | EILEEN THIASKE - VICE PRESIDENT | 2134289300 | THE LEAK OCCURRED AT A PINHOLE IN A 3/4" PRESSURE RECORDER LINE DOWNSTREAM OF A VALVE. THE PRESSURE RECORDER WAS NOT AN ACTIVE APPURTENANCE AND WAS REMOVED IN 1979. THE PINHOLE WAS CAUSED BY INTERNAL CORROSION, AND THE LINE LEAKED BECAUSE THE VALVE WAS NOT CLOSED.
2017-09-29 08:50 | YES | NO | 19910157 | 1991-09-30 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1991-08-30 | 1346 | CA | UNKNOWN | BEAUMONT | NO | N/A | NO | NEAR 4TH STREET IN BEAUMONT, CA. |  | LINE PIPE | PIPE |  | 1957 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4000000 | 3214920.5887 | 6485793.3848 | CRUDE OIL | 1 | 4200 | 3600 | NO | NO | 16 | 0.25 | 0 | WELDED |  | 1170 | 800 | YES | 24 | 1495 | 9 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | EILEEN THIASHE - VICE PRESIDENT | 2134289300 | A THIRD PARTY ROAD GRATER, GRADING AN UNUSED ROAD DUG HIS BLADE INTO THE PIP
2017-09-29 08:50 | YES | NO | 19910158 | 1991-09-25 | 1682 | BP OIL PIPELINE CO | NO | 1991-08-26 | 1100 | OH | TRUMBULL | UNKNOWN | NO | N/A | NO | APPROXIMATELY 2000 FEET EAST OF SOUTH CANAL STREET (COUNTY RD. 105) AND ONE MILE NORTH OF THE INTERSECTION OF SOUTH CANAL STREET AND CABLE LINE ROAD. |  | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 160746.0294 | 324289.6692 | GASOLINE | 3 | 690 | 524 | NO | NO | 8.63 | 0.25 | 35000 | WELDED |  | 650 | 200 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.K. NEUWERTH - EASTERN REGION SUPERINTENDENT | 2163514777 | A BULLDOZER OPERATOR EXCAVATING A PIT FOR USE FRACTURING A NATURAL GAS WELL STRUCK THE PIPELINE WITH THE DOZER BLADE JUST AS THE PIT (APPROXIMATELY 10' X50' X 4') WAS NEARLY COMPLETED. THE LINE WAS STRUCK SOMEWHAT PRIOR TO 11:00. THE BP DISPATCH CENTER WAS NOTIFIED OF THE STRIKE SHORTLY AFTER 11:00 AND THE PIPELINE WAS SHUT DOWN AT 11:07. THE FIELD FOREMAN HAD NOT NOTIFIED THE ONE CALL SYSTEM, BUT WAS ABLE TO READILY OBTAIN THE EMERGENCY NOTIFICATION NUMBER FROM A SIGN AT OUR NEARBY ROAD CROSSING.
2017-09-29 08:50 | YES | YES | 19910159 | 1991-09-18 | 3445 | DIXIE PIPELINE | YES | 1991-08-27 | 1045 | LA | CALCASIEU | UNKNOWN | NO | N/A | NO | FOUR MILES NORTH OF SULPHUR ON HIGHWAY 27. |  | PUMPING STATION | OTHER | PIPE REPLACEMENT | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 3 | 3 | 0 | 15000 | 12055.9522 | 24321.7252 | L. P. G. | 2 | 3 | 0 | YES | NO | 10 | 0.22 | 52000 | OTHER |  | 1360 | 0 | YES | 8 | 1760 | 8 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.F. PHILLIPS - GENERAL MANAGER | 4043962994 | A DIXIE PIPELINE EMPLOYEE HAD A CONTRACT CREW ON SITE AT DIXIE'S SULPHUR PUMPSTATION. THE CREW WAS TO REMOVE SOME TEMPORARY PIPING AND TIE THE PIPELINE BACK TOGETHER. DURING THE PREPARATION FOR THIS WORK CERTAIN PROCEDURES FOR ISOLATING THE LINE WERE NOT PROPERLY PERFORMED AND AS A RESULT A MOTOR OPERATED VALVE WAS ACCIDENTLY OPENED, CAUSING A FLASH FIRE THAT INJURED THREE CONTRACT WORKERS AND DAMAGED FOUR PIECES OF EQUIPMENT. INVESTIGATION CONFIRMED EMPLOYEE ERROR WAS THE CAUSE OF THIS ACCIDENT. THERE WAS NO PIPING OR EQUIPMENTFAILURE INVOLVED. A TELEPHONIC NOTIFICATION WAS MADE THE DAY OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19910160 | 1991-09-24 | 26134 | MOBIL PIPELINE CO - MOBIL WEST COAST PIPELINE | NO | 1991-08-28 | 835 | CA | LOS ANGELES | CARSON | NO | N/A | NO | CORNER OF 226TH STREET AND MONETA AVENUE, CITY OF CARSON. |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 32149.2059 | 64857.9338 | FUEL OIL | 3 | 50 | 50 | NO | NO | 12 | 0.28 | 2284 | OTHER |  | 936 | 1234 | YES | 8 | 1220 | 6 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.S. SOBEY - MANAGER OF OPERATIONS | 2134937237 | DURING A HYDROSTATIC TEST THE LINE RUPTURED AT A LOCATION WEAKENED BY EXTERNAL CORROSION. THE PIPE WAS REPLACED AND THE HYDROSTATIC TEST COMPLETED. PIPE TO SOIL READING AT THE LEAK SITE IS - 1.204V.
2017-09-29 08:50 | YES | NO | 19910161 | 1991-09-24 | 26134 | MOBIL PIPELINE CO - MOBIL WEST COAST PIPELINE | NO | 1991-08-27 | 830 | CA | LOS ANGELES | UNKNOWN | NO | N/A | NO | CORNER OF 205TH STREET AND WESTERN AVENUE, TORRANCE, CALIFORNIA. |  | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 80373.0147 | 162144.8346 | FUEL OIL | 3 | 5 | 5 | NO | NO | 12 | 0.25 | 2039 | WELDED |  | 936 | 670 | YES | 8 | 1220 | 6 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.S. SOBEY - MANAGER OF OPERATIONS | 2134937237 | DURING A HYDROSTATIC TEST, WHILE THE LINE WAS DISPLACED WITH WATER, THE PIPELINE RUPTURED AT A POINT WEAKENED BY EXTERNAL CORROSION. THE PIPE WAS REPLACED AND HYDROSTATIC TEST WAS COMPLETED. PIPE TO SOIL READING AT THE LEAK SITEWAS - 1.07V.
2017-09-29 08:50 | YES | NO | 19910162 | 1991-10-07 | 4906 | EXXON PIPELINE CO | YES | 1991-04-04 | 1130 | TX | HARRIS | PASADENA | NO | N/A | NO | EXXON PIPELINE'S PASADENA TANK FARM LOCATED ON HIGHWAY 225 JUST EAST OF PASADENA TANK 2176. |  | TANK FARM | TANK |  | 1977 | OTHER | FIRE CAUSED BY LIGHTNING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 136634.125 | 275646.2189 | GASOLINE | 3 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MR. J. B. HOLT, ENVIRONMENTAL/REGULATORY COMPLIANCE MANAGER | 7136565521 | PASADENA STATION: TANK #2176 - TANK CONTRACTOR WAS REPLACING THE PRIMARY TANK ROOF SEAL WHEN WEATHER TURNED BAD. APPROXIMATELY 90" OF THE OLD SEAL HAD BEEN REMOVED. DURING THE THUNDERSTROM (EXTREMELY HEAVY RAIN AND LIGHTNING), LIGHTNING WAS OBSERVED NEAR THE TANK, AND A FEW MOMENTS LATER FIRE AND SMOKE WERE SEEN. THE PEOPLE AVAILABLE AT THE STATION IMMEDIATELY MOVED THE PORTABLEFOAM TRAILER TO THE TANK FOAM LINE AND WITH THE HELP OF THE PASADENA FIRE DEPARTMENT FOAMED THE TANK AND EXTINGUISHED THE FIRE. AFTER THE FIRE WAS EXTINGUISHED, TWO MEMBERS OF THE PASADENA FIRE DEPARTMENT CLIMBED THE TANK AND VIEWED THE AREA. THE FOAM TRAILER WAS RECHARGED THE FOLLOWING DAY AND IS HOOKEDUP TO THE TANK FOAM LINE.
2017-09-29 08:50 | YES | NO | 19910163 | 1991-10-08 | 15156 | SINCLAIR PIPELINE CO | YES | 1991-10-02 | 1900 | WY | CARBON | UNKNOWN | NO | N/A | NO |  |  | PUMPING STATION | VALVE |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 160.746 | 324.2897 | FUEL OIL | 1 | 150 | 116 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.W. DANIELSON | 3073242636 | AT APPROXIMATELY 7:00 PM ON OCTOBER 2, 1991 A VALVE WAS FOUND NOT TO BE COMPLETELY CLOSED AT SINCLAIR PIPELINE COMPANY'S WYOMING STATION IN SINCLAIR, WYOMING IN THE NW 1/4 SEC. 21, T.21N, R.86W, CARBON COUNTY WYOMING. SINCLAIR PIPELINE EMPLOYEES WERE SENT TO THE SCENE AND THE SOURCE OF THE SPILL WAS INDENTIFIED ANDSHUT OFF. THE SPILL DID NOT REACH ANY WATER SOURCE. THE SIZE OF THE SPILL WAS ESTIMATED AT 150 BBLS. OF WHICH 116 BBLS. WERE RECOVERED VIA VACUUM TRUCK. THE LINE WAS NOT IN OPERATION WHEN THE SPILL OCCURRED.
2017-09-29 08:50 | YES | NO | 19910164 | 1991-09-30 | 4906 | EXXON PIPELINE CO | YES | 1991-08-28 | 820 | TX | NUECES | UNKNOWN | NO | N/A | NO | HARBOR ISLAND TANK FARM. TANK 1798. |  | TANK FARM | TANK |  | 1947 | OTHER | LIGHTNING STRUCK TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 26000 | 20896.9838 | 42157.657 | CRUDE OIL | 1 | 30 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.B. HOLT, ENVIRONMENTAL & REGULATORY COMPLIANCE MANAGER | 7136565521 | 8:20 AM - TANK STRUCK BY LIGHTNING, STARTED 2 SMALL FIRES IN SEAL AREA ON STATION TANK 1798. TANK EQUIPPED WITH EXTERNAL FLOATER AND PRIMARY AND SECONDARY SEALS. TWENTY-FIVE FT. FIRE ALONG CIRCUMFERENCE ON NW SIDE, FIFTEEN FT. FIRE ALONG CIRCUMFERENCE ON SE SIDE. 9:00 AM - FIRE EXTINGUISHED BY PORT ARANSAS FIRE DEPT. BY APPLYING 3% 3M LIGHT WATER FOAM.
2017-09-29 08:50 | YES | NO | 19910165 | 1991-09-30 | 4906 | EXXON PIPELINE CO | YES | 1991-08-30 | 1407 | TX | KIMBLE | UNKNOWN | NO | N/A | NO | LEAK OCCURRED AT STATION NO 5209 +08. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 14467.1426 | 29186.0702 | CRUDE OIL | 1 | 465 | 415 | NO | NO | 18 | 0.31 | 45000 | WELDED |  | 960 | 460 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.B. HOLT, ENVIRONMENTAL & REGULATORY COMPLIANCE MANAGER | 7136565521 | ON AUGUST 30, 1991, AT ABOUT 1407 HOURS OUR OIL TRAFFIC CONTROL CENTER (OTCC) IN HOUSTON RECEIVED A LOW PRESSURE ALARM AT OUR FT. MCKAVETT STATION FOLLOWED BY LOW FLOW AND LOW PRESSURE RATE OF CHANGE ALARMS. A QUICK ANALYSIS OF THE DATA INDICATED A PROBABLE LEAK AND THE AFFECTED PIPELINE SYSTEM WAS SHUT DOWN AT 1411 HOURS. AT 1420 HOURS, OTCC WAS NOTIFIED BY TELEPHONE THAT A KIMBLE COUNTY BULLDOZER HAD PUNCTURED THE PIPELINE IN THE PROCESS OF OBTAINING MATERIAL FROM A ROADWAY DITCH TO BUILD UP THE ADJACENT ROAD. AN EPC CREW WAS IMMEDIATELY DISPATCHED TO THE LEAK SITE, AS WERE VACUUM TRUCKS AND OTHER EQUIPMENT. THE SPILL WAS CONTAINED WITHIN THE ROADWAY DITCH AND A NEARBY DITCH BEING CONSTRUCTED FOR A NEW PIPELINE. FOUR HUNDRED FIFTEEN OF THE 465 BARRELS SPILLED WERE RECOVERED. PERMANENT REPAIRS WERE COMPLETED BY 1800 HOURS ON AUGUST 31 BY REPLACING A 6-FOOT SECTION OF THE 18-INCH PIPELINE.
2017-09-29 08:50 | YES | NO | 19910166 | 1991-11-19 | 12628 | MOBIL PIPELINE CO | NO | 1991-10-03 | 1630 | TX | CALDWELL |  | NO | N/A | NO | SILAS FUQUA SURVEY, PLUM CREEK CROSSING,1-2 MILES EAST OF LULING, TX. |  | LINE PIPE | PIPE |  | 1924 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 36167.8566 | 72965.1756 | CRUDE OIL | 1 | 290 | 255 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 694 | 600 | YES | 8 | 868 | 11 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | BULLET FIRED BY UNK. PERS | Null | NO DATA |  | Null | Null | D. L. DENNARD, V.P., OPERATIONS | 2146582226 | LEAK WAS CAUSED BY EXTERNAL CORROSION - CRUDE OIL SPRAYED OUT SIDE OF PIPE ONTO TRAIN TRESTLE AND DOWN INTO PLUM CREEK. BOOMS WERE INSTALLED AND OIL WAS PICKED UP AND TAKEN TO LULING STATION (MOBIL PIPELINE CO. FACILITY).PERMANENT REPAIRS WERE MADE DURING THE WEEK OF OCT. 28, 1991 BY REPLACINGAPPROX. 216 FT. OF THE PIPELINE WITH TESTED PIPE. THE FAULTY SECTION OFPIPE WAS TAKEN TO OUR MAINTENANCE FACILITY IN LULING, TX, AND AT THAT TIME ITWAS DISCOVERED THAT THE CAUSE OF ACCIDENT WAS NOT EXTERNAL CORROSION ASINITIALLY REPORTED, BUT CAUSED BY A BULLET HOLE. THE LULING POLICE DEPT. WASNOTIFIED AND THEY CONCURRED THAT A BULLET HAD BEEN FIRED AT AND PENETRATEDOUR PIPELINE AT THE PLUM CREEK CROSSING, CAUSING THE LEAK.
2017-09-29 08:50 | YES | NO | 19910167 | 1991-10-08 | 12127 | MARATHON PIPE LINE CO | YES | 1991-09-07 | 900 | IL | CRAWFORD | ROBINSON | NO | N/A | NO | MARATHON OIL COMPANY, TRUCK TERMAINAL, TR. 1, EAST, ROBINSON, IL 62454. |  | LINE PIPE | PIPE |  | 1945 | CORROSION | EXTERNAL CORROSION | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 134000 | 107699.8397 | 217274.0784 | FUEL OIL | 1 | 25 | 10 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1440 | 1250 | YES | 8 | 1800 |  | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | H.E. MILLER - VICE PRESIDENT | 4194214002 | ON SEPTEMBER 5, 1991, PERSONNEL AT MARATHON'S TRUCK TERMINAL ADVISED MARATHON PIPE LINE CO. THAT THEY WERE EXPERIENCING UNEXPLAINED GASOLINE ACCUMULATIONIN THEIR ROBINSON TERMINAL ENVIRONMENTAL CROCK. THE RIO 8" SYSTEM, WHICH TRAVERSES THE TERMINAL PROPERTY, WASSHUT DOWN AND THE PRESSURES MONITORED FOR A24-HOUR PERIOD WITH INCONCLUSIVE RESULTS. THE LINE WAS RESTARTED ON FRIDAY AFTERNOON, SEPTEMBER 6, 1991, AND A 3000 BBL. BATCH ON #2 FUEL OIL WAS MOVED AND BLOCKED IN ACROSS THE TERMINAL PROPERTY. ON SATURDAY, SEPTEMBER 7, 1991, FUEL OIL BEGAN ACCUMULATING IN THE ENVIRONMENTAL CROCK, INDICATING A SMALL LEAK ON THE RIO SYSTEM. THE NATIONAL RESPONSE CENTER WAS CALLED ON 9/7/91 AT 11:07 AM., REPORT #87310. CONCURRENT WITH THE TESTING, WE BEGAN EXCAVATION ALONG THE RIO LINE AT VARIOUS LOCATIONS IN THE TERMINAL; AND AFTER 3 DAYS OF EXCAVATION ALONG THE RIO LINE AT VARIOUS LOCATIONS IN THE TERMINAL; AND AFTER 3DAYS OF EXCAVATION, WERE UNABLE TO FIND THE LEAK LOCATION DUE TO THE DEPTH OF THE LINE, UP TO 17 FEET DEEP, AND CONGESTION OF FACILITIES IN THE AREA. ONTUESDAY, SEPTEMBER 10, 1991, IT WAS DECIDED TO RELOCATE THE RIO SYSTEM AROUND THE WEST AND NORTH SIDES OF THE ROBINSON TERMINAL PROPERTY. THE LEAKING SECTION WAS PURGED WITH NITROGEN, THE ENDS WERE WELD-CAPPED, AND THE DISCONNECTED LINE SECTION ABANDONED IN PLACE.
2017-09-29 08:50 | NO | NO | 19910168 | 1991-10-15 | 2388 | OXY USA INC | NO | 1991-09-08 | 1530 | LA | CALCASIEU | SULPHUR | NO |  | NO | KEROSENE LINE FROM CITGO TO VISTA AT PRATER ROAD & PETE MANENA ROAD, SOUTH OF INTERSTATE 10. |  | LINE PIPE | PIPE | ROAD CASING | 1956 | OTHER | FOUND NO PROBLEM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 401.8651 | 810.7242 | KEROSENE | 1 | 2 | 2 | NO | NO | 6.63 | 0.19 | 2958 | WELDED |  | 400 | 10 | YES | 8 | 611 | 1 | 85 | NO DATA | Null | YES | OTHER | N/A | NO DATA |  | Null | ONE CALL | AIR PATROL | YES | YES | NORMAN W. (BILL) STANSIFER - PIPELINE SUPERINTENDENT | 3185834642 | CITGO DUG-UP THEIR 8" HYDROGEN LINE FOR REPAIRS AND FOUND HYDROCARBONS COMINGOUT OF THE END OF THE COMMON CASING WITH OUR 6" KEROSENE LINE. TRIDENTSAMPLED THE HYDROCARBON & IT WAS FOUND TO BE HEAVIER GRAVITY & ANALYSIS,DIFFERENT THAN KEROSENE. NOTIFIED ADJOINING PIPELINE OWNERS OF POSSIBLELEAK. AT THAT TIME, 9/9/91 @ 16:15 HOURS, TRIDENT FILED A POSSIBLE PIPELINELEAK REPORT #87557. ON 9/12/91 THRU 9/13/91 TRIDENT PRESSURED UP THE PIPE-LINE AND DID A 26 HR. SHUT-IN TEST TO VERIFY PIPELINE INTEGRITY. AT THE SAMETIME MONITORED CASING FOR ANY TYPE OF HYDROCARBON LOSS. PIPELINE HELDPRESSURE AND NO SIGN OF ANY PRODUCT LOSS OR LEAK. TRIDENT IS FILING THISREPORT TO FOLLOW-UP ON INITIAL POSSIBLE LEAK REPORT #87557. AS REPORTEDEARLIER - TRIDENT NGL INC., HAS NO LEAK ON THIS LINE.
2017-09-29 08:50 | YES | NO | 19910169 | 1991-10-04 | 18718 | SUN PIPELINE CO | YES | 1991-09-07 | 730 | PA | LANCASTER | WEST COCALICO TOWNSHIP | NO |  | NO | APL 6" WEST LINE, ROAD MARKER #7, PIPE- LINE CROSSING OF SWAMP CHURCH ROAD (T-816); 1800 FT. NORTH OF SWAMP CHURCH AND BLAINSPORT ROADS. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 160746.0294 | 324289.6692 | GASOLINE | 3 | 670 | 519 | NO | NO | 6.63 | 0.26 | 35000 | WELDED |  | 1200 | 1026 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | CHARLES W. DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | SUN PIPE LINE CONTROL CENTER WAS CONTACTED ON 09/07/91 AT 0730 HOURS BYPROPERTY OWNER, MR. WALTERS, WHO STATED THERE APPEARED TO BE GASOLINEENTERING AN UNNAMED CREEK ON HIS PROPERTY FROM A TILE DRAIN THAT CROSSED OURPIPELINES. THE APL 6" AND 8" WEST LINES WERE IMMEDIATELY SHUT DOWN. CONTROLCENTER THEN CONTACTED FIELD SUPERVISORS WHO MET SORBENT BOOMS AND PADS, ANDCONSTRUCTING SORBENT FENCING IN THE STREAM. ONCE THE LEAK WAS CONTAINED, ASERIES OF EXCAVATIONS IN THE AREA DETERMINED THE SOURCE OF THE LEAK TO BE INA CORROSION PIT IN THE 6" WEST LINE, LOCATED IN THE ROAD CROSSING AT SWAMPCHURCH ROAD. A TEMPORARY REPAIR SLEEVE WAS INSTALLED AND LEAK WAS STOPPED.PERMANENT REPAIRS ARE CURRENTLY BEING PLANNED, AND REMEDIATION OFCONTAMINATION IN AND AROUND THE SITE IS CONTINUING.
2017-09-29 08:50 | YES | NO | 19910170 | 1991-10-09 | 18273 | SHELL PIPELINE CORP | YES | 1991-09-06 | 1600 | TX | WINKLER | KERMIT | NO | N/A | NO | SE 1/4, NE 1/4, SECTION 16, BLOCK 11; EIGHT MILES SOUTH OF KERMIT; HENDRICK-BARNSLEY 10-INCH |  | LINE PIPE | PIPE |  | 1936 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18500 | 14869.0077 | 29996.7944 | CRUDE OIL | 1 | 670 | 519 | NO | NO | 10 | 0.28 | 36000 | WELDED |  | 900 | 200 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | M. D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19910171 | 1991-10-10 | 18273 | SHELL PIPELINE CORP | YES | 1991-09-11 | 1400 | TX | BAYLOR | SEYMOUR | NO | N/A | NO | NW 1/4, NW 1/4, SECTION 277; FIVE MILES EAST OF SEYMOUR; MCCAMEY-CUSHING 10-INCH |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4459 | 3583.8327 | 7230.0382 | CRUDE OIL | 1 | 75 | 0 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 957 | 80 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | M. D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262
2017-09-29 08:50 | YES | NO | 19910172 | 1991-10-16 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1991-09-17 | 920 | AR | UNION |  | NO | N/A | NO | 2.7 MILES EAST OF STATE HIGHWAY 167 SOUTH, EL DORADO STATION F, EL DORADO, ARKANSAS |  | PUMPING STATION | OTHER | 1" PIPE TAP OF 20" LINE. | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 43284 | 34788.6557 | 70182.7702 | NATURAL GAS LIQUID | 3 | 602 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | O. H. CUNNINGHAM VICE PRESIDENT - OPERATIONS & ENGINEERING | 7137593615 | A CONTRACT CREW WAS DIGGING OUT THE NORTH 20" PROPERTY VALVE WITH A SMALLBACKHOE. THE BUCKET OF THE BACKHOE CAME IN CONTACT WITH AND BROKE A 1" PIPETAP OFF OF THE 20" LINE, RESULTING IN THE RELEASE OF NORMAL BUTANE.THE PIPELINE WAS FLOODED WITH WATER TO STOP THE FLOW OF BUTANE. THE 1" LEAKWAS REPAIRED AND THE LINE RETURNED TO NORMAL SERVICE.THE BUTANE DISPERSED TO THE ATMOSPHERE. NO FIRE OR INJURIES RESULTED.
2017-09-29 08:50 | YES | NO | 19910173 | 1991-10-02 | 3012 | D - S PIPE LINE CORP | NO | 1991-09-03 | 1115 | TX | KNOX | KNOX | NO | N/A | NO | 9 MILES NW OF KNOX CITY, TEXAS |  | LINE PIPE | PIPE |  | 1927 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12450 | 10006.4403 | 20187.0319 | CRUDE OIL | 1 | 1650 | 1185 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COMPANY PROGRAM | NO | NO | GERALD CHILDERS, MANAGER PIPELINE SAFETY & REGULATIONS | 8063783583 | AT 1115 HOURS ON SEPTEMBER 3, 1991, A FARMER, WHILE LAYING A WATER LINE,STRUCK AND RUPTURED OUR 10" TEXAS PLAINS CRUDE OIL PIPELINE. THE DAMAGEALLOWED 1650 BARRELS TO ESCAPE, OF WHICH 1185 BARRELS WAS SUBSEQUENTLYRECOVERED. PERMISSION WAS GRANTED BY THE TEXAS AIR CONTROL BOARD TOINTENTIONALLY BURN THE REMAINING OIL. NO INJURIES WERE SUSTAINED AS A RESULTOF THIS INCIDENT.THE PIPE WAS REPAIRED AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19910174 | 1991-10-15 | 4906 | EXXON PIPELINE CO | YES | 1991-10-01 | 1040 | TX | GILLESPIE |  | NO | N/A | NO | LEAK OCCURED @ PIPELINE STATION 9488+40.THE SPILL IS 15 MILES NE OF FREDERICKSBURG, TX & 1 1/2 MILESEAST OF HWY 16, ECKERT PUMP STATION, ON 18" PIPELINE. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 120559.5221 | 243217.2519 | CRUDE OIL | 1 | 650 | 592 | NO | NO | 18 | 0.31 | 45000 | WELDED |  | 960 | 512 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | VIS. FROM DAMAGE LOCATION | NO | NO | MR. J. B. HOLT, ENVIRONMENTAL/REGULATORY COMPLIANCE MANAGER | 7136565521 | AT 1040 HRS. ON OCT. 1, 1991, A BULLDOZER OWNED BY A PIPELINE CONTRACTORGOUGED A 4" BY 6" HOLE IN OUT PIPELINE WHILE CLEARING DEBRIS INTO A DRYDRAW. THE MANAGER OF THE BULLDOZER COMPANY NOTIFIED EXXON PIPELINE CO.'SOIL TRAFFIC CONTROL CENTER IN HOUSTON AND THE SYSTEM WAS SHUTDOWN AT 1042HOURS AND BLOCKED OFF UPSTREAM WITH A REMOTELY OPERATED VALVE.IN THE MEANTIME, THE CONTRACTOR'S DOZER BUILT FIVE EARTH DAMS IN THE DRYDRAW TO CONTAIN THE SPILL. EXXON INITIATED A FULL RESPONSE AND HAD PERSONNELAND VACUUM TRUCKS DISPATCHED TO THE LEAK SITE BY 1115 HOURS.CLEAN-UP AND REPAIR OPERATIONS WERE BEGUN BY 1645 HRS. USING VACUUM TRUCKS TOPICK UP THE OIL AND A BACKHOE TO DIG AROUND THE DAMAGED PIPE. BY 1130 ONOCT. 2, FINAL REPAIRS WERE COMPLETED BY REPLACING A 10 FT. LONG SECTION OFPIPE.
2017-09-29 08:50 | YES | NO | 19910175 | 1991-10-18 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1991-09-13 | 1415 | TX | NUECES |  | NO | N/A | NO | NW SIDE OF ROBSTOWN - WEST OF COUNTY RD.73 & 75 - 0.2 MILES NORTH OF COUNTY RD. 44. |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 6027.9761 | 12160.8626 | CRUDE OIL | 1 | 200 | 0 | NO | NO | 8 | 0 | 0 | WELDED |  | 600 | 538 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | SAFETY SUPERVISOR | 7138777370 | LEAK WAS CAUSED BY EXTERNAL CORROSION. LEAK OCCURRED IN A PLOWED FIELDAND WAS DIFFICULT TO ACCESS DUE TO HEAVY RAINS PRIOR TO THE LEAK OCCURING.
2017-09-29 08:50 | YES | NO | 19910176 | 1991-10-18 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1991-09-19 | 900 | TX | BROOKS |  | NO | N/A | NO | JONES RANCH - 15 MI. WEST OF RACHAL, TX. |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 28130.5552 | 56750.6921 | GASOLINE | 3 | 100 | 0 | NO | NO | 4 | 0.16 | 2912 | WELDED |  | 1240 | 1166 | YES | 8 | 1550 | 5 | 81 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | SAFETY SUPERVISOR | 7138777370 | LEAK WAS CAUSED BY EXTERNAL CORROSION. ACCESS TO THE LEAK SITE WAS VERYDIFFICULT DUE TO HEAVY RAINS PRIOR TO THE LEAK OCCURRING.
2017-09-29 08:50 | NO | NO | 19910177 | 1991-10-22 | 15681 | PLATTE PIPE LINE CO | YES | 1991-09-26 | 842 | MO | MONTGOMERY |  | NO | N/A | NO | MONTE STATION SEC. 16, T5N R5W MONTGOMERY COUNTY, MISSOURI |  | PUMPING STATION | PUMP |  | 1953 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 12538.1903 | 25294.5942 | CRUDE OIL | 1 | 20 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA | NOT GIVEN | NO DATA | N/A | Null | NO DATA |  | Null | Null | H. E. MILLER, OPERATIONS MANAGER | 4194222121 | INTERNAL CORROSION FROM ACCUMULATED WATER IN INFREQUENTLY USED STATION PIPINGCAUSED A PINHOLE TO FORM ON A MINIFOLD WELD. AN ESTIMATED 20 BBLS. OF CRUDEWERE RELEASED.THE WELD WAS CUT OUT AND REPAIR WAS EFFECTED BY WELDING A NEW FLANGE INPLACE.FREE OIL WAS RECOVERED TO THE EXTENET FEASIBLE WITH A VACUUM TRUCK ANDREINJECTED INTO THE PIPELINE SYSTEM. CONTAMINATED SOIL WAS COLLECTED ANDPLACED IN COVERED CONTAINERS FOR DISPOSAL. MISSOURI DNR WAS NOTIFIED OF THELEAK.
2017-09-29 08:50 | YES | NO | 19910178 | 1991-11-30 | 15490 | PHILLIPS PIPE LINE CO | YES | 1991-10-02 | 1900 | TX | UPTON |  | NO | N/A | NO | BENEDUM-SWEENY "LINE EZ" - MP 0-25+63 SEC. 1, BLOCK 50, P.B. SCOTT SURVEY. APPROX. 7 MI. NORTH OFRANKIN, TX, ON HWY. 349, THEN 10 MI. EAST ON HWY. 1555. |  | LINE PIPE | WELDING FITTING | ALSO LONGITUDIAL WELD | 1990 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 16074.6029 | 32428.9669 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 10.75 | 0.2 | 42000 | WELDED |  | 1142 | 362 | YES | 8 | 1530 | 12 | 90 | NO DATA | Null | Null | NO DATA | N/A | NO DATA | N/A | Null | NO DATA |  | Null | Null | B. L. THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | A MARATHON OIL EMPLOYEE REPORTED A POSSIBLE LEAK TO PHILLIPS PIPE LINE.INVESTIGATION CONFIRMED A VERY SMALL LEAK.THE LEAK WAS IN A DEFECTIVE LONGITUDINAL WELD ON A FULL ENCIRCLEMENT REPAIRSLEEVE.
2017-09-29 08:50 | YES | NO | 19910179 | 1991-10-25 | 2190 | CENTRAL FLORIDA PIPELINE CORP | NO | 1991-09-27 | 815 | FL | OSCEOLA | KISSIMMEE | NO | N/A | NO | BEHIND C&H SUPPLY - 735 E. DUNCAN AVE., KISSIMMEE, FL, 34744 - ON CSX RAILROAD RIGHT-OF-WAY APPROX. 0.1 MI NORTH OF DONEGAN AVE (50' FROM WEST SIDE OF TRACKS) |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 72335.7132 | 145930.3512 | DIESEL FUEL | 1 | 114 | 114 | NO | NO | 6.63 | 0.22 | 0 | WELDED |  | 1200 | 150 | YES | 24 | 1500 | 3 | 71 | NO DATA | Null | YES | NO DATA | NOT LISTED | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | E. R. FOSTER - ASST. MGR. CENTRAL FLORIDA PIPELINE CORP. | 8132411104 | J4) EXCAVATOR CALLED AFTER HE HIT THE PIPELINE.MR. BENNY SANDERSON, THE MANAGER OF C&H SUPPLY, IN KISSIMMEE, FL, WASATTEMPTING TO DIG A RETENTION POND BEHIND THE C&H SUPPLY FACILITY TO DIVERTRUNOFF RAINWATER FROM HIS BUSINESS. THE LOCATION WAS APPROX. FIVE FOOT EASTOF THE WAREHOUSE STRUCTURE BUT ON CSX RAILROAD RIGHT-OF-WAY. MR. SANDERSONWAS OPERATING A LARGE RUBBER TIRED FRONT END LOADER AND WAS SCOOPING DIRT OFFTHE TOP OF THE 6" CFPL PIPELINE WHEN THE BLADE STRUCK THE TOP OF THE PIPE-LINE, PUNCTURING THE LINE. A PIPELINE MARKER WAS PRESENT IN THE IMMEDIATEAREA AND MR. SANDERSON CALLED THE EMERGENCY NUMBER TO ADVISE OF THE RUPTURE.MR. BILL PRIEST OF TAFT TERMINAL TOOK THE CALL AND IMMEDIATELY ADVISED THEPUMPING STATION.
2017-09-29 08:50 | YES | NO | 19910180 | 1991-10-30 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1991-10-05 | 800 | CA | KERN |  | NO | N/A | NO | 300 FT. EAST OF GRAPEVINE PUMP STATION NEAR INTERSTATE 5. |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 6027.9761 | 12160.8626 | CRUDE OIL | 1 | 103 | 3 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 928 | 675 | YES | 4 | 1169 | 3 | 90 | INTERNAL | Null | YES | NO DATA | NOT LISTED | NO DATA | N/A | Null | NO DATA |  | Null | Null | EILEEN THRASHER, VICE PRESIDENT | 2134289300 | INTERNAL CORROSION IN 8" DEADLEG, LATERAL. ONE HUNDRED BARRELS CONTAINEDIN CONCRETE VAULTS. THREE BARRELS OVERFLOWED ON GROUND.
2017-09-29 08:50 | YES | NO | 19910181 | 1991-04-10 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1991-03-28 | 1405 | TX | JACKSON |  | NO | N/A | NO | APPROX. 1/2 MI. NE OF LOLITA STATION BETWEEN FM 429 & FM 430 - 1/2 MI. SOUTH OF FM 430. |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | L. P. G. | 2 | 5 | 0 | NO | NO | 8 | 0.32 | 2614 | NO DATA |  | 750 | 600 | YES | 24 | 1050 |  | 73 | EXTERNAL | Null | YES | OTHER | INTERFERENCE | NO DATA | N/A | Null | NO DATA |  | Null | Null | SAFETY SUPERVISOR | 7138777370 | FARMER REPORTED ICEY MATERIAL ON GROUND TO COASTAS DISPATCHING. DISPATCHINGNOTIFIED AREA SUPERVISOR FROM HOUSTON PIPELINE DISTRICT TO INVESTIGATE. LINEWAS IDENTIFIED AS OURS, LINE WAS REPAIRED.
2017-09-29 08:50 | YES | NO | 19910182 | 1991-04-10 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1991-04-01 | 1310 | TX | DUVAL |  | NO | N/A | NO | FREER PUMP STATION - 2 MI. EAST OF FREERON HIGHWAY 44, 1/2 MILE SOUTH OF HWY. 44 |  | PUMPING STATION | PUMP |  | 1930 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | PACKING GLAND LEAK ON PMP | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 241000 | 193698.9655 | 390769.0514 | CRUDE OIL | 1 | 10 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SAFETY SUPERVISOR | 7138777370 | PACKING GLAND BACKED OUT ON P.D. PUMP, RESULTING IN CRUDE OIL LEAKING IN PUMPHOUSE. WHEN ESD WAS ACTIVATED, A FIRE RESULTED. PUMP HOUSE WAS DESTROYED.ALSO, A CP&L TRUCK WAS DAMAGED.
2017-09-29 08:50 | YES | NO | 19910183 | 1991-06-14 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1991-05-23 | 1100 | TX | FORT BEND |  | NO | N/A | NO | ONE MILE NE OF STATE HWY. 1462 NEAR DAMON, TX. |  | LINE PIPE | BOLTED FITTING | CLAMP | 1974 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 26500 | 21298.8489 | 42968.3812 | L. P. G. | 2 | 10 | 0 | NO | NO | 8 | 0.19 | 2005 | WELDED |  | 1313 | 800 | YES | 24 | 1650 | 7 | 74 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | SAFETY SUPERVISOR | 7138777370 | ROY MARSHALL W/ THE RAILROAD COMMISSION REPORTED A LEAK TO GLEN ELSTER. MR.MARSHALL STATED THAT A MR. RODNEY MATHEWS HAD SPOTTED SOME VAPORS WHILEFLYING NEARBY. MR. ELSTER THEN WENT TO THE REPORTED LOCATION AND FOUNDVAPORS COMING FROM AN AREEA WHERE A SPLIT CLAMP HAD BEEN INSTALLED INFEB., 1990. DUG AREA AROUND VAPORS AND DISCOVERED AN ICE BALL. THE LINEWAS STOPPLED AND REPLACED W/ 140' OF NEW 8" PIPE IN ORDER TO REMOVE THESPLIT CLAMP.
2017-09-29 08:50 | YES | NO | 19910184 | 1991-06-18 | 3012 | D - S PIPE LINE CORP | NO | 1991-07-07 | 935 | TX | KNOX | KNOX | NO | N/A | YES | 7 MILES DUE WEST OF KNOX CITY, TX. |  | LINE PIPE | GIRTH | ACETYLENE WELDED | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1429620 | 1149028.693 | 2318054.9847 | CRUDE OIL | 1 | 6235 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES | FLOOD | Null | NO DATA |  | Null | Null | GERALD CHILDERS - MANAGER, PIPELINE SAFETY & REGULATIONS | 8063783583 | AT 9:38A ON JUNE 7, 1991, OUR TEXAS PLAINS 10" CRUDE OIL PIPELINE WAS SHUT-DOWN DUE TO DAMAGE CAUSED BY OUTSID NATURAL FORCES. HEAVY RAINS ON THEBRAZOS RIVER WATERSHED CREATED FLOODING CONDITIONS WHICH ERODED THE NORTHBANK AND WASHED OUT THE SUBJECT PIPELINE.THE STRESS OF EXCESSIVE WATER FLOW AND DEBRIS CAUSED A ACETYLENE GIRTH WELDFAILURE WHICH ALLOWED CRUDE OIL TO ESCAPE INTO THE RIVER. THE SPILLED OILDID NOT IGNITE AND NO INJURIES WERE SUSTAINED.SUCCESSFUL REMEDIAL ACTIONS WERE IMPLEMENTED BY COMPANY AND CONTRACTPERSONNEL THROUGH THE PLACEMENT OF BOOMS AND SORBANT MATERIALS AT THE POINTWHERE THE BRAZOS RIVER ENTERS POSSUM KINGDOM LAKE.THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY DIRECTIONALLY DRILLING A NEWRIVER CROSSING. A TOTAL OF 4,137 FEET OF NEW 10.750 O.D., 0.365 WALL, API 5LX-42, ERW PIPE WAS REPLACED AND THE PIPELINE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19910189 | 1991-10-30 | 443 | AMOCO PIPELINE CO | YES | 1991-10-03 | 100 | KY | MCLEAN | RUMSEY | NO | N/A | NO | AT THE GREEN RIVER, MILE MARKER 60.5, APPROX. 1 MI. WEST OF RUMSEY, KY, IN MCLEAN COUNTY, KY. |  | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE | SUBSIDENCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 160746.0294 | 324289.6692 | XYLENE | 3 | 1800 | 300 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1440 | 1175 | YES | 24 | 1970 |  | 77 | NO DATA | Null | Null | NO DATA | N/A | SUBSIDENCE |  | Null | NO DATA | N/A | Null | Null | R. A. STAHL - AREA MANAGER | 2197382384 | PART D - BELIEVE SUBSIDENCE CAUSED PIPE TO BUCKLE AND RUPTURE.PART K - RIVER BANK AND ADJACENT STRESS CRACKS WOULD INDICATE MOVEMENT OF THE RIVER BANK (SUBSIDENCE) WHICH CAUSED THE PIPE TO BUCKLE ON THE TOP & CRACK ON THE BOTTOM NEAR A GIRTH WELD IN THE HEAT AFFECTED ZONE.
2017-09-29 08:50 | YES | NO | 19910190 | 1991-10-31 | 809 | ARCO PIPE LINE CO | NO | 1991-10-22 | 145 | TX | HARRIS | DEER PARK | NO | N/A | NO | 1230 BATTLEGROUND RD., DEER PARK, TX. |  | LINE PIPE | OTHER | HEAT EXCHANGER STEAM TRAP | 1981 | OTHER | OVERPRESSURE OF STEAM TRP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | ETHYLENE | 2 | 15 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. J. ROGERS | 7139865225 | AT APPPROX. 11:10 P, MONDAY, OCT. 21ST, AN ETHYLENE IN STEAM ALARM WASRECEIVED BY THE APL CONTROL CENTER FROM THE SOLVEY ETHYLENE DELIVERYFACILITY. AN ENGINEERING TECHNICIAN WAS DISPATCHED TO THE SITE AND WITH THEUSE OF A GAS DETECTOR, DETERMINED THAT ETHYLENE WAS, IN FACT, LEAKING INTOTHE STEAM SIDE OF THE HEAT EXCHANGER. THE TECHNICIAN NOTIFIED THE CONTROLCENTER AND SOLVEY PERSONNEL OF THE CONDITION AND THEN LEFT THE SITE. THEDELIVERY WAS TERMINATED, AND AT APPROX. 1:45A TUESDAY, OCT. 22, THE STEAMTRAP HAD BEEN SUBSEQUENTLY REPLACED AND THE FACILITY RETURNED TO SERVICEWED., OCT. 23RD.
2017-09-29 08:50 | NO | NO | 19910191 | 1991-10-28 | 12471 | MID - VALLEY PIPELINE CO | YES | 1991-10-12 | 1700 | MS | HUMPHREYS |  | NO | N/A | NO | APPROX. 7 MI. WEST OF ISOLA, MS; MORE SPECIFICALLY, T16N R5W, NW QUARTER OF NE QUARTER SECT. 16; 50 YDS NE OF BEASLEY BAYOU; 0.75 MI EAST OF SUNFLOWER RIVER. |  | LINE PIPE | OTHER | NOT SPECIFIED | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 22 | 0.3 | 52000 | WELDED |  | 816 | 529 | YES | 24 | 1020 |  | 49 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | I. B. NEWMAN, MANAGER OF PIPELINE OPERATIONS | 9037570207 | AT APPROX. 1700 HRS. CST ON 10/12/91, A TRACTOR/SUB-SOILER OPERATED UNDER THEOPERATION OF ED NERREN ON PROPERTY OWNED BY HUMPHREYS COUNTY (16TH SECTIONPROPERTY SET ASIDE TO GENERATE REVENUE FOR SCHOLL SYSTEM) AND MANAGED BY THECOUNTY BOARD OF SUPERVISORS AND, IN THIS CASE, LEASED TO ED NERREN OF ISOLA,MS FOR FARMING PURPOSES, STRUCK AND RUPTURED THE 22" O.D. CRUDE OIL PIPELINECAUSING A CRACK 1" LONG AND CORRESPONDING DENT OF 1/4" IN DEPTH. APPROX. 20GALLONS OF CRUDE OIL WAS SPILLED OVER A 10' X 10' SURFACE AREA. THE TOP OFPIPE DEPTH AT THE LEAK POINT WAS 14". MR. NERREN HAD CONTACTED MID-VALLEY INRECENT YEARS PRIOR TO BEGINNING SUCH FARMING OPERATIONS IN ORDER THAT THELINE COULD BE MARKED. HOWEVER, IN THE FALL OF 1991, HE FAILED TO DO SO. THEPIPELINE WAS IMMEDIATELY REPAIRED BY INSTALLING A FULL-ENCIRCLEMENT SLEEVE INACCORDANCE WITH COMPANY PROCEDURES.
2017-09-29 08:50 | YES | NO | 19910192 | 1991-11-08 | 443 | AMOCO PIPELINE CO | YES | 1991-10-10 | 755 | TX | HOCKLEY |  | NO | N/A | NO | 5 MI SOUTH OF SUNDOWN, TX. SLAUGHTER STATION IS NORTH OF HGWY 41. |  | TANK FARM | PIPE |  | 1944 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 300 | 200 | NO | NO | 16 | 0 | 0 | WELDED |  | 275 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BLAINE PARROTT | 7089906107 | LEAK OCCURRED ON THE LOW PRESSURE PIPING IN THE SLAUGHTER STATION TANKMANIFOLD. CAUSE OF LEAD WAS AN UNATTENDED VALVE CLOSURE IN THE MANIFOLD.
2017-09-29 08:50 | YES | NO | 19910193 | 1991-11-06 | 18273 | SHELL PIPELINE CORP | NO | 1991-10-09 | 500 | TX | MITCHELL | COLORADO CITY | NO | N/A | NO | COLORADO CITY STATION, 10 MI NORTH OF COLORADO CITY, MCCAMEY-CUSHING 10" PIPELINE SYSTEM. |  | PUMPING STATION | VALVE |  | 1989 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 4958 | 3984.8941 | 8039.1409 | CRUDE OIL | 1 | 130 | 120 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. D. HAYS, MANAGER HEALTH, SAFETY & ENVIRONMENT | 7132416262 | A PUMP DRAIN VALVE WAS INADVERTENTLY LEFT OPEN DURING MAINTENANCE.
2017-09-29 08:50 | NO | NO | 19910194 | 1991-11-08 | 2552 | COLONIAL PIPELINE CO | YES | 1991-10-17 | 1100 | TN | DAVIDSON | NASHVILLE | NO | N/A | NO | NEAR STATE HGWY 41A |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | GASOLINE | 1 | 1 | 1 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 1440 | 15 | YES | 24 | 2000 |  | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | NO | JAMES O. COX | 4048412296 | ON OCT. 17, 1991, THE PIPELINE CONTROL CENTER IN ATLANTA, GA WAS NOTIFIED BYA CONTRACTOR THAT, WHILE TAKING SOIL SAMPLES, AN AUGER HAD STRUCK COLONIAL'S12", GASOLINE PIPELINE BETWEEN E. NASHVILLE DELIVERY FACILITY AND NASHVILLEDELIVERY FACILITY. THE INCIDENT OCCURRED BETWEEN THE NASHVILLE AND ASHLANDCITY RAILROAD AND STATE HIGHWAY 41A AND NEAR THE EAST BANK OF THE CUMBERLANDRIVER AT 11:00A, CDT.THE CONTRACTOR HAD NOTIFIED TENNESSEE'S ONE-CALL SYSTEM AT 9:52A ON OCTOBER15, 1991, STATING THAT WORK WOULD BEGIN ON OCT. 18, 1991. A COLONIALINSPECTOR VISITED THE SITE ON OCT. 16, 1991 AND NOTED THAT NO CONSTRUCTIONACTIVITY HAD BEGUN. THE CONTRACTOR HAD BEGUN WORK ON THE 17TH W/OUT ADVISINGCOLONIAL.THE TENNESSEE EMERGENCY MANAGEMENT AGENCY WAS NOTIFIED AT 12:20P, CDT ANDMR. TOM WILKER AT THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT #92596)AT 12:30 P, CDT ON OCT. 17, 1991.AT 12:45P, CDT, COLONIAL PERSONNEL AND EMERGENCY CLEAN UP AND REPAIR CREWSBEGAN ARRIVING AT THE LEAK SITE. EXCAVATION REVEALED THAT THE AUGER HADSTRUCK THE SIDE OF THE PIPELINE CAUSING A SMALL HOLE.A PLIDCO CLAMP WAS INSTALLED ON THE PIPELINE AT 5:00P, CDT ON OCT. 17, 1991.THE LINE WAS THEN PRESSURED AND MONITORED REVEALING NO ADDITIONAL LEAKAGE.AS A RESULT OF CLEAN UP ACTIVITIES THE PRODUCT WAS RECOVERED AND RETURNED TOTHE PIPELINE SYSTEM. CONTAMINATED SOIL HAD BEEN REMOVED FOR REMEDIATION.
2017-09-29 08:50 | YES | NO | 19910195 | 1991-11-04 | 809 | ARCO PIPE LINE CO | YES | 1991-10-20 | 1545 | OK | LINCOLN |  | NO | N/A | NO | NE/4 SEC. 15-T12N-R4E, 2 MI EAST NORTH OF MEEKER, OK. |  | LINE PIPE | PIPE |  | 1921 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 7715.8094 | 15565.9041 | FUEL OIL | 3 | 91 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 700 | 675 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | F. R. NEELEY - VICE PRES. & MGR., PRODUCTS BUS. | 7139865330 | A CORROSION PIT IN THE LINE CAUSED THE DISCHARGE OF APPROX. 91 BBL OF #2
2017-09-29 08:50 | NO | NO | 19910196 | 1991-11-04 | 809 | ARCO PIPE LINE CO | YES | 1991-10-20 | 1445 | KS | MONTGOMERY |  | NO | N/A | NO | APPROX. 2.5 MI SW OF TOWN OF SYCAMORE & HWY. 75 @ STATION 1635 & 86, NORTH OF SYCAMORE BLOCK VALVE. |  | LINE PIPE | PIPE |  | 1923 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | GASOLINE | 1 | 42 | 22 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 740 | 320 | YES | 10 | 334 | 10 | 91 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS | FARM IMPLEMENT | Null | ONE CALL |  | NO | NO | F. R. NEELEY - V.P. & MGR., PRODUCTS BUS. UNIT | 7139865330 | LAND OWNER DAMAGED PIPELINE W/ FARM IMPLEMENT. A COMPANY CREW WASIMMEDIATELY DISPATCHED TO REPAIR LEAD AND BEGIN SPILL CLEANUP.NOTE: TELEPHONIC NOTICE TO THE NATIONAL RESPONSE CENTER WAS MADE PRIOR TO ACCURATELY DETERMINING THE QUANTITY OF SPILLED PRODUCT. AFTER FURTHER INVESTIGATION, IT WAS FOUND THAT THE INCIDENT DIDN'T REQUIRE DOT REPORTING. HOWEVER, THIS REPORT IS BEING SUBMITTED AS A FOLLOW-UP TO THE TELEPHONE NOTICE.
2017-09-29 08:50 | YES | NO | 19910197 | 1991-11-04 | 809 | ARCO PIPE LINE CO | YES | 1991-10-18 | 1200 | OK | LINCOLN |  | NO | N/A | NO | NW/4 SEC.36-T13N-R4E, 3 MI NORTH, 3 MI EAST AND 1/2 MI NORTH OF MEEKER, OK. |  | LINE PIPE | PIPE |  | 1921 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15400 | 12377.4443 | 24970.3045 | FUEL OIL | 3 | 265 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 700 | 675 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | F. L. NEELY - V.P. & MGR., PRODUCT BUS. UNIT | 7139865330 | A CORROSION PIT IN THE LINE CAUSED THE DISCHARGE OF APPROX. 265 BBL OF #2FUEL OIL. A COMPANY CREW WAS IMMEDIATELY DISPATCHED TO REPAIR THE LEAK ANDBEGIN SPILL CLEANUP.
2017-09-29 08:50 | YES | NO | 19910198 | 1991-11-13 | 19153 | TENNECO OIL CO NATURAL GAS LIQUIDS | NO | 1991-11-06 | 1400 | TX | JACKSON | BLESSING | NO | N/A | NO | ADJACENT TO FARM ON MARKET ROAD 1862. |  | PUMPING STATION | OTHER | RELIEF VALVE | 1991 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 100 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. S. HICKMAN | 7134704902 | 2:00P - NOTIFIED OF EQUIP. MALFUNCTION.2:40P - SHUT DOWN PUMP STATION.2:45P - RELIEF VALVE RESEATED, ON-SITE PERSONNEL CLOSED BLOCK VALVE PRECEDING RELIEF VALVE. LEAK SECURED.4:20P - NEW RELIEF VALVE INSTALLED. LINE RETURNED TO SERVICE.NOTE: ALL LIQUIDS THAT CONDENSED DURING HYDRATION EVAPORATED QUICKLY AND WERE TOTALLY DISPERSED BY 4:30P AT WHICH TIME ALL PERSONAL DEPARTED.PART G (ABOVE) VOLUME ESTIMATED (100 BARRELS) IS MAXIMUM FLOW FULLY OPENEDRELIEF DEVICE FOR 45 MIN. W/ NO DROP IN PRESSURE. WE DON'T FEEL THAT AVOLUME THIS LARGE WAS VENTED, HOWEVER, WE HAVE NOTHING ON WHICH TO SUBSTAN-TIATE A LOWER VOLUME.
2017-09-29 08:50 | YES | NO | 19910199 | 1991-11-20 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1991-10-31 | 1000 | CA | SAN BERNARDINO |  | NO | N/A | YES | SECTION 28, T8N, R19E |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 64298.4118 | 129715.8677 | CRUDE OIL | 1 | 52 | 0 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1200 | 415 | YES | 24 | 1500 |  | 77 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | EILEEN THRASHER | 3104289300 | AIR PATROL REPORTED OIL ON THE GROUND OCT. 31, AT 10:00A.
2017-09-29 08:50 | YES | NO | 19910200 | 1991-11-08 | 2337 | CHEVRON PIPELINE CO | YES | 1991-10-26 | 1300 | LA | PLAQUEMINES |  | NO | N/A | NO | GRAND BAY RECEIVING STATION - N.2918.8; W.891719. |  | PUMPING STATION | PIPE |  | 1974 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 24111.9044 | 48643.4504 | CRUDE OIL | 1 | 1740 | 1600 | NO | NO | 6 | 0.28 | 24000 | WELDED |  | 200 | 150 | YES | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. L. CLUTTER - DISTRICT SUPERINTENDENT | 5045927513 | AN UNDERGROUND PIPELINE LEAK, DUE TO INTERNAL CORROSION, WAS DISCOVERED BY ACOMPANY EMPLOYEE. THE CRUDE OIL WAS CONTAINED WITHIN THE STATION COMPOUND &RECOVERED BY PUMPING INTO STATION TANKAGE. OIL SOAKED DEBRIS IS BEINGDISPOSED OF AT OUR APPROVED DISPOSAL SITE.
2017-09-29 08:50 | YES | NO | 19910201 | 1991-11-01 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1991-10-02 | 1330 | OR | LANE |  | NO | N/A | NO | AT TUALATIN CHECK VALVE, PLMP 16.4, ON- LINE SECTION 14, 250 YDS SOUTH OF THE TUALATIN RIVER. |  | LINE PIPE | PIPE |  | 1962 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 361678.5662 | 729651.7558 | GASOLINE | 3 | 26 | 0 | NO | NO | 2 | 0.15 | 35000 | WELDED |  | 1280 | 680 | YES | 24 | 1600 |  | 62 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J. M. ABBOUD, SENIOR V.P., OPERATIONS & ENGINEERING | 2134867720 | THERE IS A 2" BYPASS LINE AROUND THE TUALATIN CHECK VALVE AND BECAUSE OFFAULTY PIPE PIN HOLE LEAKS DEVELOPED.
2017-09-29 08:50 | YES | NO | 19910202 | 1991-11-18 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1991-10-25 | 2015 | OH | ALLEN |  | NO | N/A | NO |  |  | TANK FARM | VALVE |  | 1963 | OTHER | TANK DRAIN VALV FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 3 | 200 | 200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER, REGULATION COMPLIANCE COORDINATOR | 2158208300 | AT BUCKEYE'S LIMA STATION ON OCT. 25, 1991, A 2" WATER DRAIN-OFF VALVE ONHEATING OIL TANK #412 FAILED TO CLOSE COMPLETELY. THE RESULTING PRODUCTRELEASE WAS CONTAINED WITHIN THE ON-SITE OIL/WATER SEPERATOR AND THE EXISTINGTANK DIKE AREA. REMAINING HEATING OIL WAS THEN PROMPTLY TRANSFERRED FROMTANK 412 TO ALLOW PERMANENT REPAIRS TO BE MADE TO THE DEFECTIVE WATER DRAINVALVE. ALL OF THE PRODUCT RELEASED INTO THE DIKE AREA WAS RECOVERED.
2017-09-29 08:50 | YES | NO | 19910203 | 1991-11-25 | 443 | AMOCO PIPELINE CO | YES | 1991-10-26 | 330 | OK | PAYNE | CUSHING | NO | N/A | NO | AMOCO PIPELINE CO.'S CUSHING TERMINAL, 2MILES SOUTH OF HGWY 33 ON LINWOOD AVE. IN CUSHING, OK |  | TANK FARM | TANK | SLOP TANK, NOT BREAKOUT | 1976 | OTHER | SLOP TANK OVERFLOW | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 651.0214 | 1313.3732 | CRUDE OIL | 1 | 100 | 100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN W. CARICO, AREA MANAGER | 9182257271 | THE SLOP TANK RECEIVES OIL FROM AN OIL-WATER SEPERATOR. THE COMPLETE SPILLWAS CONTAINED WITHIN THE TANK'S DIKE.
2017-09-29 08:50 | NO | NO | 19910204 | 1991-11-27 | 2552 | COLONIAL PIPELINE CO | YES | 1991-10-30 | 900 | LA | EAST FELICIANA |  | NO | N/A | NO | COLONIAL PIPELINE CO'S BATON ROUGE JUNCT |  | PUMPING STATION | VALVE |  | 1962 | OTHER | CHK VALVE SHAFT GLND FAIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | FUEL OIL | 1 | 5 | 4 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX - MGR. TECHNICAL & REGULATORY | 4048412296 | ON A ROUTINE STATION CHECK, THE LOCAL OPERATOR AT COLONIAL'S BATON ROUGEJUNCTION FOUND OIL IN THE DITCH LEADING FROM STATION #2 TO RETENTION POND NO.2. RECENT HEAVY RAINFALL HAD CAUSED THE PRODUCT TO TRAVEL TO THE DITCHTHROUGH AN AREA DRAIN; NO PRODUCT HAD SURFACED IN THE STATION AREA. THESOURCE OF THE LEAK WAS DETERMINED TO BE A FAULTY CHECK VALVE SHAFT GLAND ONUNIT NO. 1 OF LINE NO. 2. REPAIRS WERE MADE TO THE CHECK VALVE AND THE AREACLEANED UP. FOUR AND ONE HALF BARRELS OF FUEL OIL WERE RECOVERED ANDRETURNED TO THE SYSTEM; THE REMAINING ONE HALF BARREL WAS LOST TO THEENVIRONMENT. APPROX. 3 CUBIC YARDS OF SOIL SATURATED W/ FUEL OIL HAS BEENACCUMULATED FROM THE CLEANUP.THE LOUISIANA DEPT. OF ENVIRONMENTAL QUALITY WAS NOTIFIED OF THE SPILL VIATELEPHONE AT 10:40A CST ON OCT. 30, 1991. THE NATIONAL RESPONSE CENTER WASNOTIFIED OF THE SPILL (REPORT #94391) AT 11:52A EST ALSO ON OCT. 30, 1991.
2017-09-29 08:50 | YES | NO | 19910205 | 1991-11-26 | 4906 | EXXON PIPELINE CO | NO | 1991-10-30 | 1545 | LA | ASCENSION |  | NO | N/A | NO | ENRON METER STATION T9S, R2E, S40; HIGH-WAY 75 (APPROX. 1 MI WEST FROM THE INTERSECTION OF HIGHWAY 73 & 75) |  | LINE PIPE | OTHER | 1/2" FITTING | 1972 | OUTSIDE FORCE DAMAGE | FISHING OPERATIONS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2411.1904 | 4864.345 | NATURAL GAS LIQUID | 2 | 37 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | FISHING OPERATIONS | MUDSLIDE IN AN EXCAVATION | Null | ONE CALL |  | Null | Null | J.B. HOLT, MGR. OF ENVIRONMENTAL & REGULATORY COMPLIANCE DPT | 7136565521 | AT 15:45 ON OCT. 30, 1991 A RELEASE OF APPROX. 37 BARRELS OF NORMAL BUTANEOCCURRED FROM EXXON PIPELINE CO.'S (EPC) ENRON METER STATION. THE RELEASEOCCURRED WHEN THE SIDE OF AN EXCAVATION SLOUGHED OFF (DUE TO HEAVY RAINS)PULLING SOME CONCRETE ENCASED CONDUIT DOWNWARD INTO THE HOLE. THE CAUSED THECONDUIT TO BREAD A 1/2" FITTING WHICH IS ATTACHED TO EPC'S 3" N-BUTANE METERRUN.A MANUAL VALVE WAS CLOSED AT THE PIPELINE TO ISOLATE THE LEAK AT APPROX.16:20.
2017-09-29 08:50 | YES | NO | 19910206 | 1991-11-26 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1991-11-02 | 1730 | OH | WOOD |  | NO | N/A | NO |  |  | LINE PIPE | OTHER | INSTRUMENTATION | 1983 | OUTSIDE FORCE DAMAGE | FISHING OPERATIONS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 91 | 90 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | FISHING OPERATIONS | VANDALISM | Null | ONE CALL |  | Null | Null | DEAN R. MOYER - REGULATORY COMPLIANCE COORDINATOR | 2158208300 | THE INCIDENT LOCATION WAS A A MAIN LINE VALVE SITE. THE CYCLONE SECURITYFENCE HAD BEEN TEMPORARILY REMOVED TO FACILITATE REPLACEMENT OF THE MAIN LINEVALVES. AT COMPLETION OF THE MAINTENANCE WORK THE PIPELINE WAS REFILLED BYOPENING THE MAIN LINE VALVES AND ADMITTING PRODUCT FROM A HIGHER ELEVATION.THIS RESULTED IN A STATIC PRESSURE OF ABOUT 100 PSIG AT TOLEDO STATION ANDABOUT THE SAME PRESSURE AT THE MAIN LINE VALVE SITE. THE SITE WAS WELLLIGHTED WITH A MERCURY VAPOR LAMP AND HAD TEMPORARY CONSTRUCTION FENCING.TWO INDEPENDENT INSPECTIONS, BY DIFFERENT BUCKEYE EMPLOYEES, OF THE SITESHORTLY AFTER THE PIPELINE WAS REFILLED WITH A PRODUCT (ABOUT 1700 AND 1730ON 11/1/91) INDICATED THAT THERE WAS NO PRODUCT RELEASE OR OTHER PROBLEMS.THE PIPELINE WAS NOT SCHEDULED TO BE PACKED AND RESTARTED TILL ABOUT NOON ON11/2/91. THE PRESSURE AT TOLEDO STATION REMAINED STEADY ALL NIGHT. THEPRODUCT RELEASE WAS DISCOVERED AT ABOUT 0800 ON 11/2/91 BY ANOTHER BUCKEYEEMPLOYEE. A SMALL TUBING QUICK DISCONNECT FITTING INSIDE A GRAVITOMETERCABINET AT THE MAIN LINE VALVE SITE HAD BEEN REMOVED AND A 3/8" VALVE WASOPENED TO ATMOSPHERE BY VANDALS SOMETIME BETWEEN 1730 ON 11/1/91 AND 0800 ON11/2/91. THIS VALVE AND SMALL TUBE FITTING ARE NORMALLY USED AS ANINSTRUMENTATION CALIBRATION CONNECTION.
2017-09-29 08:50 | YES | NO | 19910207 | 1991-11-25 | 13161 | NAVAJO PIPELINE CO | YES | 1991-11-09 | 530 | TX | EL PASO | EL PASO | NO | N/A | NO | 1000 EASTSIDE ST., EL PASO TX 79915. |  | TANK FARM | TANK |  | 1959 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 23315 | 18738.9684 | 37804.0682 | DIESEL FUEL | 3 | 1433 | 1144 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM TOWNSEND - ASST. MGR. OF PIPELINE | 5057483311 | 8" PRODUCT PIPELINE WAS BEING RECEIVED INTO TANK 206 WHICH IS A 15,400 BBL.CONE ROOF TANK. THE OPERATOR PAUL EVANS WAS ON MIDNIGHT DUTY. PAUL CAMEINTO WORK AT 23:30 HRS 11-8-91. PAUL READ THE DAILY ACTIVITY WORK SHEETWHERE ALL CUTS, SWITCHES AND BATCH TIMES ARE RECORDED WHEN CALCULATED BYPRIOR SHIFT EMPLOYEES. PAUL OVERLOOKED THE INSTRUCTIONS TO SWITCH THE 8"MAINLINE STREAM TO TANK 212 AT 01:37 HRS 11-9-91. APPROX. 1433 BARRELS OFDIESEL FUEL WAS SPILLED. THE PIPELINE NET RATE WAS APPROX. 815 BPH DURINGTHE TIME THE SPILL OCCURRED. A TOTAL OF 1144 BARRELS WERE RECOVERED.
2017-09-29 08:50 | NO | NO | 19910208 | 1991-11-19 | 809 | ARCO PIPE LINE CO | NO | 1991-11-14 | 530 | TX | HARRIS | DEER PARK | NO | N/A | NO | 1230 BATTLEGROUND RD., DEER PARK, TX |  | LINE PIPE | OTHER | HEAT EXCHANGER | 1991 | OTHER | LOOSE CONN. TO HEAT EXCH | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ETHYLENE | 1 | 10 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.J. ROGERS, OPERATIONS MGR. | 7139865225 | AT APPROX. 0530 ON THURS., NOV. 14, SOLVAY OPERATION PERSONNEL WERE IN THEPROCESS OF SHUTTING DOWN RECEIPTS FROM APL'S METER STATION. DURING THISTIME, THE ETHYLENE PIPING CONNECTION TO THE HEAT EXCHANGER BEGAN LEAKING.THE EXCHANGER WAS ISOLATED AND THE CONNECTION TO THE PIPING WAS RE-TIGHTENED.IT IS BELIEVED THAT REPEATED HEATING AND COOLING OF THE HEAT EXCHANGER SINCETHE REPLACEMENT OF THE TUBE BUNDLE ON OCT. 21 CAUSED THE CONNECTION TO THEETHYLENE PIPING TO LOOSEN. WHEN THE CONNECTION WAS RE-TIGHTENED, THE UNITWAS ABLE TO BE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19910210 | 1991-11-03 | 30503 | GIANT INDUSTRIES INC | NO | 1991-11-30 | 1000 | UT | SAN JUAN | MONTEZUMA CREEK | NO |  | NO | TANK BATTERY IN MONTEZUMA CREEK, UTAH ADJACENT TO HIGHWAY 262 |  | TANK FARM | TANK |  | 1985 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2813.0555 | 5675.0692 | CRUDE OIL | 3 | 85 | 85 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TIM KINNEY - PROJECT MANAGER | 5056323306 | AN EQUIPMENT MALFUNCTION CAUSED A DIVERSION TANK TO OVERFLOW, SPILLING OIL INTO THE CONTAINMENT DIKE SURROUNDING THE TANK. NO INJURIES OR DAMAGE TO THE SURROUNDING AREA OCCURRED.
2017-09-29 08:50 | NO | NO | 19910211 | 1991-12-04 | 18273 | SHELL PIPELINE CORP | NO | 1991-10-30 | 1030 | TX | HARRIS | PASADENA | NO | N/A | NO | PASADENA TERMINAL #457, RANCHO PIPELINE SYSTEM |  | TANK FARM | TANK |  | 1951 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | CRUDE OIL | 1 | 5 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. D. HAYS, MGR. HEALTH, SAFETY & ENVIRONMENT | 7132416262 | TANK HIGH LEVEL ALARM FAILED TO ACTIVATE WHEN RELIEF VALVE SET POINT DRIFTEDBELOW SET POINT.
2017-09-29 08:50 | YES | NO | 19910212 | 1991-11-26 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1991-11-02 | 230 | CA | FRESNO |  | NO | N/A | NO |  |  | LINE PIPE | BOLTED FITTING | FLANGE GASKET | 1989 | OTHER | FAILED INSUL. FLANGE GASK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | CRUDE OIL | 1 | 500 | 450 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. KELLEY, NORTHERN DISTRICT MANAGER | 8053270110
2017-09-29 08:50 | YES | NO | 19910213 | 1991-12-16 | 2552 | COLONIAL PIPELINE CO | YES | 1991-11-13 | 1822 | AL | GREENE | EUTAW | NO | N/A | NO | AT COUNTY RD. NO. 231 |  | LINE PIPE | PIPE |  | 1962 | OTHER | SEE MEMO FIELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 1 | 1 | YES | NO | 36 | 0.28 | 52000 | WELDED |  | 584 | 150 | YES | 24 | 0 |  | 62 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A. COX, MGR. TECHNICAL AND REGULATORY | 4048412296 | ON NOV. 13, 1991, A CONTRACTOR WAS REMOVING A SECTION OF THE PIPELINE CASINGAT ALABAMA COUNTY RD. 231 TO INSPECT A POSSIBLE PIPELINE DENT IN THE 36"SEGMENT OF COLONIAL'S, HOUSTON, TX TO GREENSBORO, NC GASOLINE PIPELINE. AT1822P EST, WHILE CUTTING AWAY THE CASING WITH A TORCH, GASOLINE VAPORSESCAPING FROM THE PIPELINE IGNITED, CAUSING A SMALL FIRE. THIS FLAME WASIMMEDIATELY EXTINGUISHED. THE PIPELINE WAS SHUT DOWN, AND THE GREENE COUNTYSHERIFF'S DEPT. AND THE EUTAW FIRE DEPT. WERE NOTIFIED AT 1832P EST. THENATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT #96173) OF THE INCIDENT AT 2018EST ON NOV. 13, 1991.AFTER SECURING THE AREA, A PIPE SAW WAS THEN EMPLOYED TO COMPLETE THE REMOVALOF THE CASING AND EXPOSE THE PIPELINE. AN INSPECTION OF THE EXPOSED PIPELINEREVEALED THE SOURCE OF THE LEAK TO BE A 1 1/4" X 1/2" HOLE. ALTHOUGH THEHOLE HAD NOT COMPLETELY PENETRATED THE PIPE WALL, THE REMAINING SEGMENT HADAPPARENTLY CRACKED ALLOWING THE PRODUCT TO ESCAPE. TWENTY-ONE GALLONS OF GASWAS LOST FROM THE PIPELINE, OF WHICH 20 WERE RECOVERED. THE INSPECTION ALSOREVEALED A NEARBY 1 1/4" DEEP BUCKLE IN THE PIPELINE.BOTH OF THESE DEFECTS WERE REPAIRED BY THE INSTALLMENT OF ONE, 5 FT., FULLENCIRCLEMENT SLEEVE TO THE PIPELINE.THE EXACT CAUSE OF THE HOLE COULD NOT BE DETERMINED BY THE INVESTIGATION OFON-SITE PERSONNEL. THE SLEEVE PREVENTED A MORE THOROUGH INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19910214 | 1991-12-16 | 15774 | PORTAL PIPELINE CO | YES | 1991-12-05 | 1950 | MT | SHERIDAN |  | NO | N/A | NO | NE 1/4 SE 1/4 SECTION 23 T-33-N R-57E |  | LINE PIPE | PIPE | PIPE AND VALVE | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 6.63 | 0.13 | 0 | WELDED |  | 1000 | 250 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | ED JOHNSON, FIELD SUPT. | 7018521087 | PICKUP RAN OFF ROAD, TRAVELLED APPROX. 400' INTO FIELD BEFORE STRIKINGPIPELINE, KNOCKING OFF A 1" VALVE ASSEMBLY CAUSING OIL TO ESCAPE.
2017-09-29 08:50 | YES | NO | 19910215 | 1991-12-16 | 19226 | TEXACO PIPELINE INC | NO | 1991-11-10 | 604 | TX | DALLAS | DALLAS | NO | N/A | NO | APPROX. 1600' SOUTH OF VENT ON SOUTH SIDE OF I-30. |  | LINE PIPE | PIPE |  | 1947 | FAILED PIPE | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 343733 | 276268.5747 | 557345.3044 | DIESEL FUEL | 1 | 2623 | 1802 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1050 | 779 | YES | 0 | 1000 |  | 48 | EXTERNAL | Null | YES | OTHER | GENERAL | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. MINER, DISTRICT MANAGER | 7139534260 | DALLAS BOOSTER STATION LOW SUCTION ALARM SOUNDED AT 6:04A. THE DENVERCONTROLLER, OBSERVING THAT THE SUCTION PRESSURE AT DALLAS WAS ABNORMALLY LOW,ISSUED THE COMMAND TO SHUT THE PIPELINE DOWN AT 6:05:28A. ALL PUMP STATIONSWERE SHUT DOWN IN SEQUENCE. AT 6:06:10 ALL PUMPING EQUIPMENT ON THE PIPELINEWAS DOWN. GROUND CREWS AND AIR PATROL WERE CALLED OUT AT 6:05A. THE BLOCKVALVE AT I-20 WAS CLOSED AT 9:00A. LEAK WAS LOCATED BY GROUND CREWS AT2:45P. CALLED OUT EMTECH ENVIRONMENTAL SERVICES FOR CLEANUP. LEAK REPAIREDAT 3:45A NOV. 11, 1991, AND THE PIPELINE WAS RETURNED TO SERVICE AT 4:02A.
2017-09-29 08:50 | YES | NO | 19910216 | 1991-12-16 | 26086 | SEADRIFT PIPELINE CORP | NO | 1991-11-22 | 1630 | TX | WHARTON |  | NO | N/A | NO | APPROX. 1 MI SOUTH OF FARM RD. 1300 AND 6 MI NORTH OF LOUISE, TX. |  | LINE PIPE | OTHER | NOT LISTED ON FORM | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20800 | 16717.5871 | 33726.1256 | L. P. G. | 2 | 550 | 0 | NO | NO | 4 | 0.24 | 3500 | WELDED |  | 1790 | 825 | YES | 24 | 2240 |  | 62 | EXTERNAL | Null | YES | OTHER | ELECTROLYTIC | NO DATA |  | Null | NO DATA |  | Null | Null | JACK L. WYATT, ENVIRONMENTAL MGR. | 5127883176 | A DEER HUNTER REPORTED A POSSIBLE PIPELINE LEAK AFTER OBSERVING GAS BUBBLESCOMING THROUGH SURFACE WATER ALONG THE PIPELINE RIGHT-OF-WAY. THE LINE WASSHUT IN AND PURGED W/ NITROGEN. THE LEAKING SECTION OF PIPE WAS REPLACED ANDTHE PIPELINE WAS RETURNED TO SERVICE. EXAMINATION OF THE PIPE REVEALED ASMALL HOLE (APPROX. 1/16" DIAMETER) RESULTING FROM EXTERNAL CORROSION.ACTIONS HAVE BEEN TAKEN TO IMPORVE THE CATHODIC PROTECTION OF THE PIPE.
2017-09-29 08:50 | YES | NO | 19910217 | 1991-12-16 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1991-11-20 | 1610 | TX | RUNNELS |  | NO | N/A | NO | APPROX. 2 MI SOUTH OF STATE HWY. 158, 0.8 MI WEST OF A COUNTY ROAD AND 8 MI NW OF THE TOWN OF BALLINGER; 0.25 MI EAST OF QUARRY CREEK. |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | CRUDE OIL | 1 | 204 | 192 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1050 | 744 | YES | 8 | 1335 | 10 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA | N/A | Null | NO DATA |  | Null | Null | BOB REED, REGULATORY COMPLIANCE SUPV. | 9152645414 | FINA'S BIG SPRING (TX) PIPELINE CONTROL CENTER WAS NOTIFIED BY LANDOWNER (RONEDDINGTON) AT 4:10P ON WED., NOV. 20, 1991, THAT AN OIL LEAK HAD OCCURRED ONHIS LAND FROM FINA'S PIPELINE. PIPELINE REPAIR PERSONNEL WERE ON SCENEWITHIN 2.5 HOURS OF THE RECEIPT OF THE REPORT. THE LEAKAGE ORIGINATED WITHINA RANCH ROAD ON THE PROPERTY, FLOWED APPROX. 282' DOWN THE ROAD, RAN ACROSSPASTURAGE LAND APPROX. 180', FORMED A POOL APPROX. 30' IN DIAMETER, THENCONTINUED FLOWING A FURTHER 600' BEFORE BEING CONTAINED. LEAKAGE AFFECTED 2PROPERTIES. PIPELINE REPAIR CONSISTED OF APPLICATION OF A 24" LONG PATCHAPPLIED TO THE BOTTOM QUARTER OF THE PIPE. POOLED OIL WAS PICKED UP BYVACUUM TRUCK AND TAKEN TO PIPELINE FACILITIES AT BRONTE STATION. CLEANUPCONSISTED OF SOME BURNING OFF OF OIL SOAKED VEGETATION (TACB AND LANDOWNERAPPROVED) AND REMOVAL OF OIL-CONTAMINATED SOILS (APPROX. 500 CY). THE SOILSWILL BE DISPOSED OF BY MIXING WITH CLEAN SOIL AND CALICHE AND APPLIED TORANCH ROADS, AS PER THE REQUEST OF THE LANDOWNER (EDDINGTON) AND BY APPROVALOF THE TEXAS RAILROAD COMMISSION. THIS WORK WILL BE DONE BY CONTRACT LABORAND EQUIPMENT, AND IS ESTIMATED TO BE COMPLETED BY DEC. 1ST.
2017-09-29 08:50 | YES | NO | 19910218 | 1991-12-16 | 4906 | EXXON PIPELINE CO | NO | 1991-10-25 | 1615 | TX | HARRIS |  | NO | N/A | NO | SUGARLAND TO PIERCE JUNCTION PIPELINE SURVEY STATION 488+26 (NEAR INTERSECTION OF SOUTH POST OAK AND OREM). |  | LINE PIPE | PIPE |  | 1928 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9644.7618 | 19457.3802 | CRUDE OIL | 1 | 250 | 240 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 573 | 100 | YES | 8 | 771 | 10 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | J. B. HOLT, ENVIRONMENTAL/REGULATORY COMPLIANCE MGR. | 7136565521 | IN THE PROCESS OF LAYING A 42" WATER LINE, A CONSTRUCTION COMPANY TRACK HOESTRUCK AND GOUGED A HOLE IN OUR 8" CRUDE OIL PIPELINE. THE SPILLED OIL WASCONTAINED IN THE WATER LINE DITCH. VACUUM TRUCKS WERE USED TO PICK UP THEOIL FROM THE DITCH. FINAL CLEANUP WAS ACCOMPLISHED AND THE LINE RETURNEDTO SERVICE.
2017-09-29 08:50 | YES | NO | 19910219 | 1991-12-16 | 4906 | EXXON PIPELINE CO | NO | 1991-11-05 | 1355 | TX | DALLAS | DALLAS | NO | N/A | NO | PIPELINE SEC. 524+88. THE SPILL WAS 6 MI SOUTH OF EPC'S IRVING TERMINAL NEAR THE INTERSECTION OF DUNCANVILLE AND KEIST RDS. (BAYTOWN-IRVING PRODUCTS SYSTEM). |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 412000 | 331136.8206 | 668036.7186 | GASOLINE | 3 | 560 | 430 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 1485 | 200 | YES | 8 | 1857 |  | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | J.B. HOLT, ENVIRONMENTAL/REGULATORY COMPLIANCE MGR. | 7136565521 | AT 1355, MANHATTAN CONSTRUCTION REPORTED A LEAK ON EPC'S WACO TO IRVINGPRODUCTS PIPELINE. CONTRACTOR (MANHATTAN CONSTRUCTION) IS CONSTRUCTING APARKING LOT ADJACENT TO EPC AND A BULLDOZER PUNCTURED EPC'S LINE CAUSINGUNLEADED GASOLINE TO SPILL. SYSTEM WAS SHUTDOWN A 1359 HRS. BY 1430 HRS.,LOCAL FIRE DEPTS. HAD CONSTRUCTED A CONTAINMENT DAM. EPC HAD PERSONNEL ON-SITE BY 1500 HRS. TO BEGIN CLEANUP AND REPAIR OPERATIONS. PERMANENT REPAIRSCOMPLETED BY 0830 HRS. ON 11-6-91. CLEANUP OPERATIONS ARE PRESENTLYCONTINUING. SYSTEM ON-LINE BY 1100 HRS ON SAME DAY OF COMPLETED REPAIR.
2017-09-29 08:50 | YES | NO | 19910220 | 1991-12-16 | 4906 | EXXON PIPELINE CO | YES | 1991-10-30 | 100 | TX | SAN PATRICIO | INGLESIDE | NO | N/A | NO | TANK 154 AT INGLESIDE STATION TANK FARM. |  | TANK FARM | TANK | ROOF, DRAIN, HOSE & VALVE | 1937 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 135000 | 108503.5699 | 218895.5267 | CRUDE OIL | 1 | 700 | 680 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | J.B. HOLT, ENVIRONMENTAL/REGULATORY COMPLIANCE MGR. | 7136565521 | HEAVY RAINS OF 12"-14" WHICH OCCURRED BETWEEN 1:00A & 3:00A ON OCT. 30, 1991,SANK EXTERNAL PAN FLOATING ROOF. ROOF DRAINS LEFT OPEN BECAUSE OF RAINFORECAST, BUT WERE OVERWHELMED. CRUDE FLOWED OUT ROOF DRAINS AFTER ROOFSUNK. ALL CRUDE WAS CONTAINED IN STATION FIREWALLS - NO OIL ESCAPED EXXONPROPERTY.
2017-09-29 08:50 | YES | NO | 19910221 | 1991-12-23 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1991-11-19 | 1212 | TX | HUTCHINSON |  | NO | N/A | NO | SECT. 27, BLOCK Y A & B E. TUMILSON SURVEY |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2889 | 2321.9764 | 4684.3643 | ANHYDROUS AMMONIA | 2 | 212 | 0 | NO | NO | 6 | 0.19 | 2610 | WELDED |  | 1420 | 1077 | YES | 24 | 1780 | 4 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | 3RD PARTY WHEN EXCAVATING | Null | OTHER | PIPELINE WARNING SIGNS | NO | NO | S. F. ISAACS, PRESIDENT | 9185811800
2017-09-29 08:50 | NO | NO | 19910222 | 1991-12-23 | 26148 | WITCO CHEMICAL CORP | NO | 1991-12-16 | 1045 | CA | KERN | OILDALE | NO | N/A | NO | 300 YDS EAST OF AIRPORT DR., 75 FT NORTHOF SEVENTH STANDARD RD. |  | LINE PIPE | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2009.3254 | 4053.6209 | CRUDE OIL | 1 | 6 | 2 | NO | NO | 6 | 0.25 | 340 | WELDED |  | 340 | 20 | YES | 4 | 420 | 11 | 90 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES LANKFORD, SUPT. TRANSPORTATION | 8053937110
2017-09-29 08:50 | YES | NO | 19910223 | 1991-12-23 | 443 | AMOCO PIPELINE CO | YES | 1991-11-21 | 950 | IN | LAKE | HAMMOND | NO | N/A | NO | CALUMET "A" PUMP STATION - 129TH ST. ANDCALUMET AVE. |  | PUMPING STATION | OTHER | 1/2" 80 PRESS. GUAGE PIPE | 1977 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | XYLENE | 3 | 100 | 95 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | SLAG-ACIDIC CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | R. A. STAHL - AREA MANAGER | 2197382384 | LEAK OCCURRED IN AN UNDERGROUND 1/2" SCH. 80 GUAGE PRESSURE LINE AND SHOWEDUP IN AN ADJACENT EXCAVATION. SYSTEM WAS UNDER CATHODIC PROTECTION BUTAPPEARED TO CORRODE BECAUSE OF ACIDIC SLAG THAT IT WAS BURIED IN.
2017-09-29 08:50 | YES | NO | 19910224 | 1991-12-27 | 18273 | SHELL PIPELINE CORP | YES | 1991-11-20 | 1030 | TX | ECTOR | ODESSA | NO | N/A | NO | ODESSA-EL PASO 6" PRODUCTS LINE; SE 1/4,SECTION 33, T-2-S, BLOCK 43. |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 22267 | 17896.6592 | 36104.7903 | GASOLINE | 3 | 325 | 155 | NO | NO | 6 | 0.28 | 46000 | WELDED |  | 2160 | 2000 | YES | 36 | 2200 |  | 58 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | M. D. HAYS, MGR. HEALTH, SAFETY & ENVIRONMENT | 7132416262 | 130 BARRELS OF PRODUCT EVAPORATED AND 40 BARRELS SOAKED INTO THE SOIL. PIPEWAS DAMAGED BY 3RD PARTY, POSSIBLY DURING LANDOWNER BUSINESS ACTIVITIES.
2017-09-29 08:50 | NO | NO | 19910225 | 1991-12-27 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1991-11-17 | 831 | CA | SAN JOAQUIN | STOCKTON | NO | N/A | NO | SFPP TERMINAL'S SUMP AT 2947 NAVY DRIVE,STOCKTON, CA 95206. |  | TANK FARM | OTHER | SUMP | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | GASOLINE | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M ABBOUD, SEN. V.P., OPERATIONS & ENGINEERING | 2134867720 | OPERATOR OVERFILLED SUMP. OES AND COAST GUARD WERE ADVISED. WET SPOT 2'-3'CREATED AND REMOVED NOV. 19, 1991.
2017-09-29 08:50 | YES | NO | 19910226 | 1991-12-27 | 10191 | KERR - MCGEE REFINING CORP | NO | 1991-12-09 | 1430 | OK | CADDO | CYRIL | NO | N/A | NO | FROM INTERSECTION OF HWY 19 & HWY 8 IN CYRIL, OK GO 0.34 MI NORTH, ON EAST SIDE OF HWY 8 |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8841.0316 | 17835.9318 | CRUDE OIL | 1 | 200 | 115 | NO | NO | 4 | 0.24 | 3610 | WELDED |  | 1530 | 375 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.B. HOOVER, GENERAL MGR OF PIPELINE OPER. & ENGINEERING | 4052703256 | PIPELINE LEAK WAS ON A 4" LATERAL THAT IS NO LONGER IN USE. THE CORROSIONLEAK WAS APPROX. ONE INCH FROM A GIRTH WELD BETWEEN THE 4" PIPE AND A 90DEGREE ELBOW. THE CAUSE OF THIS CORROSION LEAK IS SUSPECTED TO BE CATHODICSHIELDING FROM DISBONDED COATING. PERMANENT REPAIR CONSISTED OF REMOVING THE4" LATERAL.
2017-09-29 08:50 | YES | NO | 19910229 | 1991-12-19 | 13131 | CONOCO INC | YES | 1991-12-05 | 830 | WY | NIOBRARA |  | NO | N/A | NO | SEC 31, T36N, R65W |  | TANK FARM | OTHER | 1/2" SCHEDULE 80 NIPPLE | 0 | OTHER | METAL FATIGUE OF NIPPLE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2009.3254 | 4053.6209 | CRUDE OIL | 1 | 400 | 390 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DWIGHT D. JACKSON, MGR. OF OPERATIONS ENGINEERING | 7132932130 | A 1/2" X 2" SCHEDULE 80 SCREWED NIPPLE W/ A 1/2" SCREWED VALVE FAILEDRESULTING IN A CRACKED NIPPLE IN THE THREAD AREA. THIS NIPPLE WAS LOCATEDON THE DOWNSTREAM SIDE OF THE TANK FARM BOOSTER PUMP LOCATED WITHIN THETANK DIKE AT LANCE CREEK PUMP STATION. UPON FURTHER INVESTIGATION, IT WASDISCOVERED THAT A KEY IN THE COUPLING OR THE COUPLING HAD FAILED, RESULTINGIN EXCESSIVE VIBRATION ON THE BOOSTER PUMP.
2017-09-29 08:50 | YES | YES | 19910230 | 1991-12-23 | 15490 | PHILLIPS PIPE LINE CO | YES | 1991-11-19 | 150 | TX | UPTON |  | NO | N/A | NO | BENEDUM-SWEENY "LINE EZ"-MP 12-23+44. SEC. 19, BLOCK 4, UNIVERSITY LAND SURVERY. EAST OF RANKIN, APPROX 8-10 MI ON HWY 67, THEN 4 MI S ON PIPE RIGHT-OF-WAY. |  | LINE PIPE | PIPE |  | 1911 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 2 | 0 | 2 | 2000 | 1607.4603 | 3242.8967 | NATURAL GAS LIQUID | 2 | 1 | 0 | YES | NO | 10.75 | 0.19 | 60000 | OTHER |  | 1140 | 5 | YES | 8 | 2050 | 7 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B. L. THORMAN, MGR OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | WELDERS WERE COMPLETING A TIE-IN WELD. DUE TO LIQUIDS TRAPPED BETWEEN THEVAPOR BARRIER AND THE VENT, SUFFICIENT PRESSURE BUILT UP TO CAUSE A FAILUREIN THE BARRIER. THE VAPORS RELEASED IGNITED AND RESULTED IN BURNS TO 2WELDERS. THE WELDERS WERE HOSPITALIZED FOR 3 & 4 DAYS AND 7 & 8 DAYS OF
2017-09-29 08:50 | NO | NO | 19910231 | 1991-12-09 | 12627 | MOBIL OIL CORP | NO | 1991-12-01 | 1320 | CA | LOS ANGELES | LONG BEACH | NO | N/A | NO | 1705 BURNETT ST., LONG BEACH, CA |  | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 12859.6824 | 25943.1735 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 8.63 | 0.32 | 1865 | WELDED |  | 784 | 448 | YES | 8 | 1020 | 10 | 84 | EXTERNAL | Null | YES | OTHER | CONCENTRATION CELL | NO DATA |  | Null | NO DATA |  | Null | Null | S. S. SOBEY, MGR OF OPERATIONS | 3104937237 | THIRD PARTY CALLED IN POSSIBLE LEAK AT THE ABOVE SITE. AFTER EXCAVATION WEFOUND A SMALL ISOLATED EXTERNAL CORROSION LEAK AND REPAIRED IT BY FULLWRAPPING THE PIPE. ALL CONTAMINATES WERE REMOVED AND PROPERLY DISPOSED OF.
2017-09-29 08:50 | NO | NO | 19910232 | 1991-12-20 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1991-12-05 | 1130 | LA | UNION |  | NO | N/A | NO | TOWNSHIP: 20N, SECTION: 21, RANGE: 3E, MILEPOST: 43-5.74 CHAINING STA; 303+07, UNION PARISH, LA. |  | LINE PIPE | VALVE |  | 1969 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | VALVE GASKET FAILURE | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 15120 | 12152.3998 | 24516.299 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM SIMMONS, DIVISION MGR | 3144865488 | LANDOWNER NOTIFIED PRODUCT MOVEMENT COORDINATOR OF NH3 ODOR AROUND VALVE NEARHIS AT 09:45. DISPATCHER NOTIFIED PERSONNEL WHO WENT TO SITE AND VERIFIEDODOR WAS COMING FROM A BURIED 6" 900# M&J BLOCK VALVE. EQUIPMENT CALLED INTO REPAIR VALVE AND DETERMINED COMPLETE VALVE NEEDED TO BE DUG OUT. BLOCKEDIN THE 6" LINE AT 23:30 TO BEGIN VALVE REPAIR. BEGAN PROCEDURES TO STOPPLEON EACH SIDE OF VALVE TO MAKE REPAIRS. LINE RETURNED TO SERVICE AT 05:30 ON12-7-91. NO PRODUCT RELEASED IN OR NEAR ANY STREAMS OR BODIES OF WATER.MINIMAL DAMAGE TO FOILAGE AROUND VALVE SITE.
2017-09-29 08:50 | NO | NO | 19910233 | 1991-12-20 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1991-11-30 | 1100 | LA | WINN |  | NO | N/A | NO | SECT: 33, TOWNSHIP: 11N, RANGE: 1E, MILEPOST: 1-57.23, CHAINING STA: 3021+63; WINN PARISH, LA |  | LINE PIPE | PIPE |  | 1969 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 3700 | 2973.8015 | 5999.3589 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1340 | 820 | YES | 36 | 1961 | 9 | 69 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM SIMMONS, DIVISION MGR | 3144865488 | RESIDENTS NOTIFIED EMPLOYEE OF NH3 ODOR ON 11-30-91. EMPLOYEE VERIFIED ODORAND REPORTED TO THE PRODUCT MOVEMENT COORDINATOR AT 12:20. PERSONNEL ANDEQUIPMENT WERE DISPATCHED TO THE SITE. THE RURAL LOCATION OF THE RELEASESITE AND HEAVY RAIN KEPT THE PIPE FROM BEING CLAMPED UNTIL 09:45 ON 12-1-91.NO PRODUCT RELEASED INTO OR NEAR ANY STREAMS OR BODIES OF WATER. SLIGHTDAMAGE DONE TO SOME TREES SURROUNDING THE RELEASE SITE.
2017-09-29 08:50 | YES | NO | 19910234 | 1991-01-02 | 443 | AMOCO PIPELINE CO | NO | 1991-12-12 | 1435 | TX | HARRIS |  | NO | N/A | NO | HOECHST CELANESE CLEAR LAKE PLANT |  | LINE PIPE | BOLTED FITTING | ORFICE FITTING | 1975 | OTHER | BONNET GASKET LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1205.5952 | 2432.1725 | NATURAL GAS LIQUID | 2 | 43 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES P. BLACK - COMPLIANCE SUPERVISOR | 4099386900
2017-09-29 08:50 | YES | NO | 19920001 | 1992-01-09 | 15851 | PRIDE REFINING INC | NO | 1991-12-24 | 1815 | TX | RUNNELS | WINTERS | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1984 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | CRUDE OIL | 1 | 3150 | 2250 | NO | NO | 8 | 0.19 | 42000 | WELDED |  | 300 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON PIPELINE MANAGER | 9156748231
2017-09-29 08:50 | YES | NO | 19920002 | 1992-01-27 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1991-12-14 | 130 | TX | HALE | EDMONSON | NO |  | NO |  |  | LINE PIPE | OTHER | NON SPECIFIED | 1960 | OTHER | UNKNOWN AT THIS TIME | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10492 | 8432.7367 | 17012.236 | NATURAL GAS LIQUID | 2 | 685 | 0 | NO | NO | 8.63 | 0.22 | 2641 | WELDED |  | 1550 | 1441 | YES | 24 | 1987 | 4 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S F ISAACS - PRESIDENT | 9185811800
2017-09-29 08:50 | NO | NO | 19920003 | 1992-05-22 | 9175 | JAYHAWK PIPELINE CORP | YES | 1992-05-16 | 1700 | KS | MORTON |  | NO |  | NO | SE/4 SECTION 28-T34S-R40W MORTON COUNTY, KS APPROXIMATELY 3 1/2 MILES SOUTH OF ROLLA, KS IN RURAL AREA. |  | LINE PIPE | OTHER | NON SPECIFIED | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4159 | 3262.8423 | 6582.4708 | CRUDE OIL | 1 | 45 | 45 | NO | NO | 6.63 | 0.19 | 35000 | WELDED |  | 1250 | 60 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | API'S PIPELINE PUBLIC EDU | YES | NO | MARK E MOORE - PRESIDENT | 3162913254 | THE ACTUAL NUMBER OF BARRELS OF COMMODITY RECOVERDIS 208 (AFTER DRIAN FOR REPAIRS) ONLY 45 COULD BE ENTER INTO THE REPORTS SINCE 208 IS GREATER THAN NUMBER SPILLED. JAYHAWK PIPELINE WAS NOTIFIED BY TELEPHONE AT 1700, MAY 16, 1992 BY OPERATOR OF FRONT END LOADER THAT HE HAD PUNCTURED OUR PIPELINE WHILE DIGGING A HOLE ON THE FARMER'S PROPERTY TO BURY DEBRIS. THE LEAK LOCATION WASIN A RURAL AREA IN MORTON COUNTY, 3 1/2 MILE SOUTH OF ROLLA, KS. PIPELINE "WARNING" MARKERS WITH THE COMPANY IDENTIFICATION AND EMERGENCY TELEPHONE NUMBER WERE ON EACH SIDE OF ROAD AT THE ACCIDENT LOCATION. THE LINE WAS SHUT DOWN BY 1730. BLOCK VALVES EAST AND WEST OF THE LEAK LOCATION WERE CLOSED B 1900. DRAIN UP OF THE ISOLATED SECTION OF PIPELINE TEMPORARY REPAIR WAS COMPLETED BY 2300. THE DAMAGED PIPE WAS REMOVES AND A REPLACEMENT POINT 18' OF PRETESTED 6" PIPE WAS INSTALLED BY 1100, MAY 17, 1992. THE PUNCTURE WAS ON THE TOPSIDE OF THE PIPE. AN ESTIMATED 12 BARRELS OF CRUDE WAS ABSORBED BY THE SANDY SOIL IN THIS AREA.
2017-09-29 08:50 | NO | NO | 19920006 | 1992-01-17 | 443 | AMOCO PIPELINE CO | YES | 1991-12-18 | 1200 | IL | COOK | LANSING | NO |  | NO |  |  | LINE PIPE | TANK |  | 1988 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | LEAKING GASKET | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1607.4603 | 3242.8967 | XYLENE | 3 | 1 | 1 | NO | NO | 8 | 0.32 | 0 | FLANGED |  | 1440 | 1350 | YES | 4 | 1879 | 6 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R A STAHL - AREA MANAGER | 2197382384
2017-09-29 08:50 | YES | NO | 19920007 | 1992-01-17 | 19585 | TRANS - MOUNTAIN OIL PIPELINE CO | YES | 1991-12-11 | 1200 | WA | WHATCOM |  | NO |  | NO |  |  | PUMPING STATION | WELDING FITTING |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 56261.1103 | 113501.3842 | CRUDE OIL | 1 | 84 | 30 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | WORK CONDUCTED UNDER OPER | Null | YES
2017-09-29 08:50 | NO | NO | 19920008 | 1992-01-17 | 2552 | COLONIAL PIPELINE CO | YES | 1991-12-09 | 1510 | MD | CARROLL | WOODBINE | NO |  | NO |  |  | TANK FARM | VALVE |  | 1963 | OTHER | INSUFFICIENT SEALING OF V | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | FUEL OIL | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J A COX - MANAGER TECHNICAL & REGULATORY | 4048412296
2017-09-29 08:50 | NO | NO | 19920009 | 1992-05-06 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-04-27 | 1330 | AL | TALLADEGA |  | NO |  | NO | PLANTAION'S SILVER RUN PUMPING STATION LOCATED AT 1810 SILVER RUN ROAD MUNFORD, ALABAMA. |  | PUMPING STATION | BOLTED FITTING |  | 1968 | OTHER | INSULATING GASKET FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 11400 | 8943.5927 | 18042.8389 | GASOLINE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VICE PRESIDENT - OPERATIONS | 4043645916 | DUE TO THE NATURE OF THE LEAK (SMALL FLANGE LEAK) IT IS IMPOSSIBLE TO PROVIDE AN ACCURATE ESTIMATE OF THE TOTAL AMOUNT OF PRODUCT RELEASED. ON MONDAY, APRIL 27, 1992, ALPHA LEAK DETECTION, INC. WAS PERFORMING A LEAK DETECTION SURVEY ON THE STATION PIPING AT PLANTATION'S SILVER RUN STATION. THE SURVEY WAS BEING PERFORMED DUE TO PRODUCT BEING FOUND IN A MONITORING WELL AT SILVER RUN STATION. A LEAK WAS DETECTED ON THE INCOMING 30" BLOCK VALVE. THE BLOCK VALVE WAS EXCAVATED AND A LEAKING INSULATING GASKET ON THE BLOCK VALVE WAS FOUND AT 13:30 CDST. THE 30" PIPELINE WAS TAKEN OUT OF SERVICE AND THE INSULATING GASKET REPLACED. NRC REPORT NO. 115802.
2017-09-29 08:50 | NO | NO | 19920010 | 1992-01-14 | 2552 | COLONIAL PIPELINE CO | YES | 1991-12-12 | 940 | MD | CARROLL |  | NO |  | NO |  |  | TANK FARM | LONGITUDINAL WELD | 1" NIPPLE BETWEEN MAINLIN | 1984 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | GASOLINE | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J A COX - MANAGER TECHNICAL & REGULATORY | 4048412296
2017-09-29 08:50 | YES | NO | 19920011 | 1992-01-09 | 15498 | PHILLIPS GAS PIPELINE CO | YES | 1991-12-12 | 1515 | TX | GILLESPIE |  | NO |  | NO | BENEDUM-SWEENY "LINE EZ" - MP 191- 3+65, BLOCK 927, H&GNRR SURVEY. APPROXIMATELY 16 MILES N OF FREDERICKSBURG, TX, ALONG COUNTY RD. FM 2323. EAST OF FM2323 RD |  | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 20093.2537 | 40536.2087 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 10.75 | 0.25 | 42000 | WELDED |  | 910 | 240 | YES | 24 | 1310 | 4 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | B L THORMAN - MANAGER ENGINEERING & TECHNICAL SERVICES | 9186614721
2017-09-29 08:50 | NO | NO | 19920012 | 1992-01-13 | 2552 | COLONIAL PIPELINE CO | YES | 1991-12-09 | 720 | SC | EDGEFIELD | NORTH AUGUSTA | NO |  | NO | COLONIAL PIPELINE COMPANY'S NORTH AUGUSTA DELIVERY FACILITY. |  | TANK FARM | TANK | SUMP | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | TRANSMIX (PART. REFINED PETRO) | 1 | 3 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MANAGER OF TECHNICAL AND REGULATORY | 4048412296
2017-09-29 08:50 | YES | NO | 19920013 | 1992-08-10 | 18273 | SHELL PIPELINE CORP | YES | 1992-07-09 | 850 | LA | LIVINGSTON | PINE GROVE | NO |  | NO | SECTION 9, T-5-S, R-4-E 4 MILES S PINE GROVE. CAPLINE PIPELINE SYSTEM - PINE GROVE STATION. |  | PUMPING STATION | OTHER | NON SPECIFIED | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | CRUDE OIL | 1 | 60 | 58 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414506 | WHILE EXCAVATING A 24-INCH STATION DISCHARGE VALVE, THE BACKHOE BROKE A ONE-INCH NIPPLE CONNECTION ON THE DISCHARGE LINE, WHICH CAUSED THE RELEASE.
2017-09-29 08:50 | YES | NO | 19920014 | 1992-01-10 | 2337 | CHEVRON PIPELINE CO | YES | 1991-12-09 | 940 | UT | DAVIS |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1949 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 80373.0147 | 162144.8346 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 8.63 | 0.25 | 40000 | WELDED |  | 1870 | 1860 | YES | 8 | 2350 | 9 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN R MOON - AREA SUPERVISOR | 8015397293
2017-09-29 08:50 | YES | NO | 19920015 | 1992-01-06 | 15674 | PLANTATION PIPE LINE CO | YES | 1991-12-08 | 730 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO |  |  | TANK FARM | GIRTH |  | 1954 | FAILED WELD | ALSO MALFUNCTION OF CONTR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 23308.1743 | 47022.002 | TURBINE FUEL | 3 | 1256 | 1256 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M COOK - VICE PRESIDENT-OPERATIONS | 4043645916
2017-09-29 08:50 | YES | NO | 19920016 | 1992-01-06 | 809 | ARCO PIPE LINE CO | YES | 1991-11-25 | 1045 | KS | MONTGOMERY |  | NO |  | NO | APPRO. 3-1/2 MILES W AND S OF INDEPENDECE, KS. IN THE NE/4 SEC. 1, T33S, R14E, MONTGOMERY COUNTY KS |  | LINE PIPE | PIPE |  | 1923 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 80 | 60 | NO | NO | 8.63 | 0.32 | 25000 | NO DATA |  | 700 | 250 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | F L NEELEY - V P/MGR PRODUCTS BUS. UNIT | 7139865378
2017-09-29 08:50 | YES | NO | 19920017 | 1992-01-22 | 2552 | COLONIAL PIPELINE CO | YES | 1991-12-19 | 2151 | SC | GREENVILLE | SIMPSONVILLE | NO |  | NO | BETWEEN JONES MILL ROAD & CAROLINA SPRINGS COUNTRY CLUB AT DURBIN CREEK |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 200932.5368 | 405362.0866 | FUEL OIL | 1 | 13100 | 12600 | NO | NO | 36 | 0.28 | 52000 | WELDED |  | 500 | 423 | YES | 24 | 719 | 1 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES A COX - MANAGER TECHNICAL & REGULATORY | 4048412296
2017-09-29 08:50 | NO | NO | 19920018 | 1992-01-22 | 4904 | EXXON CO USA | NO | 1991-12-22 | 1530 | LA |  |  | YES | LAT 29 7' 12.1"NLONG89 38 | YES |  |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 37000 | 29738.0154 | 59993.5888 | CRUDE OIL | 1 | 7 | 3 | NO | NO | 10.75 | 0.37 | 35000 | WELDED |  | 1426 | 100 | YES | 24 | 1950 | 10 | 56 | INTERNAL | Null | YES | OTHER | PROBABLE CAUSE - SULFATE | NO DATA |  | Null | NO DATA |  | Null | Null | I S BROOKS - SR SUPERVISING ENGINEER | 5045614753 | ON DECEMBER 22, 1992, A SHEEN WAS OBSERVED IN THE GULF OF MEXICO IN WEST DELTA BLOCK 31. THE SOURCE OF THE SHEEN WAS DETERMINED TO BE THE EXXON COMPANY, U.S.A. TEN INCH OIL PIPELINE (MMS SEGMENT NO. 718) BETWEEN THE WEST DELTA 31E AND 31F PLATFORMS. THE PIPELINE WAS ISOLATED, BLED DOWN AND SUBSEQUENTLY PIGGED TO REMOVE OIL FROMT HE LINE. (THE LINE NORMALLY CONTAINS APPROXIMATELY60 TO 80% WATER.) FULL ENCIRCLEMENT CLAMPS WERE INSTALLED ON THE PIPELINE AT APPROXIMATELY 400' AND 1200 FEET FROM THE "F" PLATFORM UPON DISCOVERING PINHOLE LEAKS AT THESE EESPECTIVE LOACTIONS. THE CAUSE OF THE LEAKS ID BELIEVED TO BE INTERNAL CORROSION RESULTING FRLOM SULFATE REDUCING BACTERIA. SUBSEQUENT TO CLAMPING THE PIPELINE, IT WAS SUCCESSFULLY GAS TESTED FOR 12 HOURS TO60 PSI OVER DECEMBER 26 AND 27, AND RETURNED TO SERVICE ON DECEMBER 28, A COPY OF THE TEST CHART IS ATTACHED. THE SUBJECT PIPELINE ACCIDENT WAS REPORTED BY TELEPHONE TO THE NATIONAL RESPONSE CENTER (REPORT NO. 100693) AS WELL AS TO THE MINERALS MANAGEMENT SERVICE NEW ORLEANS DISTRICT AND MINERALS MANAGEMENT SERVICE REGIONAL PIPELINE SECTION ON DECEMBER 23, 1991 AND A FOLLOW-UP WRITTEN REPORT HAS BEEN SENT TO MMS. AS A RESULT OF THE PIPELIEN LEAK, AN ESTIMATED 6.5 BARRELS OF CRUDE OIL SPILED INTO THE GULF OF MEXICO WITH AN ESTIMATED 2.9 BARRELS RECOVERED.
2017-09-29 08:50 | YES | NO | 19920019 | 1992-03-26 | 4805 | EXPLORER PIPELINE CO | YES | 1992-03-01 | 1233 | TX | MONTGOMERY |  | NO |  | NO | JAMES A PARKER SURVEY A-418. A A/1 MILE N OF HIGHWAY 1960 AND 1 1/2 MILE WEST OF HIGHWAY 59. |  | LINE PIPE | VALVE |  | 1971 | OTHER | APPARENT CRACK IN VALVE M | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 280000 | 219667.1882 | 443157.4456 | GASOLINE | 1 | 474 | 430 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROD E SANDS, VICE PRESIDENT - OPERATIONS | 9184935106 | ON MARCH 1, 1992, AT 12:33 THE HARRIS COUNTY SHERIFF'S DEPARTMENT CALLED EXPLORER'S CONTROL CENTER IN TULSA, OKLAHOMA TO REPORT A "FENCE POST" FIRE IN THE VICINITY OF EXPLOER'S 28" PIPELINE CROSSING OF SPRING CREEK, MILEPOST 92:19AND 92.4. AT 12:43 THE HARRIS COUNTY FIRE DEPARTMENT CALLED TO REPORT A PIPELINE FIRE NEAR EXPLORER'S MILE POST MARKER AT SPRING CREEK AND WERE TRYING TO IDENTIFY IF THE FIRE WAS ON ONE OF THREE PIPELINES IN THE AREA. EXPLORER'SOPERATIONS COORDINATOR CONTACTED EXPLORER EMERGENCY RESPONSE PERSONNEL AND IMMEDIATELY INITIATED SHUT DOWN OF THE 28" PIPELINE AT 12:44 AND DECREASED PRESSURE AT THE SITE BY OPERATING DOWNSTREAM PUMPS AS LONG AS POSSIBLE. REMOTE CONTROLLED BLOCK VALVES AT MILEPOSTS 87.9 AND 101.4 WERE COMMANDED TO CLOSE AT 12:49 AND 12:58 RESPECTIVELY. THE FIRST EXPLORER EMPLOYEE ARRIVED ON THE SITE AT 13:35 AND CONFIRMED IT WAS EXPLORER'S BLOCK VALVE AT MILEPOST 92.4 THAT WAS ON FIRE. GOVERNMENT REGULATORY AGENCIES WERE NOTIFIED WAS REQUIRED. VACUUM TRUCKS, SPILL RESPONSE PERSONNEL AND PIPELINE REPAIR CONTRACTORS AND EQUIPMENT WERE DISPATCHED TO THE SITE. THE SITE WAS VERY REMOTE WITH NO RESIDENCES OR PUBLIC DWELLINGS ENDANGERED. WITH CONCURRENCE OF THE MONTGOMERY COUNTY FIRE DEPARTMENT OFFICER ON SITE, THE GASOLINE-FED FIRE WAS ALLOWED TO CONTIINUE BURNING AFTER FLOW FROM THE ISOLATED LINE SECTION STOPPED. THE FIRE WAS CONFINED TO THE IMMEDIATE AREA AROUND THE BLOCK VALVE AND ITS SECURITY FENCE. THE FIRE WAS EXTINGUISHED WITH A FEW SHOVELS OF SAND AT 18:30. IN ADDITION TO ISOLATING THE LINE SEGMENT, TRENCHES WERE DUG AND A SPILL CONTAINMENT BOOM WAS PLACED IN SPRING CREEK AS A PRECAUTIONARY MEASURE TO PREVENT ANY MIGRATING PRODUCT FROM ENTERING THE STREAM. ALL PRODUCT WAS CONTAINED IN THE EXCAVATION AREA AND PICKED UP BY VACUUM TRUCK. NONE WAS ALLOWED TO ENTER SPRINGREEK. AN ESTIMATED 44 BARRELS OF NO-LEAD GASOLINE WERE EITHER CONSUMED IN THE FIRE OR INVOLVED WITH SOIL CONTAMINATION. DRAIN DOWN OF THE PIPELINE WAS STARTED AT 16:55 MARCH 1ST WITH FINAL EVACUATION COMPLETELY BY VACUUM TRUCKS ON MARCH 2ND. INSPECTION OF THE BLOCK VALVE WITH THE MANUFACTURER'S REPRESENTATIVE INDICATED THAT A STEM SEAL FAILURE WAS THE PROBABLE SOURCE OF THE LEAK. IGNITION SOURCE OF THE FIRE HAD NOT BEEN DETERMINED. THE VALVE WAS REPAIRED BY INSTALLING NEW INTERNAL PARTS AND REPLACING THE HAND WHEEL OPERATOR. ON MARCH 3RD, PRIOR TO RESTARTING THE PIPELINE, THE LINE WAS SLOWLY REPRESSURED TO CHECK THE VALVE REPAIR. A SMALL LEAK ORIGINATING FROM A FAILURE IN THE VALVE BODY WAS DISCOVERED. IT WAS DECIDED TO REPAIR THE LINE BY TEMPORARILY REMOVING THE VALVE AND REPLACING IT WITH A PIECE OF PIPE TO RESUME OPERATION UNTIL A REPLACEMENT 28" VALVE WAS LOCATED. THIS PLAN WAS ALSO REVIEWED WITH REPRESENTATIVES OF THE U.S. DEPARTMENT OF TRANSPORTATION, OFFICE OF PIPELINE SAFETY, SOUTHWEST REGION, HOUSTON, TEXAS BEFORE IMPLEMENTATION. NEARBY BLOCKVALVES AT MILEPOSTS 92.19 AND 96.0 ARE BEING UTILIZED UNTIL THE NEW VALVE ISINSTALLED. DUE TO ABNORMAL RAINS AND TIME REQUIRED TO VAPOR FREE THE AREA FOR SAFE WELDING, REPAIRS WERE DELAYED UNTIL MARCH 7TH. THE PIPELINE RESUMED FULL OPERATION AT 1:00 MARCH 8TH. A REPLACEMNT VALVE ID SCHEDULED FOR INSTALLATION ON ABOUT APRIL 6, 1992. SOIL REMEDIATION PLANS ARE BEING COORDINATED WITH TEXAS WATER COMMISSION.
2017-09-29 08:50 | YES | NO | 19920020 | 1992-01-27 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1991-12-26 | 2345 | CA | CONTRA COSTA | RICHMOND | NO |  | NO | PLMP .3 APPROX 20 FEET FROM THE RAILROADTRACKS (SWITCH YARD TRACKS), AND APPROX 250 FEET FROM CASTROSTREET. |  | LINE PIPE | PIPE |  | 1957 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 241119.0441 | 486434.5039 | TURBINE FUEL | 3 | 1155 | 1105 | NO | NO | 8 | 0.25 | 46000 | WELDED |  | 1440 | 1380 | YES | 24 | 2130 | 1 | 70 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR VICE PRESIDENT OPERATIONS & ENGINEERING | 2134867720
2017-09-29 08:50 | NO | NO | 19920021 | 1992-06-01 | 443 | AMOCO PIPELINE CO | YES | 1992-05-01 | 1750 | MN | HENNEPIN |  | NO |  | NO | SW 1/4 - SECTION 22, TOWNSHIP 120N, RANGE 23N |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DENT FROM ORIGINAL CONSTR | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11767.8851 | 23740.5774 | OIL AND GASOLINE | 1 | 1 | 1 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1440 | 300 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA | NONE | NO DATA |  | Null | ONE CALL |  | Null | Null | KENNETH C ANDERSON | 6124254750 | A SLIGHT DENT IN THE PIPE, THAT WAS THE RESULT OF MECHANICAL DAMAGE, DELEVELOPED INTO A CRACK ABOUT 1 1/2 INCHES IN LENGTH.
2017-09-29 08:50 | YES | NO | 19920022 | 1992-01-28 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-01-09 | 1100 | GA | CARROLL | BREMEN | NO |  | NO | PLANTATION'S TANK FARM LOCATED AT BREMEN,GA, TANK NO 43, DRAWING A-DOT-27-0 ATTACHED. |  | TANK FARM | GIRTH |  | 1951 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 66000 | 51778.6944 | 104458.5407 | GASOLINE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M COOK - VICE PRESIDENT - OPERATIONS | 4043645916
2017-09-29 08:50 | YES | NO | 19920023 | 1992-01-30 | 4906 | EXXON PIPELINE CO | YES | 1992-01-06 | 1145 | LA | CLAIBORNE |  | NO |  | NO | CLAIBORNE PARISH, T2IN-R8W-S2. WEST SIDE OF HIGHWAY 534 (APPROX. 12 MILES N OF MINDEN, LA) AT WELLERSTATION. |  | PUMPING STATION | VALVE |  | 1984 | OTHER | BACK PRESSURE VALVE FAILU | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25500 | 20005.4046 | 40358.9817 | CRUDE OIL | 1 | 100 | 70 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | J B HOLT - MGR ENVIRONMENTAL & REGULATORY COMPLIANCE | 7136565521
2017-09-29 08:50 | YES | NO | 19920024 | 1992-01-30 | 443 | AMOCO PIPELINE CO | YES | 1992-01-06 | 1330 | MO | CASS |  | NO |  | NO | LEAK WAS LOCATED @ M.P. 75.5 ON THE FREEMAN TO DRUMRIGHT NO. 2 SYSTEM SW 1/4 NW 1/4 S 24, T44N, R33W |  | LINE PIPE | PIPE |  | 1923 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 392262.836 | 791352.5814 | CRUDE OIL | 1 | 586 | 557 | NO | NO | 12 | 0.38 | 25000 | THREADED |  | 695 | 491 | YES | 24 | 869 | 1 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M B WEISS - AREA MANAGER | 8168995387
2017-09-29 08:50 | YES | NO | 19920025 | 1992-02-07 | 2170 | CENEX PIPELINE | YES | 1992-01-28 | 1405 | ND | WARD | MINOT | NO |  | NO | CENEX LIGHT PRODUCT TERMINAL, 2 MILES W OF MINOT NORTH DAKOTA ON HWY 2 & 52 |  | PUMPING STATION | LONGITUDINAL WELD | AUTOMATC CONTROL VALVE | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 653 | 197 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD J LOHOF - MANAGER PIPELINE & TERMINALS | 4062529326
2017-09-29 08:50 | NO | NO | 19920026 | 1992-02-10 | 2552 | COLONIAL PIPELINE CO | YES | 1992-01-06 | 1030 | VA | PITTSYLVANIA | DANVILLE | NO |  | NO | COLONIAL PIPELINE COMPANY'S WITT PUMP STATION. |  | PUMPING STATION | VALVE |  | 1963 | OTHER | VALVE STEM SEAL LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7845.2567 | 15827.0516 | GASOLINE | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MGR TECHNICAL AND REGULATORY | 4048412296
2017-09-29 08:50 | YES | NO | 19920027 | 1992-05-18 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1992-04-18 | 1900 | IL | WILL | WHEATLAND | NO |  | NO | THREE MILES SOUTH OF CITY OF AURORA, SECTION 8, TOWNSHIP 37N, RANGE 9F, STATION #919441. |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 33780 | 26501.2772 | 53463.7804 | NATURAL GAS LIQUID | 2 | 200 | 0 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1500 | 400 | YES | 8 | 2150 | 1 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GEORGE A ROOD - VICE PRESIDENT OF OPERATIONS | 7138537876 | OPERATOR ON DUTY, AT THE LEMONT STORAGE FIELD, RECIEVED A CALL FROM AN OWNEROF A BUSINESS ADJACENT TO THE PIPELINE AT 1900 HRS ON 4-18-92. HE NOTICED AVAPOR CLOUD EXPELLING FROM THE GROUND. THE OPERATOR SHUT DOWN THE PIPELINE FLOW AND IMMDIATELY CALLED OUT THE DISTRICT PERSONNEL. THE PIPELINE WAS SHUTDOWN, AND BLOCK VALVES CLOSED TO ISOLATE THE LEAK BY 1745 HRS.
2017-09-29 08:50 | NO | NO | 19920029 | 1992-02-21 | 2190 | CENTRAL FLORIDA PIPELINE CORP | NO | 1992-01-30 | 742 | FL | POLK | LAKELAND | NO |  | NO | PARALLEL TO THE CSX MAINLINE TRACK BETWEEN TAMPA AND ORLANDO, FL. THE MILE POST MARKER IS 849 AND THE LOCATION IS ON THE SOUTH SIDE OF THE TRACK. |  | LINE PIPE | WELDING FITTING | 3/4" TAP ON LINE INSTALLE | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KEROSENE | 1 | 5 | 4 | NO | NO | 6.63 | 0.19 | 61200 | WELDED |  | 1200 | 100 | YES | 24 | 1500 | 3 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | E R FOSTER - ASST PIPELINE MANAGER | 8132482148 | AT 7:42 AM, THURSDAY 30, 1992, A CONTRACTOR BACKHOE OPERATOR WAS EXCAVATING THE 6" AND 10" CENTRAL FLORIDA PIPELINES TO MAKE AN INSPECTION OF A PIPELINE CASING. THE 6" LINE WAS BEING UNCOVERED TO ALLOW THE REPAIR TEAM TO DETERMINE THE SPACE AND DEPTH BETWEEN THE 6" AND 10" LINES. THE BACKHOE OPERATOR WASIN THE PROCESS OF SCRAPING OFF THE TOP OF THE 6" LINE DOWN TO WITHIN APPROXMIMATELY A FOOT OF COVER ON THE LINE. THE OPERATOR STRUCK A 3/4" VALVE ON THE6" LINE THAT HAD BEEN INSTALLED BY AN UNAUTHORIZED THIRD PARTY. THE THREADED PORTION BETWEEN THE NIPPLE AND THE COCK VALVE WAS DAMAGED. AFTER INVESTIGATION, IT WAS DETERMINED THAT AT SOME UNKNOWN TIME A 3/4" NIPPLE AND VALVE WERE INSTALLED ON THE CFPL 6" PIPELINE BY MISTAKE. A SIX-INCH NATURAL GAS LINE RUNS PARALLEL TO THE CFPL LINE ABOUT THREE FEET AWAY.
2017-09-29 08:50 | YES | NO | 19920030 | 1992-02-20 | 18273 | SHELL PIPELINE CORP | NO | 1992-01-17 | 1430 | TX |  |  | YES | X=2062363 Y=-46638 GULF O | YES | BOXER 16-INCH PIPELINE. SHIP SHOAL BLOCK 203. SKETCH IS ATTACHED. |  | LINE PIPE | LONGITUDINAL WELD |  | 1986 | OTHER | IMPROPERLY TORQUED FLANGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 196131.418 | 395676.2907 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 16 | 0.5 | 52000 | WELDED |  | 140 | 1200 | YES | 8 | 2349 | 1 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414507 | UPLETS" SIGHTED FROM AIR PATROL. WORK BOAT MOBILIZED AND DIVERS INVESTIFATED. ALL FLANGE BOLTS CHECKED FOR PORPER TORGUE AND SYSTEM PRESSURE TESTED PRIOR TO RETURN TO NORMAL OPERATION.
2017-09-29 08:50 | YES | NO | 19920031 | 1992-05-18 | 30614 | COASTLINE GAS PIPELINE COMPANY | NO | 1992-04-07 | 709 | TX | AUSTIN |  | NO |  | NO | SEMINOLE PIPELINE'S STORAGE FACILITY LOCATED ON COUNTY ROAD 19 APPROX. 1 MILE WEST OF FM 109 |  | LINE PIPE | OTHER | THREE (3) 1" PIPE NIPPLES | 1987 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1836014 | 1440400.1172 | 2905868.8369 | NATURAL GAS LIQUID | 2 | 0 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | NON SPECIFIED | Null | NO DATA |  | Null | Null | CAWSON - V P - OPERATIONS AND ENGINEERING | 7139633230 | ON APRIL 7, 1992, AT APPROXIMATELY 7:09 A.M. CENTRAL DAYLIGHT SAVINGS TIME AN EXPLOSION OCCURRED AT THE SALT DOME NATURAL GAS LIQUIDS STORAGE FACILITIES OF SEMINOLE PIPELINE COMPANY NEAR BRENHAM, TEXAS. AS A RESULT OF THE EXPLOSION, COASTLINE'S FACILITIES WERE DAMAGED, RESULTING IN THREE (3) 1" OD (1/2" ID) PIPE NIPPLES BEING BENT AND/OR BROKEN ALLOWING NATURAL GAS LIQUIDS IN ITS 6" LINE TO ESCAPE AND BURN. THE CAUSE OF THE EXPLOSION IS CURRENTLY UNDER INVESTIGATION BY THE NATIONAL TRANSPORTATION SAFETY BOARD AND THE RAILROAD COMMISSION OF TEXAS. AT SUCH TIME AS EITHER OF THESE AGENCIES DISCLOSES THE RESULTS OF THEIR INVESTIGATION, COASTLINE WILL SUPPLEMENT THIS REPORT.
2017-09-29 08:50 | YES | NO | 19920032 | 1992-02-20 | 15490 | PHILLIPS PIPE LINE CO | NO | 1991-12-23 | 1555 | TX | HARRIS |  | NO |  | NO | PROPYLENE SYSTEM - MP 76A-7+00, BLOCK A-18, THOMAS EARLE SURVEY. APPROXIMATELY 1 MILE NORTH OF HWY SS5 ON PHILLIPS ROAD AND THEN 600' EAST. |  | PUMPING STATION | TANK | THREADED FITTING | 1991 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 12055.9522 | 24321.7252 | L. P. G. | 2 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B L THORMAN - MANAGER OF ENGINEERING & TEACHNICAL SERVICE | 9186614721 | A WORKER NEAR THE BOOSTER STATION SITE OBSERVED AND REPORTED BUBBLESIN STANDING WATER. INVESTIGATION FOUND A PINHOLE LEAK IN THE SEAL WELD OF A THREADED1" DRAIN PLUG INSTALLED ON THE BOTTOM OF A PIPE. THIS VERY SMALL LEAK WAS REPAIRED BY REWELDING.
2017-09-29 08:50 | YES | NO | 19920033 | 1992-02-20 | 22610 | WILLIAMS PIPELINE CO | YES | 1992-01-13 | 930 | SD | MINNEHAHA | RENNER | NO |  | NO | APPRO. 400 FT S OF A MAIN LINE PIPELINE VALVE AT THE ROAD. LEAK IS IN A SOYBEAN FIELD LOCATED IN THE NE/4, NW/4 OF SECTION 15, T102N R49W, MINNEHAHA COUNTY, SD |  | LINE PIPE | LONGITUDINAL WELD |  | 1946 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 7200 | 1849 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 129 | YES | 8 | 1513 | 1 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S BALL - VICE PRESIDENT - OPERATIONS | 9185883850 | ON JANUARY 13, 1992, VERNON BERG (THE LANDOWNER) REPORTED A FUEL STAIN AT MILE POST 363+25 ON THE #1-8" SIOUX FALLS TO MARSHALL PIPELINE. THE LEAK WAS EXCAVATED AND THE PIPE REPLACED. THE LEAK WAS SUBJECTED TO A METALLURGICAL FAILURE ANALYSIS WHICH REVEALED IT TO BE 9/16" LONG HAIRLINE CRACK IN THE A.O. SMITH MANUFACTURED FLASH-WELDED ELECTRIC RESISTANCE WELF. THE PIPE SEAM HAD NOT BEEN SUFFICIENTLY WELDED IN 1946 AT THE TIME OF ORIGINAL MANUFACTURE. ITHAD OPERATED SINCE 1946, HAD SUCCESSFULLY PASSED A HYDROSTATIC TEST TO 1513 PSIG IN 1987 AND HAD BEEN INTERNALLY INSPECTED IN 1987 WITH NO FLAW DETECTED.FURTHER REVIEW OF THE LINE'S OPERATING DATA SUGGESTS THAT THE LEAK HAD BEEN SEEPING FOR SOME TIME PRIOR TO ITS DISCOVERY ON 1/13/92. BECAUSE OF THE SLOWRATE OF RELEASE (ESTMATED AT < 2 1/2 GPM), THE LEAK RELEASE WAS NOT DETECTEDBY THE NORMAL PARAMETER MONITORING PROCEDURES OR AERIAL PATROL INSPECTIONS. AN INVESTIGATION IS UNDERWAY IN COOPERATION WITH THE OFFICE OF PIPELINE SAFETY. THE SPILLED PRODUCT IS CONTAINED IN A SAND LAYER LOCATED ABOVE AN IMPERVIOUS CLAY LAYER. THIS MAKES IT PRACTICAL FOR REMEDIATION AND CLEANUP TO RECOVER A LARGE PORTION OF THE PRODUCT AND REMEDIATE AND THE BALANCE WITHOUT DANGER TO THE GROUNDWATER. AS OF 2/11/92, 1849 BBLS HAD BEEN RECOVERED WITH RECOVERY CONTINUING. ALL CLEANUP EFFORTS ARE BEING COORDINATED WITH LOCAL, STATE AND FEDERAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19920034 | 1992-05-18 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1992-04-08 | 1600 | TX | MEDINA | QUIHI | NO |  | NO | APPROX 1 1/2 MI. NW OF COMMUNITY OF QUIHI, TEXAS, AND 1 MI. E OF FM-2676: 721' SE OF OPERATOR'S HONDO PUM,P STATION. |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 31381.0269 | 63308.2065 | CRUDE OIL | 1 | 1384 | 10 | YES | NO | 10 | 0.31 | 35000 | WELDED |  | 1200 | 47 | YES | 12 | 1360 | 1 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BOB REED - REGULATORY COMPLIANCE SUPV | 9152645414 | (WE WERE NOT AWARE OF THIS EXCAVATION WORK UNTIL THE ACCIDENT OCCURRED). AT 4:30 P.M. ON APRIL 8, 1992, FINA'S BIG SPRING, TX, PIPELINE CONTROL CENTER OPRATOR RECEIVED A PHONE CALL FROM A MR. WILLIAM DORMAN, WHO IDENTIFIED HIMSELF AS THE FOREMAN FOR THE HENDRICKS RANCH. HE ADVISED THE OPERATOR (GREG CHANEY) THAT HIS IRRIGATION CONTRACTOR, WHILE DIGGING A TRENCH FOR ISTALLATION OF AN IRRIGATION PIPING SYSTEM, AND CUT INTO OUR PIPELINE (WHICH WAS NOT OPERATING AT THE TIME) AND INCURRED A PRESSURE DROP FROM A STATIC PRESSURE OF 47 PSI TO 18 PSI AT APPROX. 4:00 P.M. THIS PRESSURE DROP, BEING LESS THAN A 50 PSI DEVIATION AND THE LINE BEING INACTIVE, DID NOT TRIGGER ANY ALARMS. FINA'S LOCAL-AREA DISPATCHED TO THE SCENE AT APPROX. 5:00 P.M. BY THE COUNTY SHERIFF'S DEPT. AT 5:02 PM, THE LOCATION OF THE RUPTURE WAS CONFIRMED AND EFFORTS BEGUM TO DRAIN THE PIPELINE. AT 5:45 PM, FINA'S CONTRACTOR IS ON-SCENE, AND AT 6:15 PM CONFIRMS THAT THE FIRE HAD BEEN EXTINGUSHED. BY 7:15 PM, A REPAIR PATCH HAD BEEN INSTALLED, WITH ALL LEAKAGE STOPPED. NOTIFICATIONS TO THE TEXAS RRC WERE MADE AT 5:23 PM AND TO THE NRC AT 6:03 PM. THE PIPLINE WAS FULLY REPAIRED ON APRIL 10TH, WITH ADDITIONAL WORK IN THE AREA COMPLETED ON APRIL 14TH. THERE WERE NO INJURIES OR DAMAGE TO THE PROPERTY OF THE IRRIGATION CONTRACTOR. THERE APPEARED TO BE NO DAMAGE TO THE LANDOWNER'S PROPERTY AND THE ADJACNET ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19920035 | 1992-02-20 | 443 | AMOCO PIPELINE CO | YES | 1992-01-17 | 1130 | OK | OSAGE |  | NO |  | Null | S OF BOWRING, OKLAHOMA, SECTION 10, TOWNSHIP 27N, RANGE 11E |  | LINE PIPE | PIPE |  | 1923 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 58839.4254 | 118702.8872 | CRUDE OIL | 1 | 5000 | 4600 | NO | NO | 12 | 0.38 | 25000 | THREADED |  | 695 | 690 | YES | 8 | 880 | 12 | 82 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J W CARICO - AREA MANAGER | 9182257271 | ON JANUARY 17, 1992, AT 1130 CST, AMOCO PIPELINE'S PATROL PILOT REPORTED A SUSPECTED LEAK. THE LEAK WAS LOCATED IN A REMOTE AREA NEAR A PRODUCTION FIELD. THE OPERATING PIPELINE WAS IMMEDIATELY SHUT DOWN AND REMAINED OUT OF OPERATION UNTIL REPAIRS WERE COMPLETED. THE LEAK WAS CONFIRMED AND FOUND TO BE ONTHE #4 SYSTEM. LOCALIZED CORROSION PITTING WAS THE CAUSE OF THE LEAK.
2017-09-29 08:50 | YES | NO | 19920036 | 1992-02-20 | 30505 | SCURLOCK PERMIAN CORP | NO | 1992-01-03 | 452 | WY | CAMPBELL |  | NO |  | NO | NW/4, SEC. 22, T55N, R71W, - 44 MILES N.N.E. OF GILLETTE WYOMING ON STATE HIGHWAY 59 |  | PUMPING STATION | OTHER | NON SPECIFIED | 1991 | OTHER | PUMP PACKINGS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 150 | 125 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN DOSSEY - OPEARATION SERVICE REPRESENTATIVE | 3072346916 | PACKING GLAND ON OUR #3 PUMP HAD FAILED RESULTING IN A SPILL OF APPROXIMATELY 15 BARRELS.
2017-09-29 08:50 | YES | NO | 19920037 | 1992-02-18 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1992-01-20 | 435 | IN | JACKSON | SEYMOUR | NO |  | NO | 950 E COUNTY RD., 1/2 MILE WEST; STAR ROUTE 31, SEYMOUR. INDIANA |  | TANK FARM | TANK |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2698 | 2116.6503 | 4270.1385 | FUEL OIL | 1 | 450 | 314 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC | PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | JESSE L MITCHELL - MANAGER OF CORROSION AND DOT COMPLIANCE | 7137593784 | ON JANUARY 20, 1992, AT APPROXIMATELY 4:35 P.M., A SPILL FROM TANK #3003 WASDETECTED BY TEXAS EASTERN PRODUCTS PIPELINE COMPANY PERSONNEL AT THE SEYMOUR TERMINAL, LOCATED IN JACKSON COUNTY, INDIANA. IMMEDIATELY, CONTINGENCY PROCEDURES WERE INITIATED. PUMPING OF THE REMAINING PRODUCT IN TANK #3003 TO OTHER STORAGE TANKS WITHIN THE TERMINAL WAS BEGUN. THE ESTIMATED AMOUNT SPILLED WAS 450 BARRELS OF NO. 2 FUEL OIL. UTILIZING VACUUM EQUIPMENT, 314 BARRELSOF STANDING PRODUCT WERE RECOVERED. CONTAMINATED SOILS INSIDE THE TANK RETAINING WALL WERE REMOVED, CONTAINED AND COVERED IN PLASTIC ON-SITE, PENDING DISPOSAL. CALCULATIONS INDICATE THAT AN ADDITIONAL 135 BARRELS OF #2 FUEL OIL WERE CONTAINED IN THIS SOIL. THE REMAINING SOIL WITHIN THE RETAINING WALL WHICH CONTAINS ONE (1) BARREL WAS PREPARED FOR IN SITU BIO-REMEDIATION. IT HASBEEN DETERMINED THAT THE SPILL WAS THE RESULT OF A SMALL INTERNAL CORROSION PIT LOCATED IN THE TANK BOTTOM.
2017-09-29 08:50 | YES | NO | 19920038 | 1992-02-18 | 15681 | PLATTE PIPE LINE COMPANY | YES | 1992-01-09 | 2232 | MO | CHARITON |  | NO |  | NO | NE 1/4, SECTION 14, T53N, R17N, CHARITONCOUNTY, MISSOURI. |  | LINE PIPE | PIPE | LONGITUDINAL WELD | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 900000 | 706073.1048 | 1424434.6466 | CRUDE OIL | 1 | 5375 | 5375 | NO | NO | 20 | 0.34 | 52000 | WELDED |  | 1248 | 1200 | YES | 24 | 1560 | 7 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C A RYSENGA - PRESIDENT | 4194212000 | ON JANUARY 9, 1992, AT ABOUT 2232 HRS., AN APPARENT PIPE SEAM FAILURE OCCURRED APPROXIMATELY 3.8 MILE SDOWN STREAM OF THE SALISBURY PUMP STATION ON THE PLATTE 20" PIPELINE. MARATHON PIPE LINE COMPANY OPERATIONS PERSONNEL IMMEDIATELY SHUT DOWN THE LINE. LOCAL FIELD EMPLOYEES AND CONTRACTOR PERSONNEL WEREDISPATCHED TO THE RELEASE SIGHT WHERE THE OIL WAS CONTAINED IN A DRY STREAM BED. AN ESTIMATED 5375 BARRELS OF WYOMING ASPHALT CRUDE OIL WERE RELEASED. 4700 BARRELS HAVE BEEN RECOVERED AND RETURNED TO THE PIPELINE SYSTEM. THE REMAINING 675 BARRELS HAVE BEEN PICKED UP ALONG WITH SOIL IMPACTED BY THE RELEASE AND TRANSPORTED TO A SPECIAL WASTE LANDFILL THAT WAS APPROVED BY THE MISSOURI DEPARTMENT OF NATURAL RESOURCES (DNR). FINAL CLEANUP WAS COMPLETED 2/7/92 AND REVIEWED BY THE MISSOURI DNR. THE FAILED JOINT OF PIPE WAS REPLACED WITH SUITABLY PRETESTED (4 HOUR TEST AT 1610 PSI) PIPE. THE TIE-IN WELDS WERE X-RAYED AND THE LINE RETURNED TO SERVICE UNDER A REVISED OPERATING PRESSURE AT ABOUT 210O HRS. ON JANUARY 11, 1992. AT THE REQUEST OF THE CENTRAL REGION CHIEF, OF THE OFFICE OF PIPELINE SAFETY, THE OPERATING PRESSURE OF THE SALISBURY, MO TO WOOD RIVER, IL LINE SECTION WAS REDUCED TO 80% OF THE PREVIOUSLY ESTABLISHED OPERATING PRESSURE.
2017-09-29 08:50 | YES | NO | 19920039 | 1992-02-14 | 4906 | EXXON PIPELINE CO | YES | 1992-01-06 | 2245 | TX | SAN PATRICIO |  | NO |  | NO | INGLESIDE TO VANDERBILT 16-INCH (= STA. 750+32) 2/3 MILE SOUTH OF CHILTIPIN CREEK, SOUTHWEST OF BAYSIDE, TEXAS. |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 670000 | 525632.2003 | 1060412.4591 | CRUDE OIL | 1 | 1700 | 550 | NO | NO | 16 | 0.22 | 56000 | WELDED |  | 1104 | 1072 | YES | 4 | 1380 | 1 | 66 | EXTERNAL | Null | YES | GALVANIC | PITTING, UNDER DISBONDED | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MANAGER OF ENVIRONMENTAL/REGULATORY COMPLIANCE D | 7136565521 | AT 10:45 P, OM 1//92, OUR OIL TRAFFIC CENTER CONFIRMED A PROBABLE LEAK ON THE INGLESIDE TO VANDERBILT 16" CRUDE OIL PIPELINE. MOMENTS EARLIER THE INGLESIDE PUMPS HAD SHUTDOWN ON AN OPERATIONAL TRIP AFTER SWITCHING FROMA VERY LIGHT PLANT DISTILLATE TO A VERY HEAVY CRUDE. AT THAT TIME THE RECORDING PRESSURE CHART AT INGLESIDE SHOWED A MOMENTARY PRESSURE INCREASE TO 1145 PSI AT THE STATION (3.7% ABOVE MOP, WELL WITHIN THE 10% SURGE ALLOWABLE). APPARENTLY ATTHE SAME TIME A LEAK OCCURRED 14.2 MILES DOWNSTEAM (MAXIMUM PRESSURE AT THE LEAK WAS ABOUT 1072, WELL BELOW THE 1104 PSI MOP). THE NEXT MORNING THE AIR PATROL, HAMPERED BY FOG, FLEW THE LINE AND DISCOVERED THE LEAK SITE AT 10:45 AM EPC MAINTENANCE CREWS WERE DISPATCHED AND APPROPRIATE AGENCIES WERE NOTIFIED. ABSORBENT BOOM WAS LAID OUT AROUND THE SPILL FOR CONTAINMENT. REPAIRS CONSISTED OF REPLACING 63 FEET OF LINE USING ONE WELD PLUS END AND LINE WAS BACK IN SERVICE. AT 8:30 AM ON 6/11/92. CLEAN UP IS COMTINUING UNDER THE DIRECTION OF THE TEXAS GENERAL LAND OFFICE.
2017-09-29 08:50 | YES | NO | 19920040 | 1992-02-14 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1992-01-13 | 1530 | NY | CAYUGA |  | NO |  | NO | BUKEYE PIPE LINE COMPANY'S AUBURN STATION GATES ROAD; ROUTE 6, BOX 86; AUBURN NY 13021. |  | TANK FARM | TANK |  | 1973 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 112 | 86 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R MOYER - REGULATORY COMPLIANCE COORDINATOR | 2158208300 | UNLEADED GASOLINE WAS OBSERVED AROUND TANK # 318 IN THE TANK DIKE AREA. IMMEDIATELY AFTER THE DISCOVERY OF THE PRODUCT. TANK #318 WAS EMPTIED TO REMOVETHE SOURCE OF PRODUCT. ALMOST ALL OF THE RELEASED GASOLINE WAS RECOVERED AND RECYCLED. AFTER A COMPLETE TANK BOTTOM INSPECTION, THE SOURCE OF THE PRODUCT RELEASE WAS INDENTIFIED AS A FAILED WELD NEAR THE TANK SUMP STRUCTURE. THETANK REPAIR WAS COMPLETED PRIOR TO BEING RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19920041 | 1992-05-19 | 18273 | SHELL PIPELINE CORP | NO | 1992-04-13 | 700 | TX | UPTON | MCCAMEY | NO |  | NO | SE 1/4, NW 1/4, SECTION 7, BLOCK R TWO MILES EAST OF MCCAMEY MCCAMEY TANK FARM. |  | TANK FARM | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 392.2628 | 791.3526 | CRUDE OIL | 1 | 150 | 130 | NO | NO | 12 | 0.25 | 35000 | COUPLED |  | 275 | 10 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414506 | RELEASE OCCURRED AND WAS CONTAINED WITHIN TANK FIREWALL.
2017-09-29 08:50 | YES | NO | 19920043 | 1992-02-13 | 14295 | OLYMPIC PIPE LINE CO | YES | 1992-01-24 | 837 | WA | THURSTON |  | NO |  | NO | 11710 VAIL CUT-OFF ROAD; RAINIER WA |  | PUMPING STATION | PUMP | 3/4" STAINLESS STEEL TUBI | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | FAILED STAINLESS STEEL TU | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 58839.4254 | 118702.8872 | DIESEL FUEL | 1 | 75 | 10 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM A MULKEY | 2062357745 | A 3/4" 304 STAINLESS STEEL HIGH-PRESSURE TUBING USING THE PRODUCT BEING PUMPED FOR COOLING THE OUTBOARD BEARING OF A 2500-HP CENTRIFUGAL PUMP BROKE AND SEPARATED AT A COMPRESSION FITTING ON THE PUMP.
2017-09-29 08:50 | NO | NO | 19920044 | 1992-03-12 | 809 | ARCO PIPE LINE CO | YES | 1992-02-27 | 840 | IL | COOK |  | NO |  | NO | OUTSIDE TOWN OF EAST CHICAGO HEIGHTS, 70' EAST OF COTTAGE GROVE AVE., 1/2 MILE SOUTH OF HWY 30. |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 392.2628 | 791.3526 | FUEL OIL | 2 | 1 | 0 | NO | NO | 8 | 0.32 | 24000 | THREADED |  | 795 | 300 | YES | 1 | 925 | 7 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | ONE CALL |  | NO | YES | L E GRAVES - MANAGER, OPERATIONS COMPLIANCE, PRODUCTS BUSINE | 7139865330 | LEAK WAS SPOTTED BY ARCO PIPE LINE COMPANY PATROL PILOT. CREW WA S DISPATCHED TO SITE TO INVESTIGATE. MINIMAL SHEEN ON WATER WAS ONSERVED. LEAK WAS TRACED BACK YO SEGMENT OF LINE WHICH APPEARED TO BE THE SOURCE. BACKHOE EXPOSED LINE WHERE PIN HOLE WAS DISCOVERED TO BE THE SOURCE OF THE LEAK. REPAIR ONLINE HAS BEEN COMPLETED. NOTE: SHEEN ON WATER HAS BEEN INDENTIFIED TO A PREVIOUS LEAK, NOT RELATED TO OUR LINE.
2017-09-29 08:50 | YES | NO | 19920045 | 1992-02-09 | 10318 | KOCH REFINING CO | NO | 1992-01-10 | 1400 | TX | WILSON |  | NO |  | NO | APPROX. 1/2 MILE EAST OF US HWY 181, 8 MILES NORTH OF FLORESVILLE TEXAS NEAR THE EAGLE CREEK DEVELOPMENT. |  | LINE PIPE | PIPE |  | 1989 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 750 | 390 | NO | NO | 16 | 0.25 | 65000 | WELDED |  | 1440 | 800 | YES | 8 | 1800 | 1 | 89 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHRIS WILKINS - DIVISION MANAGER | 8176853411 | EXTERNAL CORROSION PIT APPARENTLY CAUSED BY CATHODIC INTERFERENCE FROM ANOTHER PIPELINE COMPANY'S RECTIFIER AND GROUNDED IN THE GENERAL AREA OF THE LEAK. REPAIRS WERE MADE ON JANUARY 11.
2017-09-29 08:50 | YES | NO | 19920046 | 1992-03-09 | 22610 | WILLIAMS PIPELINE CO | YES | 1992-02-06 | 720 | NE | OTOE |  | NO |  | NO | TANK 795 IN WPL NEBRASKA CITY TANK FARM LOCATED ON EAST SIDE OF HIGHWAY 73 & 75 IN THE NW 1/4 OF SECTION 25, T9N, R13E IN OTOE COUNTY NEBRASKA. |  | TANK FARM | TANK | 2"X1" SCREWED REDUCING EL | 1957 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 2899 | 1772 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA | FREEZING WATER IN WATER D | Null | NO DATA |  | Null | Null | STEVEN S BALL - VICE PRESIDENT - OPERATIONS | 9185883850 | ON FEBRUARY 6, 1992 AT 7:20 THE NEBRASKA CITY AREA SUPERVISOR DISCOVEREDUNLEEADED GASOLINE LEAKING FROM THE WATER DRAW VALVE ON TANK 795 AS HEARRIVED AT THE LOCATION. OUR AUTOMATED TANK GAUGING RECORDS INDICATE THE LEAKSTARTED ON FEBRUARY 5, 1992 AT 9:25. ALL PRODUCT WAS CONTAINED TO THE DIKEDAREA SURROUNDING TANK 795. APPROXIMATELY 2,899 BARRELS OF GASOLINE AND 367BARRELS OF TANK BOTTOM WATER WERE RELEASED FORM TANK 795. APPROXIMATELY 1,772BARRELS OF GASOLINE AND 1,094 BARRELS OF WATER HAVE BEEN RECOVERED AND PUMPEDTO TANK 831. THIS LEAVES 1,127 BARRELS OF GASOLINE UNACCOUNTED FOR. SOMESTANDING WATER IN THE DIKED AREA WAS COLLECTED WITH THE SPILLED GASOLINE.THIS ACCOUNTS FOR THE ADDITIONAL WATER COLLECTED. MOST OF THE MISSING 1,127BARRELS OF GASOLINE EVAPORATED. USING STANDARD EMISSION CALCULATIONS WE HAVECALCULATED THAT AS MUCH AS 1,600 BARRELS COULD HAVE EVAPORATED. SOME OF THEMISSING 1,127 BARRELS SOAKED INTO THE SOIL. WPL WAS CONTRACTED ANENVIRONMENTAL CONSULTANT TO DETERMINE THE EXTENT OF SUBSURFACECONTAMINATION. THE LEAK RESULTED FRM ICE IN THE WATER DRAW PIPING THAT FORCEDTHE PLUG OFF THE END OF A WATER DRAW PIPING THAT FORCED THE PLUG OFF THE ENDOF A WATER DRAW VALVE BY STRIPPING THE NIPPLE THREADS. WHEN THE ICE THAWED,PRODUCT ESCAPED THROUGH THE PARTIALLY OPEN WATER DRAW VALVE. THIS VALVE ISLEFT IN THE PARTIALLY OPEN POSITION TO PREVENT WATER FROM BEING TRAPPED INTHE VALVE BODY AND RUPTURING IT WHEN IT FREEZES. STEPS HAVE SINCE BEEN TAKENTO INCLUDE DEVIATION ALARM MONITORING OF IDLE TANKAGE. THROUGH THISPROCESS, THE OPERATIONS CONTROL CENTER IN TULSA CAN SET DEVIATION ALARMS THATWILL ALARM AUTOMATICALLY IF THE LEVEL CHANGES IN AN IDLE TANK BEYOND THEDEVIATION PARAMETER SETTING. SUPPLEMENTAL REPORT 9/26/94 INDICATES A CHANGE INPART D/CAUSE OF ACCIDENT FROM "OTHER - ICE FREEZING IN WATER DRAIN" TO"OUTSIDE FORCE DAMAGE." ALSO NOTED AN ERROR IN SPECIFIC LOCATION. CHANGESMADE 1/17/95.
2017-09-29 08:50 | YES | NO | 19920047 | 1992-03-09 | 22610 | WILLIAMS PIPELINE CO | YES | 1992-02-04 | 840 | KS | WYANDOTTE | KANSAS | NO |  | NO | WILLIAMS PIPE LINE COMPANY TANK 1241 AT 401 E DONOVAN RD IN KANSAS CITY, KANSAS. |  | TANK FARM | SCRAPER TRAP |  | 1991 | OTHER | FAILURE OF PUMP MOTOR THR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | GASOLINE | 3 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVENS S BALL - V P OPERATIONS | 9185883850 | ON FEBRUARY 4, 1992 AT APPROXIMATELY 8:40 A.M., THE WPL AREA MANAGER REPORTEDA FIRE IN THE KANSAS CITY TANK FARM AT TANK 1241. HE HAD ALREADY CALLED 911AND, LEFT IMMEDIATELY TO GO TO THE FIRE. HE DISCOVERED THAT A 200 HO VERTICAL CAN PUMP ADJACENT TO TANK 1241 WAS ON FIRE. THE FIRE WAS APPROXIMATELY 8 TO 10 FEET SOUTH OF THE TANK. THE WIND WAS ACARRING THE HEAT AND FLAME AWAY FROM THE TANK INTO ADJACENT MANIFOLD AREA. WPL EMPLOYEES FROM THE KANSAS CITY COMPLEX AND KANSAS CITY MAINTENANCE CREW, FOUGHT THE FIRE USING DRY CHEMICAL EXTINGUISHERS. THEY WERE SUCCESSFUL IN KNOCKING THE FIRE DOWN BUT WERE UNABLE TO COMPLETELY EXTINGUISH IT WITH THE EQUIPMENT AVIALABLE. A GASOLINE MIST CONTINUED TO SPRAY FROM THE PUMP AND WAS REIGNITED BY THE HOT PIPING IN THEMANIFOLD AREA. THE KANSAS CITY FIRE DEPARTMENT ARRIVED ON SITE VERY QUICKLYAND EXTINGUISHED THE FIRE USING FOAM AND WATER. IN ALL, THE FIRE LASTED APPROXIMATELY 17 MINUTES. THERE WERE NO INJURIES. DUE TO THE QUICK RESPONSE OFOUR EMPLOYEES AND THE FIRE DEPARTMENT, THE DAMAGE WAS KEPT TO A MININUM. THERE WAS NO SPILL ASSOCIATED WITH THIS INCIDENT AS ALL GASOLINE SPRAYING FROM THE PUMP WAS CONSUMED IN THE FIRE. CAUSE: THE FIRE WAS CAUSED BY A THRUST BEARING FAILURE ON THE BOOSTER PUMP MOTOR. WHEN THE BEARING FAILED, THE MOTORDROPPED SLIGHTLY, ALLOWING GASOLINE TO SPRAY OUT FROM THE PUMP SEAL. THE BEARING FAILURE ALSO CREATED METAL TO METAL CONTACT BETWEEN THE SEAL COLLAR AND THE GLAND PLATE. THIS WAS THE HEAT SOURCE WHICH CAUSED IGNITION. DAMAGE: THE 200 HP PUMP ANDMOTOR SUSTAINED SIGNIFICANT DAMAGE. IN ADDITION, AN ADJACENT 200 HP VERTICAL CAN PUMP WAS SLIGHTLY DAMAGED. THE FIRE DESTROYED SIX MOTOR OPERATORS MOUNTED ON GENERAL TWIN SEAL VALVES IN THE MANIFOLD AREA MUCHOF THE CONDUIT AND WIRING FOR THESE OPERATORS AND FOR THE BOOSTER PUMPS WAS ALSO DESTROYED. THE TOTAL DAMAGE IS ESTIMATED TO BE $50,000. DESIGN MODIFICATIONS: THE PUMP MANUFACTURER IS FURINISHING NEW "THRUST BALANCED" IMPELLERS TO LESSEN THE THRUST WHEN PUMPING AT LESS THAN OPTIMUM DESIGN FLOW RATE. ADDITIONAL ENGINEERING MODIFICATIONS ARE BEING EXAMINED TO PREVENT ANY FUTUREOCCURENCE.
2017-09-29 08:50 | NO | NO | 19920048 | 1992-03-02 | 2552 | COLONIAL PIPELINE CO | YES | 1992-02-08 | 1442 | NJ | GLOUCESTER | WEST DEPTFORD | NO |  | NO | COLONIAL PIPELINE CPMPANY'S WOODBURY TANK FARM |  | TANK FARM | BOLTED FITTING |  | 1976 | OTHER | INSUFFICIENTLY TIGHTENED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | GASOLINE | 1 | 8 | 4 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES COX A - MANAGER, TECHNICAL & REGULATORY | 4048412296 | AT 1442 EST ON FEBRUARY 8, 1992, DURING A DELIVERY OF GASOLINE INTO TANK 1214 AN OPERATOR DISCOVERED GASOLINE ESCAPING FROM S 24" BOLTED CONNECTION AT THE TANK GATE VALVE. THE GASOLINE DELIVERY WAS IMMEDIATELY RE-DIRECTED INTO ANOTHER TANK AND THE PRODUCT IN TANK 1214 WAS TRANSFERRED TO TANK1211. TANK 1214 HAD BEEN OUT OF SERVICE FOR REPAIRS AND THIS DELIVERY WAS THE FIRST SINCE THE TANK HAD BEEN RETURNED TO SERVICE. AT APPROXIMATELY 1522 EST THE AREA MANAGER NOTIFIED THE NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION AND ENERGY (NJDEPE). AFTER THE RECOVERU OF 1.5 BARRELS OF PRODUCT, COLONIAL MAINTENANCE PERSONNEL, AS A TEMPORARY MEASURE, TIGHTENED THE BOLTS AND STOPPED THE LEAK. AN INVESTIGATION REVEALED THAT ALTHOUGH THE CONNECTION BOLTS WERE TORGUED PROPERLY, EITHER ICE OR OTHER CONTAMINANTS TRAPPED IN THE TAPPED HOLES OF THE VALVE PREVENTED THE CONNECTION FROM TIGHTENING PROPERLY. A CONTRACT CREW BEGAN EXCAVATING CONTAMINATED SOIL AND THE RECOVERY OF ADDITIONAL PRODUCTAND ON FEBRUARY 10, 1992, IT WAS DETERMINED THAT THE COST OF THE CLEAN UP AND REPAIR WOULD EXCEED $5,000. AT APPROXIMATELY 1200 EST ON FEBRUARY 10, 1992,THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 106178). RECENTLY, THE VALVE BODY BOLT HOLES WERE RECONDITIONED AND NEW STUD BOLTS INSTALLED AND TIGHTENED SUFFICIENTLY WITH NO EVIDENCE OF ADDITIONAL LEAKAGE. IT IS ESTIMATED THAT 8 BARRELS OF PRODUCT ESCAPED AND TO DATE, 4 BARRELS HAVE BEEN RECOVERED. CLEAN UO ACTIVITIES ARE CONTINUING.
2017-09-29 08:50 | YES | NO | 19920049 | 1992-03-09 | 18273 | SHELL PIPELINE CORP | YES | 1992-02-04 | 900 | MT | FALLON | BAKER | NO |  | NO | NINE MILES W OF HWY 12. BUTTE - BAKER STATION. SW 1/4, NW 1/4, SECTION 4, T-7-N, R-58-E |  | TANK FARM | GIRTH |  | 1955 | OTHER | CORROSION, INTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 67000 | 52563.22 | 106041.2459 | CRUDE OIL | 1 | 190 | 160 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414506 | DAMAGE TO FLOATING ROOF LEG AND FLOOR STRIKE PLATE RESULTED IN DAMAGE TO THETANK BOTTOM COATING AND TANK BOTTOM STEEL. MECHANICAL DAMAGE WAS THEN ACCOMPANIED BY CORROSION TO CREATE A SMALL HOLE IN THE TANK BOTTOM.
2017-09-29 08:50 | YES | NO | 19920050 | 1992-07-30 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1992-07-28 | 1320 | CA | LOS ANGELES |  | NO |  | NO |  |  | LINE PIPE | LONGITUDINAL WELD | ON A 1/4 INCH USED TO FEE | 0 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2745.8399 | 5539.4681 | CRUDE OIL | 1 | 60 | 60 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | CAUSED DURING INSTALLATIO | Null | NO DATA |  | Null | Null | EILEEN J THRASHER - COMMON CARRIER BUSINESS UNIT MANAGER | 3104289300 | THE PIPE FAILED AT A PRESSURE BELOW OPERATING PRESSURE. THE METALLURGICAL REPORT INDICATES THE FAILURE ORIGINATED AT AN EXTERNAL HOOK CRACK EXTENDING TOMIDWALL. FATIGUE CRACKS INITIATED AT MIDWALL AT THE EDGE OF THE HOOK CRACK AND PROPAGATED TOWARD THE INSIDE SURFACE. WHEN COMBINED HOOK AND FATIGUE CRACKREACHED CRITICAL SIZE, THE WELD FRACTURED.
2017-09-29 08:50 | YES | NO | 19920051 | 1992-03-02 | 26044 | GULF INTERSTATE ENERGY INC | NO | 1992-02-06 | 2032 | PA | DELAWARE |  | NO |  | NO | GULF INTERSTATE ENERGY, INC. - MARCUS HOOK PUMP STATION 1111 WEST RIDGE ROAD. LINWOOD PA 19061 |  | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1176788.508 | 2374057.7443 | FUEL OIL | 1 | 1208 | 900 | NO | NO | 18 | 0.38 | 52000 | WELDED |  | 1440 | 1050 | YES | 24 | 1800 | 1 | 76 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | L C SPARKMAN - SR. VICE PRESIDENT | 2153638520 | THE INTERSTATE ENERGY COMPANY 18" PIPELINE, OPERATED BY GULF INTERSTATE ENERGY, INC., RUPTURED AT 2032 ON THE EVENING OF FEBRUARY 6, 1992, AT THE MARCUS HOOK PUMP STATION (ORIGINATING PUMP STATION). THE RUPTURE WAS LOCATED APPROXIMATELY TWELVE (12) FEET DOWNSTREAM OF THE SCRAPER LAUNCHING BARREL AT AN ABOVE GROUND TO BELOW GROUND TRANSITION AND WAS CAUSED BY EXTERNAL CORROSION. THE PIPELINE IS INSULATED WITH 2" OF POLYURETHANE INSULATION. THE PRODUCT BEING PUMPED WAS NO. 6 FUEL OIL AT A TEMPERATURE OF 160 F. A DELIVERY WAS BEINGMADE TO THE CROMBY STATION AT MILEPOST 27.3 WITH BOOSTER PUMP PI AND MAINLINE PUMP P4 ON LINE WITH A DISCHARGE PRESSURE OF 751 PSI. AT 2032 MAINLINE PUMP P5 WAS BROUGHT ON LINE IN PREPARATION FOR THE SWITCH OUT OF CROMBY TO MARTINS CREEK (MILEPOST 84). THE PIPELINE RUPTURED AT 2032 WIHT A DISCHARGE PRESSURE OF 1050 PSI. ALL PUMP UNITS SHUT DOWN INSTANTLY DUE TO LOW SUCTION PRESSURE. THE MARCUS HOOK OPERATOR IMMEDIATELY NOTIFIED THE DISPATCHER AND THE OIL SPILL CONTINGENCY PLAN WAS PUT INTO EFFECT. AN OPERATOR WAS DISPATCHED TO THE FIRST DOWNSTREAM BLOCK VALVE LOCATED AT MILEPOST 9.53 AND THIS VALVE WAS CLOSED AT 2130. THE GULF INTERSTATE ENERGY, INC. EMERGENCY RESPONSE TEAM WASNOTIFIED, AND ARRIVED ON SITE AT 2230 TO REPAIR THE RUPTURE. FOUR (4) SPILLCONTRACTORS WERE NOTIFIED AND THEY ARRIVED ON SITE AT APPROXIMATELY 2230. THE OIL LEFT THE PUMP STATION PROPERTY AND TRAVELED APPROXIMATELY 1100' DOWN ADRAINAGE DITCH, 1,300' THROUGH AN UNDERGROUND CULVERT, AND INTO NAMAAN'S CREEK. SPILL BOOMS WERE PLACED IN NAMAAN'S CREEK AND THE OIL WAS CONTAINED AT THE LOCATION. A "FULL SOLE" REPAIR SLEEVE WAS WELDED OVER THE PIPELINE RUPTURE AND A NITROGEN DISPLACEMENT OF THE PIPELINE WAS STARTED ON FEBRUARY 7, 1992. THE RUPTURE WAS ABOUT 7" LONG AND IT APPEARED THAT THERE WAS APPROXIMATELY 1/8" OF PIPE WALL REMAINING OF THE ORIGINAL .375" WALL PIPE. THIS SECTION WILL BE CUT OUT WHEN PERMANENT REPAIRS ARE MADE AND SENT TO A LAB FOR ANALYSIS.
2017-09-29 08:50 | YES | NO | 19920052 | 1992-03-09 | 15851 | PRIDE REFINING INC | NO | 1992-02-27 | 1140 | TX | RUNNELS | WINTERS | NO |  | NO | APPROX. 17 MILES W OF WINTERS TX OFF FM 2146 |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 150 | 100 | Null | Null | 0 | 0 | 0 | NO DATA |  | 20 | 20 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON | 9156748231 | AT APPROXIMATELY 11:40 AM ON 2-27/92 PIPELINE GAUGER LYNN WILLIAMS WENT TO CHECK THE BRYAN PUMP AND FOUND OIL WAS SURFACING NEAR THAT PUMP. HE THEN CONTACTED STEVE ODOM HE THEN DISPATCHED PERSONNEL TO AID IN THE CLEAN-UP OF THE SPILL. DUE TO THE WET CONDITIONS OF THE AREA WITH RAIN, A BURN PERMIT WAS OBTAINED FROM THE TEXAS RAILROAD COMMISSION AND THE TEXAS AIR CONTROL BOARD APPROXIMATELY 50 BBLS OF CRUDE OIL WAS BURNED. PLEASE NOTE PIPELINE IS A LOW PRESSURE GATHERING LINE OPERATING AT LESS THAN 20% SMYS.
2017-09-29 08:50 | YES | NO | 19920053 | 1992-02-25 | 12628 | MOBIL PIPELINE CO | NO | 1992-01-29 | 905 | TX | LIBERTY |  | NO |  | NO | BACKWATER AREA ON THE EAST SIDE OF THE TRINITY RIVER, APPROXIMATELY 2 MILES NORTHWEST OF LIBERTY TX |  | LINE PIPE | PIPE |  | 1924 | OTHER | THE DAMAGED PIPE WILL BE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 800000 | 627620.5376 | 1266164.1303 | CRUDE OIL | 1 | 137 | 130 | Null | Null | 8.63 | 0.32 | 35000 | WELDED |  | 800 | 850 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D. L. DENNARD VICE PRESIDENT OPERATIONS | 2146582226 | WHILE CLEANING THE PIPELINE IN PREPARATION FOR A HYDROSTATIC TEST, A SQUEEGEE LODGED IN A 4" SCRAPER BARREL RECEIVING BYPASS LINE, CAUSING THE MAINLINE PUMP STATION AT EASTGATE TO SHUTDOWN ON HIGH DISCHARGE PRESSURE (850 PSIG). FURTHER INVESTIGATION OF THE EASTGATE TO HULL SECTIONS OF PIPELINE REVEALED THAT A LEAK HAD OCCURRED AT MP 174.5. MAINTENANCE CREWS WERE DISPATCHED TO THESITE AND INITIATED RECOVERT AND CLEANUP OPERATIONS. PERMANENT REPAIRS WERE MADE BY REPLACING THE DAMAGED SECTION PIPE WITH TESTED PIPE. BEFORE THIS SEGMENT OF PIPELINE SYSTEM ACROSS THE TRINITY RIVER BOTTOM IS RETURNED TO SERVICE, IT WII BE HYROSTATICALLY TESTED.
2017-09-29 08:50 | YES | NO | 19920054 | 1992-03-23 | 30528 | BAYSIDE PIPELINE SYSTEM | NO | 1992-02-21 | 1835 | TX | HARRIS |  | NO |  | NO | NORTH SIDE OF EVERGREEN ROAD; PARALLEL TO TABBS BAY. |  | LINE PIPE | SCRAPER TRAP |  | 1956 | OTHER | FISHING OPERATIONS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRANSMIX (PART. REFINED PETRO) | 2 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | FISHING OPERATIONS | COW STRUCK BLEEDER VALVE | Null | NO DATA |  | Null | Null | THOMAS J MOORE - ADMINISTRATIVE SUPERVISOR | 7134704900 | AT SOME TIME IN THE AFTERNOON OF FEBRUARY 21, 1992, A COW BRUSHED AGAINST A SCRAPER TRAP BLEEDER. A BLEEDER VALVE ON THE TRAP WAS SLIGHTLY OPENED, CAUSING SLIGHT LEAKAGE OF HVL FROM THE TRAP. WE WERE NOTIFIED OF THE VENTING PRODUCT AT 6:35 P.M. AND WE CLOSED THE VALVE AT 7:15 P.M. ALL PRODUCT SPILLED VAPORIZED. PETTY OFFICER EVANSON, NATIONAL RESPONSE CENTER, NOTIFIED AT APPROXIMATELY 8:30PM. HE ASSIGNED REPORT NUMBER 107752. RAILROAD COMMISSION OF TEXAS TRANSPORTATION/GAS UTILITIES DIVISION ANSWERING SERVICE NOTIFIED IMMEDIATELY AFTER CALL TO NRC.
2017-09-29 08:50 | YES | NO | 19920055 | 1992-02-28 | 15851 | PRIDE REFINING INC | NO | 1992-02-16 | 1620 | TX | JONES | ABILENE | NO |  | NO | APPROX. 7 MILES N OF ABILENE, TX OFF HWY 277 SURVEY H. MILLARD, TRACT 21, ABSTRACT 263. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OIL AND GASOLINE | 2 | 350 | 346 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 600 | 470 | YES | 8 | 750 |  |  | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON | 9156748231 | AT APPROXIMATELY 4:30 PM ON FEBRUARY 16, 1992 A MR DANNY FAULKS (LAND OWNER)STOPPED BY OUR REFINERY BILLING OFFICE AND NOTIFIED US THAT PRODUCT WAS LEAKING FROM OUR PIPELINE. AT WHICH TIME THEY NOTIFIED THE OPERATION SUPERVISOR STEVE ODOM, HE THEN CONTACTED MAINTANANCE CREWS TO ATTEND THE LEAK. EM-TEC ENVIRONMENTAL SERVICES WAS ALSO CONTACTED, THERE CREWS WERE DISPATCHED TO AID IN THE CLEAN UP. ALL MATERIAL WAS REMOVED AND CLEANED UP TO LAND OWNERS AND RAILROAD COMMISSIONS SPECIFICATIONS BY FEBRUARY 19TH,
2017-09-29 08:50 | YES | NO | 19920056 | 1992-03-04 | 809 | ARCO PIPE LINE CO | YES | 1992-03-04 | 1042 | OH | LUCAS | TOLEDO | NO |  | NO | TOLEDO STATION, 359 SINCLAIR, TOLEDO, OH. 43605 |  | TANK FARM | BOLTED FITTING |  | 1989 | OTHER | FAILED FLANGE GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 2 | 100 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY E GRAVES - MANAGER, OPERATIONS COMPLIANCE | 7139865330 | DELIVERY OF GASOLINE TO TANK 3514. SKILLET BLIND LEAKED UNTIL IT WAS DETECTED BY FIELD PERSONNEL. LINE WAS SHUT DOWN AND EMERGENCY RESPONSE WERE CALLED IN TO CLEAN UP SPILL.
2017-09-29 08:50 | YES | NO | 19920057 | 1992-03-20 | 26088 | SIGMOR PIPELINE CO | NO | 1992-01-21 | 1510 | TX | BEE | BERCLAIR | NO |  | NO | A 1/2 MILE SOUTH OF STATE HWY 59, APPROXIMATELY 9 1/2 MILES NORTH EAST OF BEEVILLE, TX |  | LINE PIPE | GIRTH |  | 1946 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 60400 | 47385.3506 | 95595.3918 | NATURAL GAS LIQUID | 2 | 6415 | 0 | Null | Null | 8 | 0.32 | 35000 | WELDED |  | 500 | 300 | YES | 24 | 760 | 7 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS - MANAGER PIPELINE SAFETY & REGULATIONS | 8063783583 | ON JANUARY 21, 1992, AT APPROXIMATELY 1510 HOURS (3:10 P.M.), THE SIGMOR PIPELINE COMPANY EXPERIENCED A PIPELINE BLOW-OUT ON THE REFUGIO/BERCLAIR SEGMENTOF THE 8" REFUGIO TO THREE RIVERS LPG PIPELINE. THE RUPTURE WAS THE RESULT OF A WELD FAILURE DUE TO CONSTRUCTION DEFECT. THERE WERE NO FATALITIES, INJURIES, FRIES OR EXPLOSIONS CONNECTED TO THIS ACCIDENT. THE SYSTEM WAS FULLY OPERATIONAL AT 1545 HOURS (3:45P.M.), JANUARY 25, 1992.
2017-09-29 08:50 | YES | NO | 19920058 | 1992-02-21 | 443 | AMOCO PIPELINE CO | YES | 1992-02-20 | 1500 | TX | HOCKLEY |  | NO |  | NO | GO SOUTH OF SUNDOWN, TX ON HWY 303 FOR 3 MILES, TURN WEST AT FIRST CURVE IN ROAD, GO WEST ON COUNTY ROAD 2 MILES TO FIRST CATTLEGUARD. AFTER CROSSING CATTLE GAU |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3138.1027 | 6330.8207 | CRUDE OIL | 1 | 60 | 50 | NO | NO | 16 | 0.25 | 0 | WELDED |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALBERT L WOOD JR. - PIPELINE MAINT. FOREMAN | 8068946187
2017-09-29 08:50 | YES | NO | 19920059 | 1992-03-20 | 18273 | SHELL PIPELINE CORP | NO | 1992-02-19 | 1015 | CA | KERN | BAKERSFIELD | NO |  | NO | BAKERSFIELD -CALIOLA 14-INCH. 2 1/2 MILES N OF TWISSELMAN ROAD NW 1/4, NW 1/4, SECTION 7, T-25-S,R-2--E |  | LINE PIPE | PIPE |  | 1967 | OTHER | CORROSION, EXTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 141214.621 | 284886.9293 | CRUDE OIL | 1 | 250 | 212 | NO | NO | 14 | 0.25 | 52000 | WELDED |  | 1170 | 1114 | YES | 24 | 1580 | 1 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.H. SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414506 | ELECTRICAL POWER OUTAGE RESULTED IN PRESSURE SURGE DUE TO PUMP STATION SHUTDOWN. PIPE FAILED AT EXTERNAL CORROSION PIT.
2017-09-29 08:50 | YES | NO | 19920060 | 1992-03-20 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1992-02-27 | 2124 | CA | CORONA |  | NO |  | NO | 275 N MAPLE ST, CORONA CA (LINE 90) |  | PUMPING STATION | PIPE |  | 1982 | OTHER | CRACK IN NIPPLE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 47071.5403 | 94962.3098 | CRUDE OIL | 1 | 600 | 500 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EILEEN J THRASHER/VICE PRESIDENT | 3104289300
2017-09-29 08:50 | YES | NO | 19920061 | 1992-03-16 | 13131 | CONOCO INC | YES | 1992-02-11 | 0 | MO | ST CHARLES | AUGUSTA | NO |  | NO | SECTION 8, TOWNSHIP 44 N, RANGE 1 E, ST.CHARLES COUNTY, MO. MILE POST 425.6 |  | LINE PIPE | VALVE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | GASOLINE | 2 | 624 | 573 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 900 | 250 | YES | 8 | 1167 | 7 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | LARRY F CLYNCH, MID-CONTINENT DIVISION MANAGER | 4057676352 | ON FEBRUARY 11, 1992 AT 12:15 HRS., A TRACK HOE OPERATED BY MURPHY BROTHERS CONSTRUCTED COMPANY, STRUCK AND RUPTURED CONOCO PIPE LINE'S NO. 1 WOOD RIVER LINE. THE CONTRACTOR WAS MOVING EARTH IN PREPARATION OF BACKFILLING A 16" GAS PIPELINE BEING LAID PARALLEL TO CONOCO'S TWO 10" LINES BY MISSOURI PIPELINECOMPANY. CONOCO'S LINES HAD BEEN PREVIOUSLY MARKED VIA THE ONE-CALL SYSTEN IOPERATING IN MISSOURI. ADDITIONALLY, CONOCO HAD INSTRUCTED MURPHY BROTHERS CONSTRUCTION NOT TO EXCAVATE OR MOVE HEAVY EQUIPMENT OVER THE MARKED LINES. HAVING NOT COMPILED WITH CONOCO'S REQUEST, THE LINE WAS RUPTURED. THE LINE WAS IMMEDIATELY ISOLATED WITH AUTOMATED BLOCK VALVES, AND REPAIR CREW DISPATCHED, BY OUR OIL MOVEMENTS GROUP IN HOUSTON, WHO MONITOR THE LINES 24 HOURS A DAY. ONCE ON SITE, CONTAINMENT DAMS WERE CONSTRUCTED TO LIMIT PRODUCT MIGRATION AWAY FROM THE RUPTURED LINE. CLEANUP WAS INITIATED AND THE LINE WAS REPAIRED AS SOON AS CONDITIONS WOULD ALLOW THE REPAIRS TO BE CONDUCTED SAFELY.
2017-09-29 08:50 | YES | NO | 19920062 | 1992-03-18 | 15490 | PHILLIPS PIPE LINE CO | YES | 1992-02-19 | 1500 | TX | MIDLAND |  | NO |  | NO | GOLDSMITH-BENEDUM, LINE 80-1-6, MP 60-04+22. SEC 27, BLOCK 37, T4S, T&P SURVEY. APPROXIMATELY 6 MILES NORTH OF MIDKIFF, TX, ON HWY. 3095, THEN EAST APPROXIMAT |  | LINE PIPE | BOLTED FITTING | BOLTED LEAK CLAMP | 1952 | OTHER | OLD BOLTED CLAMP BEGAN LE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 13336.9364 | 26905.9878 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 1100 | 840 | YES | 24 | 1375 | 9 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L J SCHIMTZ - TECHNICAL SERVICES COORDINATOR | 9186614814 | GAS ODOR WAS REPORTED BY THIRD PARTY. UPON EXCAVATION AN OLD BOLTED CLAMP WAS FOUND TO BE LEAKING. THE CLAMP AND PIPE SECTION WERE REPLACED WITH NEW PIP
2017-09-29 08:50 | NO | NO | 19920063 | 1992-03-20 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-02-25 | 835 | NC | GUILFORD | GREENSBORO | NO |  | NO | TANK 144 - PLANTATION'S GREENSBORO TANK FARM. ADDRESS: 6907-A WEST MARKET ST. GREENSBORO, NC 27409 |  | TANK FARM | TANK |  | 1973 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 16800 | 13180.0313 | 26589.4467 | TURBINE FUEL | 1 | 2 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - V P - OPERATION | 4043645916 | ON THE MORNING OT FEBRUARY 25, 1992, DURING A HEAVY RAINSTORM, A DISCOLORATION WAS NOTICED AT THE BOTTOM OF THE SHELL OF TANK 1444 AT PLANTATION'S GREENSBORO TANK FARM. PUMPOUT OF THE TANK BEGAN IMMEDIATELY AND WAS COMPLETED ON THE AFTERNOON OF FEBRUARY 26. THE TANK WAS CLEANED ON FEBRUARY 26TH AND 27TH. INSPECTION ON FEBRUARY 28TH REVEALED THAT PORTIONS OF THE FILLET WELD CONNECTING THE FILL LINE TO THE FLOOR PLATES HAD FAILED. SEVERAL CRACKS HAD OCCURRED IN AN AREA OF APPROXIMATELY EIGHT INCHES IN LENGTH WITH THE LONGEST SINGLE CRACK BEING APPROXIMATELY TWO INCHES. THE WELD WAS REPAIRED AND NON-DESTRUCTIVELY TESTED BY THE VACUUM BOX AND DYE PENETRANT INSPECTION METHODS.
2017-09-29 08:50 | YES | YES | 19920064 | 1992-03-17 | 10313 | KOCH PIPELINE INC | YES | 1992-03-29 | 912 | TX | MONTGOMERY |  | NO |  | NO | LOCATION OF ACCIDENT WAS WITHIN THE TEXACO CHEMICAL PLANT EMPLOYEE'S PARKING LOT, LOCATED ON JEFFERSON CHEMICAL ROAD, EAST OF CONROE, TEXAS. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 2 | 0 | 2 | 200000 | 156905.1344 | 316541.0326 | L. P. G. | 2 | 6713 | 0 | YES | NO | 10 | 0.37 | 30000 | WELDED |  | 750 | 652 | YES | 24 | 1007 | 5 | 81 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PERSONAL CONTACT BY COMP | NO | YES | JAMES H ELMORE, GENERAL MANAGER | 4053952377 | AN OUTSIDE CONTRACTOR WORKING ON A PARKING LOT STRUCK THE PIPELINE WITH CONSTRUCTION EQUIPMENT, TEARING A HOLE AND ALLOWING PRODUCT TO BE RELEASED WHICH IGNITED.
2017-09-29 08:50 | YES | NO | 19920065 | 1992-03-17 | 10313 | KOCH PIPELINE INC | NO | 1992-02-18 | 1036 | OK | CLEVELAND |  | NO |  | NO | ON PENN AVE 1 1/2 MILE S OF 149TH ST - OKLAHOMA CITY, OK. |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | L. P. G. | 2 | 2240 | 0 | NO | NO | 8 | 0.16 | 52000 | WELDED |  | 1200 | 750 | YES | 10 | 1587 | 10 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JAMES H ELMORE, GENERAL MANAGER | 4053952377 | DURING EXCAVATION BY A THIRD PARTY INSTALLING AN INTERSECTION PIPELINE, THISEXISTING PIPELINE WAS STRUCK AND RUPTURED ALLOWING LPG MIX PRODUCT TO RELEASE
2017-09-29 08:50 | YES | NO | 19920066 | 1992-03-16 | 12628 | MOBIL PIPELINE CO | YES | 1992-02-17 | 1000 | TX | FT WORTH |  | NO |  | NO | MRS GENEVA LEWIS - RESIDENCE. PHONE #817/457-5444 7633 JOHN T. WHITE ROAD; FT. WORTH, TX. |  | LINE PIPE | PIPE | PRE-FABRICATED 30DEG BEND | 1979 | OTHER | FLAW IN PRE-FABRICATED 30 | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 93600 | 73431.6029 | 148141.2032 | CRUDE OIL | 1 | 795 | 790 | NO | NO | 16 | 0.31 | 42000 | WELDED |  | 300 | 150 | YES | 25 | 1480 | 9 | 79 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.L. DENNARD - V P - OPERATIONS | 2146582226 | ON FEBRUARY 11, 1992, A SMALL NON-REPORTABLE CRUDE OIL LEAK WAS REPORTED BY THE LANDOWNER ON THE NORTH SIDE OF JOHN T. SHITE ROAD, FT WORTH, TX. CREW WERE DISPATCHED TO THE AREA AND THE PIPE WAS EXCAVATED. THIS LEAK WAS CAUSED BY A 1-1/2" CIRCUMFERENTIAL CRACK ON THE INSIDE RADIUS OF A PIPE BEND. TEMPORARY REPAIR WAS MADE. A DECISION WAS MADE TO REPLACE THE TWO PIPE BENDS AT THIS LOCATION. THE PIPELINE WAS SHUT DOWN AND THE EXCAVATION WAS LEFT OPEN. THIS SITE WAS MONITORED DAILY BY COMPANY PERSONNEL WHILE NEW PIPE BENDS WERE BEING MANUFACTURED AND TESTED. ON FEBRUARY 17, 1992, THE EXCAVATED BELL REMOVEAL OF THE CRUDE OIL. VACUUM TRUCKS WERE DISPATCHED. AFTER REMOVAL OF THE CRUDE OIL, A SECOND PIPE BEND FAILURE WAS FOUND. THIS FAILURE WAS CAUSED BY A CIRCUMFERENTIAL CRACK EXTENDING 3/4'S OF THE WAY AROUND THE PIPE BEND APPROXIMATELY 40" UPSTREAM OF THE FIRST CRACK. ON FEBRAURY 19, 1992, THE TWO FAULTYPIPE BENDS WERE CUT OUT AND REPLACED WITH NEW ONES. UPON REPLACEMENT OF THENEW PIPE BENDS, THE LINE WAS FILLED WITH CRUDE OIL AND RETURNED TO SERVICE.THE FAULTY PIPE BENDS HAVE BEEN TAKEN TO HOUSTON TO METALLURGIACL CONSULTANTS, INC. FOR TESTS TO BE CONDUCTED TO DETERMINE THE CAUSE OF FAILURE.
2017-09-29 08:50 | NO | NO | 19920067 | 1992-03-24 | 2552 | COLONIAL PIPELINE CO | YES | 1992-02-21 | 1900 | AL | BIBB |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S VANCE PUNP STATION. |  | PUMPING STATION | VALVE |  | 1972 | OTHER | UNIT CHECK VALVE SHAFT SE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6500 | 5099.4169 | 10287.5836 | KEROSENE | 2 | 3 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J L GAMBRELL - ADMIN. TECHNICAL & REGULATORY | 4048412402 | AT 1900 EST ON FEBRUARY 21, 1992, DURING A ROUTINE CHECK OF VANCE PUMP STAION NEAR VANCE, AL A TECHNICIAN DISCOVERED OIL STAINS ON THE GRAVEL NEAR A CHECKVALVE IN THE NO. 2 LINE STATION. THE NO. 2 LINE IS A 36" DIAMETER PIPELINE ORIGINATING IN HOUSTON, TX AND TERMINATING IN GREENSBORO, NC. SUPERVISORY PERSONNEL WERE NOTIFIED AND MAINTANANCE AND CLEAN UP CREWS CALLED. THE SOIL SURROUNDING THE CHECK VALVE AT THE NO. 3 PUMP WAS EXCAVATED. THE CAUSE TO THE LEAK WAS FOUND TO BE FAILED "O" RING ON THE CHECK VALVE SHAFT. THE PIPELINE WAS SHUTDOWN AND REPAIRS TO BE CHECK VALVE WERE MADE. APPROXIMATELY 3 BARRELS OF KEROSINE ESCAPED, ONE BARREL WAS RECOVERED AND RETURNED TO THE SYSTEM, THE BALANCE WAS ABSORBED INTO THE SURROUNDING SOIL AND GRAVEL. SOIL SAMPLES WERE TAKEN FROM THE SITE AND FORWARDED TO A LABORATORY FOR ANALYSIS. ON MARCH12, 1992, AFTER ANALYSES OF THE SOIL SAMPLES WERE RECEIVED, IT BECAME APPARENT THAT SOIL REMEDIATION COSTS WOULD PUSH TOTAL REPAIR COSTS PAST $5,000.00. AT 0920 EST ON MARCH 12, 1992, THE NATIONAL RESPONSE CENTER WAS ADVISED OF THE LEAK (REPORT NO. 110204).
2017-09-29 08:50 | NO | NO | 19920068 | 1992-03-25 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1992-02-06 | 1320 | TX | RUNNELS |  | NO |  | NO | APPROX. 7.1 MILES SE OF BRONTE, TX, AND 2.1 MILES SW OF HWY 158 (BRONTE-BALLINGER HWY); 5,000'E. OF COKE/RUNNELS COUNTY LINE, AT A POINT AT WHICH THE FINA PIPEL |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 47071.5403 | 94962.3098 | CRUDE OIL | 1 | 5 | 5 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED - REGULATORY COMPLAINCE SUPV | 9152645414 | FINA'S AERIAL PATROL REPORTED APPARENT LEAKAGE CAUSING A SHEEN ON THE COLORADO RIVER AT THE PIPELINE CROSSING SITE. THIS REPORT WAS MADE TO FINA'S FIELDPERSONNEL WERE ON-SCENE AT 3:45 P.M. THAT SAME DAY AND CONFIRMED LEAKAGE ANDBEGAN DEPLOYMENT OF CONTAINMENT DEVICES IN THE RIVER. REPORTS TO GOVERNMENTAGENCIES WERE MADE DURING THE AFTERNOON OF FEB. 6TH. AT THAT TIME, IT WAS ADSSUMED THAT THE LEAKAGE WAS ORIGINATING FROM THE ESIXTING 10"-DIAMATER PIPELINE. THIS PIPELINE WAS SHUT-DOWN, DISCONNECTED AT BOTH SIDES OF THE CROSSING, DRAINED OF OIL AND DISPLACED WITH WATER. A TEMPORARY 6" PIPELINE WAS INSTALLLED AT THE CROSSING SO AS TO ALLOW CONTINUED USE OF THE FACILITY DURING REPAIRS TO THE 10" LINE. EXCAVATION OF THE LEAKING PIPELINE WAS BEGUN ON FEBRUARY 14'TH, WITH THE INTENT OF THE COMPLETE REMOVAL AND REPLACEMENT OF THE CROSSING. EXCAVATION REVEALED THAT THE POINT OF LEAKAGE WAS ORIGINATING FROM A SECTION OF ABANDONED PIPE THAT THE PREVIOUS OWNER OF THE PIPELINE (ATLANTIC P/L CO.) HAD CUT-LOOSE AND LEFT IN THE CROSSING, WITH OIL REMAINING IN THE PIPE., WHEN THE CROSSING WAS REPLACED IN 1963. THE EXISTING, ACTIVE 10" PIPE AT THE CROSSING WAS HYRO-TESTED TO INSURE ITS INTEGRITY AND WAS RECONNECTED. THE SECTION OF ABANDONED, CORRODED AND LEAKING PIPE WAS REMOVED FROM THE CROSSIN
2017-09-29 08:50 | YES | NO | 19920069 | 1992-03-25 | 15851 | PRIDE REFINING INC | NO | 1992-02-12 | 1900 | TX | COLEMAN | VALERA | NO |  | NO | 1 MILE EAST OF VALERA ON NORTH SIDE SIDE OF HWY 67 IN COLEMAN COUNTY. |  | TANK FARM | TANK | TANK WAS VANDALIZED BY PE | 0 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4707.154 | 9496.231 | CRUDE OIL | 1 | 1000 | 823 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | VANDALIZED | Null | ONE CALL |  | Null | Null | JOHN T MACON - MANAGER PIPELINE | 9156748231 | SUPPLEMENTAL REPORT ON 8/16/94 INDICATED THAT AT APPROXIMATELY 7:00AM ON2-12-92, A CALL CAME INTO OUR 24 HOUR OPERATION DEPARTMENT THAT OIL WASSTANDING IN THE TANK DIKE AT OUR VALERA STATION. AT THAT TIME, WE DISPATCHEDAN EMPLOYEE TO CHECK OUT THE SITUATION. UPON ARRIVING, WE FOUND A 2"WATER-DRAW OFF VALVE OPEN WITH THE PLUG REMOVED, THUS RELEASING THE VOLUME OFOIL FROM THE STORAGE TANK. DOT #106484.
2017-09-29 08:50 | YES | NO | 19920071 | 1992-04-07 | 12471 | MID - VALLEY PIPELINE CO | YES | 1992-03-11 | 1711 | KY | GRAYSON |  | NO |  | NO | GRAYSON COUNTY, KENTUCKY (LAT 37 DEG. 18'35", LONG. 86 DEG.23'32" |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1569051.344 | 3165410.3257 | CRUDE OIL | 1 | 3780 | 3300 | YES | NO | 22 | 0.3 | 1021 | WELDED |  | 816 | 510 | YES | 24 | 1020 | 1 | 50 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | I B NEWMAN - MANAGER OF PIPELINE OPERATIONS | 9037570207 | APPROXIMATELY 50 RESIDENTS WERE EVACUATED BY THE SHERIFF'S DEPT., GRAYSON COUNTY, KY, FOR THE NIGHT OF MARCH 11. ONE OF THE RESIDENTS, A MRS. MCHUGH, COMPLAINED OF RESPIRATORY PROBLEMS, AND WAS TAKEN TO A LOCAL PHYSICIAN. THE ACTUAL CAUSE TO HER PROBLEM IS UNKNOWN AT THIS TIME. ON MARCH 12, READINGS ALONG THE ENTIRE ROUTE OF THE SPILL WERE TAKEN FOR H2S, LEL, AND HYDROCARBON VAPOR. BASED ON FINDINGS (NON DETECTABLE), THE FIRE CHIEF, LEITCHFIELD, KY, ADVISED ALL RESIDENTS THAT IT WAS SAFE TO RETURN TO THEIR HOMES THAT AFTERNOON.THERE WAS NO FIRE OR EXPLOSION AT THE TIME OF RELEASE. A FIRE DID OCCUR HOWEVER, ON MARCH 12, WHEN A BACKHOE WAS EXCAVATING THE PIPELINE AT THE ACCIDENTSITE. THE BUCKET OF THE BACKHOE STRUCK A ROCK, CAUSING IGNITION OF CRUDE REMAINING IN THE "BELL HOLE". THE FIRE WAS EXTINGUISHED WITH POWER AND FOAM,AND THERE WERE NO INJURIED NOR IMMEDIATE DANGER TO EMPLOYEES OF THE GENERALPUBLIC. ON MARCH 11, 1992, AT 1711 HRS. CST, MID-VALLEY'S 22" PIPELINE. LOCATED NEAR LEITCHFIEDL, GRAYSON COUNTY, KY, RUPTURED SPILLING APPROXIMATELY3,780 BBLS. OF CRUDE OIL INTO HARGUS CREEK AND BEAR CREEK. THE DROP IN PRESSURE WAS NOTED BY OUR DISPATCHERS AT LONGVIEW, TX, AND IMMEDIATE ACTION WASTAKEN TO SHUTDOWN AND ISOLATE THE LINE SECTION INVOLVED. SUCH ACTION WAS TAKEN PRIOR TO RECEIVING NOTIFICATION FROM ON OF OUR GRANTORS AND THE SHERIFF'SDEPT., GRAYSON COUNTY. THE LONGITUDINALLY ORIENTED SPLIT IN THE X52, .300",SEAMLESS PIPE, WAS 23" LONG ( AT THE 6:00 O'CLOCK POSITION), AND 3" WIDE ATTHE CENTER. THE PIPE WALL WAS WEAKENED BY THE LOSS OF METAL FROM EXTERNAL LOCALIZED CORROSION THAT EXTENDED FOR 65". THE REMAINING WALL THICKNESS ALONGTHE SPLIT RANGED FROM 50 TO 200 MILS. A CLOSE INTERVAL SURVEY, DONE IN 1990,1990, IDEICATED THAT THE PIPELINE WAS PROPERLY PROTECTED, WITH READINGS WELLABOVE 900MV, NEGATIVE, IN THE AREA OF THE FAILURE. REPAIRE TO THE 22" PIPELINE WERE COMPLETED AND THE LINE RETURNED TO SERVICE AT 1000HRS., MARCH 14,BY REMOVING A 57' SECTION OF PIPE, AND INSERTING 57' OF NEW PRETESTED .375"WALL X52 PIPE. THIS AMOUNT OF PIPE WAS NECESSARY TO FACILITATE PROPER LINEUPPRIOR TO WELDING. HOT TAPS WERE MADE APPROXIMATELY 1000' EITHER SIDE OF THEREPAIR SECTION IN ORDER TO REMOVE ANY REMAINING OIL IN THE PIPELINE, AND TOENSURE SAFETY DURING THE WELDING PROCESS. ALL OF THE WELDS USED IN THISREPAIR WERE 100% X-RAYED. THE LINE PRESSURE IN THIS AREA OF FAILURE ISBEING HELD TO A MAXIMUM OF 300 PSI UNTIL INSPECTION BY A MAGNAFLUX "SMART PIG" IS COMPLETE IN EARLY APRIL, 1992.
2017-09-29 08:50 | YES | NO | 19920072 | 1992-04-13 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1992-02-25 | 1300 | TX | REFUGIO | REFUGIO | NO |  | NO | 1.5 MI SOUTH OF REFUGIO PUMPING STATION BETWEEN HWY 774 AND HWY 2678 |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | L. P. G. | 2 | 20 | 0 | NO | NO | 10 | 0.19 | 1609 | WELDED |  | 750 | 340 | YES | 8 | 938 | 1 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W D PARTLOW | 7138777370 | LEAK WAS CAUSED BY EXTERNAL CORROSION. WAS REPAIRED BY REPLACING WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 19920073 | 1992-04-13 | 3370 | DIAMOND SHAMROCK REFINING & MARKETING CO | YES | 1992-02-20 | 917 | TX | WICHITA | IOWA PARK | NO |  | NO | 8 MILE SNORTH OF IOWA PARK ON FM HWY 368 AND 4 1/2 MIILES WEST ON FM 2345 THEN 1/2 MILE SOUTH. T.E. WILLIAMS SURVEY NO. 2, ABSTRACT 581. |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 64000 | 50209.643 | 101293.1304 | NATURAL GAS LIQUID | 2 | 4961 | 0 | NO | NO | 8 | 0.2 | 52000 | WELDED |  | 1550 | 1175 | YES | 24 | 2135 | 4 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COMPANY PROGRAM | NO | NO | GERALD CHILDERS - MANAGER, PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APPROXIMATELY 0917 HOURS ON FEBRUARY 20, 1992, WE EXPERIENCED A PIPELINE BLOW-OUT ON THE DAVIDSON TO WICHITA FALLS SEGMENT OF OUR 8" TRANS TEXAS LPG PIPELINE. THE RUPTURE WAS DUE TO A 3RD PARTY CONTRACTOR DIGGING A PIT FOR A DRILLING RIG. THERE WERE NO FATALITIES, INJURIES, FIRE OR EXPLOSIONS IN CONNECTION WITH THIS ACCIDENT. THE PIPELINE WAS REPAIRED AND RETURNED TO SERVICE WITHOUT FURTHER INCIDENT.
2017-09-29 08:50 | YES | NO | 19920074 | 1992-04-08 | 18706 | SUN PIPELINE CO | YES | 1992-03-04 | 2250 | PA | DELAWARE | EDGMONT | NO |  | NO | APPROX. 350 NW OF MEADOW LANE, EDGMONT TWP., DELAWARE CO., PA. |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1244000 | 975949.936 | 1968885.2226 | JET FUEL | 1 | 933 | 833 | NO | NO | 8 | 0.25 | 2430 | WELDED |  | 1100 | 500 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BOB ARNET - MANAGER, RISK MANAGEMENT EASTERN AREA | 2159755823 | SUN PIPE LINE CONTROL CENTER RECEIVED CALL FROM RESIDENT OF SHEPHERD LANE THAT OIL WAS SPRAYING OVER THE ROAD AT MEADOW & SHEPHERD LANE. UPON EXCAVATIONAND EXAMINATION, A 9" SPLIT WAS OBSERVED ON THE PIPE. IN CLOSE PROXIMITY TO THE SPLIT THERE WERE INDICATORS OF MECHANICAL DAMAGE TO THE PIPE.
2017-09-29 08:50 | YES | NO | 19920075 | 1992-04-20 | 4906 | EXXON PIPELINE CO | YES | 1992-03-20 | 900 | LA | ST MARTIN |  | NO |  | NO | OCCURRED IN ST. MARTIN PARISH, LA. FROM1-10, SOUTH ON LA HIGHWAY 31 APPROXIMATELY 2 MILES TO LA HIGWAY 94. FROM THE INTERSECTION OF HIGHWAY 31 AND 94 GO WEST |  | LINE PIPE | SCRAPER TRAP |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 137291.9926 | 276973.4035 | CRUDE OIL | 1 | 815 | 805 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | J B HOLT - MANAGER OF ENVIRONMENTAL AND REGULATORY COMPLAINC | 7136565521 | EXXON PIPELINE COMPANY (EPC) FIELD GAUGER WAS CONDUCTING ROUTINE WORK ASSIGNMENTS WHEN HE DISCOVERED THAT A 1/2 INCH VALVE WAS MISSING (DUE TO THIRD PARTY INTERVENTION) OFF A PIPELINE SENDING TRAP. THE CRUDE OIL WAS BEING RELEASEAT THIS POINT. EPC EMPLOYEE SECURED THE TRAP AND CONTACTED HIS SUPERVISOR.AT THIS TIME EPCS DIVISION OIL SPILL RESPONSE TERAM AND OIL SPILL CLEAN-UP CONTRACTORS WERE DISPATCHED TO THE LOCATION WITH OIL CONTAINMENT AND RECOVERYEQUIPMENT. THE CRUDE OIL WAS CONTAINED AND RECOVERED. THERE WERE NO DEATHSOR INJURIES, --- SPLOC CONTINUED - OCCURRED IN ST. MARIN PARISH, LA. FROM I-10, SOUTH ON LA HIGHWAY 31 APPROXIMATELY TWO MILES TO LA HIGHWAY 94. FROM THE INTESECTION OF HIFGHWAY 31 AND 94, GO WEST ON HWY 94 APPROXIMATELY THREE MILES TO OIL FIELD ROAD, SOUTH OF HWT 94. TAKE OIL FIELD ROAD (STAYING RIGHT) APPROXIMATELY TWO MILES TO LOCATION.
2017-09-29 08:50 | YES | NO | 19920076 | 1992-04-06 | 19585 | TRANS - MOUNTAIN OIL PIPELINE CO | YES | 1992-03-07 | 1600 | WA | WHATCOM |  | NO |  | NO | LAUREL STATION, 1009 EAST SMITH ROAD, BELLINGHAM, WASHINGTON. |  | TANK FARM | OTHER | RELIEF VALVE | 1992 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 78452.5672 | 158270.5163 | CRUDE OIL | 1 | 1250 | 1218 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  | 6037395280 | THE SUPPLY OF PRESSURIZED NITROGEN TO A GROVE PRESSURE RELIEF VALVE FAILED ALLOWING THE VALVE TO OPEN AT A PRESSURE BELOW THE SPECIFIED RELIEF SETTING. CRUDE OIL FROM THE PASSING STREAM FLOWED THROUGH THE RELIEF VALVE TO A RELIEFTANK. THE RELIEF TANK OVERFLOWED INTO ITS SURROUNDING DYKE AND APPROXIMATELY 50 BARRELS ESCAPED FROM THE DYKE. OF THE TOTAL 1250 BARRELS WHICH OVERFLOWED THE RELIEF TANK, 1218 BARRELS HAVE BEEN RECOVERED.
2017-09-29 08:50 | NO | NO | 19920077 | 1992-03-23 | 12627 | MOBIL OIL CORP | NO | 1992-03-02 | 800 | CA |  | LEBEC | NO |  | NO | M-1 ONEIL CANYON ROAD, LEBEC, CA |  | LINE PIPE | PIPE |  | 1982 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20100 | 15768.966 | 31812.3738 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 12.75 | 0.25 | 52000 | NO DATA |  | 1248 | 100 | YES | 8 | 1560 | 10 | 84 | EXTERNAL | Null | YES | NO DATA | CONCENTRATED CORROSION CE | NO DATA |  | Null | NO DATA |  | Null | Null | S S SOBEY, MANAGER OF OPERATIONS | 3104937237 | AIR PATROL NOTIFIED MOBIL OF POSSIBLE LEAK, MOBIL RESPONED IMMEDIATELY TO THE LOCATION AND SHUT THE PIPELINE DOWN. THE PIPELINE WAS EXCAVATED AND REPAIRED WITH A FULL ENCIRCLEMENT. PIPELINE SEGMENT WILL BE REPLACED PRIOR TO MAY,1992.
2017-09-29 08:50 | NO | NO | 19920078 | 1992-03-30 | 562 | ARCO OIL & GAS CO - DIV OF ATLANTIC RICHFIELD | NO | 1992-02-27 | 1500 | CA |  | LONG BEACH | NO |  | NO | 8TH STREET LONG BEACH, WEST OF SANTA FEE AVENUE (STATION 143+00 ON THE PIPELINE) |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 23535.7702 | 47481.1549 | OIL AND GASOLINE | 2 | 2 | 1 | NO | NO | 12 | 0.32 | 52000 | WELDED |  | 720 | 225 | YES | 4 | 900 | 11 | 90 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD L SOLOMON | 3104289027 | PIPELINE LEAKED AT LOCATION OF CORROSION PITTING.
2017-09-29 08:50 | YES | NO | 19920079 | 1992-03-24 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1992-02-29 | 1625 | NE | GAGE | BEATRICE | NO |  | NO | SECTION 31, TOWNSHIP 4 NORTH, RANGE 7 EAST, GAGE COUNTY, NEBRASKA |  | LINE PIPE | OTHER | NON SPECIFIED | 1969 | FAILED PIPE | CAUSE OF BREAK UNKNOWN AT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 235357.7016 | 474811.5489 | GASOLINE | 2 | 837 | 0 | NO | NO | 8.63 | 0.16 | 1881 | WELDED |  | 1354 | 1346 | YES | 24 | 1743 | 8 | 69 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S F ISAACS - PRESIDENT | 9185811800 | PIPE FAILED AT PRESSURE BELOW OPERATING PRESSURE. THE PIPE FIALED IN THE BASEMETAL, FIVE INCHES FROM THE ERW SEAM. THE FAILURE OCCURED AT A SPOT AFFECTEDBY LOCALIZED EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19920080 | 1992-03-27 | 12628 | MOBIL PIPELINE CO | YES | 1992-03-01 | 618 | TX | MONTAGUE |  | NO |  | NO | 3 MILES NORTH OF RINGGOLD, TX - RINGGOLD STATION |  | TANK FARM | TANK |  | 1961 | OTHER | ROOF DRAIN LINE RUPTURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1900 | 1705 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D L DENNARD - VICE PRESIDENT OPERATIONS | 2146582226 | THE ROOF DRAIN HOSE FOR TANK #2720 RUPTURED, THUS CAUSING CRUDE OIL TO ESCAPE FROM THE TANK. DUE TO RECENT HEAVY RAINS IN THE AREA, THE DIKE DRAIN VALVEFOR TANK #2720 WAS OPEN AND CRUDE OIL DRAINED FROM THE CONTAINMENT AREA. CREWS WERE DISPATCHED AND INITIATED RECOVERY AND CLEAN-UP OPERATIONS. TANK #2720 WAS PUMPED DOWN AND ISOLEATED UNTIL PERMANENT REPAIRS CAN BE MADE.
2017-09-29 08:50 | YES | NO | 19920081 | 1992-04-20 | 18277 | SHELL OIL CO | YES | 1992-03-18 | 1030 | TX | WINKLER | NORTREES | NO |  | NO | NE 1/4, NE 1/4, SECTION 19, BLOCK 7. WHEELER STATION. |  | TANK FARM | TANK |  | 1947 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 3530.3655 | 7122.1732 | CRUDE OIL | 1 | 4370 | 4350 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414507 | A 4-INCH GATE VALVE ON THE TANK DRAIN LINE FAILED. ALL BARRELS RELEASED WERE CONTAINED WITHIN THE TANK FIREWALL.
2017-09-29 08:50 | YES | NO | 19920082 | 1992-03-20 | 2733 | CHEVRON PIPELINE CO - MIDLAND DIV | YES | 1992-03-19 | 2315 | TX | MIDLAND |  | NO |  | NO | ROBERTS RANCH LPG PLANT, MIDLAND, TX 1/4 MILE SOUTH OF ROBERTS RANCH ROAD BETWEEN FM 1788 AND HWY 385. |  | LINE PIPE | PIPE |  | 0 | FAILED PIPE | CORROSION | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 78452.5672 | 158270.5163 | L. P. G. | 2 | 0 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | K C CROWELL - DISTRICT SUPERVISOR | 9153356210 | AT ABOUT 11:15 PM AN OXY USA DRY GAS LINE RUPTURED. THE 4" PIPE RUPTURED UNDERNEATH CPL'S KOCH QUANNA LPG METER SKID. ROBERTS RANCH PLANT PERSONNEL INDICATED THERE WERE 2 MASSIVE EXPLOSIONS AND A RESULTING FIRE. FIRE OFFICIALS RESPONDED BUT DID NOT INTERVENE AND FIRE WAS ALLOWED TO BURN ITSELF OUT. CPL'S LPG METERING FACILITY WAS COMPLETELY DESTROYED BY THE EXPLOSION AND FIRE.SINCE EXPLOSION AND FIRE WAS CAUSED BY OXY'S PIPELINE RUPTURE, WE CANNOT FILL OUT SECTIONS H AND I ON THE ACCIDENT REPORT FORM.
2017-09-29 08:50 | YES | NO | 19920083 | 1992-04-17 | 4906 | EXXON PIPELINE CO | YES | 1991-10-30 | 950 | TX | REFUGIO |  | NO |  | NO | 1 MILE NORTH OF MELON CREEK, 10 MILES SOUTHEAST OF REFUGIO CITY, TX ON INGLESIDE TO VANDERBILT 16-INCH PIPELINE. |  | LINE PIPE | GIRTH |  | 1966 | FAILED WELD | SUBSIDENCE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 241119.0441 | 486434.5039 | CRUDE OIL | 1 | 1150 | 1100 | NO | NO | 16 | 0.22 | 56000 | WELDED |  | 1104 | 820 | YES | 4 | 1380 | 1 | 66 | NO DATA | Null | Null | NO DATA |  | SUBSIDENCE |  | Null | NO DATA |  | Null | Null | J B HOLT - ENVIRONMMENTAL/REGULATORY COMPLAINCE MANAGER | 7136565521 | AT APPROXIMATELY 0950 HOURS ON 10-30-91, IT WAS NOTED THAT THE FLOW RATE AT INGLESIDE WAS INCREASING WHILE THE LINE PRESSURE AT SITE FM 136 WAS DECREASING. OTCC SHUTDOWN THE LINE AT 0954 HOURS. THE LINE WAS FLOWN AND THE LEAK WAS DETECTED APPROXIMATELY ONE MILE FROM THE MISSION RIVER AT 1230 HOURS AND IMMEDIATELY REPORTED. EMERGENCY CREWS WERE DISPATCHED TO REPAIR THE LINE AND CLEAN UP THE AREA. A PLIDCO SLEEVE WAS PLACED OVER THE LEAK AND OPERATIONS RESUMED AT 0230 HOURS ON 10-31-91. CLEAN UP CONSISTED OF REMOVING OIL WITH VACUUM TRUCKS TO FRAC TANKS, AND BURNING OFF OIL RESIDUE AND OILY WEEDS WITH A CONTROLLED FIRE PER THE LANDOWNER'S REQUEST. AUTHORITY FOR THE FIRE WAS RECEIVED FROM TOM PALMER OF THE TABC ON 11-4-91.
2017-09-29 08:50 | YES | NO | 19920084 | 1992-04-21 | 18706 | SUN PIPELINE CO | YES | 1992-03-18 | 1230 | PA | LANCASTER | PA | NO |  | NO | ROSEVILLE RD., MANHEIM TWP., LANCASTER PA |  | LINE PIPE | PIPE |  | 1955 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 708000 | 555444.1758 | 1120555.2553 | TOLUENE | 3 | 400 | 200 | NO | NO | 2 | 0.22 | 2590 | WELDED |  | 1200 | 792 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KEVIN D. FULMER - ENVIRONMENTAL SPECIALIST | 2159755920 | A CALL WAS MADE TO THE GLENHARDIE CONTROL CENTER BY BETTY KIMMET, AN EMPLOYEE OF SCHWANGER BROS OIL COMPANY, ON WHOSE PROPERTY THE LINE WAS LOCATED, TO ADVISE OF THE STAIN AND POOL OF PRODUCT AT A 2" TAKE-OFF TO OLD LANCASTER TERMINAL. A SUN PIPE LINE EMPLOYEE WAS IN THE AREA AND RESPONDED WITHIN 15 MINUTES. THE INVESTIGATION CONFIRMED THE LEAK WAS FROM THE SUN PIPE LINE FACILITIES AND RESPONSE SET IN MOTION. VALVES ON EACH SIDE OF THE LEAK AREA WERE CLOSED. THE LINE WAS NOT OPERATING AT THE TIME OF THE INCIDENT.
2017-09-29 08:50 | YES | NO | 19920085 | 1992-05-04 | 13131 | CONOCO INC | YES | 1992-04-15 | 2015 | MT | MISSOULA |  | NO |  | NO | SEC 8, T13N, R19N |  | PUMPING STATION | VALVE |  | 1953 | OTHER | O-RING GASKET FAILED ON S | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 47071.5403 | 94962.3098 | GASOLINE | 1 | 75 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W BEGGS - COORDINATOR OF REGULATORY COMPLIANCE | 3036494090
2017-09-29 08:50 | YES | NO | 19920086 | 1992-05-05 | 4906 | EXXON PIPELINE CO | NO | 1992-04-05 | 1900 | TX | GALVESTON |  | NO |  | NO | ACCIDENT OCCURRED ON UNION CARBIDE PLANT PROPERTY IN TEXAS CITY, GALVESTON CO., NEAR 5TH AVE AND GRANT STREET. |  | PUMPING STATION | OTHER | EXACT ITEM UNKNOWN | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 235357.7016 | 474811.5489 | L. P. G. | 2 | 67 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | J B HOLT - MANAGER ENVIRONMENTAL/ REGULATORY COMPLAINCE DEPT | 7136565521 | ON APRIL 5, 1992 AT APPROXIMATELY 1800 HOURS, UNION CARBIDE CALLED EXXON PIPELINE'S OTCC (OIL TRAFFIC CONTROL CENTER) DISPATCHER AND REPORTED A FIRE AT EPC'S UNION CARBIDE METER SKID. THE OTCC DISPATCHER IMMEDIATELY SHUTDOWN THE PIPELINE SYSTEM AND REMOTELY CLOSED THE BLOCK VALE ON 38TH STREET. THE PIPELINE WAS COMPLETELY DRAINED BY 2235 HOURS. THE FIRE WAS EXTINGUISED BY THE LOCAL FIRE DEPARTMENT APPROXIMATELY AT 2300 HOURS. ON APRIL 6, 1992, FIRE DAMAGED ASSESSMENT WAS UNDERWAY. BURNED FACILITIES (METER AND CONTROL BUILDING) WERE REMOVED FROM SITE AND PREPARATIONS MADE FOR REPLACEMENT. CAUSE OF FIRE STILL UNDER INVESTIGATION AND UNDERTERMINED AT THIS TIME.
2017-09-29 08:50 | YES | NO | 19920088 | 1992-02-17 | 443 | AMOCO PIPELINE CO | NO | 1992-02-15 | 530 | TX | GALVESTON |  | NO |  | NO | AMOCO PIPELINE COMPANY, TEXAS CITY STATION (PRODUCTS PUMP STATION) AMOCO OIL REFINERY PLANT PROPERTY. |  | PUMPING STATION | OTHER | POP-OFF VALVE | 1991 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 784525.672 | 1582705.1629 | GASOLINE | 2 | 50 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES P BLACK - COMPLIANCE SUPERVISOR | 4099386900 | POP-OFF VALVE MALFUNCTIONED AND RELIEVED PRODUCT INTO THE STATION SUMP. THESUMP OVERFLOWED RELEASING APPROXIMATELY 50 BBL'S. OF UNLEADED GASOLINE. ALLTHE GASOLINE WAS CONTAINED ON AMOCO OIL REFINERY PROPERTY.
2017-09-29 08:50 | YES | NO | 19920089 | 1992-04-13 | 2731 | CHEVRON PIPELINE CO | NO | 1992-03-31 | 1600 | TX | FORT BEND | THOMPSON | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1176.7885 | 2374.0577 | CRUDE OIL | 1 | 100 | 98 | NO | NO | 6.63 | 0.25 | 0 | WELDED |  | 30 | 30 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R E CURL - SAFETY SPECIALIST | 4098393100 | AT APPROXIMATELY 7:QA.M. ON 2-12-92 CALL CAME INTO OUR 24HR. OPERATION THAT OIL WAS STANDING IN THE TANK DIKE AT OUR VALERA STATION. AT THAT TIME WE DISPATCHED EMPLOYEE TO CHECK OUT THE SITUATION. UPON ARRIVUNG WE FOUND A 2" WATER-DRW OFF VALVE OPEN WIHT THE PLUG REMOVED, THUS RELEASING VOLUME OF OIL FROM STORAGE TANK. CALLED D.O.T. AT APPROXIMATELY 8:15 A.M. 2-12-92. DOT #106484
2017-09-29 08:50 | NO | NO | 19920090 | 1992-05-15 | 10312 | GULF CENTRAL PIPELINE CO | YES | 1992-04-16 | 840 | IA | WOODBURY |  | NO |  | NO | TWN 86N, RANGE 43W, SEC 19, MILEPOST 7-71.6 |  | LINE PIPE | PIPE |  | 1970 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 156.9051 | 316.541 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 6 | 0.19 | 35000 | NO DATA |  | 1340 | 400 | YES | 72 | 1991 | 5 | 70 | NO DATA | Null | Null | NO DATA |  | OTHER | NON SPECIFIED | Null | NO DATA |  | Null | Null | JIM NORVELL - GOV'T REGULATION COORDINATOR | 3144865488 | ON 4/16/92 BRAIN STICKNEY OF SMITHLAND, IOWA (TEL.712/889-2111) REPORTED SMALL WISP OF NH3 VAPOR COMING FROM GROUND. HE THOUGHT HE MAY HAVE HIT THE PIPETHE NIGHT BEFORE WITH HIS PLOW WHILE FARMING. COMPANY PERSONNEL RESPONDED AND FOUND A 1" GASH ON THE LINE. A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED ON THE GASH AND A SECOND SLEEVE WAS INSTALLED ON A DENT FROM THE SAME INCIDENT. A TERRACE WILL BE BUILT TO PROTECT THE PIPELINE AT THIS SITE. RETURNED TO SERVICE @ 1920 HOURS. NO CONTAMINATION OF WATER OR DAMAGE TO WILDLIFE.
2017-09-29 08:50 | YES | NO | 19920091 | 1992-07-30 | 443 | AMOCO PIPELINE CO | YES | 1992-06-30 | 1000 | OK | CREEK | DRUMRIGHT | NO |  | NO | AMOCO PIPELINE COMPANY'S DRUMRIGHT STATION. SOUTHWEST QUARTER OF SECTION 33, TOWNSHIP 18 N, RANGE 7EAST. |  | TANK FARM | PIPE |  | 1966 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 784.5257 | 1582.7052 | CRUDE OIL | 1 | 80 | 79 | NO | NO | 2 | 0 | 0 | WELDED |  | 275 | 100 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA | NON SPECIFIED | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN W CARICO - AREA MANAGER | 9182257271 | WHILE TESTING RELIEF VALVES AT OUR DRUMRIGHT STATION, A LEAK OCCURRED IN 1 2" LINE IN THE MANAIFOLD PIPING. APPROXIMATELY 10 BARRELS OF CRUDE OIL WAS INITIALLY RELEASED BEFORE A CATCH BASIN/PIT WAS DUG AT THE RELEASE POINT. THE ADDITIONAL 70 BARRELS REPORTED WAS RELEASED INTO THIS PIT WHILE VACUUM TRUCKSCONTINUALLY RECOVERED IT.
2017-09-29 08:50 | NO | NO | 19920093 | 1992-05-12 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-03-20 | 1500 | MS | COVINGTON | COLLINS | NO |  | NO | PLANTATION'S TANK FARM LOCATED AT COLLINS, MISSISSIPPI; TANK NO. 110 |  | TANK FARM | TANK |  | 1963 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 23000 | 18044.0905 | 36402.2187 | TURBINE FUEL | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VICE PRESIDENT - OPERATIONS | 4043645916 | ON AFTERNOON OF MARCH 20, 1992, DURING A ROUTINE EXTERNAL INSPECTION, A DISCOLORATION WAS NOTICED IN THE GRAVEL ADJACENT TO THE VALVE BOX FOR TANK 110 ATPLANTATION'S COLLINS TANK FARM. THE TANK WAS EMPTY, THOUGH NOT DRY, AT THE TIME OF THIS DISCOVERY. THE TANK WAS IMMEDIATELY TAKEN OUT OF SERVICE, AND CLEANING OF THE TANK WAS PERFORMED MARCH 24-25. INSPECTION ON MARCH 26 REVEALED A BY 6-INCH LONG CRACK IN A WELD CONNECTING THE SUMP TO THE FLOOR OF THE TANL. THE WELD WAS REPAIRED AND A HYDROSTATIC BOTTOM LEAK TEST WAS PERFORMED.
2017-09-29 08:50 | NO | NO | 19920095 | 1992-04-30 | 2330 | CHEVRON PIPELINE CO | YES | 1992-04-23 | 1130 | OR | MALHEUR |  | NO |  | NO | WEST 1 1/2 MILES ON HIGHWAY 201 FROM 184 EXIT 274 |  | LINE PIPE | OTHER | WELD PLUS ENDS | 1950 | FAILED WELD | FAILED WELD PLUS END | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | GASOLINE | 1 | 0 | 0 | Null | Null | 8 | 0.25 | 45000 | WELDED |  | 1856 | 700 | YES | 8 | 2325 | 1 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN A MARTOCCIA | 2083751463 | THE MAIN LINE CREW WAS VERIFYING DATA FROM BRITISH GAS SMART PIG. THEY FOUND CONTAMINATED SOIL, THEY EXPOSED 60' OF MAIN LINE AND UNCOVERED TWO WELD PLUS ENDS WHICH WERE WEEPING. PRESSURE AT THAT TIME WAS 700 PSI. THE WELD PLUSENDS WERE CUT OUT AND NEW PIPE INSTALLED.
2017-09-29 08:50 | YES | NO | 19920096 | 1992-06-04 | 18273 | SHELL PIPELINE CORP | YES | 1992-05-03 | 730 | OK | PAYNE | CUSHING | NO |  | NO | SW 1/4, NE 1/4, SECTION 15, T-17-N, R-5-E CUSHING TANK FARM |  | TANK FARM | VALVE |  | 1938 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 3415 | 2679.1552 | 5404.9381 | CRUDE OIL | 1 | 221 | 180 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414506 | A HEADER VALVE WAS IN ADVERTENTENTLY LEFT OPEN ALLOWING OIL TO BE RELEASED FROM A DEAD LEG OF PIPING. THE PIPING WAS REMOVED AND THE VALVE WAS BLINDED.
2017-09-29 08:50 | NO | NO | 19920097 | 1992-05-24 | 12127 | MARATHON PIPE LINE CO | YES | 1992-05-01 | 1300 | IL | CLARK |  | NO |  | NO | IN A CORNFIELD 1/2 MILE NE OF THE TOWN OF MARTINSVILLE, IN MARTINSVILLE TOWNSHIP, CLARK COUNTY, ILLINOIS, S5, TION, R13W. |  | LINE PIPE | LONGITUDINAL WELD |  | 1960 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19613.1418 | 39567.6291 | OIL AND GASOLINE | 3 | 0 | 0 | Null | Null | 10 | 0.31 | 35000 | WELDED |  | 1200 | 0 | YES | 8 | 1682 | 1 | 1988 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J W KINNISON - PRESIDENT | 4194222121 | ON MAY 1, 1992, AT APPROXIMATELY 1300 HOURS CENTRAL DAYLIGHT SAVINGS TIME, MARATHON PIPE LINE COMPANY, MARTINSVILLE OFFICE, WAS NOTIFIED OF A 2-FOOT WET SPOT OF PETROLEUM PRODUCT IN A FARMER'S CORNFIELD. UPON NOTIFICATION, THE OPERATIONS CENTER WAS INSTRUCTED NOT TO RESTART THE LINE UNTIL FURTHER NOTICE. MPL PERSONNEL RESPONDED TO THE LEAK SITE AND EXCAVATED THE AREA SURROUNDING THE PIPELINE SECTION. A CRACK IN A LONGITUDINAL WELD ON A PREVIOUSLY INSTALLED LEAK PLATE WAS DETERMINED TO BE THE SOURCE OF THE LEAK. THE WELD CRACK WASPATCHED WITH A CLAMP UNTIL PIPE REPLACEMENT COULD TAKE PLACE. ON MAY 2, 1992, THE LINE WAS PLACED BACK INTO SERVICE AND THE INTEGRITY OF THE CLAMP WAS VISUALLY CONFIRMED. THE MAOP WAS REDUCED FROM THE NORMAL 1200 PSI TO 500 PSI. ON MAY 7, 1992, THE DEFECTIVE SECTION WAS REPLACED WIHT 95 FT. OF COMPARABLE, HYDROSTATICALLY TESTED, NEW PIPE AND THE MAOP WAS RETURNED TO THE NORMAL 1200 PSI.
2017-09-29 08:50 | YES | NO | 19920098 | 1992-05-24 | 12127 | MARATHON PIPE LINE CO | YES | 1992-05-01 | 859 | IN | ST JOSEPH | SOUTH BEND | NO |  | NO | SOUTH BEND, NORTH OF CLEVELAND RD. ON MAYFLOWER RD. DEAD END SOUTH ON INDIANA TOLL ROAD I80 & 90. SEC. 20, T38N, R2E, GERMAN TWP., ST. JOSEPH COUNTY, INDIANA. |  | LINE PIPE | PIPE |  | 1957 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | GASOLINE | 3 | 119 | 0 | NO | NO | 6 | 0.25 | 42000 | WELDED |  | 1440 | 80 | YES | 8 | 1955 | 1 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | J W KINNISON - PRESIDENT | 4194222121 | ON MAY 1, 1992, AT 0859 CENTRAL DAYLIGHT SAVINGS TIME, MARATHON PIPE LINE OPERATIONS CENTER RECEIVED A CHANGE IN PRESSURE ALARM. AT 0902, A METER FAILURE ALARM (INDICATING NO FLOW) WAS RECEIVED AND BY 0903 PUMPING UNITS WERE SHUTDOWN AT HAMMOND, INDIANA, TERMINAL. AN EXCAVATION CONTRACTOR GRATING TOP SOIL WITH A BULLDOZER, PUNCTURED THE 6" PIPELINE WITH THE BLADE. THE PIPELINE REMAINED COVERED WITH EARTH REDUCING THE AMOUNT OF PRODUCT LOSS. THE LINE HAD BEEN PREVIOUSLY LOCATED AND FLAGGED BY MPL EMPLOYEES AND WAS FOUND AT A DEPTH OF 3.5'. AT THE TIME THE LINE WAS PUNCTURED, RIGHT-OF-WAY MARKERS AND UTILTITY SIGNS WERE IN PLACE, 58' NORTH AND UPGRADE OF THE POINT OF IMPACT. APPROXIMATELY THREE FEET OF THE DAMAGED PIPE WAS REPLACED WITH COMPARABLE HYDROSTATICALLY TESTED PIPE. THE EXCAVATION CONTRACTOR IS COORDINATING WITH THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT THE REMEDIATION OF THE AFFECTED AREA.
2017-09-29 08:50 | YES | NO | 19920099 | 1992-05-29 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-05-02 | 2055 | GA | COBB |  | NO |  | NO | 101 FEET WEST OF IVY POINTE DRIVE |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 535000 | 419721.2345 | 846747.2621 | GASOLINE | 3 | 165 | 165 | NO | NO | 26 | 0.31 | 52000 | WELDED |  | 720 | 520 | YES | 24 | 1204 | 8 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ROY M CROOK | 4043645916 | (DUE TO NATURE OF LEAK (3" HAIRLINE CRACK IN THE PIPE). IT IS IMPOSSIBLE TOPROVIDE AN ACCURATE ESTIMATE OF THE TOTAL AMOUNT OF PRODUCT RELEASED.) ($400,000 OT THE ESTIMATED TOTAL PROPERTY DAMAGE IS TO COVER EXPECTED ENVIRONMENTAL CLEAN-UP COSTS DURING THE NEXT 2-3 YEARS.) AT APPROXIMATELY 8:55 P.M., EDT, ON MAY 2, 1992, A LEAK WAS DISCOVERED ON PLANTATION'S 26-INCH, .312 WALL THICKNESS, GRADE X-52, PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN COLLINS, MISSISSIPPI, AND GREENSBORO, NORTH CAROLINA. THE LEAK OCCURRED 101 FEETWEST OF IVY POINTE DRIVE IN COBB COUNTY, GEORGIA. THE LINE PIPE HAD A THREE-INCH LONG HAIRLINE CRACK IN THE TWELVE O'CLOCK POSITION. THE SECTION OF THEPIPE WHICH FAILED WAS SEVERLY SCRATCHED AND DENTED OVER APPROXIMATELY 14 FEET OF THE PIPE. THE SCRATCHES AND DENTS WERE APPARENTLY MADE DURING SUBDIVISION DEVELOPMENT BY EXCAVATION EQUIPMENT WHILE BURYING BUILDING DEBRIS (WOODEN POLES, RAILROAD TIES, PIPE AND PIECES OF METAL) OVER THE PIPELINE. THE PIPECRACKED THROUGH ONE OF THE DENTS. THE PIPELINE WAS REPAIRED WITH TWO 3' LONG FULL ENCIRCLEMENT SLEEVES AND ONE 8' LONG FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19920100 | 1992-06-05 | 13131 | CONOCO INC | YES | 1992-05-24 | 230 | OK | GRANT |  | NO |  | NO | 5 MILES NORTH AND 4 MILES EASY OF KREMLIN, OKLAHOMA |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 392.2628 | 791.3526 | TRANSMIX (PART. REFINED PETRO) | 2 | 34 | 0 | NO | NO | 4 | 0.13 | 42000 | WELDED |  | 1152 | 246 | YES | 8 | 1440 | 1 | 82 | EXTERNAL | Null | YES | OTHER | CREVICE (SPOT) CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | MAX COBB | 4057673563 | AT APPROXIMATELY 12:30 ON THE 23RD OF MAY A PRESSURE DROP WAS ONSREVED ON THE DESCRIBED PIPELINE. A SPILL CLEAN-UP CREW WAS DISPATCHED, AND THE RELEASE WAS FOUND BY 02:30 ON THE 24TH. AS SOON AS THE AREA WAS CLEAR OF PBC VAPORS,THE LINE WAS DUG OUT AND REPAIRED. BY 10:30 ON THE 24TH, THE PIPELINE WAS REPAIRED AND PLACED BACK INTO SERVICE.
2017-09-29 08:50 | NO | NO | 19920101 | 1992-06-05 | 22610 | WILLIAMS PIPELINE CO | YES | 1992-05-09 | 1230 | IL | FRANKLIN |  | NO |  | NO | IN NATIONAL CONCRETE PIPE COMPANY'S YARD - 11825 FRANKLIN AVENUE, FRANKLIN PARK, ILLINOIS. |  | LINE PIPE | GIRTH |  | 1956 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 15690.5134 | 31654.1033 | OIL AND GASOLINE | 3 | 42 | 6 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1000 | 619 | YES | 8 | 1514 | 11 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S BALL - VICE PRESIDENT - OPERATIONS & ENGR | 9185883850 | ON MAY 6, 1992, NATIONAL CONCRETE PIPE COMPANY CALLED SAYING THEY THOUGHT THEY SMELLED GAS. THE PIPELINE WAS IDLE AT THE TIME AND HAD BECOME SLACK. THE#6-12" LINE TEES INTO DUAL 8" LINES ON THE PROPERTY. THE LINE WAS PRESSUREDUP AND EXPERIENCED A SLOW DROP IN PRESSURE. THE 8" LINES WERE ISOLATED BY BLIND FLANGES AND DETERMINED THAT ONE HELD SOLID AND THE OTHER CONTINUED TO EXPERIENCED A SLOW PRESSURE DROP. THE LINE WAS PURGED WITH WATER AND PRESSURE TESTED USING A TRACER GAS UNTIL THE LEAK WAS FOUND. THE LEAK WAS IN A DEFECTIVE GIRTH WELD. IT WAS REPAIRED USING A FULL ENCIRCLEMENT SLEEVE. PRESSURERECORDS INDICATE THE LINE BEGAN LEAKING APRIL 8, 1992, AND APPROXIMATELY 42 BARRELS LEAKED BASED ON PRESSURE CALCULATIONS. THE ORIGINAL CALL WAS COINCIDENTAL AS IT TURNED OUT IT WAS NOT THE LEAK, BUT SOME TYPE OF SPILLED SOLVENT BEING SMELLED.
2017-09-29 08:50 | YES | NO | 19920102 | 1992-06-22 | 18718 | SUN PIPELINE CO | NO | 1992-05-27 | 945 | OK | PIERSON | OKLAHOMA | NO |  | NO | SOUTH OF PIERSON 2 1/2 MILES ON OLD HIGWAY TO WATER TANKS, EAST 1 1/4 MILES SOUTH INTO SW 1/4 SECTION 33-7N-4E |  | LINE PIPE | PIPE |  | 1974 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2353.577 | 4748.1155 | CRUDE OIL | 1 | 180 | 175 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 790 | 400 | YES | 24 | 1075 | 9 | 76 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MARK D PACSKOWSKI | 9185866942 | ST. LOUIS WELL SERVICE WAS WORKING ON WELL AT THIS LOCATION. PRODUCER HIREDP & H CONSTRUCTION COMPANY TO AID IN REMOVING WOR OVER RIG. P & H CONSTRUCTION COMPANY DOZER OPERATOR WAS REBUILDING ROAD DITCH WHEN HE STRUCK THE PIPELINE, WHICH WAS VERY WELL MARKED, WITH DOZER BLADE PUNCTURING 6" TO 7" GASH INPIPELINE. DOZER IMMEDIATELY CONSTRUCTED A DAM CONTAINING MOST OF THE CRUDE OIL. (CONTRACTOR NEVER CALLED ONE-CALL TO REQUEST TEMPORARY MARKING OF PIPELINE).
2017-09-29 08:50 | YES | NO | 19920103 | 1992-06-30 | 11237 | T E PRODUCTS PIPELINE COMPANY, L P | YES | 1991-05-27 | 1330 | AR | PULASKI | NORTH LITTLE ROCK | NO |  | NO | APPRO. 1.0 MILE E OF INTERSECTION OF STATE HWY 130 AND U.S. ROUTE 70, NORTH LITTLE ROCK. |  | LINE PIPE | OTHER | GASKET | 1978 | OTHER | GASKET FAILURE-UNKNOWN RE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 66000 | 53046.1897 | 107015.5908 | DIESEL FUEL | 3 | 1520 | 1500 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O HORTON CUNNINGHAM - V P - OPERATIONS | 7137593615 | AT 1840 HOURS, MAY 27, 1992, TEPPCO PERSONNEL WERE NOTIFEID THAT A LEAK HAD BEEN OBSERVED WITH DIESEL FUEL ESCAPING FROM A VALVE BOX ON T.E. PRODUCTS PIPELINE COMPANY'S 16" LINE P-62. EMERGENCY SHUT DOWN PROCEDURES WERE INITIATEDIMMEDIATELY BY THE PRIMARY CONTROL CENTER, LOCATED IN HOUSTON, TEXAS AND THESECONDARY CONTROL POINT, LOCATED IN EL DORADO, ARKANSAS. THE UPSTREAM BLOCKVALVES WERE CLOSED. THE DOWNSTREAM STATIONS WERE ALLOWED TO RUN TO REDUCE THE PRESSURE AT THE LEAK SITE. THE BLOCK VALVES DOWNSTREAM WERE THEN CLOSED AND THE LEAK SITE WAS ISOLATED. ONCE ISOLATED, IT WAS DETERMINED A LEAKING GASKET HAD CAUSED THE RELEASE. REMOVAL OF THE FAULTY GASKET AND INSTALLATION OF A NEW GASKET WAS COMPLETED BY 0345 HOURS, MAY 28, 1992. THE LINE WAS THENREPRESSURIZED AND THE FLANGES WERE CHECKED TO DETERMINE THERE WAS NO LEAKAGE. THE SYSTEM WAS RESTARTED AT 0450 HOURS, MAY 28, 1992.
2017-09-29 08:50 | YES | NO | 19920104 | 1992-06-23 | 4906 | EXXON PIPELINE CO | YES | 1992-05-21 | 1000 | TX | RUSK |  | NO |  | NO | OCCURRED IN RUSK COUNTY, TX. FROM THE INTERSECTION OF HWY 42&64, W ON HWY 64 APPRO. 2.5 MI, S ON OIL FIELD RD APPROX. 3 MILES UNTIL EPC R-O-W, W APPRO. 250YDS |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 37000 | 29027.4499 | 58560.091 | CRUDE OIL | 1 | 500 | 490 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 800 | 720 | YES | 8 | 1000 | 1 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MANAGER ENVIRONMENTAL & REGULATORY COMPLAINCE DEP | 7136565521 | EXXON PIPELINE COMPANY (EPC) WAS CONDUCTING A ROUTINE SCRAPER RUN ON THE BULLARD TO ARP 8" TRUNK LINE. APPARENTLY, THE SCRAPER BECAME LODGED IN RECEIVING TRAP BLOCK VALVE WHICH CAUSED THE LINE TO PRESSURE UP. ALSO, THE PIPELINE HAD EXTERNAL CORROSION IN THE AREA OF THE LEAK PROVIDING A WEAK SEGMENT IN THE LINE. THE COMBINATION OF LINE PRESSURE AND EXTERNAL CORROSION CAUSED THE LEAK. THE SYSTEM DID LICK-OUT ON HIGH DISCHARGE. AIR PATROL REPORTED A LEAK; EPC PERSONNEL AND CONTRACTORS RESPONDED TO THE SITE TO REPAIR THE LINE AND TO CONTAIN AND RECOVER THE CRUDE OIL. THERE WERE NO INJURIES AND DEATHS. NRC TELEPHONE CONTACT: 11:55, 5/21/92; INCIDENT NO. 118670.
2017-09-29 08:50 | YES | NO | 19920105 | 1992-06-30 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-05-15 | 1000 | CA | LOS ANGELES | CARSON | NO |  | NO | SFPP'S WATSON TANK FARM, 20410 S WILMINGTON AVE, CARSON CA 90810 TANK W-4 (JP-4 FUEL) |  | TANK FARM | TANK |  | 1961 | OTHER | FAILURE IN BOTTOM PLATE O | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 54916.797 | 110789.3614 | JET FUEL | 3 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR V P - OPERATIONS & ENGINEERING | 2134867720 | PINHOLE LEAK IN BOTTOM OF TANK W-4 REVEALED BY EXISTENCE OF 2-FOOT SQUARE WET SPOT ON GROUND. TANK WAS EMPTIED AND REPAIRS MADE.
2017-09-29 08:50 | NO | NO | 19920106 | 1992-06-25 | 18273 | SHELL PIPELINE CORP | YES | 1992-05-21 | 1510 | IL | DE WITT | CLINTON | NO |  | NO | SW 1/4, SW 1/4, SECTION 3, T-19-N, R-3-EFOUR MILES SOUTHEAST OF CLINTON. NORTH LINE 14-INCH |  | LINE PIPE | VALVE |  | 1952 | OTHER | MALFUNCTION OF VALVE OPER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 54000 | 42364.3863 | 85466.0788 | TRANSMIX (PART. REFINED PETRO) | 3 | 5 | 0 | NO | NO | 12 | 0.5 | 42000 | FLANGED |  | 1197 | 560 | YES | 8 | 1496 | 1 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414506 | PRODUCT WAS RELEASED FROM AN O'RING ON THE VALVE OPERATOR
2017-09-29 08:50 | YES | NO | 19920107 | 1992-06-22 | 809 | ARCO PIPE LINE CO | YES | 1992-05-27 | 1535 | OK | WASHINGTON |  | NO |  | NO | 3 MILES NORTH OF DEWEY, OK 1/4 MILE WEST OF HWY 75 ON RD 12 |  | LINE PIPE | PIPE |  | 1948 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 24351 | 19103.9846 | 38540.4534 | GASOLINE | 2 | 689 | 591 | NO | NO | 8 | 0.25 | 24000 | NO DATA |  | 700 | 720 | YES | 0 | 1000 | 1 | 48 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BARRY P HILL - COMPLIANCE COORDINATOR, PDTS BUSINESS UNIT | 7139865356 | PIPELINE STARTED UP AGAINST A BLOCKED VALVE, CAUSING PIPELINE TO RUPTURE, RELEASING PRODUCT TO GROUND. EMERGENCY RESPONSE PERSONNEL WERE IMMEDIATELY DISPATCHED TO SITE FOR CLEAN UP AND REPAIRS.
2017-09-29 08:50 | YES | NO | 19920108 | 1992-07-02 | 22430 | WEST SHORE PIPE LINE CO | YES | 1992-06-05 | 1617 | IL | COOK |  | NO |  | NO | S PALENTINE RD- W OF WOLF RD - BEHIND PROPERTY 1440 S WOLF RD WHEELING, IL. ALONG E AND W SIDE OF WISCONSIN CENTRALL RAILROAD. |  | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 3548 | 2453 | NO | NO | 16 | 0.25 | 0 | WELDED |  | 1170 | 500 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | R A WILSON - AREA MANAGER | 7082577550 | THIRD PARTY CONTRACTOR WAS MAKING A 30" BORE (WEST TO EAST) UNDER RAILROAD TRACKS, WHEN IT HIT THE WEST SHORE PIPE LINE (NORTH-SOUTH ROUTE) RUNNING ON THE EAST SIDE OF TRACKS.
2017-09-29 08:50 | YES | YES | 19920109 | 1992-06-09 | 18194 | SEMINOLE PIPELINE CO | NO | 1992-04-07 | 710 | TX | WASHINGTON |  | NO |  | NO | S M WILLIAMS SURVEY, ABSTRACT 110, WASHINGTON COUNTY, TEXAS |  | NO DATA | NO DATA | UNKNOWN | 1982 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 3 | 0 | 3 | 22 | 2 | 20 | 0 | 0 | 0 | L. P. G. |  | 0 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S F ISAACS - PRESIDENT | 9185811800 | ((DEATH AND INJURY INFORMATION BASED UPON MEDIA REPORTS)). AN EXPLOSION ANDFIRE OCCURRED IN THE AREA AROUND SEMINOLE PIPELINE COMPANY'S BRENHAM STATION. THIS INCIDENT IS CURRENTLY UNDER INVESTIGATION BY THE NATIONAL TRANSPORTATION SAFETY BOARD TO DETERMINE THE CAUSE.
2017-09-29 08:50 | YES | NO | 19920110 | 1992-06-29 | 6856 | GULF CENTRAL PIPELINE CO | YES | 1992-06-01 | 0 | IA | KOSSUTH |  | NO |  | NO | TWN 96NM R 30W, SEC.28, MILEPOST 6-270.3 |  | NO DATA | WELDING FITTING |  | 1991 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 196.1314 | 395.6763 | ANHYDROUS AMMONIA | 2 | 300 | 0 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1340 | 650 | Null | 83 | 1882 | 9 | 70 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  |  | ON 5/271992 LANDOWNER DARRELL SCHMIDT (515/925-3574) REPORTED CROPS WERE NOTGROWING AT PREVIOUS REPAIR SITE ON HIS PROPERTY. WE WERE MADE AWARE ON 6/1/92 AND SENT MAINTENANCE CREW TO INVESTIGATE. PINHOLE LEAKS WERE FOUND IN WELD OF STOPPLE TEE FROM PREVIOUS REPAIR. A WELD CAP & LATRO-LET WERE INSTALLEDON END OF STOPPLE FITTINGS ON 6/2/1992. PRODUCT LOSS IS ESTIMATED DUE TO DISCOVERY ON MAINTENANCE INVESTIGATION. SOIL SAMPLES HAVE BEEN SENT TO IOWA DNR. NRC CASE #120225. IOWA DNR #06012-KL-1643.
2017-09-29 08:50 | YES | NO | 19920111 | 1992-07-15 | 737 | ASHLAND PIPELINE CO | NO | 1992-06-13 | 1800 | KY | CLARK | WINCHESTER | NO |  | NO | EIGHT MILES EAST OF WINCHESTER ON STONER-EPHESUS ROAD COORDINATES: 1-R-66 |  | LINE PIPE | OTHER | NON SPECIFIED | 1973 | OTHER | STRESS CRACK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 31381.0269 | 63308.2065 | CRUDE OIL | 1 | 100 | 100 | NO | NO | 24 | 0.25 | 1083 | WELDED |  | 780 | 600 | YES | 24 | 1083 | 1 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EARL N NEUMAN - SUPERINTENDENT | 5026832485 | (TOTAL PROPERTY DAMAGE IS UNKNOWN. ESTIMATE IN EXCESS OF $40,000 INCLUDING CLEANUP, REPAIRS, ANDDAMAGE SETTLEMENTS.) AT APPROXIMATELY 6:00 PM, JUNE 13, 1992, ROY SMITH, PROPERTY OWNER, CALLED OUR PIPE LINE CONTROL IN ASHLAND, KENTUCKY AND SAID HE SMELLED AND HAD FOUND OIL IN A DITCH ON HIS PROPERTY. THE CONTROL CENTER IMMEDIATELY NOTIFIED THE STATION OPERATOR AT OWENSBORO STATION WHO NOTIFIED LOU MORGAN, THE SUPERVISOR ON CALL, AND EARL NEWMAN, SUPERINTENDENT. THE AFFECTED PIPE LINE WAS SHUT DOWN AND ASHLAND'S EMPLOYEE CALL-OUT PROCEDURE IMPLEMENTED. IN THE INTERIM, THE LOCAL FIRE DEPARTMENT, COUNTY RAOD DEPARTMENT, AND LANDOWNER INSTALLED AN EARTHERN DAM TO STOP THE PROGRESS OF THE OIL. THE ASHLAND MAINTENANCE CREWS USED VACUUM TRUCKS TO RECOVER OIL. IT IS ESTIMATED THAT APPROXIATELY 100 BBLS OF CRUDE OIL WAS SPILLED AND THAT ALL OF THE FREE STANDING OIL WAS RECOVERED. THE LEAK WAS REPAIRED ON 6-14-92 USING A 24" X 36" PLIDCO SPLIT SLEEVE. HERITAGE ENVIRONMETAL, SPILL CONTRACTOR, WAS CALLED OUT 6-15-92 TO ASSIST ASHLAND IN CLEANUP EFFORTS. CONTAMINATED VEGEGATION, SOIL, AND OILY RESIDUE WAS REMOVED FROM THE SITE, BAGGED AND COLLECTED FOR PROPER DISPOSAL. THE CONTAMINATED MATERIALS WAS DISPOSED OF AAT BFI'S BENSON VALLEY AREA LANFILL IN FRANKFORT, KENTUCKY.
2017-09-29 08:50 | YES | NO | 19920112 | 1992-08-10 | 7660 | HUNT REFINING CO | NO | 1992-07-16 | 1130 | AL | CHOCTAW | BARRYTOWN | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1975 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 392.2628 | 791.3526 | CRUDE OIL | 1 | 100 | 99 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | G A GILBERT - MANAGER OF TRANSPORTATION | 2057716953 | BACHHOE WAS DIGGING A DITCH FOR A NEW 8" GATHERING SYSTEM PIPELINE NEAR OUR EXISTING 6" GATHERING SYSTEM PIPELINE. THE BACKHOE PUNCTURED A SMALL HOE IN THE EXISTING LINE, CAUSING A SPILL. THE BACKHOE SEALED BOTH ENDS OF THE DITCH, CONTAINING THE OIL IN A VERY SMALL AREA ON COMPANY RIGHT-OF-WAY. PERSONNEL CLOSED 2 BLOCK VALVES, AND OIL WAS CONTAINED IN THE DITCH. THE OIL WAS VACUUMED OUT AND PUMPED INTO OUR WOMACK HILL STORAGE TANK FOR RECOVERY. MS. KELLY WILLIAMS OF THE ALABAMA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT AND MR. L.C. BONEY OF THE ALABAMA STATE OIL AND GAS BOARD INSPECTED THE SITE THE MORNING OF THE 17TH. BOTH WERE SATISFIED WITH OUT CLEANUP EFFORTS AND STATED NO FURTHER ACTION WOULD BE NECESSARY. THE NAME AND ADDRESS OF THE CONTRACTOR PERFORMING THE CONSTRUCTION OF OUR NEW 8" GATHERING SYSTEM PIPELINE IS: SME, INC. P.O. BOX 3884, BATESVILLE, ARKANSAS 72503.
2017-09-29 08:50 | YES | NO | 19920113 | 1992-07-13 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | NO | 1992-06-15 | 1320 | TX | CARSON |  | NO |  | NO | SECTION 46, CARSON COUNTY, TX SURVEY I&GN R.R. BLOCK 4 |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3384 | 2654.8349 | 5355.8743 | NATURAL GAS LIQUID | 2 | 281 | 0 | NO | NO | 4.5 | 0.14 | 2632 | WELDED |  | 1702 | 600 | YES | 24 | 2166 | 11 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PIPELINE WARNING SIGNS | NO | NO | S F ISAACS - PRESIDENT | 9185811800 | 3RD PARTY PUNCTURED LINE WITH HOLE AUGER.
2017-09-29 08:50 | YES | NO | 19920114 | 1992-07-06 | 25140 | UNOCAL CORP | NO | 1992-06-25 | 1023 | CA | LOS ANGELES | TORRANCE | NO |  | NO | INTERSECTION OF 182ND ST & PRAIRE AVE. CITY OF TORRANCE, CA- UNOCAL 8" TURBINE FUEL LINE - WEST SIDE OF PRAIRE AVE. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9414.3081 | 18992.462 | JET FUEL | 2 | 10 | 10 | NO | NO | 8 | 0.25 | 2030 | WELDED |  | 1000 | 600 | YES | 4 | 1500 | 2 | 90 | NO DATA | Null | YES | OTHER | INCIDENT NOT RELATED TO C | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | KATHY HINNENKAMP - SUPERVISOR, HEALTH AND SAFETY | 3109038319 | WHILE USING AN AUGER AND A DRILLING CREW MANNED BY SOUTHWESTERN LABORATORIES, INC., HUNTINGDON ENVIRONMENTAL CONSULTING DRILLED INTO UNOCAL SOUTHERN CALIFORNIA DIVISION'S 8" TURBINE FUEL LINE FLOWING FROM THE UNOCAL LOS ANGELES REFINERY, WILMINGTON TO THE LAX AIRPORT TANKAGE. IN SPITE OF THE FACT THAT THELINES WERE MARKED AS PER UNDERGROUND SERVICE ALERT GUIDELINES, NO POTHOLE TESTING WAS PERFORMED IN THE AREA AS PER DEPARTMENT OF TRANSPORTATION REQUIREMENTS IN ORDER TO CONFIRM THE LOCATION OF THE RIGHT OF WAY OF THE PIPELINE. THE DRILLING CREW COMMENTED THAT THEY DID NOT EXPECT A PIPELINE TO BE IN THE LOCATION DURING THE COURSE OF UNOCAL'S ON SITE INVESTIGATION.
2017-09-29 08:50 | YES | YES | 19920115 | 1992-07-06 | 25140 | UNOCAL CORP | NO | 1992-06-03 | 920 | CA | LOS ANGELES | TORRANCE | NO |  | NO | UNOCAL SOUTHERN CA DIV PIPELINE TORRANCE TANK FARM, 2650 W LOMITA BLVD. TORRANCE CA 90505 |  | LINE PIPE | PIPE |  | 1952 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 0 | 2 | 50000 | 39226.2836 | 79135.2581 | DIESEL FUEL | 3 | 320 | 320 | NO | NO | 8 | 0.25 | 2030 | WELDED |  | 450 | 15 | YES | 4 | 720 | 4 | 91 | NO DATA | Null | YES | OTHER | CORROSION WAS NOT A FACTO | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | STATION PROCEDURES | YES | YES | KATHY A HINNENKAMP - SUPERVISOR, HEALTH AND SAFETY | 3109038319 | ON JUNE 3, 1992, AT APPROXIMATELT 09:20 AM AN INCIDENT OCCURRED AT UNOCAL'S TORRANCE TANK FARM. SE PIPELINE COMPANY WAS HIRED BY UNOCAL TO LOWER TWO SHORT SEGMENTS OF THE LAR WILMINGTON REFINERY TO TORRANCE PRODUCT LINES INSIDE THE TORRANCE TANK FARM. THE GASOLINE LINE WAS SCHEDULED TO BE LOWERED FIRST, AND AS SUCH IT WAS DISPLACED WITH WATER, BLOCKED OFF, AND TAGGED OUT. FOR CAUSES STILL UNDER INVESTIGATION, THE SECOND PIPELINE, NORMALLY USED FOR SHIPMENTS OF DIESEL, WAS CUT, UNDER THE ASSUMPTION THAT IT WAS THE GASOLINE LINE. BEFORE WELDING WAS STARTED, THE TORRANCE STATION RECEIVED AN ORDER TO LINE UP APPROPRIATE TANKAGE TO RECEIVE DIESEL FROM LAR WILMINGTON REFINERY. WHEN THEVALVES WERE OPENED TO THE TANK, DIESEL RUSHED BACKWARDS, CAUSING A PLUMMER'SPLUG INSERTED IN THE END OF THE OPEN LINE TO DISLODGE AND STRIKE ONE OF THE SE PIPELINE EMPLOYEES IN THE HAND AND WRIST, AND ANOTHER SE PIPELINE EMPOYEE IN THE FOREARM.
2017-09-29 08:50 | NO | NO | 19920116 | 1992-07-27 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1992-06-04 | 900 | OH | UNION | JEROME | NO |  | NO |  |  | LINE PIPE | TANK |  | 1955 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | FUEL OIL | 3 | 17 | 15 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R MOYER - REGULATORY COMPLIANCE ADMINSTRATOR | 2158208300 | THE PIPELINE WAS BEING DRAINED TO INSTALL A NEW MAIN LINE VALVE. PRODUCT WAS BEING SIPHON DRAINED PAST THE WORK SITE WHICH WAS AT A HIGHER ELEVATION LOCATED BETWEEN THE VENT SITE AND THE DRAIN SITE. AN EMPLOYEE INADVERTENTLY OPENED AVALVE AT THE WORK SITE PRIOR TO COMPLETING THE DRAINAGE. THIS BROKE THE SIPHON AND REVERSED PRODUCT FLOW BACK TOWARDS THE VENT SITE. THE RELEASE OCCURRED AT THE VENT SITE.
2017-09-29 08:50 | YES | NO | 19920117 | 1992-07-06 | 18273 | SHELL PIPELINE CORP | YES | 1992-06-10 | 1757 | LA | ST JOHN | GARYVILLE | NO |  | NO | SW 1/4, SW 1/4, SECTION 73, T-12-S, R-6-F. TEN MILES EAST OF LAPLACE . NORCO-BATON ROUGE 12-INCH |  | LINE PIPE | PIPE |  | 1954 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 117678.8508 | 237405.7744 | GASOLINE | 3 | 4 | 2 | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 1200 | 0 | YES | 12 | 1600 | 1 | 55 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G H SHERWIN - MANAGER ENVIRONMENTAL & TECHNICAL | 7132414506 | PRODUCT WAS RELEASED THROUGH A LONGITUDINAL HAIRLINE CRACK IN THE PIPE. THEPIPE WAS REPAIRED AND THE LINE WAS PLACED IN SERVICE.
2017-09-29 08:50 | YES | NO | 19920118 | 1992-07-13 | 809 | ARCO PIPE LINE CO | NO | 1992-06-19 | 1630 | TX | VICTORIA |  | NO |  | NO | PECAN MOBIL HOME PARK. 120 PECAN RD. INTERSECTION OF BEN JORDAN AND LAURENT, VICTORIA, TX |  | LINE PIPE | PIPE |  | 1948 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 442500 | 347152.6099 | 700347.0346 | GASOLINE | 2 | 159 | 42 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 750 | 775 | YES | 0 | 845 | 1 | 48 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BARRY P HILL - COMPLAINCE COORDINATOR | 7139865356 | THE INCIDENT OCCURRED WHEN A BATTERY BACKUP SYSTEM FAILED CAUSING THE RATE CONTROL VALVE TO ABRUPTLY CLOSE AT OUR VICTORIA TERMINAL DELIVERY FACILITY DURING A FULL STREAM DELIVERY OF UNLEADED GASOLINE, CAUSING A SURGE CONDITION TORUPTURE THE LINE.
2017-09-29 08:50 | YES | NO | 19920119 | 1992-07-13 | 809 | ARCO PIPE LINE CO | NO | 1992-06-10 | 1030 | TX | GUADALUPE | GONZALES | NO |  | NO | 10 MILES S OF GONZALES, TX ON 183, 1.5 MILES WEST OF GATES CEMENTARY RD., 700' NORTH OF PIPELINE CROSSING, GUADALOUPE CO. |  | NO DATA | OTHER | NON SPECIFIED | 1948 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 141214.621 | 284886.9293 | GASOLINE | 2 | 661 | 105 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 750 | 700 | YES | 0 | 845 | 1 | 48 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BARRY P. HILL - COMPLIANCE COORDINATOR | 7139865356 | THE INCIDENT OCCURRED WHEN A COIL IN A CONTROL VALVE ON OUR REMOTELY OPERATED YOAKUM STATION PUMP FAILE, ALLOWING THE VALVE TO FLY FULLY OPEN ON START OFTHE UNIT, CAUSING A SURGE CONDITION TO RUPTURE THE LINE.
2017-09-29 08:50 | YES | NO | 19920120 | 1992-07-30 | 443 | AMOCO PIPELINE CO | YES | 1992-07-01 | 1345 | OK | CADDO |  | NO |  | NO | NORTHEAST QUARTER OF SECTION 14, TOWNSHIP 10 NORTH, RANGE 10 WEST. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 21000 | 16475.0391 | 33236.8084 | CRUDE OIL | 1 | 100 | 20 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 945 | 280 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | JOHN W CARICO - AREAR MANAGER | 9182257271 | WHILE EXCAVATING THE PIPELINE FOR A REPAIR, OUR CONTRACT BACKHOE OPERATOR STRUCK AND PUNCTURED THE PIPELINE CAUSING THIS LEAK.
2017-09-29 08:50 | YES | NO | 19920121 | 1992-07-21 | 15490 | PHILLIPS PIPE LINE CO | YES | 1992-06-28 | 1809 | TX | BRAZORIA |  | NO |  | NO | 12" SWEENY-PASADENA LINE - MP 17-01+75, BLOCK A-17, JAMES E.B AUSTIN SURVERY. APPROX. 4 MILES E OF W OF COLUMBIA, TX |  | LINE PIPE | OTHER | FABRICATED PIPE BEND | 1956 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 156905.1344 | 316541.0326 | DIESEL FUEL | 3 | 618 | 195 | NO | NO | 12.75 | 0.25 | 46000 | WELDED |  | 1270 | 950 | YES | 24 | 1650 | 1 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B L THORMAN - MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | PIPE FAILURE IN A HOT FABRICATED BEND. THE SPLIT ORIGINATED IN A HARD AREA BELIEVED TO HAVE BEEN CAUSED BY LOCALIZED QUENCHING DURING FABRICATION.
2017-09-29 08:50 | YES | NO | 19920122 | 1992-07-20 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1992-06-16 | 500 | OK | PAYNE |  | NO |  | NO | NW/4 SECT 15 17N-53 PAYNE COUNTY, OK |  | LINE PIPE | PIPE |  | 1983 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 60 | 60 | NO | NO | 6 | 0.19 | 1700 | WELDED |  | 720 | 21 | NO | 0 | 0 | 1 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JEFF SPEER - AREA SUPERINTENDENT | 9182256867 | NON- JURISDICTIONAL PIPELINE
2017-09-29 08:50 | YES | NO | 19920123 | 1992-07-20 | 12471 | MID - VALLEY PIPELINE CO | YES | 1992-07-03 | 900 | KY | BUTLER | WHITTINGHILL | NO |  | NO | 7/8 MILE EAST OF WHITTINGHILL, KY |  | LINE PIPE | PIPE |  | 1949 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 392262.836 | 791352.5814 | CRUDE OIL | 1 | 350 | 300 | NO | NO | 22 | 0.3 | 52000 | WELDED |  | 816 | 386 | YES | 24 | 1020 | 1 | 50 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | I B NEWMAN - MANAGER, PIPELINE OPERATIONS | 9037570207 | JUST AFTER 0900 HOURS CDT ON JOULY 3, 1992, THE LONGVIEW, TEXAS CONTROL CENTER RECEIVED A PHONE CALL FROM THE BUTLER COUNTY, KY CIVIL DEFENSE OFFICE. ANEMPLOYEE OF THAT OFFICE INFORMED THE DISPATCHER THAT OIL HAD BEEN OBSERVED IN REEDY CREEK WHERE IT CROSSES STATE ROUTE 70. THE MID-VALLEY DISPATCHER IMMEDIATELY SHUT DOWN THE PIPELINE AND CLOSED APPROPRIATE VALVES TO ISOLATE THEPIPELINE SECTION BETWEEN ELKTON AND CLARKSON PUMP STATIONS. MIW-VALLEY PERSONNEL WERE SENT TO THE SITE AND DEPLOYED CONTAINMENT BOOMS ON THE CREEK WITH ESCAPING INTO THE CREEK SYSTEM. THE PIPELINE REMAINED SHUT DOWN WHILE STOPPLE PLUGGING EQUIPMENT WAS BROUGHT TO THE SITE AND INSTALLED. AFTER DRAINING DOWN APPROXIMATELY 1300 FEET IN PIPE, THE DEFECTIVE PIPE (CONTAININT THE WELDED REPAIR SLEEVE) WAS CUT OUT AND REPLACED WITH A 35' 8" LONG JOINT OF NEW 22".281 WALL X-60 PIPE. THE LINE WAS RESTARTED AT REDUCED PRESSURE AFTER ALL REPAIRS WERE COMPLETE. TOTAL DOWNTIME WAS 88 HOURS.
2017-09-29 08:50 | NO | NO | 19920124 | 1992-07-28 | 10012 | KANEB PIPELINE CO | YES | 1992-06-28 | 1030 | KS | REPUBLIC |  | NO |  | NO | SW 1/4, SEC. 21, T 3S, R5W |  | LINE PIPE | GIRTH |  | 1935 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 10198.8337 | 20575.1671 | JET FUEL | 3 | 5 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L L ANDERSON - MANAGER OF REGULATORY AFFAIRS | 3162621408 | THIS INCIDENT WAS DUE TO THE FAILURE OF AN ANOMALY WITHIN A GIRTH WELD. THEANOMALY OCCURRED DURING THE ORIGINAL CONTRUCTION OF THE PIPE LINE. THE FAILURE OF THE ANOMALY RESULTED IN A PIN HOLE TYPE LEAK. REPAIR WAS ACCOMPLISHEDBY INSTALLING A FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19920125 | 1992-07-20 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1992-06-15 | 2145 | MN | MARSHALL | VIKING | NO |  | NO | LAKEHEAD'S VIKING PUMP STATION. APPROX. 1 1/2 MILE SOUTHWEST OF VIKING, MN ON COUNTY RD. 2 |  | PUMPING STATION | OTHER | GLANGE GASKET | 0 | OTHER | GASKET ON DISCHARGE SIDE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7845.2567 | 15827.0516 | CRUDE OIL | 1 | 150 | 145 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E STAUDOHAR - SECRETARY & GEN MGR. CORPORATE SERVICES | 7153941404 | AT APPROXIMATELY 21:45 MST, JUNE 15, 1992, LAKELAND EXPERIENCES A LEAK AT ITS VIKING, MN PUMP STATION WHERE A GASKET ON THE LINE 3 PUMP DISCHARGE FLANGE CONNECTION FAILED. LAKEHEAD CREWS WERE COINCIDENTALLY ON-SITE AT THE TIME OFTHE LEAK TO FACILITATE AN INTERNAL INSPECTION BEING PERFORMED ON LAKEHEAD'S LINE 1. VIKING STATION WAS IMMEDIATELY ISOLATED AND BY-PASSED. THE SPILL OIL WAS CONTAINED ON STATION PROPERTY WITH AN EXTIMATED 150 BARRELS OF CRUDE OIL RELEASED AND 145 RECOVERED AND RE-INJECTED INTO THE LINE. THE PUMP WAS REPAIRED AT 10:00 MST JUNE 16 AND VIKING LINE 3 PUMP STATION WAS RETURNED TO NORMAL OPERATIONS, AT 1330 MST 6/17/92. NATIONAL RESPONSE CENTER CALLED AT 3:18CST, RPT. #122171. MN DUTY OFFICER CALLED AT 2:04 CST.
2017-09-29 08:50 | YES | NO | 19920126 | 1992-07-28 | 15681 | PLATTE PIPE LINE CO | YES | 1992-07-09 | 845 | WY | FREMONT |  | NO |  | YES | SECTION 2 T38N R91W |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | CRUDE OIL | 1 | 625 | 615 | NO | NO | 8 | 0.32 | 30000 | WELDED |  | 872 | 138 | YES | 8 | 1090 | 8 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J A FISHER - REGULATORY COORDINATOR | 4194213201 | A ROAD GRADER, OPERATED BY FREMONT COUNTY PERSONNEL, STRUCK AND PENETRATED AN 8" CRUDE OIL PIPELINE WHILE DEEPENING A COUNTY ROAD BORROW DITCH. WITHIN AFEW MINUTES, COUNTY PERSONNEL NOTIFIED THE LOCAL AREA FOREMAN, BY TELEPHONE,OF THE INCIDENT. THE LINE WAS IMMEDIATELY SHUT DOWN. CONTRACTORS WERE MOBILIZED TO THE SCENE AND BLOCK VALVES WERE CLOSED TO ISOLATE THE LEAK AREA. THE RELEASED CRUDE OIL WAS GENERALLY CONFINED TO THE BORROW DITCH, AND RECOVERYWAS INITIATED. THE WYOMING DEQ, NRC, USBLM AND LOCAL LOW ENFORCEMENT AUTHORITIES WERE PROMPTLY NOTIFIED OF THE SPILL. 625 BARRELS OF CRUDE OIL WERE RELEASED. 615 BARRELS OF FREE OIL WERE RECOVERED WITH VACUUM TRUCKS AND INJECTED BACK INTO THE PIPELINE SYSTEM. THE REMAINING 10 BARRELS SOAKED INTO THE SOIL, WHICH WILL BE DISPOSED OF UNDER THE DIRECTION OF THE WYOMING DEPARTMENT OF ENVIRONMENTAL QUALITY. THE DAMAGED SECTION OF PIPE WAS REPLACED WITH PRE-TESTED COMPARABLE PIPE. THE REPAIRS TO THE LINE LINE WERE COMPLETED IN APPROXIMATELY 12 HOURS. PLANS ARE BEING MADE TO LOWER THE LINE AS SOON AS POSSIBLE.
2017-09-29 08:50 | YES | YES | 19920127 | 1992-08-11 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1992-07-29 | 1330 | CA | CONTRA COSTA | CONCORD | NO |  | NO | 1450 SOLANO WAY, CONCORD, CALIFORNIA 94520 |  | PUMPING STATION | OTHER | NON SPECIFIED | 0 | OTHER | UNKNOWN-VACUUM TRUCK HOSE | ALL OTHER CAUSES | MISCELLANEOUS | 1 | 1 | 0 | 1 | 1 | 0 | 2000 | 1569.0513 | 3165.4103 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E KELLEY - NORTHERN DISTRICT MANAGER | 8053270110 | A SECTION OF THE 20" COALINGA-AVON PIPELINE WAS BEING PURGED USING NITROGEN AND TWO RUBBER SPHERES IN PREPARATION FOR A RELOCATION TIE-IN. AFTER THE SPHERS REACHED THE AVON FACILITY IN CONCORD, AS INDICATED BY 1 PIG-SIGNAL, A VACUUM TRUCK BEGAN RECEIVING CRUDE AND NITROGEN THROUGH A 4" HOSE CONNECTED BY A CAM-LOCK TO A 6" LINE FROM THE PIPELINE. SHORTLY AFTER THE VACCUM TRUCK WAS APPROXIMATELY 1/4 FULL, THE CAM-LOCK CONNECTION SEPARATED, SPRAYING THE AREA WITH CRUDE OIL AND FRAGMENTS FROM A RUBBER SPHERE.
2017-09-29 08:50 | YES | NO | 19920128 | 1992-08-04 | 2552 | COLONIAL PIPELINE CO | YES | 1992-06-02 | 706 | SC | ABBEVILLE |  | NO |  | NO | APPROX. 5 MILES NORTH OF DUE WEST, SC |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 19000 | 14905.9878 | 30071.3981 | FUEL OIL | 2 | 32 | 31 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1318 | 528 | YES | 24 | 1367 | 1 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | J A COX - MANAGER, TECHNICAL & REGULATORY | 4048412296 | WHILE INVESTIGATING AN ANOMALY ON COLONIAL'S 8 INCH LATERAL LINE FROM BELTON,SC TO NORTH AUGUSTA, SC, A MAINTENACE PIPELINE CONTRACTOR'S BACKHOE ACCIDENTAL PUNCTURED THE LINE AT 0706 EST ON 6/02/92. THE ANOMALY WAS DETECTED ON ANEARLIER MAGNETIC TOOL INSPECTION. COLONIAL'S INSPECTOR IMMEDIATELY ORDERED THE LINE SHUT DOWN AND NOTIFIED LOCAL SUPERVISION. OF THE 32 BARRELS OF FUELRELEASED INTO THE DITCH, 31 BARRELS WERE RECOVERED AND RETURNED TO THE SYSTEM. A TWO FOOT, FULL ENCIRCLEMENT SLEEVE WAS INSTALLED OVER THE DAMAGED PIPE AND THE LINE WAS RESTARTED AT 1420 EST ON 6/02/92. WHEN IT WAS DETERMINED THAT SOIL REMEDIATION COSTS MIGHT REULTS IN TOTAL PROPERTY DAMAGES EXCEEDING $5,000.00, PHONE CALLS WERE MADE TO STATE ENVIRONMENT PERSONNEL AT 1530 EST ON 6/2/92, AND TO THE NATIONAL RESPONSE CENTER (REPORT NO. 120145) AT 1612 EST ON 6/2/92. SOIL EXCAVATED FROM THE LEAK SITE HAS BEEN CONTAINED AND WILL BE DISPOSED OF AT AN APPROVED, OFFSITE FACILITY.
2017-09-29 08:50 | YES | NO | 19920129 | 1992-08-17 | 443 | AMOCO PIPELINE CO | YES | 1992-07-13 | 1300 | TX | SCHLEICHER | ELDORADO | NO |  | NO | 2 MILES SW OF ELDORADO, TEXAS ON HWY 277, RANCHO PIPELINE SYSTEM YARD, ON WEST SIDE OF HIGHWAY. |  | TANK FARM | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1569.0513 | 3165.4103 | CRUDE OIL | 1 | 305 | 300 | NO | NO | 30 | 0.38 | 0 | WELDED |  | 150 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES S BLUME - RELIEF PIPELINE MAINT, FOREMAN | 9155733589 | THE LEAK WAS LOCATED AT CONCHO STATION IN THE TANK LINE FOR TANK #451. APPROXIMATELY 300 BBLS., WAS PICKED UP. A 30" REPAIR CLAMP WAS INSTALLED. THE CRUDE OIL WAS CONTAINED INSIDE A 15' X 20' BELLHOLE INSIDE THE TANK FAREWELL.
2017-09-29 08:50 | YES | NO | 19920130 | 1992-08-14 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-03-30 | 1030 | CA | ALAMEDA | SAN LEANDRO | NO |  | NO | SFPP LINE SECTION 41, PLMP 10.8 (DOWNSTREAM SIDE OF DAVIS BLOCK VALVE), APROX. 50 FEET FROM SPRR TRACKS AND 300 FEET FROM PRIVATE BUILDINGS. |  | LINE PIPE | OTHER | 1" THREAD LEAK | 1969 | OTHER | THREAD LEAK (DRIP) | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 54916.797 | 110789.3614 | GASOLINE | 3 | 0 | 0 | NO | NO | 10 | 0.22 | 52000 | THREADED |  | 1300 | 544 | YES | 24 | 1910 | 1 | 69 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENOIR VICE PRESIDENT, OPERATIONS & ENGINEERING | 2134867720 | A SMALL DRIP WAS DISCOVERED OOZING FROM A 1" PIPE THREAD. THE PIPE WAS REMOVED AND THE OPENING PLUGGED. NOTE: INITIAL ESTIMATED OF THE TOTAL PROPERTY DAMAGE CAUSED BY THIS OCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAS RAISED THOSE ESTIMATES TO EXCEED $5,000 AND WE NOW SUBMIT THIS REPORT TO COMPLY WITH THE INTENTOF THE REGULATION.
2017-09-29 08:50 | NO | NO | 19920131 | 1992-08-14 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-07-13 | 1903 | AZ | MARICOPA | GLENDALE | NO |  | YES | N/A - IN TANK FARM ON LUKE AFB |  | TANK FARM | OTHER | SUMP OVERFLOWED | 1986 | OTHER | SUMP OVERFLOWED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 23535.7702 | 47481.1549 | JET FUEL | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR VICE PRESIDENT, OPERATIONS & ENGINEERING | 2134867720 | SUMP AY LUKE AFB OVERFLOWED. SIX-INCH LINE WAS SHUT DOWN UPON DISCOVERY. LESS THEN ONE BARREL OF PRODUCT RELEASED. SPEEDY DRY AND WATER APPLIED. AFFECTED SOIL REMOVED FOR PROPER DISPOSAL.
2017-09-29 08:50 | YES | NO | 19920132 | 1992-08-17 | 3012 | D - S PIPE LINE CORP | NO | 1992-07-10 | 2120 | TX | HASKELL | RULE | NO |  | NO | 3 MILES S OF RULE TEXAS ON HWY. 6 AND 2 MILES EAST SECTION 66, BLOCK 1, H&TC SURVEY, HASKELL COUNTY, TEXAS. |  | LINE PIPE | PIPE |  | 1927 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 4200 | 3295.0078 | 6647.3617 | CRUDE OIL | 1 | 3020 | 2870 | NO | NO | 10 | 0.37 | 25000 | THREADED |  | 460 | 0 | YES | 24 | 601 | 5 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS, MANAGER PIPELINE SAFETY & REGULATIONS | 8063783583 | AT APPROXIMATELY 2120 HOURS ON JULY 10, 1992, OUR 10" HAWLEY TO MCKEE CRUDE OIL PIPELINE RUPTURED ALLOWING 3020 BARRELS OF CRUDE OIL TO ESCAPE, OF WHICH 2870 BARRELS WERE SUBSEQUENTLY RECOVERED. THE RUPTURE OCCURRED IN A DRY RAVINE AND WAS WITHIN A SMALL REMOTE AREA. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE CAUSE WAS ATTRIBUTED TO FAILURE IN THE PIPE'S LONGITUDINAL LAP-WELD SEAM. THE PIPELINE WAS REPAIRED WITHOUT INCIDENTS BY REPLACING 84 FEET WITH 10" PRE-TESTED PIPE AND THE LINE RETURNED TO SERVICE.
2017-09-29 08:50 | NO | NO | 19920133 | 1992-08-21 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1992-07-17 | 1016 | WI | DOUGLAS | SUPERIOR | NO |  | NO | LAKEHEAD'S SUPERIOR, WI TERMINAL FACILITY, 2100 E. 21ST ST., SUPERIOR, WI |  | TANK FARM | SCRAPER TRAP |  | 1953 | OTHER | SCRAPER TRAP DOOR FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | CRUDE OIL | 1 | 7 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E STAUDOHAR - SECRETARY & GENERAL MANAGER CORPORATE SERV | 7153941401 | IN PREPARATION FOR HYDROTESTING A SECTION OF LAKEHEAD'S 30" LINE 5, A WATER BATCH WAS INJECTED AT OUR SUPERIOR, WI TERMINAL FACILITY. A BATCHING PIG WASINSERTED INTO THE LINE 5 SENDING TRAP AT THE TAIL END OF THE WATER BATCH. WHILE FILLING AND EQUALIZING THE SCRAPER TRAP, THE EARS ON THE TRAP DOOR FAILED AT APPROXIMATELY 535 PSI. THE DOOR WAS BLOWN OFF, RELEASING HYDROTEST WATERAND APPROXIMATELY 7 BARRELS OF OIL. ALL OIL AND WATER WAS CONTAINED ON COMPANY PROPERTY WITH 5 OF THE 7 BARRELS OF OIL RECOVERED. THE NATIONAL RESPONSECENTER WAS NOTIFIED AT 21:50 (MST). A FLANGE WAS WELDED ON THE END OF THE TRAP AND A 34" BLIND INSTALLED. METALLURGIACL ANALYSIS OF THE SCRAPER TRAP DOOR WILL BE PERFORMED TO DETERMINE THE CAUSE OF FAILURE.
2017-09-29 08:50 | YES | NO | 19920134 | 1992-08-20 | 4906 | EXXON PIPELINE CO | YES | 1992-07-21 | 1630 | TX | SUTTON |  | NO |  | NO | SECTION 79, BLOCK "B" OF H.E. & W.T. R.R. CO. SURVEY |  | LINE PIPE | PIPE |  | 1927 | OTHER | THERMAL EXPANSION CAUSED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 58839.4254 | 118702.8872 | CRUDE OIL | 1 | 30 | 0 | NO | NO | 12 | 0.38 | 25000 | THREADED |  | 668 | 0 | YES | 8 | 835 | 3 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT, MANAGER OF ENVIRONMENTAL & REGULATORY COMPLAINCE D | 7136565521 | ON JULY 21, 1992 AT APROXIMATELY 1630 HOURS, MR. L. FINKLEA CALLED EXXON PIPELINE COMPANY'S OIL TRAFFIC CONTROL CENTER TO REPORT A CRUDE OIL LEAK ON HIS PROPERTY. THE OTCC DISPATCHER IMMEDIATELY SHUT THE SYSTEM DOWN. THE LEAK WASLOCATED ON AN ISOLATED SECTION OF THE SYSTEM THAT WAS OUT OF SERVICE AT THE TIME OF THE INCIDENT. THE MAIN SYSTEM WAS PUT BACK INTO OPERATION ON JULY 22, 1992. THE ISOLATED SECTION WAS REPAIRED WITH A 21 FOOT SECTION OF NEW PIPE. THE VALVES WERE LEFT IN THE OPEN POSITION TO PREVENT THE REOCCURANCE OF THEINCIDENT. CLEANUP WAS PERFORMED BY REMOVING AND REPLACING THE CONTAMINATED SOIL.
2017-09-29 08:50 | YES | NO | 19920135 | 1992-08-21 | 22610 | WILLIAMS PIPELINE CO | YES | 1992-07-27 | 2230 | MN | MEEKER | GREENLEAF | NO |  | NO | DRIVE SOUTH OUT OF LITCHFIELD, MN ON HWY 22 FOR 9 MILES TO GREENLEAF, MN. TURN E ON COUNTY RD 1/4 MI. THE VALVE IS ON THE S SIDE OF THE ROAD. |  | LINE PIPE | VALVE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1569.0513 | 3165.4103 | FUEL OIL | 3 | 2 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | STEVEN S BALL - V.P. - OPERATIONS & ENG | 9185883850 | THE GATE VALVE BAX WAS TAMPERED WITH BY AN UNKNOWN THIRD PARTY APPARENTLY INORDER TO STEAL GASOLINE OR FUEL OIL. THE VALVE BOX LID LOCK WAS NOT FOUNDANYWHERE AROUND THE SITE. THE VALVE FITTINGS HAD BEEN TAMPERED WITH. IT ISNOT KNOWN WHAT STARTED THE FIRE IN THE VALVE BOX. THE VALVE BOX LID WAS OPENWHEN THE LITCHFIELD FIRE DEPARTMENT ARRIVED AND EXTINGUISHED THE FIRE. THESHERIFF'S OFFICE AND THE FIRE MARSHALL EACH PERFORMED AN INVESTIGATION. ATTHIS POINT, NO SOLID CLUES OR DETERMINATION CAN BE MADE. SUPPLEMENTAL REPORT9/26/94 INDICATES A CHANGE IN THE CAUSE OF THE ACCIDENT (PART D), FROM "OTHER- UNAUTHORIZED TAMPERING" TO "OUTSIDE FORCE DAMAGE." REPORT SUBMITTED BYSTEVEN BALL/RICHARD HARRIS (918) 588-3454.
2017-09-29 08:50 | YES | NO | 19920136 | 1992-08-21 | 2552 | COLONIAL PIPELINE CO | YES | 1992-07-21 | 1030 | LA | ACADIA |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S CHURCH POINT STATION |  | PUMPING STATION | VALVE |  | 1963 | OTHER | FAILED CHECK VALVE STEM S | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 6276.2054 | 12661.6413 | GASOLINE | 2 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J A COX - MANAGER - TECHNICAL/REGULATORY | 4048412296 | ON JULY 21, 1992, A COLONIAL CONTRACTOR WAS EXCAVATING AND INSPECTING VALVESIN THE NO. 1 STATION AT CHURCH POINT STATION WHEN A GASOLINE ODOR WAS NOTED NEAR VALVES OF UNITS NO.1 AND NO. 2. THE EXCAVATED SOIL WAS DISCOLORED AND CONTAINED TRACES OF GASOLINE. EXCAVATION CONTINUED AND ON JULY 30, 1992, THE SOURCE OF THE LEAK WAS FOUND TO BE A FAULTY CHECK VALVE STEM SEAL. THIS STEMSEAL WAS REPAIRED AND THE VALVE RETURNED TO SERVICE. IT WAS DETERMINED THATAPPROXIMATELY 5 BARRELS OF GASOLINE SOAKED INTO THE SURROUNDING SOIL OF WHICH NONE WAS RECOVERED. AT 0330 CDT ON JULY 31, 1992, IT WAS DETERMINED THAT DAMAGED RELATED COSTS WOULD EXCEED $5,000 AND AS SUCH, IS A D.O.T. REPORTABLE LEAK. AT THIS TIME THE NRC WAS NOTIFIED (REPORT NO. 129897) OF THE LEAK. CONTAMINATED SOIL HAS BEEN CONTAINED AND IS AWAITING DISPOSAL.
2017-09-29 08:50 | YES | NO | 19920137 | 1992-08-21 | 26125 | CALNEV PIPELINE CO | YES | 1992-08-19 | 930 | CA | SAN BERNARDINO |  | NO |  | NO | 2051 W SLOVER AVENUE, COLTON, CA 92324 |  | TANK FARM | TANK |  | 0 | OTHER | MALFUNCTION OF HIGH LEVEL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7845.2567 | 15827.0516 | DIESEL FUEL | 1 | 67 | 40 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID ANDRIES - MANAGER OF ENGINEERING | 7148887771 | OPERATOR WAS RECEIVING DIESEL FUEL INTO TANK 136 AT THE COLTON TERMINAL. THE SIDE GAUGE WAS OUT OF CALIBRATION; THEREFORE THE TWO HIGH LEVEL ALARMS DIDNOT SIGNAL AT THEIR PROPER SETTING, AND INFACT, DID NOT ALARM AT ALL. THE INDEPENDENT HIGH LEVEL DID ALRAM, BUT THE OPERATOR HAD INSUFFICIENT TIME TO DIVERT FLOW TO ANOTHER TANK BEFORE THE OVERFLOW OCCURRED.
2017-09-29 08:50 | YES | NO | 19920138 | 1992-08-24 | 443 | AMOCO PIPELINE CO | YES | 1992-07-30 | 1300 | TX | JOHNSON |  | NO |  | NO | 4 MILES S OF CLEBURNE, TEXAS APPRO. THREE HUNDRED YARDS WEST OF HWY 171. |  | LINE PIPE | PIPE |  | 1943 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 784.5257 | 1582.7052 | CRUDE OIL | 1 | 450 | 440 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | C H STEPHENS - PIPELINE MAINT FOREMAN | 8175622381 | LINES HAD BEEN PARTIALLY STAKED THROUGH AREA AND AMOCO PERSONNEL WERE ENROUTETO FINISH LOCATING THE LINES. CONTRACTOR HIT OUR EIGHT INCH LINE WITH HIS BULLDOZER. ALL OF THE OIL WAS CONTAINED IN A SMALL AREA THAT THE CONTRACTOR HAD BEEN WORKING ON. MOST OF THE OIL WAS PICKED UP WITH VACUUM TRUCKS AND RETURNED TO OUR PUMP STATION. AFTER OBTAINING PERMISSION FROM TEXAS AIR CONTROLBOARD AND NOTIFYING PROPER AGENCIES, REMAINDER OF OIL WAS BURNED.
2017-09-29 08:50 | YES | NO | 19920139 | 1992-08-24 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1992-07-24 | 2000 | TX | HARRIS | LA PORTE | NO |  | NO | 3/4 MILE NORTH OF HWY. 225 & EAST OF MILLER CUT OFF RD LAPORTE, TEXAS |  | LINE PIPE | PIPE |  | 1944 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12100 | 9492.7606 | 19150.7325 | FUEL OIL | 3 | 1268 | 890 | NO | NO | 10.75 | 0.25 | 0 | WELDED |  | 725 | 550 | YES | 0 | 1000 | 1 | 69 | EXTERNAL | Null | YES | OTHER | EROSION CORROSION | DAMAGE BY NATURAL FORCES | WASHOUT | Null | NO DATA |  | Null | Null | O HORTON CUNNINGHAM - VICE PRESIDENT ENGINEERING & ROW | 7137593615 | AT 2025 HOURS JULY 24, 1992, TEPPCO PERSONNEL OBSERVED A REDUCTION IN FLOW RATE ON THE COMPANY'S 10" P-8 PIPELINE AND SHUT DOWN THE SYSTEM TO INVESTIGATETHE ABNORMAL OPERATION. WHILE THE OPERATORS WERE INVESTIGATING, THEY WERE NOTIFIED THAT #2 FUEL WAS ESCAPING FROM OUR PIPELINE. EMERGENCY PROCEDURES WERE INITIATED IMMEDIATELY BY THE CONTROL POINT OPERATOR. THE SYSTEM WAS BLOCKED IN, AND RESPONSE PERSONNEL WERE NOTIFIED AND DISPATCHED TO THE LEAK LOCATION. UPON ISOLATION OF THE SITE, IT WAS DETERMINED THAT A 13" SECTION OF PIPE HAD FAILED. REMOVAL OF THIS SECTION OF PIPE AND INSTALLATION OF NEW PIPE WAS COMPLETED ON JULY 26, 1992. THE SYSTEM WAS RESTARTED ON JULY 27, 1992. PRODUCT RECOVERY AND CLEAN-UP OPERATIONS WERE DECLARED COMPLETE BY THE COAST GUARD ON JULY 28, 1992.
2017-09-29 08:50 | YES | NO | 19920141 | 1992-08-31 | 12627 | MOBIL OIL CORP | NO | 1992-08-07 | 905 | CA | LOS ANGELES | CASTAIC | NO |  | YES | SEC 33 T 6 N - R 17 W |  | LINE PIPE | PIPE |  | 1983 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19613.1418 | 39567.6291 | CRUDE OIL | 1 | 600 | 600 | NO | NO | 16 | 0.31 | 2028 | WELDED |  | 1177 | 80 | YES | 8 | 1520 | 9 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | S S SOHNY - MANAGER OF OPERATIONS | 3104937237 | AT APPROXIMATELY 9:05 A.M. ON AUGUST 7, 1992 A PIECE OF EXCAVATION EQUIPMENTHIT MOBIL'S ACTIVE 16" CRUDE OIL PIPELINE AND RUPTURED IT. THE PIPELINE WASIMMEDIATELY SHUT DOWN. BLOCK VALVES WERE CLOSED TO ISOLATE THE DAMAGED SECTI
2017-09-29 08:50 | YES | NO | 19920142 | 1992-08-31 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1992-07-21 | 1745 | NJ | UNION |  | NO |  | NO |  |  | TANK FARM | TANK |  | 1975 | OTHER | FATIGUE CRACK NEAR WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11767.8851 | 23740.5774 | TURBINE FUEL | 3 | 125 | 125 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R MOYER - REGULATORY COMPLIANCE ADMINISTRATOR | 2158208300 | DURING ROUTINE TANK INSPECTIONS A STAINED AREA WAS NOTICED IN THE SOIL NEXT TO TANK #149. THE TANK WAS EMPTIED OF TURBINE FUEL, REMOVED FROM ACTIVE SERVICE AND THEN GAS FREED FOR INTERNAL TANK INSPECTION. ALL APPLICABLE AGENCIESWERE NOTIFIED, AND THE PRODUCT RELEASE WAS CONTAINED WITHIN THE DIKE AREA. AFTER INSPECTING THE TANK BOTTOM ACRACK WAS NOTED IN THE TANK FLOOR PLATE NEAR THE RING WALL WITHIN THE HEAT AFFECTED ZONE OF THE WELD. THE TANK FLOOR WAS REPAIRED BASED ON COMPANY REPAIR POLICY. UPON COMPLETION OF REPAIR WORK THE TANK WAS RETURNED TO ACTIVE SERVICE.
2017-09-29 08:50 | YES | NO | 19920143 | 1992-08-31 | 18214 | SHAMROCK PIPE LINE CORP | YES | 1992-07-25 | 1525 | TX | HUTCHINSON | BORGER | NO |  | NO | SECTION 3, BLK 3, D&SE SURVEY, HUTCHINSON COUNTY, TX. APPROX. TWO (2) MILES E SE OF THE CITY OF BORGER, TX ON HWY 152 AND TWO (2) MILES EAST NE OF FM HWY 2171 |  | LINE PIPE | PIPE |  | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 46500 | 36480.4437 | 73595.7901 | GASOLINE | 3 | 1170 | 270 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COMPANY PROGRAM | YES | YES | GERALD CHILDERS - MANAGER, PIPELINE SAFETY & REGULATIONS | 8063783583 | AT APPROXIMATELY 1525 HOURS ON JULY 25, 1992, A TRACK HOE OPERATED BY A THIRD PARTY STRUCK AND RUPTURED OUR 8" SOUTHLAKE PRODUCTS PIPELINE. THE ACCIDENTALLOWED 1170 BARRELS OF UNLEADED GASOLINE TO ESCAPE, OF WHICH 270 BARRELS WAS RECOVERED. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THEPIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING 44 FT. 4 IN. OF LINE WITHPRETESTED PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | NO | NO | 19920144 | 1992-09-02 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-03-12 | 1130 | CA | CONTRA COSTA | PACHECO | NO |  | NO | 15 FEET FROM INTERSECTION OF PACHECO BLVD & MUIR RD (NW CORNER), L.S. 8, PLMP 20.6 |  | LINE PIPE | LONGITUDINAL WELD |  | 1958 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 47071.5403 | 94962.3098 | JET FUEL | 3 | 0 | 0 | NO | NO | 8.63 | 0.25 | 46000 | WELDED |  | 1440 | 144 | YES | 8 | 2130 | 10 | 70 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENOIR VICE PRESIDENT, OPERATIONS & ENGINEERING | 2134867720 | LINE RIDER FOUND 30 FEET OF LOOSE AND SOFT COATING PLUS AN ODOR IN SOIL AT SITE - NO FREE PRODUCT - CAUSED BY A BAD WELD ON A WELD-PLUS END. FORTYTWO FEET OF PIPE WERE CUT OUT AND REPLACED. NOTE: INITIAL ESTIMATES OF THE TOTAL PROPERTY DAMAGE CAUSED BY THIS OCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAS RAISED THOSE ESTIMATES TO EXCEED $5,000 AND WE NOW SUBMIT THIS REPORT TO COMPLY WITH THE INTENT OF THE REGULATION.
2017-09-29 08:50 | YES | NO | 19920145 | 1992-08-31 | 2371 | CINIZA PIPELINE INC | NO | 1992-08-03 | 903 | NM | RIO ARRIBA | LYBROOK | NO |  | YES | SE 1/4 OF NE 1/4 SECTION 15-T23N-R7N |  | LINE PIPE | OTHER | NON SPECIFIED | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 7958 | 6243.2553 | 12595.1677 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 4 | 0.11 | 42000 | WELDED |  | 800 | 610 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT ULLO - GENERAL MANAGER | 5056328006 | DEFECT IN WELD JOINT.
2017-09-29 08:50 | YES | NO | 19920146 | 1992-09-02 | 12127 | MARATHON PIPE LINE CO | NO | 1992-08-06 | 2315 | IN | PORTER | PORTAGE | NO |  | NO | 5306 & 5308 AVE, PORTAGE, PORTER COUNTY, INDIANA NW 1/4, SE 1/4 SECTION 10, T36N R7N |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 58839.4254 | 118702.8872 | FUEL OIL | 3 | 70 | 68 | NO | NO | 6 | 0.25 | 42000 | WELDED |  | 1440 | 789 | YES | 8 | 1955 | 5 | 85 | EXTERNAL | Null | YES | OTHER | STRAY CURRENT INTERFERENC | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | JOSEPH A FISHER - REGULATORY COORDINATOR | 4194213201 | ON AUGUST 6, 1992, AT APPROXIMATELY 2300 HOURS, MARATHON PIPE LINE COMPANY'S("MPLC") GRIFFITH, INDIANA, STATION OPERATOR WAS NOTIFIED OF A POTENTIAL RELEASE ON MPLC'S NILES 6" SYSTEM IN THE TOEN OF PORTAGE, INDIANA. UPON RECEIPTOF SUCH NOTIFICATION, THE GRIFFITH STATION OPERATOR CONTACTED MPLC'S OPERATIONS CENTER IN FINDLAY, OHIO, WHICH IMMEDIATELY SHUT DOWN THE LINE. MPLC PERSONNEL AND CONTRACT PERSONNEL THEREUPON RESPONDED TO THE RELEASE SITE, FOUND TO BE AT 5308 PLAZA AVENUE, PORTAGE, INDIANA. THE PORTAGE FIRE AND POLICE DEPARTMENTS ALSO RESPONDED TO THE RELEASE SITE, AND THE FIRE DEPARTMENT EVACUATED SEVERAL HOMES IN THE AREA OF THE SITE. INITIAL EFFORTS WERE DIRECTED AT CONTAINMENT AND RECOVERY OF THE RELEASE PRODUCT (NO. 2 FUEL OIL). THE PIPELINE WAS THEREUPON EXAMINED, AND A CORROSION PIT EXPOSED AT THE POINT OF CROSSING WITH TWO COPPER WATER LINES SERVING THE RESIDENTS AT 5308 PLAZA AVENUE. THE TWO COPPER WATER LINES, INSTALLED ABOVE BUT IN CONTACT WITH THE PIPELINE, ARE BELIEVED TO HAVE CAUSED THE CORROSION PROBLEM. THE WATER LINES ARE BELIEVED TO HAVE BEEN INSTALLED PRIOR TO MPLC'S OWNERSHIP OF THE PIPELINE. THE WATER LINES WERE CUT OUT AT THE POINT OF CROSSING, AND REINSTALLED WITH AT LEAST TWO FEET OF SEPARATION FROM THE PIPELINE. THE PIPELINE WAS REPAIRED BY WELDING IN PLACE A 24-INCH LONG FULL ENCIRCLEMENT WAS WRAP. THE LINE WAS RETURNED TO SERVICE AT 1123 HOURS ON SUGUST 9, 1992, UNDER NORMAL OPERATING CONDITIONS. AN ESTIMATED 70 BARRELS OF NO. 2 FUEL OIL WAS RELEASED. THIRTY-FIVE (35) BBLS. WERE PICKED UP IN EXCAVATED SAND. CLEANUP AND DISPOSAL OF EXCAVATED SAND IS BEING CONDUCTED UNDER THE DIRECTION OF THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT. ..... *TWO 3/4" WATER LINES CROSSING AND IN CONTACT WITH 6" STEEL PIPELINE CAUSED STRAY CURRENTS TO FLOW AT THE POINT OF CONTACTRESULTING IN A CORROSION PIT.
2017-09-29 08:50 | NO | NO | 19920147 | 1992-09-01 | 737 | ASHLAND PIPELINE CO | YES | 1992-08-13 | 2100 | IL | WAYNE |  | NO |  | NO | APPROX. 50' FROM CENTERLINE OF DITCH BANK ROAD. APPROX. 6.5 MILES WEST OF ALBION. ILLINOIS SECTION 35 - RANGE 1S - TOWNSHIP 9E |  | NO DATA | PIPE |  | 1968 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8629.7824 | 17409.7568 | CRUDE OIL | 1 | 2 | 2 | NO | NO | 20 | 0.22 | 1139 | WELDED |  | 820 | 420 | YES | 24 | 1097 | 1 | 74 | NO DATA | Null | Null | NO DATA |  | OTHER | OWNERSHIP OF DAMAGING EQU | Null | ONE CALL |  | Null | Null | JAMES O SIMPSON - DIVISION SUPERINTENDENT | 6182624106 | WHILE SETTING AN ABOVE GROUND MAGNET FOR AN INTERNAL INSPECTION TOOL, AN ASHLAND PIPE LINE COMPANY EMPLOYEE DISCOVERED A SMALL AMOUNT OF CRUDE OIL AROUNDTHE MARKER STAKE. THE TEST PROBING IN THE AREA INDICATED OIL IN THE GROUND,AND THE PIPELINE WAS SHUT DOWN. THE PIPELINE WAS ESCAVATED AND AN EQUIPMENTAND AN EQUIPMENT GOUGE WAS FOUND (4" LONG, 1/2" WIDE AND .070" DEEP). THE LEAK WAS FROM STRESS CRACKING AT THIS GOUGE. A "U-BOLT" REPAIR CLAMP WAS INSTALLED AND MONITORED AT THE SITE UNTIL A PLIDCO SPLIT+SLEEVE COULD BE INSTALLED ON 8/15/92. TELEPHONIC NOTIFICATION WASMADE AT 11:20 PM, 8/3/92, OT THE APPROPRIATE STATE ENVIRONMENTAL OFFICIALS AS SOON AS A DETERMINATION OF SOURCE WAS VERIFIED. DUE TO THE MINOR NATURE OF SPILL, 2 BBLS. ON DRY LAND WITH NO SIGNIFIACNT ENVIRONMENTAL IMPACT, AND DUE TO A LACK OF CONSENSUS WITHIN THE COMPANY (AND WITHIN OPS) AS TO WHAT ELEMENTS SHOULD BE INCLUDED IN THE $5,000.00 PROPERTY DAMAGE CRITERIA, NO NOTIFICATION WAS MADE TO THE NRC. ON 8/14/92, AFTER AN ANALYSIS OF THE TOTAL COST OF RESPONSE, REPAIR, LAND DAMAGES, AND CLEANUP WAS COMPLETED, A MANAGEMENT DECISION WAS MADE TO REPORT THE INCIDENT AS PER CRF 195.50 AND 195.52 EVEN THOUGH THE SPILL IMPACT WAS NEGLIGIBLE.
2017-09-29 08:50 | YES | NO | 19920148 | 1992-09-16 | 443 | AMOCO PIPELINE CO | YES | 1992-08-18 | 1400 | TX | LUBBOCK |  | NO |  | NO | LUBBOCK COUNTY BLOCK A. SOUTHEAST SECTION OF 42 AND THE SOUTHWEST SECTION OF 45. EAST 2 MILES, 1/2 MILE NORTH OF INTERSECTIONS OF HWY I-27 AND HWY 254I |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 370 | 320 | NO | NO | 8 | 0.38 | 0 | WELDED |  | 700 | 25 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | LUBBOCK COUNTY (MAINT. GR | Null | ONE CALL |  | NO | Null | RUBEN R GUAJARDO - RELIEF PIPELINE MAINT. FOREMAN | 8068946187
2017-09-29 08:50 | YES | NO | 19920149 | 1992-09-04 | 25140 | UNOCAL CORP | NO | 1992-08-03 | 1905 | CA | SAN LUIS OBISPO |  | NO |  | NO | APPROX. 50 FEET WEST OF CAVE LANDING ROAD AT UNOCAL'S BACK GATE NEAR AVILA BEACH, CALIFORNIA. |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 11000000 | 8629782.3923 | 17409756.7914 | CRUDE OIL | 3 | 150 | 100 | NO | NO | 12 | 0.25 | 0 | WELDED |  | 800 | 700 | YES | 4 | 1125 | 9 | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R L JAMES - DIVISION PIPELINE MANAGER | 8055437600 | SYMS = X-42. AN EIGHT INCH RUPTURE IN AN AREA OF PIPE WALL THINNING DUE TOISOLATED EXTERNAL CORROSION OCCURRED IN A DRAINAGE DITCH. OIL FLOWED DOWN THE DRAINAGE DITCH INTO THE PACIFIC OCEAN NEAR FOSSIL POINT EAST OF AVILA BEACH, CALIFORNIA. APPROXIMATELY 120 BBLS ENTERED THE OCEAN. CLEANUP WAS SUPERVISED BY U.S. COAST GUARD AND CALIFORNIA FISH AND GAME.
2017-09-29 08:50 | YES | NO | 19920150 | 1992-09-09 | 443 | AMOCO PIPELINE CO | YES | 1992-08-06 | 735 | ND | CASS | WEST FARGO | NO |  | YES | SW 1/4 - SECTION 18, TOWNSHIP 139N , RANGE 49W |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 31381.0269 | 63308.2065 | GASOLINE | 1 | 1593 | 1443 | NO | NO | 10 | 0.03 | 42000 | WELDED |  | 1440 | 100 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PUBLIC EDUCTION MAILINGS | NO | YES | KENNETH C. ANDREEN - AREA MANAGER | 6124254750 | CONTRACTOR WORKING FOR THE CORP. OF ENGINNERS HIT THE PIPELINE WITH EARTH MOVING EQUIPMENT (SCRAPER) DURING THE CONSTRUCTION OF A 4 FOOT DEEP DRAINAGE DITCH.
2017-09-29 08:50 | YES | NO | 19920151 | 1992-09-11 | 9175 | JAYHAWK PIPELINE CORP | YES | 1992-08-30 | 1200 | KS | HARVEY |  | NO |  | NO | SW/4 SECTION 24/T24S/RSW, HARVEY COUNTY KANSAS. APPROX. 3 1/2 MILES SOUTH OF HALSTEAD, KS IN PLOWED FIELD. |  | LINE PIPE | PIPE |  | 1958 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7845.2567 | 15827.0516 | CRUDE OIL | 1 | 250 | 190 | NO | NO | 10.75 | 0.25 | 46000 | WELDED |  | 1250 | 770 | YES | 8 | 1570 | 4 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MCMOORE - PRESIDENT | 3162913254 | THE DELIVERY VALVE ON THE DOWNSTREAM SIDE OF THE FAILURE WAS INADVERTENTLY CLOSED AND ALTHOUGH THE MANIFOLD LINE PRESSURE DID NOT EXCEED 785 PSIP THE LINE SPLIT OUT IN AN ERW PIPE SEAM. THE PIPELINE WAS BING MONITORED AT THE TIMEAND IMMEDIATELY ISOLATED. THE DISPATCHER WAS NOTIFIED BY AN AREA RESIDENT OF THE FAILURE AND OPERATORS WERE DISPATCHED TO THE SITE. THE LINE WAS REPAIRED ON MANDAY, AUGUST 31, 1992, BY REPLACING 134.1' OF LINE PIPE WITH PRE-TESTED PIPE AND OPERATORS WERE RESUMED AT A REDUCED MOP OF 600 PSIG AT 20.30 HOURS, AUGUST 31, 1992.
2017-09-29 08:50 | YES | NO | 19920152 | 1992-09-14 | 22610 | WILLIAMS PIPELINE CO | YES | 1992-08-24 | 1100 | WI | DOUGLAS | SUPERIOR | NO |  | NO | 2301 WINTER STREET WPL METERING DELIVERY POINT. |  | NO DATA | OTHER | PROVER LOOP/SUMP TANK | 1957 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 72000 | 56485.8484 | 113954.7717 | FUEL OIL | 1 | 69 | 65 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S BALL - VICE PRESIDENT, OPERATIONS & ENGINEERING | 9185883850 | ON SATURDAY, AUGUST 22, 1992, THE WPL SUPERIOR OPERATOR OPENED A 2" DRAIN VALVE ON THE STATION PROVER TO REDUCE THE PRESSURE LOCKED IN ON THE METER STATION PIPING. THE PRESSURE AT THE TIME WAS 375 PSI. THE THERMAL RELIEF VALVE WAS SET AT 750 PSI. THIS IS A STANDARD OPERATING PROCEDURE AIMED AT ENSURING MINIMAL PRESSURE ON THE METER STATION PIPING IN THE EVENT OF A PROBLEM. THE OPERATOR LEFT THE DRAIN VALVE OPEN (IN ERROR) AND WHEN THE LINE WAS STARTED TWO DAYS LATTER THE SUMP TANK WAS OVERFILLED. A HIGH SUMP ALARM WAS RECEIVEDIN DISPATCHING, THE LINE WAS PROMPTLY SHUT DOWN AND AN OPERATOR WAS DISPATCHED TO THE LOCATION. CONTAINMENT BOOMS WERE PROMPTLY PLACED ACROSS THE DRAINAGE DITCH AND THE PRODUCT WAS CONTAINED WITHIN THE DITCH. THE WISCONSIN DEPARTMENT OF NATURAL RESOURCES WAS SATISFIED WITH THE CLEANUP MEASURES TAKEN.
2017-09-29 08:50 | YES | NO | 19920153 | 1992-09-11 | 1682 | BP OIL PIPELINE CO | NO | 1992-08-17 | 1612 | LA | PLAQUEMINES | QUATRE BAYOU PASS | YES | LAT.29DEG.18'58" LONG89DE | NO | EAST SIDE OF PASS (OFFSHORE CORDINATES = LAT. 29DEG. 18'58" LONG. 89DEG. 50' 57") |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 920 | 30 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 1100 | 419 | YES | 8 | 1378 | 1 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | LES OWEN - REGION SUPERINTENDENT | 5043926601 | A CONTRACTOR WORKING FOR COLUMBIA GULF TRANSMISSION WAS REMOVING A BULKHEAD IN THE VICINITY OF THEIR SUBMERGED 30" PIPELINE. DURING THE REMOVAL PROJECT THE CONTRACORS' EQUIPMENT CONTACTED ONE OF BP OIL PIPELINE'S TWO 12" PIPELINES. THE PIPELINE SUFFERED A 1" TO 1 1/4" GOUGE IN ONE LOCATION AND A DENT AT A SECOND LOCATION. (ESTIMATED OF AMOUNT OF COMMODITY INVOLVED IN SPILL IS BASED ON SYSTEM SHORTAGES. USCG AND BP PERSONNEL ON SITE DID NOT ESTIMATE THIS VOLUME.)
2017-09-29 08:50 | YES | NO | 19920154 | 1992-09-08 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1992-08-10 | 1600 | UT | SAN JUAN |  | NO |  | NO | NW 1/4 SECTION 5, T-41S, R-24E, SAN JUAN COUNTY, UTAH. |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 27458.3985 | 55394.6807 | CRUDE OIL | 1 | 60 | 50 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 525 | 190 | YES | 8 | 879 | 7 | 77 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION OF PIP | NO DATA |  | Null | NO DATA |  | Null | Null | EILEEN J THRASHER - BUSINESS UNIT MANAGER | 3104289300 | LEAK WAS REPORTED TO FOUR CORNERS OPERATING CONTROL CENTER BY THIRD PARTY AT5:00 PM. FOUR CORNERS PERSONNEL WERE ON SCENE AT 6:00 PM AND FLOW STOPPED AT10:00 PM. CLAMP WAS INSTALLED AT 11:00 PM.
2017-09-29 08:50 | YES | NO | 19920155 | 1992-09-04 | 15490 | PHILLIPS PIPE LINE CO | YES | 1992-08-05 | 845 | KS | MIAMI |  | NO |  | NO | PAOLA TERMINAL ON BORGER-E.CHICAGO LINE. 3.5 MILES SOUTH OF PAOLA, KS, ON HENSON RD. |  | PUMPING STATION | OTHER | RELIEF VALVE | 1951 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2250 | 1765.1828 | 3561.0866 | L. P. G. | 2 | 150 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B L THORMAN - MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | FOLLOWING THE SHUTDOWN OF AN ENGINE DRIVEN PUMPING UNIT, A PRESSURE SURGE CAUSED THE RELIEF VALVE ON A DEHYDRATOR VESSEL TO OPERATE. THE RELIEF VALVE STUCK OPEN FOR 11-25 MINUTES RELEASING AN ESTIMATED 150 BARRELS OF PROPANE.
2017-09-29 08:50 | NO | NO | 19920156 | 1992-09-08 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1991-12-18 | 900 | CA | LOS ANGELES | POMONA | NO |  | NO | LINE SECTION 108 - WATSON-COLTON - PLMP 39.1 - HAMILTON BLOCK VALVE, APPROX 150 FEET WEST OF HAMILTON AVE. |  | LINE PIPE | VALVE | TOR | 1979 | OTHER | DRIP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 8037.3015 | 16214.4835 | TRANSMIX (PART. REFINED PETRO) | 3 | 0 | 0 | NO | NO | 20 | 0.44 | 60000 | WELDED |  | 1336 | 150 | YES | 24 | 1670 | 1 | 79 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR V.P. OPERATIONS & ENGINEERING | 2134867720 | LINE RIDER FOUND A DRIP FROM TOR AND LUBE PIPING ON THE BLOCK VALVE. FIELD DISMANTLED, RETAPED AND RESEALED VALVE, REPLACED O-RING AND THREAD SEALANT ONTOR CAP. NO DAMAGE DONE, NO REPORT TO OTHER AGENCIES ISSUES. NOTE: INITIAL ESTIMATES OF THE TOTAL PROPERTY DAMAGE CAUSED BY THIS OCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAS RAISED THOSE ESTIMATES TO EXCEED $5,000 AND WE NOW SUBMIT THIS REPORT TO COMPLY WITH THE INTENT OF THE REGULATION.
2017-09-29 08:50 | YES | NO | 19920157 | 1992-09-22 | 19226 | TEXACO PIPELINE INC | NO | 1992-08-31 | 1100 |  |  |  | YES | X=2230631' Y=100476' | NO | GULF OF MEXICO, SOUTH PELTO AREA, BLOCK 8 |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 855000 | 670769.4496 | 1353212.9142 | CRUDE OIL | 1 | 2000 | 1090 | NO | NO | 20 | 0.41 | 52000 | WELDED |  | 1440 | 900 | YES | 24 | 2014 | 8 | 76 | NO DATA | Null | Null | NO DATA |  | SHIP ANCHOR |  | Null | NO DATA |  | Null | Null | E D LEWIS | 5048765645 | DURING HURRICANE "ANDREW" IN AUGUST 1992, WHILE THE PIPELINE WAS SHUT IN DUETO THE STORM, THE SEMISUBMERSIBLE DRILLING RIG "TREASURE 75" OWNED BY WILRIG(U.S.A.) INC., DRIFTED FROM THE EAST SIDE OF THE AFFECTED PIPELINE TO THE WEST SIDE, DRAGGING 4 - 30,000LB. ANCHORS. THE ANCHORS WERE ATTRACHED TO THE RIG WITH 3 - 1/8" CHAIN WEIGHING 90 LB/FT. THE ANCHOR WHICH HIT THE PIPELINE HAD APPROXIMATELY 1500' OF ANCHOR CHAIN WHICH DRAGGED ACROSS THE PIPE CUTTINGTHREE GROOVES IN THE O.D. THE ANCHOR FINALLY HIT THE PIPE CAUSING A DENT WHICH CONCENTRATED STRESS AT THE LONGITUDUNAL WELDSEAM. WHEN THE LINE CAME BACK NEAR NORMAL OPERATING PRESSURE, A FRACTURE OCCCURED ALONG THE LONGITIDINAL WELD.
2017-09-29 08:50 | YES | YES | 19920158 | 1992-09-25 | 4906 | EXXON PIPELINE CO | Null | 1992-08-31 | 1055 | LA | ASCENSION |  | NO |  | NO | FACILITY LOCATED IN ASCENSION PARISH, LA APPROXIMATELY 1 MILE NORTH OF THE INTERSECTION OF I-10 AND HIGHWAY 61 TO HIGHWAY 3140 |  | LINE PIPE | SCRAPER TRAP |  | 1971 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 2 | 2 | 0 | 5000 | 3922.6284 | 7913.5258 | NATURAL GAS LIQUID | 2 | 1 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT, MANAGER, ENVIRONMENTAL & REGULATORY COMPLIANCE | 7136565521 | EMPLOYEE WAS ASSISTING IN THE OPEING OF SCRAPER TRAP DOOR ON 12-INCH BUTANE SCRAPER TRAP. THE TRAP HAD BEEN ISOLATED AND DEPRESSURED. EMPLOYEE WAS USING AN ELECTRIC IMPACT WRENCH TO UNBOLT SCRAPER TRAP DOOR. AFTER PARTIALLY LOOSENING TWO BOLTS, LIQUID BUTANE STARTED TO DRAIN. THE EMPLOYEE STEPPED AWAY FROM TRAP APPROXAIMATELY 10 MINUTES. THE EMPLOYEE THEN LOOSENED THE TOP BOLT. HE THEN PUT THE WRENCH ON THE BOTTOM BOLT BUT AS SOON AS HE TURNED THE WRENCH ON, A FIRE OCCURRED. THE EMPLOYEE RECEIVED SECOND DEGREE BURNS TO BOTH ARMS AND FIRST DEGREE BURNS TO HIS FACE. THE SECOND EMPLOYEE RECEIVED MINOR BURNS WHICH ONLY REQUIRED FIRST AID TREATMENT.
2017-09-29 08:50 | NO | NO | 19920159 | 1991-09-30 | 18706 | SUN PIPELINE CO | YES | 1991-08-30 | 1130 | OH | SUMMIT | STOW | NO |  | NO | STATION NUMBER 0/4841, 810' WEST OF CORNER OF PROGRESS PARK AND EASTWICKE BLVD. |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | NOT GIVEN |  | 0 | 0 | NO | NO | 6.63 | 0.28 | 35000 | WELDED |  | 950 | 100 | YES | 8 | 1576 | 1 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | CHARLES W DURRETT - MANAGER, RISK MANAGEMENT | 9185866231 | WENGER EXCAVATING WAS TRENCHING FOR OHIO EDISON FOR PRIMARY POWER SERVICE. NO ONE-CALL NOTIFICATION WAS GIVEN FOR THE WORK. WENGER EXCAVATING TRENCHED ACROSS THE SUN PIPE LINE 10" AND SUN PIPE LINE 6" TWICE, HITTING THE SUN PIPE LINE AT 1130 ON AUGUST 30, 1991. A PIPELINER ARRIVED WITHIN TWENTY (20) MINUTES BUT THE LINES HAD ALREADY BEEN CROSSED AND THE 6" LINE HAD BEEN HIT. THE 6" SUN LINE WAS DOWN AT THE TIME OF THE HIT AND WAS NOT TO START UP UNTIL FURTHER NOTICE. A 6" X 18" 1500 PSI PLIDCO SLEEVE WAS INSTALLED BECAUSE OF THE DAMAGE BY THE BACKHOE TEETH.
2017-09-29 08:50 | YES | NO | 19920160 | 1992-10-02 | 26360 | HOUSTON LIGHTING & POWER CO | NO | 1992-08-13 | 1100 | TX | GALENA PARK |  | NO |  | NO | IN JACINTO CITY TEXAS, APPROXIMATELY 2460' EAST OF HOLLAND AVENUE, NORTH AND EAST OF HUNTING BAYOU, NORTH OF P.T.R.A. RAILROAD. |  | LINE PIPE | PIPE |  | 1975 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 226000 | 177302.8019 | 357691.3668 | FUEL OIL | 3 | 7 | 2 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 1440 | 4 | YES | 24 | 1835 | 1 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.S. DAVIES - MANAGER, WATER & ECOLOGICAL RESOURCES DIVISION | 7139458196 | AN OIL PATCH WAS DISCOVERED AT 11:00 A.M. BY A MAINTANENCE WORKER. THE SECTION WAS ISOLATED AND SURFACE OIL REMOVED. THE FILL WAS EXCATED TO REVEAL THAT THE CAUSE OF THE SPILL WAS A PINHOLE LEAK LOCATED APPROXIMATELY 4 INCHES FROM A GIRTH WELD. THE DAMAGED SECTION OF THE PIPELINE WAS REPLACED AND THE WELDS TESTED.
2017-09-29 08:50 | YES | NO | 19920163 | 1992-10-02 | 2323 | CHEVRON U.S.A. INC. - PIPELINES | NO | 1992-08-28 | 1000 |  |  |  | YES | X = 2,617,177 Y = 64,855 | NO | PIPELINE DAMAGE IS NEAR SOUTH PASS 77 "A" PLATFORM (COORDINATES ABOVE). AN EXACT LOCATION AND DESCRIPTION OF THE DAMAGE WILL BE FILED WITH THE REPAIR REPORT TO |  | LINE PIPE | PIPE | 1-IN PIPE; 2- IN SAFTY JO | 1978 | OUTSIDE FORCE DAMAGE | MUDSLIDE | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1569051.344 | 3165410.3257 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 10 | 0.5 | 42000 | WELDED |  | 1440 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | MUDSLIDE |  | Null | NO DATA |  | Null | Null | STEVE PASTOR - CUSA FACILITY ENGINEER | 5043642016 | PIPELINE WAS BROKEN FROM MUDSLIDES OCCURRING DURING HURRICANE ANDREW. A COMPLETE REPAIR REPORT WILL BE FILED WITH MMS WITHIN 30 DAYS AFTER COMPLETING REPAIRS. PIPELINE DAMAGE WAS DISCOVERED AT 1000 HOURS AUGUST 28, 1992 FOLLOWING HURRICANE ON AUGUST 26, 1992.
2017-09-29 08:50 | YES | NO | 19920164 | 1992-10-13 | 18718 | SUN PIPELINE CO | NO | 1992-09-12 | 1205 | TX | JEFFERSON |  | NO |  | NO | 1 MILE NORTH OF NEDERLAND OFF HWY 347 APPROX. 200 FEET ON COMPANY PROPERTY. |  | NO DATA | NO DATA | SUMP OVERFLOW | 0 | OTHER | 3/4 INCH DRAIN LINE VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 215 | 213 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L W MORRIS - L W MORRIS SUPERINTENDENT | 4077214843 | 3/4 INCH DRAIN LINE VALVE TO SUMP WAS PARTIALLY OPEN CAUSING SUMP TO FILL THEN OVER FLOW. CORRECTIVE ACTIONS: VALVE CLOSED SUMP EMPTIED, OIL CONTAINED IN DRAINAGE DITCH ON COMPANY PROPERTY BY EARTHEN DIKES VACUUM TRUCKS RECOVERED FREE OIL, DITCH LINE WASHED DOWN WITH WATER OILY WATER RECOVERED AND DISPOSED OF IN ON SITE WASTE WATER TREATMENT SYSTEM. REGULATORY AGENCIES NOTIFIED;NATIONAL CENTER, TEXAS GENERAL LAND OFFICE, UNITED STATES COAST GUARD AND TEXAS WATER COMMISSION.
2017-09-29 08:50 | YES | NO | 19920165 | 1992-10-13 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1992-09-11 | 1820 | TX | HARRIS | HOUSTON | NO |  | Null | 11750 ALMEDA RD |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 50994.1687 | 102875.8356 | NATURAL GAS LIQUID | 2 | 732 | 0 | YES | YES | 6.63 | 0.19 | 46000 | WELDED |  | 1440 | 1043 | YES | 8 | 1820 | 11 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | EXERNAL DAMAGE | Null | OTHER | LINE MARKERS | Null | Null | W D PARTLOW - ENVIRON. & SAFETY SUPV. | 7138777370 | ON 9/11/92 AT APPROXIMATELY 1820 HOURS A NORMAL BUTANE LEAK AND FIRE OCCURRED ON THE 6" ALMEDA TO WEBSTER JUNCTION PIPELINE. THE FIRE APPEARS TO HAVE BEEN IGNITED BY A PASSING AUTOMOBILE ADJACENT TO THE LEAK SITE. THE FIRE BURNED OUT AT 0930 HOURS ON 9/12/92. UPON EXCAVATION OF THE LEAKSITE, PRELIMINARYINDICATIONS SHOW DAMAGE BY AN OUTSIDE FORCE (BACKHOE), TO THE DEGREE OD A LARGE SCRAPE ON THE SIDE OF THE PIPE. ALSO, CONSIDERABLE COATING DAMAGE BY BACKHOE. THE LONGITUDINAL RUPTURE AT THE DAMAGED AREA WAS 10" LONG X 13/16" OPEN AT THE CENTER. REPLACED APPROXIMATELY 43' OF LINE WITH NEW PIPE. THERE WAS NO EXCAVATION ACTIVITY ON OR NEAR THE PIPELINE LEAKSITE AT THE TIME OF THE ICIDENT. IT HAS YET TO BE DETERMINED WHO THE RESPONSIBLE PARTY MAY BE.
2017-09-29 08:50 | YES | NO | 19920166 | 1992-10-08 | 443 | AMOCO PIPELINE CO | YES | 1992-09-06 | 318 | IN | LAKE | HAMMOND | NO |  | NO | AMOCO PIPELINE CO, CALUMET PUMPING STATION 129TH AND CALUMET AVE, HAMMOND IN |  | PUMPING STATION | TANK | GASKET | 1991 | OTHER | HASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 23535.7702 | 47481.1549 | XYLENE | 3 | 290 | 250 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. A. STAHL - AREA MANAGER | 2197382384 | CONTROL CENTER DETECTED SYSTEM FAULT AND SHUT DOWN PUMPING UNITS. AMOCO PIPELINE PERSONNEL WERE DISPATCHED TO SCENE AND VERIFIED LEAK. CAUSE OF ACCIDENT WAS A GASKET FAILURE ON AN ABOVE GROUND FLANGE. OUTAGE WAS CONTAINED WITHIN THE IMMEDIATE AREA AND IS IN THE PROCESS OF BEING CLEANED UP AND REMEDIATION PLANS ARE BEING ASSESSED.
2017-09-29 08:50 | YES | NO | 19920167 | 1992-10-13 | 18273 | SHELL PIPELINE CORP | YES | 1992-09-15 | 1420 | TX | CRANE | CRANE | NO |  | NO | NW 1/4, SE 1/4, SECTION 1, BLOCK 6 EIGHT MILES SOUTH OF CRANE, THEN FOUR MILES WEST HENDRICK-MCCAMEY 10-INCH - GREENLEE STATION. |  | PUMPING STATION | OTHER | TWO-INCH NIPPLE | 1936 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | CRUDE OIL | 1 | 90 | 60 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | G H SHERWIN (FOR) - MANAGER ENVIRON. & TECHNICAL | 7132414506 | DURING EXCAVATION FOR PRESSURE TESTING, A 2-INCH NIPPLE WAS BROKEN OFF.
2017-09-29 08:50 | YES | NO | 19920169 | 1992-10-19 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1992-10-01 | 700 | CA | SANTA BARBARA |  | NO |  | NO | CUYAMA PUMP STATION, 2 MILES W. OF NEW CUYAMA, CA ON STATE HWY, 166 |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5883.9425 | 11870.2887 | CRUDE OIL | 1 | 500 | 400 | NO | NO | 8 | 0.38 | 40000 | WELDED |  | 620 | 600 | YES | 0 | 0 | 1 | 50 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION OF PIP | NO DATA |  | Null | NO DATA |  | Null | Null | EILEEN J THRASHER - BUSINESS UNIT MANAGER | 3104289300 | EIGHT-INCH (8) DEAD LEG SECTION COMING PFF OD PUMP DISCHARGE DEVELOPED A 3/8-INCH HOLE. THIS RESULTED IN THE LEAK. LEAK FILLED PUMP PAD AND THEN PUMP STATION GROUND TO THE NORTH. PUMP WAS SHUT DOWN AND LEAK CLEANED UP.
2017-09-29 08:50 | YES | NO | 19920170 | 1992-10-15 | 4906 | EXXON PIPELINE CO | YES | 1992-09-16 | 815 | LA | LAFOURCHE |  | NO |  | NO | OCCURRED IN LAFOURCHE PARISH, LA. FROM LA HWY 308 & GRAND ISLE EXIT ON HWY 308 APPROX. 1.5 MILES ON HWY 308 TILL "LOOP INC" EXIT. EXIT ON ASPHALT RD, LEFT GRAVE |  | PUMPING STATION | SCRAPER TRAP |  | 1981 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 900000 | 706073.1048 | 1424434.6466 | CRUDE OIL | 1 | 261 | 220 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT, MANAGER ENVIRON. & REGULATORY COMPLAINCE DEPARTMEN | 7136565521 | D A CRUDE OIL SPILL AT IT'S CLOVELLY STATION LOCATED IN LAFOURCHE PARISH, LA. APPROXIMATELY 261 BARRELS OF CRUDE OIL WAS SPILLED DUE TO INCORRECT OPERATION OF A PIPELINE SCRAPER TRAP. EPC EASTERN DIVISION OIL SPILL RESPONSE TEAMWAS MOBILIZED TO THE LOCATION. ALSO, VARIOUS OIL SPILL CLEAN-UP CONTRACTORSWERE DISPATCHED TO THE SITE WITH OIL SPILL CONTAINMENT AND RECOVERY EQUIPMENT. EPC AND CONTRACT PERSONNEL QUICKLY CONTAINED THE OUTAGE BY DEPLOYING OIL SPILL CONTAINMENT BOOMS. THE OIL WAS CONTAINED AND CLEAN-UP OPERATIONS COMMENCED. THERE WERE NO INJURIES OR DEATHS WHICH RESULTED FROM THIS ACCIDENT.
2017-09-29 08:50 | YES | NO | 19920171 | 1992-10-21 | 4906 | EXXON PIPELINE CO | YES | 1992-09-22 | 930 | NC | BRUNSWICK |  | NO |  | NO | FROM INTERSECT. OF HWY 74/76 & HWY 133-S, GO S. APPROX. 3.5 MILES TILL EXXON PIPELINE CO RIGHT-OF-WAY, GO E ON RIGHT-OF-WAY FROM HWY 133-S APPROX. 120 YDS TO VA |  | LINE PIPE | VALVE |  | 1973 | OTHER | O-RING/BONNET SEAL FAILUR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 54916.797 | 110789.3614 | XYLENE | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MGR ENVIRON. & REGULATORY COMPLIANCE | 7136565521 | EXXON PIPELINE COMPANY (EPA) EMPLOYEES WERE EXCAVATING THE BURIED VALVE SITETO REMOVE A CHECK VALVE. AFTER DIGGING A FEW FEET PARAXYLENE VAPORS AND POSSIBLY HEAVY FUEL OIL VAPORS WERE DETECTED. THE PARAXYLENE LINE WAS SHUT-DOWN. THE HEAVY FUEL OIL PIPELINE WAS IDLED. PARAXYLENE WAS FOUND LEAKING FROM A 4-INCH VALVE BONNET. THE VALVE WAS TEMPORARILY REPAIRED AND THE LINE WAS PLACED BACK INTO SERVICE. CURRENTLY, PLANNING IS UNDER-WAY TO REPLACE THE VALVE.
2017-09-29 08:50 | YES | NO | 19920172 | 1992-10-27 | 2527 | COASTAL STATES GAS TRANSMISSION CO | NO | 1992-09-19 | 1750 | TX | SAN PATRICIO |  | NO |  | NO | 5 MI WEST OF PORTLAND PM FM 893 |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 47071.5403 | 94962.3098 | JET FUEL | 3 | 1009 | 300 | NO | YES | 12.75 | 0.2 | 52000 | WELDED |  | 1193 | 1000 | YES | 4 | 1496 | 2 | 1989 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | W D PARTLOW - ENVIRONMENTAL & SAFETY SUPERVISOR | 7138777370 | LEAK WAS CAUSED BY EXTERNAL CORROSION. THE AMOUNT OF PRODUCT LOST WAS 709 BARRELS. APPROXIMATELY 91'9" OF NEW 12" PIPE WAS INSTALLED WHERE LEAK OCCURRED
2017-09-29 08:50 | YES | NO | 19920173 | 1992-10-27 | 12127 | MARATHON PIPE LINE CO | YES | 1992-09-26 | 920 | IN | KNOX |  | NO |  | NO | FOUR MILES SOUTH OF BEAL, IN, COUNTY OF KNOX, COUNTY RD. 900W AND 1450S |  | LINE PIPE | OTHER | FLANGE GASKET | 1992 | OTHER | FAILED GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 133369.3642 | 269059.8777 | NATURAL GAS LIQUID | 2 | 2300 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A FISHER, REGULATORY COORDINATOR | 4194213201 | DURING THE RECOMMISSIONING OF THE 4" LPG LINE FROM PRINCETON, IN, TO ROBINSON, IL (LINE WAS DOWN FOR BLOCK VALVE INSTALLATION), THE SYSTEM EXPERIENCED A GASKET FAILURE ON THE NEWLY INSTALLED BLOCK VALVE. THE BLOCK VALVE ASSEMBLY ( INCLUDING VALVES, FLANGES, GASKETS, AND 4' OF PIPE ON BOTH SIDES OF VALVE) HAD BEEN HYDROTESTED PRIOR TO INSTALLATION. THE LINE WAS SHUT DOWN AT 0900 HOURS ON 9/26/92, BECAUSE THE BATCHING PIG WAS NOT RECEIVED AT THE DELIVERY STATION. AT 0920 HOURS A CALL WAS RECEIVED BY THE MPL OPERATIONS CENTER VIA THE 1-800 EMERGENCY NUMBER REPORTING A VISUAL CONFIRMATION OF A RELEASE. MPL EMERGENCY REPONSE PERSONNEL ARRIVED ON SCENE AT APPROXIMATELY 1000 HOURS ON 9/26/92 TO VERIFY THE RELEASE AND SECURE THE AREA. THE GASKET FAILURE INVESTIGATION IS IN PROGRESS. THE NATIONAL RESPONSE CENTER, INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT, AND LOCAL SHERIFF AND FIRE DEPARTMENT WERE TIMELY NOTIIFED.
2017-09-29 08:50 | NO | NO | 19920174 | 1992-10-27 | 26134 | MOBIL PIPELINE CO - MOBIL WEST COAST PIPELINE | NO | 1992-10-09 | 1615 | CA | KERN |  | NO |  | NO | SEC 15 TIIN R20W ONE MILE S OF HWY 166, E SIDE OF WATER RESOURCES ROAD |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19613.1418 | 39567.6291 | CRUDE OIL | 1 | 4 | 4 | NO | NO | 12.75 | 0.31 | 2050 | WELDED |  | 1248 | 900 | YES | 4 | 4600 | 8 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | Null | J A CROTTY, ACTING NORTHERN AREA MANAGER | 8057652058 | DURING CONSTRUCTION OF REPLACEMENT PIPELINE, THE ACTIVE M-1 LINE WAS STRUCK BY A TRENCHING MACHINE. THIS LINE HAD BEEN EXPOSED EACH 100', THE NEAREST BEING 30' TO THE NORTH OF THE DAMAGE LOCATION. THE ORIGINAL LAY IN THIS AREA INCLUDED A LONG RADIUS BEND. A 47" SECTION OF PIPE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19920175 | 1992-10-27 | 15498 | PHILLIPS GAS PIPELINE CO | YES | 1992-09-26 | 800 | TX | SCHLEICHER |  | NO |  | YES | BENEDUM-SWEENY LINE, MP 83-43+42. 3.5 MILES WEST OF ELDORADO, TEXAS. APPRO. 350 FEET N OF SH 190. |  | LINE PIPE | PIPE |  | 1991 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 47071.5403 | 94962.3098 | NATURAL GAS LIQUID | 2 | 35 | 0 | NO | NO | 10.75 | 0.19 | 60000 | WELDED |  | 1433 | 810 | YES | 8 | 1940 | 9 | 91 | EXTERNAL | Null | YES | OTHER | ELECTROLYTIC | NO DATA |  | Null | NO DATA |  | Null | Null | B L THORMAN, MANAGER OF ENGINEERING & TECHNICAL SERVICES. | 9186614721 | LANDOWNER REPORTED AN ODOR AND ICE CRYSTALS ON THE RIGHT-OF-WAY TO THE ODESSA PIPELINE CONTROL CENTER. THEY IMMEDIATELY SHUT DOWN AND BLOCKED IN THE SECTION. EXTERNAL CORROSION AT A DAMAGED COATING SITE CAUSED A SMALL LEAK. THE
2017-09-29 08:50 | YES | NO | 19920176 | 1992-11-02 | 18214 | SHAMROCK PIPE LINE CORP | NO | 1992-09-28 | 1700 | TX | POTTER |  | NO |  | NO | 20 MILES N OF AMARILLO, TX ON U.S. HWY 87 AND 1 1/2 MILES EAST. SECTION 81, BLOCK 3, G&M SURVEY, POTTER COUNTY, TEXAS |  | LINE PIPE | PIPE |  | 1984 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 71500 | 56093.5855 | 113163.4191 | GASOLINE | 3 | 972 | 63 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COMPANY PROGRAM | Null | NO | GERALD CHILDERS | 8063783583 | AT APPROXIMATELY 1700 HOURS ON SEPTEMBER 28, 1992, A DITCHING MACHINE OPERATED A THIRD-PARTY STRUCK AND RUPTURED OUR 8" MCKEE TO AMARILLO PRODUCTS PIPELINE. THE ACCIDENT ALLOWED 909 BARRELS OF GASOLINE TO ESCAPE, OF WHICH 63 BARRELS WAS SUBSEQUENTLY RECOVERED. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING A 35-FOOT 8" SECTION OF PIPE WITH PRETESTED PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19920177 | 1992-11-02 | 2731 | CHEVRON PIPELINE CO | NO | 1992-09-24 | 1600 |  |  |  | YES |  | Null | APPX. CENTER OF TIMBALIER ISLAND COORDINATES - N.29.04.29 W 90.18.57 |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | CRUDE OIL | 1 | 70 | 65 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 600 | 100 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | OTHER | DOTTIE | NO | NO | A P WHITE NATURAL TEAM LEADER | 5043963325 | CAUSS OF INCIDENT: BEAN DREDGING WHO WAS CONTRACTED BY GREENHILL PETROLEUM STRUCK CHEVRON'S PIPELINE WITH ITS "CLAM BUCKET" WHILE DREDGING A CHANNEL INTO TIMBAILER BAY. (NO NOTIFICATION WASMADE BY DREDGING COMPANY TO CHEVRON PIPELINE COMPANY OR TO THE "DOTTIE" ONE CALL SYSTEM TO IDENTIFY PIPELINES IN AREA OF DREDGING. PROTECTIVE MEASURES TAKEN: PIPELINE WAS SHUT DOWN AND ISOLATED IMMEDIATELY. LEAK SITE WAS BOOMED AND SECONDARY BOOM INSTALLED. PATERSON RIEDEL AND ICI CREWS WITH EQUIPMENT WERE DEPLOYED TO CONTAIN AND CLEAN UP SPILL. FREE OIL WAS PUMPED BACKED INTO PIPELINE SYSTEM. A CLAMP WAS PLACED ON THE PIPELINE UNTIL PERMANENT REPAIRS COULD BE MADE.
2017-09-29 08:50 | NO | NO | 19920178 | 1992-11-02 | 2552 | COLONIAL PIPELINE CO | YES | 1992-09-30 | 1530 | NC | GUILFORD | GREENSBORO | NO |  | NO | COLONIAL PIPELINE COMPANY'S GREENSBORO TANK FARM |  | TANK FARM | TANK |  | 1963 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | GASOLINE | 1 | 3 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MGR TECHNICAL & REGULATORY | 4048412296 | ON SEPTEMBER 29, 1992, A CONTRACTOR SANDBLASTING THE FLOOR OF TANK 833 AT COLONIAL PIPELINE COMPANY'S GREENSBORO, NC TANK FARM DISCOVERED 3 TOPSIDE CORROSION PITS THAT CONTAINED SMALL HOLES PENETRATING THROUGH THE PLATE. THESE HOLES WERE ABOUT THE SIZE OF A PENCIL POINT. ON SEPTEMBER 30TH, TWO INCH DIAMETER COUPONS WERE CUT FROM THE FLOOR SURROUNDING EACH CORROSION PIT TO DETERMINE IF PRODUCT HAD LEAKED INTO THE SOIL BELOW THE TANK. AT APPROXIMATELY 1550 EDT ON SEPTEMBER 30TH IT WAS DETERMINE THAT PRODUCT HAD IN FACT LEAKED INTO THE SOIL BELOW THE TANK. SUBSEQUENT SAMPLING AT OTHER POINTS UNDER THE TANK INDICATED THAT THE CONTAMINATION HAD MIGRATED TOWARD THE SUMP AREA AND THE TANKLINE. AT 1638 EDT ON SEPTEMBER 30TH, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 138789) BY TELEPHONE AFTER IT WAS DETERMINED THAT DUE TO SOILREMEDIATION, THE TOTAL DAMAGE RELATED COSTS WOULD EXCEED $5,000.00. WHILE THE AMOUNT OF PRODUCT LEAKED FROM THE TANK IS UNDETERMINED, 3.4 BARRELS OF PRODUCT HAVE BEEN RECOVERED TO DATE FROM MONITORING WELLS LOCATED NEAR THIS TANK. PLANS ARE CURRENTLY BEING FORMULATED TO MAKE NECESSARY REPAIRS TO THE TANK AND CLEAN UP THE CONTAMINATION.
2017-09-29 08:50 | YES | NO | 19920179 | 1992-11-03 | 443 | AMOCO PIPELINE CO | YES | 1992-10-16 | 0 | OK | PAYNE |  | NO |  | NO | NORTHEAST QUARTER OF SECTION 18, TOWNSHIP 17 NORTH, RANGE 5 EAST. |  | LINE PIPE | PIPE | COLLAR | 1921 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 23535.7702 | 47481.1549 | CRUDE OIL | 1 | 300 | 275 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 720 | 20 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | T.O. MC GEEHAN - ACTING AREA MANAGER | 9182257271 | ON OCTOBER 16, 1992, A DOZER OPERATOR WAS CLEARING BRUSH AND TREES AND PERFORMING MINOR DIRTWORK. THE DOZER APPARENTLY DROVE OVER OR STTRUCK AMOCO'S 8" PIPE CAUSING THE PIPE'S COLLAR TO PULL AND STRIP THE TREADS. THE OIL FLOWED TO AN ADJACENT EROSION GULLY AND FOLLOWED IT ABOUT 100 FEET TO EUCHEE CREEK.THE DOZER OPERATOR MADE NO REPORT TO AUTHORITIES. THE PIPELINE WAS NOT OPERATING AT THIS TIME. ON OCTOBER 17, 1992, AN OKLAHAMA CORPORATION COMMISSION INSPECTOR SAW THE OIL WHILE CROSSING A NEARBY BRIDGE. HE CONTACTED AMOCO, AND WITHIN AN HOUR THE SOURCE OF THE OIL WAS VERIFIED. THE OIL WAS EASILY CONTAINED BY NIGHTFALL.
2017-09-29 08:50 | YES | NO | 19920180 | 1992-10-27 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-10-09 | 2155 | VA | HENRY | MARTINSVILLE | NO |  | NO | OFF FOXFIRE ROAD (VA ROUTE 658) BETWEEN DYERS STORE ROAD (VA ROUTE 657) AND BARROWS HILL ROAD (VA ROUTE 663) |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 35303.6552 | 71221.7323 | FUEL OIL | 3 | 95 | 2 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1450 | 1180 | YES | 24 | 1884 | 10 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VICE PRESIDENT - OPERATIONS | 4043645916 | AT APPROXIMATELY 9:55 P.M., EDT ON OCTOBER 9, 1992, A LEAK WAS DISCOVERED ONPLANTATION'S 8.625-INCH O.D., 0.188" WALL THICKNESS, GRADE X-52, PETROLEUMPRODUCTS WHICH OPERATES BETWEEN GREENSBORO, NORTH CAROLINA AND ROANOKE, VIRGINIA. THE LEAK OCCURED IN A REMOTE AREA NEAR FOXFIRE ROAD (VA ROUTE 658) BETWEEN DYERS STORE ROAD (VA ROUTE 657) AND BARROWS HILL ROAD (VA ROUTE 663) IN HENRY COUNTY, VIRGINIA. THE SEAMLESS LINE PIPE HAD A I-INCH LONG HAIRLINE CRACK AT THE ONE O'CLOCK POSITION. THE CRACK WAS WITHIN A DENT WHICH MEASURED 0.360" IN DEPTH. DURING EXCAVATION OF THE PIPELINE LEAK, A ROCK WAS DISCOVERED RESTING ON THE PIPE. THE PIPELINE WAS REPAIRED WITH A 3-FOOT LONG FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | NO | NO | 19920181 | 1992-10-27 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-10-03 | 1935 | GA | HARALSON |  | NO |  | NO | 1278 FEET EAST OF SANGAMORE ROAD |  | LINE PIPE | PIPE |  | 1951 | FAILED PIPE | INTERNAL MILL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 35303.6552 | 71221.7323 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 14 | 0.38 | 35000 | WELDED |  | 1165 | 970 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VICE PRESIDENT - OPERATIONS | 4043645916 | AT APPROXIMATELY 7:35 P.M., EDST ON OCTOBER 3, 1992, A LEAK WAS DISCOVERED ON PLANTATION'S 14-INCH, .375" WALL THICHKNESS, GRADE B, PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN BREMEN, GEORGIA, AND GREENSBORO, NORTH CAROLINA. THE LEAK OCCURRED 1,278 FEET EAST OF SANGAMORE ROAD IN HARALSON COUNTY, GEORGIA. THE SECTION OF PIPE WHICH FAILED AND HAD TWO LONGITUDINAL, HAIRLINE CRACKS, EACH 2" LONG, AT THE 3 O'CLOCK POSITION. NO VISIBLE PRODUCT WAS ENCOUNTERED DURING EXCAVATION OF THE PIPELINE. THE PIPELINE WAS REPAIRED WITH ONE5' LONG FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19920182 | 1992-10-27 | 4906 | EXXON PIPELINE CO | YES | 1992-09-28 | 1545 | LA | PARISH | NACHITOCHES | NO |  | NO | EVENT OCCURRED IN NACHITOCHES PARISH, LA, T9N, R8W, S25. FROM I-49 AND HWY. 6 GO EAST ON HIGHWAY AND EXIT ON HIGHWAY 504. GO NORTH APPROXIMATELY 5 MILES UNTIL |  | LINE PIPE | PIPE |  | 1953 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CONDENSATE |  | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MGR ENVIRON. & REGULATORY COMPLIANCE | 7136565521 | EXXON PIPELINE COMPANY EMPLOYEES WERE PREPARING A 22-INCH PIPELINE FOR HYDROSTATIC TEST. THE PIPELINE WAS OUT OF SERVICE. PIPELINE STOPPLES WERE PLACEDIN THE LINE. A WELD CAP WAS PLACED IN THE SOUTH END OF THE LINE. ON THE NORTH END AN 8 FOOT SECTION OF LINE WAS REMOVED BY COLD CUTTING. A POLY PIG WAS INSERTED 8 FEET INTO THE NORTH END IN ORDER TO DISPLACE THE LINE AND TO BLOCK VAPORS FROM ESCAPING . A WELDER BEGAN TO BEVEL THE LINE, APPROXIMATELY 5MINUTES AFTER THE WELDER BEGAN TO BEVEL, THE PIG WAS EJECTED FROM THE LINE.A FLASH FIRE OCCURRED WHEN THE PIG EMERGED FROM THE LINE. A FIRE EXTINGUISHER WAS USED TO EXTINGUISH THE FIRE. THERE WERE NO INJURIES OR DEATHS FROM THIS EVENT.
2017-09-29 08:50 | YES | NO | 19920183 | 1992-10-27 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1992-10-01 | 15 | IL | MORRIS |  | NO |  | NO | 4755 E ROUTE 6, MORRIS, IL 60450 |  | TANK FARM | OTHER | FREE WATER KNOCKOUT VESSE | 1973 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | L. P. G. | 2 | 1 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GEORGE A ROOD - V. P . OPERATIONS | 7138537876 | EMLOYEES WERE ATTEMPTING TO CLEAR A HIGH LEVEL WATER ALARM CONDITION IN THE FREE WATER KNOCKOUT VESSEL BY MANUALLY OVERRIDING THE DUMP VALVE PNEUMATIC CONTROLLER. IT APPEARS THAT ETHAN WAS INADVERTENTLY DUMPED INMTO THE WATER DISCHARGE LINE (DRAIN LINE). HYDRATES IN THE ETHANE CAUSED THE WATER TO FREEZE CREATING AN ICE PLUG IN THE WATER DRAIN LINE. AS THE WATER AND ETHANE WAS DUMPED INTO THE DRAIN LINE, PRESSURE INCREASED UNTIL A REPAIR CLAMP IN THE WATER LINE LEAKED. ETHANE GOT INTO THE ATMOSPHERE, DRIFTED TO A SALT BATH HEATERAND IGNITED.
2017-09-29 08:50 | NO | NO | 19920184 | 1992-11-10 | 2552 | COLONIAL PIPELINE CO | YES | 1992-07-14 | 900 | LA | EAST FELICIANA |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S BATON ROUGE TANK FARM |  | TANK FARM | OTHER | THREADED FITTING | 1971 | OTHER | FAILED THREADED COUPLING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | GASOLINE | 2 | 4 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX | 4048412296 | ON JULY 14, 1992, DURING A ROUTINE STATION CHECK, OPERATOR PERSONNEL NOTED ASMALL AMOUNT OF PRODUCT IN AN EXCESS WELL IN THE NO. 2 TANK FARM MANIFOLD ATCOLONIAL PIPELINE COMPANY'S BATON ROUGE, LOUISIANA TANK FARM. DAILY MONITORING AND RECOVERY OPERATIONS CONTINUED AND ON JULY 31, 1992, THE NATIONAL REPOSNSE CENTER WAS NOTIFIED(REPORT NO. 129899) WHEN IT WAS DETERMINED THAT DAMAGED RELATED COSTS WOULD EXCEED $5,000. ON AUGUST 14, 1992, WE NOTIFIED THE OFFICE OF PIPELINE SAFETY THAT THE CAUSE OF THE LEAK HAD NOT BEEN DETERMINED AND THAT A COMPLETE REPORT WOULD BE FILED AT A LATER DATE WHEN MORE FACTS WERE KNOWN. ON OCTOBER 12, 1992, AFTER EXTENSIVE EXCAVATION, THE LEAK WAS FOUND TO BE ORIGINATING FROM A THREADED SLEEVE COUPLING ON 2" LINE USED TO VENT BOTHTHE OIL AND THE GASOLINE CAN PUMPS. UPON EXAMINATION, THE COUPLING AND VENTPIPE WERE FOUND TO HAVE SEPARATED, APPARENTLY THE RESULT OF GROUND SETTLEMENT. REPAIRS TO THE LINE HAVE BEEN COMPLETED AND SOIL REMEDIATION IS CONTINUING.
2017-09-29 08:50 | YES | NO | 19920185 | 1992-11-10 | 22610 | WILLIAMS PIPELINE CO | YES | 1992-10-14 | 1030 | NE | RICHARDSON |  | NO |  | NO | NE/4 SECTION 27, T2N, R15E RICHARDSON COUNTY, NEBRASKA 300 YDS SOUTH OF WPL'S FALLS CITY, NEBRASKA PUMP STATION. |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7845.2567 | 15827.0516 | DIESEL FUEL | 3 | 60 | 37 | NO | NO | 8.63 | 0.2 | 35000 | WELDED |  | 1150 | 80 | YES | 8 | 1483 | 6 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | STEVEN S BALL - V.P. - OPERATIONS AND ENGINEERING | 9185883850 | VERNON BUCKMINISTER CALLED TO REPORT HE HAD PUNCTURED THE PIPELINE WITH A SUBSOILER AT 10:30 ON 10/14/92. THE LINE WAS IMMEDIATELY SHUT DOWN AND THE SHERIFF CLOSED THE NEARBY HIGHWAY BECAUSE THERE WAS A POSSIBLITY OF THE SPRAY REACHING THE HIGHWAY. THE VALVES WERE CLOSED AND THE HIGHWAY WAS REOPENED. THE #2 DIESEL FUEL WAS CONTAINED WITHIN THE FARMER'S TERRACE. A TOTAL OF 30 BBLS WERE RECOVERED USING A VACUUM TRUCK. SOIL BORINGS WERE PERFORMED 10/20/92 TO DEFINE THE EXTENT OF THE CONTAMINATION AND THE REMAINING 30 BBLS WERE THENRECOVERED THROUGH EXCAVATION OF APPROXIMATELY 950 CUBIC YARDS OF CONTAMINATED SOIL. THE LINE WAS 6 TO 8 INCHES DEEP WHERE IT WAS HIT IN THE CENTER OF A TERRACED FIELD. THE LINE WAS CLEARLY MARKED AT EACH FENCE LINE 617 FT. TO THENORTH AND 712 FT. TO THE SOUTH. THE LANDOWNER DID NOT CALL WPL OR ONE CALL TPRIOR TO PLOWING. THE MOST RECENT SHALLOW LINE SURVEY WAS DONE BY WPL IN 1982 AT 200 FT INTERVALS. AT THE TIME OF THE SURVEY, LINE DEPTHS IN THIS FIELDWERE MEASURED AT 22", 32", AND 33". A TOTAL OF 80 FT OF NEW PIPE WAS INSTALLED BECAUSE THE LINE HAD BEEN DAMAGED IN EACH OF THE TWO PREVIOUS PASSES PRIOR TO THE PUNCTURE. COATING DAMAGE INDICATED HITS IN PREVIOUS YEARS ALSO.
2017-09-29 08:50 | NO | NO | 19920186 | 1992-11-09 | 15851 | PRIDE REFINING INC | NO | 1992-10-08 | 1000 | TX | PALO PINTO | MINGUS | NO |  | NO | APPROXIMATELY 1 MILE NORTH OF CITY OF MINGUS, TEXAS ON WEST SIDE OF FM 108 APPROXIMATELY 1/2 MILE. |  | LINE PIPE | PIPE |  | 1984 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 784.5257 | 1582.7052 | DIESEL FUEL | 3 | 8 | 6 | NO | NO | 6.25 | 0.19 | 42000 | WELDED |  | 1563 | 0 | YES | 8 | 1954 | 1 | 84 | EXTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON - PIPELINE MANAGER | 9156748231 | AT APPROXIMATELY 10:00 A.M. ON THE MORNING OF 10-08-92, OUR 24HR. NUMBER RECEIVED A TELEPHONE CALL FROM A LEASE OPERATOR CHECKING HIS GAS COMPRESSOR THATHYDROCARBOON WAS SURFACING NEAR ONE OF HIS METER RUNS. WE THEN IN TURN MOBILIZED OUR CREWS TO THE AREA AT THE SAME TIME SHUT DOWN THE OPERATION OF OUR PIPELINE. WE CLAMPED THE LEAK AND STARTED CLEAN-UP PROCEDURES. ON 10/15/92 PERMANENT REPAIRS WERE MADE BY INSTALLING A FULL ENCIRCLEMENT SLEAVE. DOT ACCIDENT #139868.
2017-09-29 08:50 | YES | NO | 19920187 | 1992-11-12 | 10012 | KANEB PIPELINE CO | YES | 1992-10-12 | 2059 | NE | FILLMORE |  | NO |  | NO | NW 1/4, SECTION 30, R-2-W, T-7-N, FILLMORE COUNTY, NEBRASKA. |  | TANK FARM | TANK |  | 1953 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9414.3081 | 18992.462 | DIESEL FUEL | 3 | 532 | 204 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L LEROY ANDERSON - MANAGER OF REGULATORY AFFAIRS | 3162621408 | THE FOLLOWING OPERATION WAS TAKING PLACE WHEN THE ACCIDENT OCCURRED AT GENEVA TERMINAL. DIESEL FUEL WAS BEING RECEIVED OFF OF THE 16" MAIN LINE IN TO TANK 30-3 WHILE AT THE SAME TIME PART OF THE STREAM WAS BEING PUMPED (BOOSTED) UP LINE NUMBER 4 (GENEVA TO YANKTON). THE OPERATOR ON DUTY AT GENEVA MISCALCULATED THE FILL TIME WHICH RESULTED IN THE TANK OVERFLOWING.
2017-09-29 08:50 | NO | NO | 19920188 | 1992-09-24 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-09-25 | 800 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | PLANTATION'S TANK FARM AT BATON ROUGE, LOUISIANA. |  | PUMPING STATION | OTHER | COMPRESSED ASBESTOS GASKE | 1951 | OTHER | FAILURE OF FLANGE GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 18500 | 14513.7249 | 29280.0455 | GASOLINE | 3 | 3 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M COOK - V.P. OPERATIONS | 4043645916 | ON MONDAY, AUGUST 24, WE NOTICED A SMALL AMOUNT OF GASOLINE IN A STROM WATERDRAIN LOCATED ON OUR PROPERTY. WE RECOVERED APPROXIMATELY 0.5 BARRELS OF GASLINE THAT NIGHT. ON TUESDAY, A SET OF FLANGES ON THE SUCTION LINE OF OUR MAINLINE PUMPING UNIT WAS EXCAVATED TO LOCATE THE SOURCE OF THE RELEASE. THE EXCAVATION WAS INSPECTED ROUTINELY THROUGH THE EVENING OF AUGUST 26 AND NO PRODUCT WAS OBSERVED. ON THE MORNING OF AUGUST 27, APPROXIMATELY 2.5 BARRELS OF GASOLINE WAS OBSERVED IN THE EXCAVATION. APPARENTLY THE SET OF FLAGES WAS LEAKING INTERMITTENTLY DUE TO A FAILED GASKET. ON AUGUST 28 AT 1:30 A.M., THE REPLACEMENT OF THE FAILED GASKET WAS COMPLETED.
2017-09-29 08:50 | YES | NO | 19920189 | 1992-11-09 | 443 | AMOCO PIPELINE CO | YES | 1992-10-09 | 1800 | MO | CASS | FREEMAN | NO |  | NO |  |  | TANK FARM | TANK | ROOF DRAIN HOSE FAILURE | 0 | OTHER | FAILED DRAIN HOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3138.1027 | 6330.8207 | CRUDE OIL | 1 | 750 | 749 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M B WEISS - AREA MANAGER | 8168995387 | A FAILURE OF THE FLEXIBLE DRAIN HOSE WITHIN TANK #7079, WHICH IS USED TO REMOVE WATER FROM THE SURFACE OF THE FLOATING ROOF, RESULTED IN THE DISCHARGE OFAPPROXIMATELY 750 BARRELS OF CRUDE OIL TO THAT TANK'S FIREWALL. AT THE TIMEOF THE SPILL, PER ESTABLISHED OPERATING PROCEDURE, THE SWINGLINE USED FOR DRAINING WATER FROM THE FIREWALL WAS IN THE UP (CLOSED) POSITION. VACUUM TRUCKS WERE UTILIZED FOR RECOVERY OF THE FREE OIL AND APPROXIMATELY 1,000 CUBIC YARDS OF CONTAMINATED SOIL WAS MOVED TO AN APPROVED "SPECIAL WASTE" LAND FILL IN KANSAS CITY, MO.
2017-09-29 08:50 | YES | NO | 19920190 | 1992-11-06 | 2552 | COLONIAL PIPELINE CO | YES | 1992-10-06 | 600 | NC | CABARRUS |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S KANNAPOLIS PUMP STATION |  | PUMPING STATION | OTHER | NO. 1 SCRAPER PASSAGE IND | 1978 | OTHER | FAILED O-RING IN SCRAPER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7845.2567 | 15827.0516 | GASOLINE | 2 | 5 | 1 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES A COX - MGR. TECHNICAL & REGULATORY | 4048412296 | AT 0600 EDT ON OCTOBER 6, 1992, A PAINTING CONTRACTOR NOTIFIED PERSONNEL AT COLONIAL PIPELINE COMPANYS CHARLOTTE DELIVERY THAT GASOLINE WAS FOUND ON THE SURFACE OF RAINWATER THAT HAD ACCUMULATED AT THE MAINLINE BLOCK VALVE AT THE KANNAPOLIS, NC PUMP STATION. A COLONIAL REPRESENTATIVE WAS DISPATCHED TO THE FACILITY AND FOUND THAT A SMALL LEAK DUE TO A FAILED 0-RING ON THE NO.1 SCRAPER PASSAGE INDICATOR LOCATED ON THE 40" DIAMETER GASOLINE PIPELINE RUNNING THROUGH THE STATION. IT WAS ESTIMATED THAT APPROXIMATELY 5 BARRELS OF GASOLINE HAD ESCAPED BUT WAS CONTAINED WITHIN THE STATION YARD. WHEN IT WAS DETERMINED THAT DUE TO SOIL REMEDIATION, THE TOTAL DAMAGE COSTS ASSOCIATED WITH THE LEAK WOULD EXCEED $5000.00, THE NATIONAL REPONSE CENTER WAS NOTIFIED AT 0930 EDT ON OCTOBER 6, 1992. THE NRC REPORT NUMBER IS 139440. AT 0940 EDT, AS A COURTESY, THE SOUTHERN REGION OFFICE OF PIPELINE WAS NOTIFIED SAFETY OF THE CALL TO THE NRC. RECOVERY OPERATIONS RESULTED IN THE RECOVERY AND RETURN TO THE SYSTEM OF 1 BARREL OF GASOLINE; THE REMAINDER BEING LOST TO THE SURROUNDING SOIL AND TO EVAPORATION. REMEDIATION OF THE CONTAMINATED SOIL IS CONTINUING. REPAIRS WERE MADE BY INSTALLING A NEW SCRAPER PASSAGE INDICATOR UNIT.
2017-09-29 08:50 | YES | NO | 19920191 | 1992-11-16 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1992-10-13 | 1505 | PA | ALLEGHENY | MOON | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 196131.418 | 395676.2907 | JET FUEL | 3 | 105 | 0 | NO | NO | 18 | 0.28 | 52000 | WELDED |  | 430 | 130 | YES | 24 | 1118 | 3 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | DEAN R MOYER - REGULATORY COMPLAINCE ADMINSTRATOR | 2158208300 | A CONTRACTOR AT A NEW HOUSING SUBDIVISION WAS MOVING SOME EARTH WITH A BULLDOZER AND DAMAGED THE PIPELINE WITH THE DOZER'S BLADE. A GOUGE OF ABOUT 6" X 3" WAS PUT IN THE PIPELINE. THE ORIGINAL PIPE DEPTH PRIOR TO ANY EARTH MOVING WAS 40 INCHES. THE PIPELINE SHUT DOWN IMMEDIATELY ON AUTOMATIC CONTROLS. STATE & FEDERAL AGENCIES WERE NOTIFIED AS REQUIRED. PRODUCT RELEASE CONTAINMENT OPERATIONS COMMENCED PROMPTLY. APPROXIMATELY 200 CUBIC YARDS OF AFFECTEDSOIL WAS REMOVED UNDER THE DIRECTION OF THE PENNSYLVNIA DEPARTMENT OF ENVIRONMENTAL RESOURCES. THE DAMAGED PIPELINE SECTION WAS REPLACED WITH PRETESTED STOCK PIPE, X-RAYED, AND PIPELINE SERVICE RESTORED 10/15/92.
2017-09-29 08:50 | YES | NO | 19920192 | 1992-11-16 | 809 | ARCO PIPE LINE CO | YES | 1992-10-28 | 2155 | TX | COOKE |  | NO |  | NO | 1/4 TO 1/2 MILE SOUTH OF RED RIVER; 600' WEST OF I-35 |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 3530.3655 | 7122.1732 | KEROSENE | 2 | 280 | 0 | NO | NO | 8 | 0.32 | 2400 | NO DATA |  | 728 | 220 | YES | 8 | 910 | 10 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | VANDALISM/GUN SHOT | Null | ONE CALL |  | NO | NO | BARRY HILL | 7139865356
2017-09-29 08:50 | YES | NO | 19920193 | 1992-11-13 | 1248 | BELLE FOURCHE PIPELINE CO | NO | 1992-10-12 | 1010 | WY | NIOBRARA |  | NO |  | NO | NE 1/4 SECTION 36 T36N R67W |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 94143.0806 | 189924.6195 | CRUDE OIL | 1 | 6000 | 810 | NO | NO | 12.75 | 0.25 | 52000 | WELDED |  | 850 | 850 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | STEVE RIEGER - ENGINEER/SAFETY COORDINATOR | 3072660235 | A WORK CREW FROM THE NIOBRARA COUNTY ROAD AND BRIDGE DEPARTMENT WAS EXCAVATING FOR GRAVEL ROAD MATERIAL ADJACENT TO BELLE FOURCHE PIPELINE COMPANY'S CRUDE OIL PIPELINE AND PENETRATED THE WALL OF THE PIPELINE WITH THE BUCKET OF THEFRONT-END LOADER.
2017-09-29 08:50 | YES | NO | 19920194 | 1992-11-18 | 18273 | SHELL PIPELINE CORP | YES | 1992-10-25 | 900 | LA | ST JAMES | ST JAMES | NO |  | NO | ST JAMES TERMINAL (CAPILINE SYSTEM) TWO MILES SOUTH OF ST JAMES. |  | TANK FARM | TANK |  | 1968 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19613.1418 | 39567.6291 | CRUDE OIL | 1 | 3000 | 2900 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A R HAVEY - MANAGER REGULATORY COMPLIANCE | 7132410132 | INADVERDENT OPENING OF A TANK MANIFOLD VALVE CAUSED A TANK TO OVERFLOW.
2017-09-29 08:50 | NO | NO | 19920195 | 1992-11-18 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-09-30 | 1315 | CA | LOS ANGELES | CARSON | NO |  | NO | 16-INCH SURGE MANIFOLD AREA OF SFPP'S WATSON STATION. |  | PUMPING STATION | BOLTED FITTING | GASKET ON SURGE SYSTEM | 1986 | OTHER | RUPTURED GASKET ON SURGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 53000 | 41579.8606 | 83883.3736 | FUEL OIL | 3 | 30 | 8 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENOIR V.P. - OPERATIONS & ENGINEERING | 2134867720 | SURGE PUMP BEING USED TO TRANSFER PRODUCT TO GATX THROUGH 10 INCH TRANSMIX LINE. PUMP USED CANNOT EXCEED MAXIMUM OPERATING PRESSURE OF THE LINE. WHEN PUMP WAS SHUT DOWN, A SURGE OCCURRED BACK AGAINST THE CHECK VALVE DOWNSTREAM OF PUMP. GASKET WAS THE ORIGINAL INSTALLED WHEN PUMP AND PIPING INSTALLED. HIGHEST PRESSURE NOTED WAS ABOUT 150 PSI. GASKET FAILED AND PRODUCT SPRAYED FROM FLANGE ON DOWNSTREAM SIDE OF CHECKVALVE. NOTE: INITIAL ESTIMATES OF THE TOTAL PROPRETY DAMAGE CAUSED BY THIS OCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAD RAISED THOSE ESTIMATES TO EXCEED $5,000 AND WE NOW SUBMIT THIS REPORT TO COMPLY WIHT THE INTENT OF THE REGULATION.
2017-09-29 08:50 | NO | NO | 19920196 | 1992-11-18 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-10-09 | 1030 | CA | SAN DIEGO | CAMP PENDLETON | NO |  | YES | IN CHECK VALVE VAULT INSIDE FENCE AT SFPP'S PENDLETON BOOSTER FACILITY, CAMP PENDLETON USMC BASE (LS SD-2) |  | PUMPING STATION | VALVE |  | 1970 | OTHER | FAILED O-RING IN CHECK VA | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | GASOLINE | 3 | 8 | 8 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENOIR V.P. - OPERATIONS & ENGINEERING | 2134867720 | O-RING N MAINLINE CHECK VALVE FAILED. PRODUCT SPRAYED FROM VALVE AGAINST WALL OF VAULT, AND ACCUMULATED ON FLOOR OF VAULT. AAPROXIMATELY 8 BARRELS OF PRODUCT WERE RELEASED.
2017-09-29 08:50 | NO | NO | 19920197 | 1992-11-18 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-03-24 | 1300 | AZ | YUMA | YUMA | NO |  | YES | SANTA FE PACIFIC PIPELINE'S COMPOUND ON MCAS, YUMA, ARIZONA |  | NO DATA | PIPE | SUMP OVERFILLED | 1959 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 43148.912 | 87048.784 | JET FUEL | 3 | 13 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR V.P. - OPERATIONS & ENGINEERING | 2134867720 | DUE TO HEAVY RAINS, MILITARY PERSONNEL RELEASED MORE PRODUCT AND WATER THAN USUAL AND SUMP OVERFLOED 13 BARRELS OF JP-5 ONTO GROUND. REMEDIATION EFFORTSCURRENTLY IN PLANNING STAGE.
2017-09-29 08:50 | NO | NO | 19920198 | 1992-11-18 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-04-06 | 1300 | CA | ALAMEDA | OAKLAND | NO |  | NO | VALVE #1, LS 42 AT SFPP OAKLAND TANK (IN SPRR SWITCHYARD), JUST OFF 7TH STREET/BAY STREET IN OAKLAND |  | LINE PIPE | VALVE | PACKING GLAND LEAK ON 1-I | 1969 | OTHER | PACKING GLAND FAILED. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8800 | 6903.8259 | 13927.8054 | TURBINE FUEL | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR V.P. - OPERATIONS & ENGINEERING | 2134867720 | AREA SUPERVISOR DAVE NORD DISCOVERED PACKING GLAND LEAK ON 1-INCH VALVE. PACKING GLAND TIGHTENED AND 1-INCH VALVE REPLACE WITH NEW ONE. NOTE: INITIAL ESTIMATES OF THE TOTAL PROPERTY DAMAGE CAUSED BY THIS OCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAS RAISED THOSE ESTIMATES TO EXCEED $5,000 AND WE NOW SUBMIT THIS REPORT TO COMPLY WITH THE INTENT OF THE REGULATION.
2017-09-29 08:50 | NO | NO | 19920199 | 1992-11-18 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1992-07-28 | 1400 | NM | DONA ANA | ANTHONY | NO |  | NO | SFPP LINE SECTION 5, PLMP 31.81, APPROXIMATELY 120 FEET FROM HIGHWAY 460, JUST NORTH OF ANTHONY (RIO GRANDE VALLEY EAST BLOCK VALVE). NO RAILROAD OR BUILDINGS |  | NO DATA | OTHER | 2-INCH DRAIN HOSE CONNECT | 0 | OTHER | FISHING OPERATIONS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19613.1418 | 39567.6291 | DIESEL FUEL | 3 | 10 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | FISHING OPERATIONS | EQUIPMENT FAILURE | Null | OTHER | PLANNED LINE WORK | YES | YES | J M ABBOUD - SENIOR V.P.- OPERATIONS & ENGINEERING | 2134867720 | DURING A PIPELINE TIE-IN OPERATION AT THE RIO GRANDE VALLEY EAST BLOCK VALVE, A 2-INCH HOSE TO A VACUUM TRUCK SEPARATED FROM ITS COUPLING, SPILLING APPROXIMATELY 10 BARRELS OF DIESEL FUEL INTO THE PIPE DITCH. VALVE WAS CLOSED OFFTO HALT SPILL AND APPROXIMATELY 30 CUBIC FEET OF CONTAMINATED SOIL WERE REMOVED FROM SITE. NOTE: INITIAL ESTIMATES OF THE TOTAL PROPERTY DAMAGE CAUSED BY THIS OCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAS RAISED THOSE ESTIMATES TO EXCEED $5,000 AND WE NOW SUBMIT THIS REPORT TO COMPLY WITH THE INTENT OF THE REGULATI
2017-09-29 08:50 | YES | NO | 19920200 | 1992-09-28 | 2552 | COLONIAL PIPELINE CO | YES | 1992-07-16 | 2150 | AL | SHELBY | PELHAM | NO |  | NO | COLONIAL PIPELINE COMPANY'S PELHAM TANK FARM |  | PUMPING STATION | VALVE |  | 1962 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | GASOLINE | 2 | 15 | 9 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MGR. TECHNICAL & REGULATORY | 4048412296 | AT 2150 CDT ON JULY 16, 1992, APPROXIMATELY 4 GALLONS OF PRODUCT WERE DISCOVERED IN AN ACCESS WELL NEAR THE LINE NO. 1 STATION STRAINER AT COLONIAL PIPELINE COMPANY'S PELHAM JUNCTION. AT 1000 CDT ON JULY 17, COLONIAL DETERMINED THAT A REPORTABLE LEAK WITH AN UNKNOWN SOURCE EXISTED. AFTER ESTIMATING THATDAMAGE RELATED COSTS (DUE TO SOIL REMEDIATION) WOULD EXCEED $5,000, A CALL WAS MADE AT 1040 CDT ON JULY 17, TO THE NATIONAL RESPONSE CENTER (REPORT NO. 127304). IT WAS ESTIMATED THAT 15 BARRELS OF PRODUCT HAD ESCAPED INTO THE SURROUNDING SOIL. ON AUGUST 11, 1992, AFTER AN EXTENSIVE EXCAVATION OF THE STATION PIPING, PRIMARILY BY HAND DIGGING, PRODUCT WAS FOUND TO BE SEEPING FROM AROUND A PET COCK LOCATED ON THE BOTTOM OF THE NUMBER 1 STATION LOOP DISCHARGEVALVE. ON AUGUST 13, THIS PET COCK WAS REMOVED AND A PLUG INSERTED INTO THETHREADED OPENING. THIS PET COCK WAS SUBSEQUENTLY ANALYZED BY AN INDEPENDENTLABORATORY. THE RESULTING ANALYSIS FOUND THAT THE LEAKAGE WAS CAUSED BY PITTING CORROSION OF THE PET COCK SEAT. PRESENTLY, ALL SIMILAR PET COCKS IN THESTATION WERE BEING REMOVED AND PLUGS INSERTED. THE CONTAMINATED SOIL HAS BEEN STOCKPILED AND AWAITS REMEDIATION.
2017-09-29 08:50 | YES | NO | 19920201 | 1992-11-20 | 2552 | COLONIAL PIPELINE CO | YES | 1992-10-22 | 1240 | TX | JEFFERSON | NEDERLAND | NO |  | NO | COLONIAL PIPELINE COMPANY'S HEBERT INJECTION. |  | PUMPING STATION | OTHER | HYDROSTATIC WATER PURGE L | 1992 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11767.8851 | 23740.5774 | KEROSENE | 2 | 60 | 58 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MGR TECHNICAL & REGULATORY | 4048412296 | AT 1240 CDT ON OCTOBER 22, 1992, KEROSENE WAS DETECTED IN HYDROSTATIC TEST WATER DURING THE DISPLACEMENT OF COLONIAL PIPELINE COMPANY'S NEWLY CONSTRUCTEDPIPELINE CONNECTING THE MPBIL REFINERY AND COLONIAL'S HERBERT INJECTION AT NEDERLAND, TEXAS. THE DISPLACING KEROSENE BATCH HAD BYPASSED THE POLLY-PIG INSTALLED TO SEPARATE THE HYDROSTATIC TEST WATER AND THE PRODUCT. WHEN THE WATER/KEROSENE INTERFACE REACHED THE DISCHARGE POINT EARLIER THAN EXPECTED, THE MISTURE SPILLED INTO THE STORM WATER DRAINAGE DITCH AND THE ACCOMPANYING BAR DITCHES OF WEST PORT ARTHUR ROAD. AS SOON AS THE PRODUCT WAS DETECTED IN THEDISCHARGE WATER, THE DISPLACEMENT WAS DISCONTINUED AND RECOVERY BEGUN. NOTIFICATION OF LOCAL POLICE, FIRE, AND REGULATORY AUTHORITIES BEGAN IMMEDIATELY AND AT 2008 CDT ON OCTOBER 22, WHEN IT BECAME APPARENT THAT THE RELEASED VOLUME EXCEEDED 50 BARRELS, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO.141667). APPROXIMATELY 58 BARRELS OF KEROSENE WERE RECOVERED. THE SOIL CONTAINING THE REMAINING ABSORBED KEROSINE HAS SINCE BEEN REMOVED FROM THE DITCHED AND STOCKPILED FOR PROPER DISPOSAL.
2017-09-29 08:50 | YES | NO | 19920202 | 1992-11-20 | 2552 | COLONIAL PIPELINE CO | YES | 1992-09-15 | 1225 | MD | CECIL |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S CONOWINGI PUMP STATION |  | PUMPING STATION | VALVE |  | 1980 | OTHER | FAILED CHECK VALVE SHAFT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 392262.836 | 791352.5814 | GASOLINE | 2 | 143 | 137 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES A COX - MGR TECHINAL & REGULATORY | 4048412296 | ON SEPTEMBER 15, 1992 AT 1225 EDT THE NRC WAS NOTIFIED (REPORT NO. 136749) AFTER PETROLEUM PRODUCT WAS DETECTED IN MONITORING WELLS AT COLONIAL PIPELINE COMPANY'S CONOWINGO PUMP STATION IN CECIL COUNTY, MARYLAND. PERIODIC MONITORING INDICATED THAT ACTIVE LEAKAGE WAS POSSIBLE AND EXCAVATION OF STATION PIPING ENSUED. AT APPROXIMATELY 1500 EDT ON OCTOBER 20, 1992, PRODUCT WAS FOUNDESCAPING FROM THE STATION DISCHARGE CHECK VALVE. AN INSPECTION OF THE CHECKVALVE REVEALED THAT THE INTERNAL SHAFT SEAL HAD FAILED. ADDITIONALLY, A THREADED PIPE CAP ON THE SHAFT HOUSING WAS FOUND TO BE SUFFICIENTLY TIGHTENED. THIS ALLOWED PRODUCT TO ESCAPE THE HOUSING AND ENTER THE SURROUNDING SOIL. CONTAMINATED SOIL WAS REMOVED FROM AROUND THE CHECK VALVE TO ALLOW FOR TEMPORARY REPAIRS. PERMANENT REPAIRS WILL BE MADE AT A LATER DATE. TO DATE, APPROXIMATELY 62 BARRELS OF A MIXTURE OF PETROLEUM PRODUCTS HAVE BEEN RECOVERED. EXCAVATION AND INSPECTION OF OTHER UNDERGROUND PIPING CONTINUES TO ENSURE THATNO OTHER LEAKAGE EXISTS. CONTAMINATED SOIL HAS BEEN STOCKPILED AND AWAITS DI
2017-09-29 08:50 | YES | NO | 19920203 | 1992-11-25 | 13131 | CONOCO INC | YES | 1992-11-10 | 130 | WY | UINTA | WYOMING | NO |  | YES | SW, SW S34, T16N, R116W. APPROXIMATELY 20 MILES EAST OF EVANSTON, WY |  | LINE PIPE | LONGITUDINAL WELD |  | 1953 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 52000 | 40795.3349 | 82300.6685 | JET FUEL | 1 | 1834 | 0 | NO | NO | 8.63 | 0.32 | 42000 | WELDED |  | 2256 | 2200 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W BEGGS - COORDINATOR, REGULATORY COMPLIANCE | 3036494090 | AT APPROXIMATELY 1:30 A.M. ON NOVEMBER 10, 1992, A SEAM FAILED ON THE 8-INCHPIONEER PIPE LINE SYSTEM IN UINTA COUNTY IN SOUTHWEST WYOMING. THIS FAILURERELEASED APPROXIMATELY 1834 BBLS. F COMMERCIAL JET FUEL (KEROSENE) TO THE ENVIRONMENT. THE PRODUCT ENTERED A DRAW ADJACENT TO THE RIGHT OF WAY AND FLOWED ABOUT 3/4 MILE; NO SURFACE WATER WAS PRESENT IN THIS DRAINAGE. THE CAUSE OF THE SEAM FAILURE IS UNKNOWN AT THIS TIME, HOWEVER, A METALLURGICAL ANALYSISWILL BE PERFORMED ON THE PIPE TO DETERMINE THE CAUSE.
2017-09-29 08:50 | YES | YES | 19920204 | 1992-11-18 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1992-10-27 | 1130 | KS | KIOWA |  | NO |  | NO | SECTION THREE, TOWNSHIP 29, S., RANGE 16W., KIOWA COUNTY, KANSAS |  | PUMPING STATION | OTHER | TEMPORARY PIPELINE PLUGGI | 0 | OTHER | TEMPORARY PLUGGING DEVICE | ALL OTHER CAUSES | MISCELLANEOUS | 1 | 0 | 1 | 2 | 1 | 1 | 3 | 2.3536 | 4.7481 | ANHYDROUS AMMONIA | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | WELDED |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C G MCCONNELL - PRESIDENT | 9185811800 | NON-PIPELINE PIPING INVOLVED. TEMPORARY PLUGGING DEVICE RELEASED FROM OPEN PIPING DURING STATION REPAIR WORK.
2017-09-29 08:50 | YES | NO | 19920205 | 1992-11-30 | 14295 | OLYMPIC PIPE LINE CO | YES | 1992-10-30 | 1230 | WA | KING | RENTON | NO |  | NO |  |  | PUMPING STATION | TANK | FLANGE GASKET LEAK | 1972 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | VALVE DID NOT SEAT COMPLE | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TURBINE FUEL | 2 | 40 | 40 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM MULKEY - SUPERVISOR REGULATORY & ENVIRONMENTAL | 2062357745 | INCOMPLETE CLOSURE OF REMOTELY OPERATED VALVE ALLOWED EXCESSIVE PRESSURE AGAINST CHECK VALVE FLANGE GASKET. GASKET RUPTURED AND RELEASED APPROXIMATELY FORTY (40) BARRELS OF KERO BASE TURBINE FUEL INSIDE A DIKED ENCLOSURE. NO PRODUCT LOSS TO ENVIRONMENT. CONTAINED FUEL WAS REPORTED AS MINIMAL REPORTABLE QUANTITY TO FEDERAL, STATE AND LOCAL AUTHORITIES, HOWEVER, CLEANUP [RPVED QUANTITY TO BE LESS THAN 50 BARRELS.
2017-09-29 08:50 | YES | NO | 19920206 | 1992-12-02 | 2330 | CHEVRON PIPELINE CO | YES | 1992-11-03 | 1200 | WA | LINCOLN | SPRAGUE | NO |  | NO | M.P. 658.2 1/2 MILE SOUTHWEST OF INTERSECTION OF DOERSCHLAG ROAD & GRANGE ROAD |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 48000 | 37657.2323 | 75969.8478 | JET FUEL | 1 | 366 | 0 | NO | NO | 8.63 | 0.25 | 42 | WELDED |  | 1080 | 450 | NO | 0 | 0 | 1 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | CPL PUBLIC AWARENESS PROG | NO | NO | WARREN R SYTH | 5095472545 | FARMER (GIL SHEFFELS) WAS SUB SOILING HIS WHEAT FIELD AND HIT CHEVRON PIPE LINE'S PIPE. SPOKANE STATION CLOSED BECAUSE OF LOW FLOW AND THE LEAK DETECTION ALARMED. SALT LAKE CONTROL NOTIFIED PASCO OPERATOR. PASCO OPERATOR SHUT DOWN MAINLINE PUMPS. TWENTY-FIVE MINUTES AFTER THE ACCIDENT THE FARMER HAD GOTTEN TO A PHONE AND CALLED SALT LAKE CONTROL CHEVRON PIPE LINE PERSONNEL WEREDISPATCHED TO M.P. 658 WITH SPILL TRAILER AND REPAIR EQUIPMENT. SALT LAKE COMPLIANCE NOTIFIED ALL REQUIRED. THE PIPELINE WAS REPAIRED AND PLACED BACK IN SERVICE. THE AFFECTED SOIL WAS TRANSPORTED TO AN INCINERATOR FOR THERMAL DESORPTION (HEATED TO 800 DEGREE F TO REDUCE THE TOTAL PETROLEUM HYDROCARBON LEVEL TO ABOUT 20 PPM), AND TRANSPORTED BACK TO THE SITE. NO INJURIES OR ADDITIONAL PROPERTY DAMAGE OCCURRED. THE NEED TO CALL BEFORE DIGGING, DEEP TILLING WORK, AND SO FORTH, WAS DISCUSSED WITH SEVERAL FARMERS ADJACENT TO THE SITE
2017-09-29 08:50 | YES | NO | 19920207 | 1992-12-02 | 19226 | TEXACO PIPELINE INC | YES | 1992-11-04 | 1853 | DE | NEW CASTLE | DELAWARE CITY | NO |  | NO | OFF ROUTE 9 IN DELAWARE CITY IN THE STAR ENTERPRISE REFINERY ON "J" STREET. |  | PUMPING STATION | BOLTED FITTING |  | 1983 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | FAILED GASKET | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | DIESEL FUEL | 2 | 360 | 360 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LEANARD J SAGER - PIPELINE SUPERINTENDENT | 3028346079 | (ACTUAL NUMBER OF BARRELS RECOVERED IS 381 - THIS INCLUDES SOME RAIN WATER)AT 1853 HOURS ON NOVEMBER 4, 1992 A LEAKING BOLTED FLANGE WAS DISCOVERED AT THE TEXACO PIPELINE INC. BOOSTER STATION. AFTER UNBOLTING THE FLANGE WAS DISCOVERED THAT THE FLANGE GASKET HAD SPLIT CAUSING A FAILURE IN THE SEAL BETWEEN THE TWO BOLTED FLANGE FACES.
2017-09-29 08:50 | NO | NO | 19920208 | 1992-12-07 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-10-23 | 200 | CA | CONTRA COSTA | RICHMOND | NO |  | NO | IN SFPP'S RICHMOND STATION YARD (MANIFOLD AREA), 520 CASTRO STREET, RICHMOND, CA 94801 |  | TANK FARM | VALVE | TATTLE-TALE VALVE | 1957 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7845.2567 | 15827.0516 | GASOLINE | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR VICE PRESIDENT - OPERATING & ENGINEERING | 2134867720 | A TATTLE-TALE VALVE WAS LEFT OPEN DURING A DELIVERY AND PRODUCT SPILLED OUT OF THE FUNNEL ONTO THE GROUND. UOPN DISCOVERY THE VALE WAS CLOSED AND FLOW STOPPED. NOTE: INITIAL ESTIMATES OF THE TOTAL PROPERTY DAMAGE CAUSED BY THISOCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAS RAISED THOSE ESTIMATES TO EXCEED $5,000AND WE NOW SUBMIT THIS REPORT TO COMPLY WITH THE INTENT OF THE REGULATION.
2017-09-29 08:50 | NO | NO | 19920209 | 1992-12-07 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1992-11-08 | 1930 | NV | WASHOE | SPARKS | NO |  | NO | AT SFPP'S RENO TERMINAL YARD ( IN TRANSMIX MANIFOLD AREA), 301 NUGGET AVENUE, SPARKS, NV 89431 |  | TANK FARM | VALVE |  | 1957 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 6276.2054 | 12661.6413 | TRANSMIX (PART. REFINED PETRO) | 3 | 45 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR VICE PRESIDENT - OPERATIONS & ENGINEERIN | 2134867720 | A TATTLE-TALE VALVE IN THE TRANSMIX MANIFOLD AREA WAS LEFT OPEN DURING A DELIVERY, ALLOWING APPROXIMATELY 45 BARRELS OF TRANSMIX TO SPILL ONTO THE GROUND. UPON DISCOVERY THE VALVE WAS CLOSE AND CLEANUP PERFORMED.
2017-09-29 08:50 | NO | NO | 19920210 | 1992-12-08 | 15851 | PRIDE REFINING INC | NO | 1992-11-11 | 1500 | TX | PALO PINTO | GORDON | NO |  | NO | EXIT S OF INTERST. 20 ON PANAMA FL AT RDGO E APPROX. 3 MILES TURN RT. THROU. GATE WITH WAGON WHEELS PROCEED S ON LEASE RD, TURN E DOWN PIPELINE RT.-OF-WAY 1 MIL |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 78.4526 | 158.2705 | FUEL OIL | 3 | 5 | 0 | NO | NO | 6.25 | 0.25 | 40000 | COUPLED |  | 377 | 300 | YES | 8 | 471 | 1 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN MACON - PIPELINE MANAGER | 9156748231 | AT APPROXIMATELY 3:00 P.M. HENRY WHITELY, PRIDE EMPLOYEE WAS INSTALLING PIPELINE SIGNS AND CAME UPON A LEAK. A TEMPORARY REPAIR SLEEVE WAS INSTALLED ANDSITE CLEAN-UP BEGAN. PERMANENT REPAIRS WILL BE MADE AT A LATER DATE.
2017-09-29 08:50 | YES | NO | 19920211 | 1992-12-08 | 22907 | WYCO PIPE LINE CO | YES | 1992-11-28 | 1100 | CO | ADAMS | DUPONT | NO |  | NO | TANK #13 AT DUPONT TERMINAL |  | TANK FARM | PIPE |  | 1948 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 235.3577 | 474.8115 | DIESEL FUEL | 1 | 170 | 150 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | D.A. SHROYER - AREA MANAGER | 3032866411 | A 1-INCH PRESSURE RELIEF LINE FOR TANK # 13 FROZE, CAUSING THE PIPE TO SPLIT. ALL THE PRODUCT WAS CONTAINED WITHIN THE TANK DIKE AND VACUUMED UP.
2017-09-29 08:50 | NO | NO | 19920212 | 1992-12-08 | 15674 | PLANTATION PIPE LINE CO | YES | 1992-10-26 | 1100 | NC | GUILFORD | GREENSBORO | NO |  | NO | TANK 121 - PLANTATION'S GREENSBORO TANK FARM. ADDRESS: 6907-A WEST MARKET ST., GREENSBORO, NC 27409 |  | TANK FARM | TANK |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 16500 | 12944.6736 | 26114.6352 | FUEL OIL | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | STRESS CORROSION CRACKING | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK, V.P. PRESIDENT - OPERATIONS | 4043645916 | ON OCTOBER 26, 1992, A DISCOLORATION WAS NOTICED ON THE RINGWALL OF TANK 121AT PLANTATION'S GREENSBORO TANK FARM. PUMPOUT OF THE TANK WAS COMPLETED ON THE MORNING OF NOVEMBER 3, 1992. THE TANK WAS CLEANED ON NOVEMBER 3 AND 4, 1992. INSPECTION ON NOVEMBER 9, 1992, REVEALED AN 8-INCH LONG STRESS CRACK INTHE FLOOR PLATE ORIGINATING IN AN AREA OF MINOR CORROSION. THE SECTION OF FLOOR PLATE WAS REMOVED AND REPLACED.
2017-09-29 08:50 | YES | NO | 19920213 | 1992-12-03 | 4906 | EXXON PIPELINE CO | NO | 1992-11-08 | 920 | TX | HARRIS | WEBSTER | NO |  | NO | EXXON PIPELINE CO WEBSTER STATION. 20004 OLD GALVESTON RD (1 MI. SO OLD GALVESTON RD/NASA 1 INTERSECTION WEBSTER, HARRIS COUNTY, TEXAS |  | LINE PIPE | OTHER | VALVE & STATION PIPING | 1919 | OTHER | CORROSION, INTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 70607.3105 | 142443.4647 | CRUDE OIL | 1 | 120 | 118 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MANAGER- ENVIRON & REGULATORY COMPLIANCE DEPART | 7136565521 | CATTLE LEASE FOR EPC WEBSTER STATION REPORTED POSSIBLE CRUDE OIL LEAK 11/08/92. 9:20 AM, TO EPC OIL TRAFFIC CONTROL CENTER. SYSTEM SHUT DOWN, ISOLATED. SUBSEQUENT ON-SITE INVESTIGATION SHOWED 2 SEPARATE LEAKS ON STATION PROPERTY: 1) CRACKED VALVE ON INCOMING SOUTH BOLING-WEBSTER 8",AND 2) INTERNAL CORROSION ON TANK 123 LINE. 95 BARRELS OF CRUDE OIL ENTERED CLEAR CREEK AT THE SOUTHERN PROPERTY BOUNDARY OF WEBSTER STATION. ALL RELEASED OIL WAS CONTAINED AND PICKED UP USING VACUUM TRUCK AND SORBENT MATERIALS. OUTAGE REPORTED TO NRC (USCG CHIEF PETTY OFFICE JAMES BORDERS) AT 1109 HRS - LOGGED AS EVENT # 141976.
2017-09-29 08:50 | YES | NO | 19920214 | 1992-12-04 | 808 | ARCO TERMINAL SERVICES CORP | NO | 1992-11-05 | 930 | CA | LONG BEACH |  | NO |  | NO | BETWEEN TERMINAL ISLAND FREEWAY (RTE 47)& RR TRACKS SOUTH OF WILLOW ST, LONG BEACH, CA. (VALVE VAULT). |  | LINE PIPE | BOLTED FITTING | FLANGE IN VALVE VAULT ON | 1992 | OTHER | FLANGE BOLTS MAY BE LOOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 133369.3642 | 269059.8777 | GASOLINE | 2 | 750 | 500 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 720 | 147 | YES | 4 | 900 | 6 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD L SOLOMON - BUSINESS UNIT MANAGER | 3104289027 | LEAK FROM VALVE VAULT WAS REPORTED TO OPERATIONS CONTROL CENTER BY COMPANY PERSONNEL AT APPROX. 9:30 AM FOLLOWING WHICH LINE WAS SHUT DOWN. COMPANY PERSONNEL THEN SECURED THE SITE. VAULT WAS PUMPED OUT AND AFTER SAFE ACCESS TO THE VAULT WAS OBTAINED FLANGE WAS TIGHTENED AND LEAK WAS STOPPED.
2017-09-29 08:50 | NO | NO | 19920215 | 1992-12-07 | 2552 | COLONIAL PIPELINE CO | YES | 1992-11-03 | 703 | GA | COBB |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1979 | OTHER | PIPE RESTING ON ROCK/CRAC | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | GASOLINE | 2 | 2 | 1 | NO | NO | 16 | 0.25 | 60000 | WELDED |  | 1350 | 935 | YES | 24 | 1704 | 1 | 79 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MGR. TECHNICAL & REGULATORY | 4048412296 | ON 0730 EST ON NOVEMBER 3, 1992, THE COBB COUNTY, GEORGIA, FIRE DEPARTMENT NOTIFIED COLONIAL'S CONTROL CENTER THAT GASOLINE HAD BEEN DISCOVERED ON COLONIAL'S RIGHT-OF-WAY NEAR THE INTERSECTION OF GEORGIA HIGHWAYS 120 AND 176. THEFIRE DEPARTMENT HAD INVESTIGATED AFTER RECEIVING A REPORT OF A GASOLINE ODORIN THIS VICINITY. THE 10", 12", AND 16" PARALLEL PIPELINES IN THIS AREA WERE SHUT DOWN AND A COLONIAL MAINTENANCE TEAM WAS DISPATCHED TO THE SITE AND VERIFIED THAT A LEAK EXISTED. NOTIFICATION WAS MADE TO THE GEORGIA ENVIRONMENTAL PROTECTION DIVISION AT 0902 EST AND TO THE NATIONAL RESPONSE CENTER (REPORT NO. 143111) AT APPROXIMATELY 0930 EST. ON NOVEMBER 5, 1992, AFTER EXTENSIVE EXCAVATIONS, THE 16" ATLANTA JUNCTION TO CHATTANOOGA, TENNESSEE, PIPELINE WAS FOUND LYING ON A ROCK. THE ABRASION BETWEEN THE ROCK AND PIPELINE HAD RESULTED IN SOME WALL THICKNESS REDUCTION AND A SMALL DENT AND CRACK. THE PIPELINE WAS REPAIRED BY INSTALLING A 16" X 36" FULL ENCIRCLEMENT SLEEVE AND AFTERNONDESTRUCTIVE TESTING, EAST RETURNED TO SERVICE. AN ESTIMATED 2 BARRELS OFGASOLINE ESCAPED FROM THE SYSTEM. ONE BARREL OF GASOLINE WAS RECOVERED. ONE BARREL WAS LOST TO EVAPORATION AND ABSORPTION INTO THE SURROUNDING SOIL. CONTAMINATED SOIL IS STOCKPILED AWAITING DISPOSAL.
2017-09-29 08:50 | YES | NO | 19920216 | 1992-12-15 | 4906 | EXXON PIPELINE CO | YES | 1992-11-16 | 800 | LA | LAFOURCHE |  | NO |  | NO | STATION LOCATED IN T17S-R21E-S48. FROM HIGHWAY 90 & 308 GO SOUTH IN HIGHWAY 308, CROSS THE GULF INTRACOASTAL WATERWAY. AT HIGHWAY 308 "T", GO NORTH ON HWY 308 |  | PUMPING STATION | VALVE |  | 1971 | OTHER | 16" CHECK VALVE O-RING LE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 210000 | 164750.3911 | 332368.0842 | CRUDE OIL | 1 | 66 | 54 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MANAGER ENVIRONMENTAL & REGULATORY COMPLIANCE DEP | 7136565521 | DURING AN OVERFLIGHT OF EXXON PIPELINE COMPANY'S (EPC) PIPELINE RIGHT-OF-WAY, THE LINE FLYER SPOTTED OIL ON THE GULF INTRACOASTAL WATERWAY. AT THIS TIMEEPC'S DIVISION OIL SPILL RESPONSE TEAM ALONG WITH ASSISTANCE FROM OTHER EXXON AFFILIATES AND OIL SPILL CLEAN-UP CONTRACTORS WERE DISPATCHED TO THE LOCATION WITH OIL CONTAINMENT AND RECOVERY EQUIPMENT. CRUDE OIL WAS CONTAINED AND RECOVERED. THERE WERE NO DEATHS OR INJURIES. THE NATIONAL RESPONSE CENTER WAS CONTACTED AT 09:45, ON 11/16/92. REPORT NUMBER 145038.
2017-09-29 08:50 | YES | NO | 19920217 | 1992-12-15 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1992-11-12 | 1521 | OH | WOOD | CENTER | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 62762.0538 | 126616.413 | CRUDE OIL | 3 | 50 | 33 | NO | NO | 10 | 0.22 | 52000 | WELDED |  | 1214 | 850 | YES | 24 | 1926 | 1 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | DEAN R MOYER - REGULATORY COMPLIANCE ADMINSTRATOR | 2158208300 | PLANNED REPAIRS WERE BEING MADE TO A NEARBY PARALLEL BUCKEYE PIPELINE. THE REPAIR INVOLVED RELOCATING AND REPLACEMENT OF ABOUT 100 FEET OF PIPELINE. DURING THE EXCAVATION FOR THE PIPELINE REPAIR, THE SUBJECT PARALLEL PIPELINE WAS DAMAGED BY THE BACKHOE BUCKET. EMERGENCY RESPONSE PLANS WENT INTO AFFECT IMMEDIATELY. ALL REQUIRED NOTIFICATIONS WERE MADE IN A TIMELY MANNER. ALMOSTALL OF THE PRODUCT THAT DID NOT EVAPORATE WAS RECOVERED. THE DAMAGED PIPELINE SEGMENT WAS REPLACED WIHT PRETESTED STOCK PIPE. CLEANUP WAS COMPLETED IN CONJUNCTION WITH THE OHIO ENVIRONMENTAL PROTECTION AGENCY.
2017-09-29 08:50 | YES | NO | 19920218 | 1992-12-14 | 2733 | CHEVRON PIPELINE CO - MIDLAND DIV | YES | 1992-11-03 | 1030 | TX | ECTOR | ODESSA | NO |  | NO | 2 MILES WEST OF JUDKINS STATION (CALL FOR DIR.) SECTION 8; BLOCK 16; SURVEY = PSL; MILE POST = 42.7 |  | LINE PIPE | OTHER | BELL SPICKET JOINT | 1927 | OTHER | A BELL & PICKET JOINT PUL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6400 | 5020.9643 | 10129.313 | CRUDE OIL | 1 | 3200 | 3060 | NO | NO | 10.5 | 0.37 | 0 | WELDED |  | 850 | 85 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KEN C CROWELL - SYSTEM TEAM LEADER | 9157137123 | A BELL AND SPICKET JOINT PULLED APART.
2017-09-29 08:50 | YES | NO | 19920220 | 1992-12-11 | 443 | AMOCO PIPELINE CO | YES | 1992-11-24 | 845 | TX | YOAKUM |  | NO |  | NO | 1 MILE NORTH AND 2 3/4 MILES EAST OF DENVER CITY, TEXAS |  | PUMPING STATION | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 247 | 222 | NO | NO | 2 | 0 | 0 | WELDED |  | 275 | 135 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES L HOMER - P/L MAINT. FOREMAN | 5053962817 | LEAK WAS IN 2" LINE THAT IS IN DRAIN SYSTEM FOR PUMP STATION.
2017-09-29 08:50 | YES | NO | 19920221 | 1992-12-10 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1992-10-23 | 1130 | TX | SAN PATRICIO |  | NO |  | NO | 5 MILES WEST OF PORTLAND ON FM 893 |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 244000 | 191424.264 | 386180.0597 | TRANSMIX (PART. REFINED PETRO) | 3 | 6500 | 750 | NO | NO | 12.75 | 0.2 | 52000 | WELDED |  | 1193 | 800 | YES | 4 | 1496 | 2 | 89 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W D PARTLOW - ENVIRON. & SAFETY SUPERVISOR | 7138777370 | LEAK WAS CAUSED BY EXTERNAL CORROSION. THE AMOUNT OF PRODUCT LOST WAS +/- 5750 BBLS. APPROXIMATELY 40' OF NEW 12" PIPE WAS INSTALLED WHERE THE LEAK OCCURRED.
2017-09-29 08:50 | YES | NO | 19920222 | 1992-12-21 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1992-11-21 | 1640 | OH | LUCAS | OREGON | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 117678.8508 | 237405.7744 | GASOLINE | 3 | 800 | 450 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 1245 | 1240 | YES | 24 | 1590 | 1 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R MOYER - REGULATORY COMPLIANCE ADMINSTRATOR | 2158208300 | DURING SUDDEN SHUTDOWN OF DOWNSTREAM PUMP UNITS, THE MAIN LINE PRESSURE ROSETO ABOUT 1240 PSI. THE PIPELINE FAILED BECAUSE OF LOCALIZED CORROSION. THEUPSTREAM PUMP STATION SHUT DOWN IMMEDIATELY. EMERGENCY PROCEDURES WERE INITIATED INCLUDING THE NEARBY COAST GUARD WERE NOTIFIED IN A TIMELY MANNER. THEPRODUCT THAT ESCAPED INTO A NEARBY STREAM WAS CONTAINED PRIOR TO ENTERING THE MAUMEE BAY. THERE WAS NO APPARENT DAMAGE TO WILDLIFE. CLEANUP WAS COMPLETED AS DIRECTED BY THE LOCAL COAST GUARD AND THE OHIO ENVIRONMENTAL PROTECTIONAGENCY. THE FAILED PIPE SEGMENT WAS SENT TO KIEFNER ASSOCIATES IN COLUMBUS,OHIO, FOR LABORATORY ANALYSIS.
2017-09-29 08:50 | YES | NO | 19920223 | 1992-12-21 | 2552 | COLONIAL PIPELINE CO | YES | 1992-11-19 | 1100 | AL | SUMTER | EPES | NO |  | NO | COLONIAL PIPELINE COMPANY'S EPES PUMP STATION. |  | PUMPING STATION | VALVE |  | 1966 | OTHER | FAILED CHECK VALVE SEAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | GASOLINE | 2 | 16 | 15 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MGR. OF TECHNICAL & REGULATORY | 4048412296 | AT APPROXIMATELY 1100 CST ON NOVEMBER 19, 1992, DURING A ROUTINE STATION CHECK, THE STATION OPERATOR NOTICED PRODUCT STAINED GRAVEL AND AN ACCUMULATION OF PRODUCT IN THE OIL/WATER SEPARATOR AT THE EPES, ALABAMA, NO. 1 PUMP STATION. AFTER CONFIRMING THAT A LEAK EXISTED AND THAT DAMAGE RELATED COSTS WOULD EXCEED $5,000, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 145656) AT 1430 CST. THE ALABAMA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT WAS ALSO ADVISED OF THE LEAK. EXCAVATION OF THE STATION DISCHARGE CHECK VALVE REVEALED THAT GASOLINE WAS LEAKING FROM THE LEFT SPRING HOUSING COVER. THE STATION WAS SHUT DOWN AND THE STATION LOOP DRAINED. THE CHECK VALVE WAS REPAIRED BY REPLACING THE SPRING HOUSING COVER O-RING, THE SHAFT SEAL AND THE PACKING GLAND.AN ESTIMATED 16 BARRELS OF GASOLINE ESCAPED FROM THE SYSTEM. OF THIS TOTAL,15 BARRELS HAVE BEEN RECOVERED. CLEAN UP ACTIVITIES ARE CONTINUING AND THE CONTAMINATED SOIL IS BEING STOCKPILED AWAITING DISPOSAL.
2017-09-29 08:50 | NO | NO | 19920224 | 1992-12-21 | 2552 | COLONIAL PIPELINE CO | YES | 1992-11-19 | 945 | MD | ANNE ARUNDEL | BALTIMORE | NO |  | NO | COLONIAL PIPELINE COMPANY'S CURTIS BAY CROWN DELIVERY LINE |  | LINE PIPE | PIPE |  | 1968 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3922.6284 | 7913.5258 | TRANSMIX (PART. REFINED PETRO) | 2 | 1 | 1 | NO | NO | 12.75 | 0.25 | 35000 | WELDED |  | 275 | 50 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A COX - MGR. TECHNICAL & REGULATORY | 4048412296 | AS PART OF AN ENVIRONMENTAL ASSESSMENT OF THE MARYLAND TERMINAL COMPLEX, COLONIAL PRESSURE TESTED ITS DELIVERY LINE BETWEEN THE CURTIS BAY DELIVERY FACILITY AND CROWN CENTRAL ON NOVEMBER 19, 1992. AT APPROXIMATELY 0945 EST, DURING THIS PRESSURE TEST, COLONIAL PERSONNEL DETERMINED THAT AN UNEXPLAINED PRESSURE LOSS INDICATED A POSSIBLE LEAK. AT 1045 EST, THE MARYLAND DEPARTMENT OF THE ENVIRONMENTAL WAS NOTIFIED THAT A LEAK WAS SUSPECTED ON THE DELIVERY LINE. AT APPROXIMATELY 1500 EST, A TELEPHONE CALL ( REPORT NO. 145646) WAS MADE TO THE NATIONAL RESPONSE CENTER AFTER DETERMINING THAT THE SUBSEQUENT INVESTIGATION AND EXPECTED CLEANUP COSTS WOULD EXCEED $5,000. AS A COURTESY, NOTIFICATION WAS ALSO GIVEN TO THE EASTERN REGION OF THE OFFICE OF PIPELINE SAFETY.ON NOVEMBER 20, THE FUEL OIL WAS DISPLACED WITH NITROGEN AND APPROXIMATELY 20 GALLONS OF PRODUCT WAS RECOVERED FROM THE RIGHT OF WAY NEAR THE CSX RAILROAD THAT CROSSES THE PIPELINE. THE NITROGEN IN THE PIPELINE WAS DISPLACED BY WATER TO FACILITATE TESTING OF THE LINE IN AN ATTEMPT TO LOCATE A SOURCE OF THE LEAK. EXCAVATION OF THE PIPELINE BEGAN NEAR THE RAILROAD CROSSING AND AT APPROXIMATELY 1130 EST ON NOVEMBER 25TH, THE LEAK WAS FOUND TO BE ORIGINATING FROM A 1/8" DIAMETER HOLE IN THE BASE OF A 3/4" DIAMETER CORROSION PIT AT A POINT 10 FEET UPSTREAM OF THE CASED RAILROAD CROSSING. ON DECEMBER 4TH, A SECTION OF CORRODED PIPE WAS REMOVED AND REPLACED WITH A 38 FOOT SECTION OF PIPE. AFTER HYDROSTATIC TESTING OF THE REPAIRED LINE, NORMAL DELIVERIES TO CROWNCENTRAL RESUMED ON DECEMBNER 9TH. CLEAN-UP AND RECOVERY OF PRODUCT WILL CONTINUE FOR AN EXTENDED PERIOD OF TIME.
2017-09-29 08:50 | YES | NO | 19920225 | 1992-12-21 | 13131 | CONOCO INC | YES | 1992-11-15 | 1640 | MO | WARREN | WASHINGTON | NO |  | NO | SE 1/4 SEC. 24-T44N-R1W, WARREN COUNTY, MO MILE POST 422, SOUTHWEST OF MISSOURI RIVER BLOCK VALVE |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 23535.7702 | 47481.1549 | FUEL OIL | 2 | 311 | 296 | NO | NO | 10 | 0.5 | 35000 | WELDED |  | 900 | 242 | YES | 8 | 1167 | 7 | 90 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOE ANDERSON - DIR. ENVIRON. & REGULATORY COMPLIANCE | 4057672367 | ON NOVEMBER 15, 1992 AT 14:30 HOURS, THE OIL MOVEMENTS GROUP OF CONOCO PIPE LINE (CPL) LOCATED IN HOUSTON RECEIVED A CALL REPORTING A SUSPECTED RELEASE NEAR THE NORTH BANK OF THE MISSOURI RIVER, JUST NORTH OF WASHINGTON, MO. BY 14:36, BOTH 10 INCH LINES OPERATED BY CPL CROSSING THE RIVER HAD BEEN SHUT DOWN AT THIS LOCATION AND ISOLATED BY CLOSING THE MAINLINE BLOCK VALVES UPSTREAMOF THE RIVER CROSSING. AT 14:37, CPL PERSONNEL IN THE ST. CHARLES AREA WERENOTIFIED OF THE INCIDENT AND PROCEEDED TO THE LOCATION. 16:40 UPON ARRIVAL AT THE LOCATION, CPL PERSONNEL CONFIRMED THAT THERE WAS PRODUCT FORMING A SHEEN ON THE SURFACE OF THE RIVER NEXT TO THE RIVER BANK WHERE THE NO. 1 WOOD RIVER LINE COMES ASHORE. CONTAINMENT BOOMS WERE DEPLOYED TO CATCH THE SHEEN ENTERING THE RIVER, AND PRODUCT RECOVERY OPERATIONS WERE BEGUN. AS THE LOCATION OF THE SUSPECTED LEAK WAS IN THE BANK OF THE RIVER ITSELF, AND CONSEQUENTLY UNDER CORP. OF ENGINEERS JURISDICTION, PERMISSION TO EXCAVATED HAD TO BE OBTAINED PRIOR TO UNCOVERING THE PIPELINE AND DISTURBING THE RIVER BANKS PERMEABILITY/COMPACTION STANDARDS. DUE TO HEAVY RAINS IN THE AREA, THE RIVER WAS RIING AND PREDICTED TO CREST ABOVE THE ELEVATION AT WHICH CPL NEEDED TO EXCAVATE, THE CPL EMERGENCY STAFF WERE UNSUCCESSFUL IN OBTAINING PERMISSION FROM THE CORPS. REPRESENTATIVES TO EXCAVATE UNTIL 16:00 HOURS ON NOVEMBER 16. AT THIS TIME, VERBAL PERMISSION WAS RECEIVED TO BEGIN EXCAVATION. WRITTEN AUTHORIZATION WAS NOT RECEIVED UNTIL THE MORNING OF THE 17TH. THE NO. 1 LINE SHOWED NO PRESSURE DEVIATION BEFORE, OR AFTER, THE SUSPECTED RELEASE WAS REPORTED,BUT WAS LOCATED NEAREST THE SURFACING PRODUCT. BECAUSE OF THE DELAY IN OBTAINING PERMISSION TO EXCAVATE, IT WAS DECIDED TO DISPLACE THE NO 1 LINE WITH WATER TO PREVENT ANY FURTHER CONTAMINATION IF THE LINE WAS LEAKING. DUE TO CPL'S INABILITY TO EXCAVATE THE RIVER BANK WITHOUT CORPS. AUTHORIZATION, ABSOLUTE CONFIRMATION OF THE LEAK COULD NOT BE MADE. THUS, THE SHORT DELAY IN MAKING THE REPORT TO THE NATIONAL RESPONSE CENTER RESULTED. THE REPORT TO THE NRC WAS MADE AT 09:15 ON NOVEMBER 16, 1992. AFTER EXCAVATING THE LINE, THE EXCAVATION REVEALED A CORROSION PIT WHICH WAS THE SOURCE OF THE RELEASE. IT WASDETERMINED NOT TO MAKE REPAIRS TO THE EXISTING RIVER CROSSING, BUT ABANDON IT IN PLACE. IN LIEU OF MAKING REPAIRS, IT WAS DECIDED TO WAIT FOR THE COMPLETION OF THE NEW RIVER-CROSSING, WHICH WAS NEARING COMPLETION AT THE TIME OF THE INCIDENT. THE EXISTING LINES WILL BE DISPLACED WITH AN INERT MATERIAL ANDABANDONED.
2017-09-29 08:50 | YES | NO | 19920226 | 1992-12-21 | 22387 | WEST EMERALD PIPE LINE CORP | YES | 1992-11-15 | 842 | NM | QUAY |  | NO |  | NO | TOWNSHIP 11 NORTH, RANGE 35 EAST, SECTION 4 3 MILES N AND 7 3/4 MILES WEST OF THE CITY OF ENDEE, NEW MEXICO ON STATE ROAD 392 |  | LINE PIPE | PIPE |  | 1958 | OTHER | CORROSION, EXTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 145000 | 113756.2224 | 229492.2486 | TURBINE FUEL | 3 | 2297 | 209 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1440 | 680 | YES | 0 | 0 | 1 | 58 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS - MANAGER, PIPELINE SAFETY AND REGULATION | 8063783583 | AT APPROXIMATELY 0842 HOURS ON NOVEMBER 15, 1992, OUR 6" ALBUQUERQUE PRODUCTS PIPELINE RUPTURED. THE CAUSE WAS DUE TO MOISTURE AND DIRT TRAPPED BENEATH THE COATING DURING CONSTRUCTION ALLOWING EXTERNAL CORROSION. THE ACCIDENT ALLOWED 2,244 BARRELS OF TURBINE FUEL TO ESCAPE, OF WHICH 209 WAS SUBSEQUENTLY RECOVERED. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REAPIRED WITHOUT INCIDENT BY REPLACING 51 FEET OF LINE WITH PRE-TESTED PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19920227 | 1992-12-18 | 13161 | NAVAJO PIPELINE CO | YES | 1992-11-21 | 1440 | TX | EL PASO | EL PASO | NO |  | NO | 1/2 MILE NORTH OF ZARAGOSA ROAD & VISTA DEL SOL (MP 148.1) |  | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 720800 | 565486.1044 | 1140813.8814 | GASOLINE | 3 | 800 | 75 | NO | NO | 6.63 | 0.16 | 1978 | WELDED |  | 1100 | 1480 | YES | 9 | 700 | 10 | 92 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JIM G TOWNSEND | 5057483311 | AT APPROXIMATELY 2:40 P.M. NOVEMBER 21, 1992 THE ARTESIA OPERATOR BECAME AWARE THAT THE CPU ON THE 6" LINE AND FAULTED. WITHIN MINUTES THE OPERATOR IN ARTESIA, NEW MEXICO NOTICED THE DECREASE IN FLOW. OPERATOR CALLED PRODUCT FOREMAN AND SHUTDOWN MAINLINE PUMPS AND BOOSTER STATION, THEN CALLED EL PASO TERMINAL AND ADVISED THE 6" LINE BE SHUT IN AT EL PASO. EL PASO TERMINALMAN CALLED TO INFORM ARTESIA OPERATOR THAT JOHN HAYDEN WITH THE EL PAS FIRE DEPT. HADCALLED AND REPORTED GASOLINE LEAK IN THE ZARAGOSA RD. & VISTA DEL SOL AREA.TERMINALMAN HAD BLOCK VALVE AT YSLETA TERMINAL CLOSED WHICH IS UNPSTREAM OFTHE LEAK, STOPPING FLOW. NAVAJO EMPLOYEES AND EQUIPMENT AS WELL AS CONTRACTOR EMPLOYEES AND EQUIPMENT WERE IMMEDIATELY DISPATCHED TO REPAIR PIPELINE HADCLEAN SPILL AREA. WHEN THE PIPE WAS UNCOVERED IT WAS EVIDENT THAT THE PIPELINE RUPTURED AT A POINT ON THE LINE WHERE IT HAD BEEN HIT BY UNKNOWN PARTIESCAUSING DEFORMATION OF THE PIPE INCLUDING LOSS OF APPROXIMATELY 40% OF THE WALL THICKNESS (A GOUGE ABOUT 12" LONG AND 3/8" IN WIDTH). PIPELINE WAS REPAIRED AND OPERATIONS RESUMED AT 6:45 ON 11/22/92. CLEAN UP OF SPILL AREA IS INPROGRESS. *THE NORMAL OPERATING PRESSURE AT THIS POINT ON THE PIPELINE IS LESS THAN 200 PSIG WHEN FLOWING. FOR THAT REASON WE NORMALLY LEAK TEST THIS PORTION OF THE PIPELIN AT APPROXIMATELY 750 TO 800 PSIG, HOWEVER WITH THE CONTROL VALVE CLOSING WE HAVE CALCULATED THAT THE PRESSURE MAY HAVE REACHED 140-1480 PSIG. SINCE THE RUPTURE WE HAVE DESIGNED AND ARE PRESENTLY INSTALLING A CONTROL VALVE 15 MILES UPSTREAM OF RESIDENTIAL AREAS IN EL PASO (MP 128). THIS VALVE WILL PREVENT THE PRESSURE FORM EXCEEDING SAFE WORKING PRESSURE. WE HAVE FORMED A SUB-COMMITTEE WITH CHEVRON PIPELINE COMPANY AND SOUTHERN PACIFICPIPELINE COMPANY TO WORK MORE CLOSELY WITH THE EL PASO FIRE DEPARTMENT AND THE ZONING AND PLANNING DIVISIONS OF THE CITY OF EL PASO TO HELP PREVENT THIRDPARTY DAMAGE. WE ARE ALSO DESIGING AND WILL INSTALL RELIEF VALVES SIZED TOPREVENT HIGH PRESSURE CONDITIONS WITHIN EL PASO. THESE RELIEF VALVES WILL BELOCATED AT THE EL PASO EASTSIDE TERMINAL AND WILL RELIEVE INTO TANKAGE AT THE TERMINAL. ADDITIONAL COMPUTER CONTROLS HAVE BEEN ADDED TO MONITOR THE POSITION OF THE RELIEF VALVES. SUPPLEMENTAL REPORT RECEIVED 1/24/97 CHANGESPROPERTY DAMAGE FROM $300,000 TO $720,800.
2017-09-29 08:50 | YES | NO | 19920228 | 1992-12-29 | 15681 | PLATTE PIPE LINE CO | YES | 1992-12-03 | 615 | WY | WASHAKIE |  | NO |  | NO | CHATHAM STATION, WASHAKIE COUNTY, WYOMING, NE 1/4 SECTION 20 T45N, R94W |  | PUMPING STATION | PUMP | BOLTED FITTING | 1952 | OTHER | FAILURE OF FOUR LINER CAP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19613.1418 | 39567.6291 | CRUDE OIL | 1 | 482 | 197 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A FISHER - REGULATORY COORDINATOR | 4194213201 | AT 0615 HOURS ON DECEMBER 3, 1992, A LEAK FROM THE #4 PUMP UNIT AT CHATHAM STATION WAS DISCOVERED. FOURS BOLTS, WHICH SECURE THE PISTON LINER CAP TO THE PUMP HOUSING, HAD FAILED CAUSING THE DISCHARGE OF 482 BBLS. OF CRUDE OIL. PROMPT NOTIFICATIONS WERE MADE TO THE NRC AND THE WYOMING DEPARTMENT OF ENVIRONMENTAL QUALITY. THE RELEASE OIL, WHICH WAS CONTAINED ON THE STATION PROPERTY, WAS ACCUMULATED IN AN EMERGENCY SPILL CONTAINMENT DIKE. AN ESTIMATED 196 BBLS. WERE RECOVERED FROM THE DIKE AREA AND THE BALANCE OF 285 BBLS WAS BURNED IN ACCORDANCE WITH A WYOMING DEPARTMENT OF ENVIRONMENT QUALITY PERMIT. THEEXTREMELY COLD WEATHER RESTRICTED THE AMOUNT OF FREE LIQUID THAT COULD BE PICKED UP BY CONVENTIONAL MEANS. THE DISPOSITION OF AFFECTED SOIL WILL BE COORDINATED WITH THE WYOMING DEQ.
2017-09-29 08:50 | YES | YES | 19920229 | 1992-12-22 | 10313 | KOCH PIPELINE INC | YES | 1992-12-11 | 810 | WI | EAU CLAIRE | PLEASANT VALLEY | NO |  | NO | LEGAL DESCRIPTION IS E 1/2 OF SE 1/4 SECTION 3, T25N, R9W, PLEASANT VALLEY TOWNSHIP, EAU CLAIRE COUNTY, WISCONSIN |  | PUMPING STATION | VALVE |  | 1992 | OTHER | VALVE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 276 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARC S DEVARENNES - MGR OF OPERATIONS, MIKE KOSTELKY-RECS CO | 6124592424 | THE INITIAL NOTIFICATION WAS RECEIVED BY OUR PIPELINE CONTROL CENTER AT APPROXIMATELY 8:10 A.M. ON FRIDAY, DECEMBER 11, 1992. THE PROBLEM TOOK PLACE ON THE INCOMING 6 INCH DIAMETER PIPELINE SCRAPER TRAP. THE PRODUCT INVOLVED IN THE INCIDENT WAS PROPANE. THE KOCH PERSONNEL ON THE SCENE IMMEDIATELY RESPONDED BY MAKING PROPER NOTIFICATION TO LOCAL EMERGENCY RESPONSE AGENCIES, AND NOTIFIED THE COTTAGE GROVE DIVISION OFFICE. THEY THEN BEGAN TO DETOUR TRAFFIC ON HIGHWAY 93 AND EVACUATE THE PEOPLE IN THE AREA WHERE A VAPOR CLOUD WAS FORMING. THE PIPELINE CONTROL CENTER, ALONG WITH KOCH PERSONNEL, BEGAN TO CLOSE THE APPROPRIATE VALVES TO ISOLATE THE AFFECTED AREA. BY 8:51 A.M. THE STATION WAS ISOLATED, THE LEAK HAD STOPPED, AND THE VAPOR CLOUD AND BEGUN TO DISSIPATE. THE SCENE WAS CONTINUALLY BEING MONITORED USING GASTECH GX-82 AIR MONITORS.
2017-09-29 08:50 | YES | NO | 19920230 | 1992-12-22 | 443 | AMOCO PIPELINE CO | YES | 1992-11-20 | 928 | MN | HENNEPIN | BROOKLYN PARK | NO |  | NO | 100 FEET EAST OF WOODHALL CROSSING ON REENT PARKWAY, BROOKLYN PARK, MN |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 235357.7016 | 474811.5489 | GASOLINE | 2 | 350 | 50 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1440 | 150 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KENNETH C ANDREEN - AREA MANAGER | 6124254750 | A CONTRACTOR HIT THE PIPELINE WITH EARTH MOVING EQUIPMENT (I.E. SCRAPER) DURING THE CONSTRUCTION OF A ROADWAY. THE ROADWAY THAT WAS UNDER CONSTRUCTION WAS REGENT PARKWAY.
2017-09-29 08:50 | YES | NO | 19920231 | 1992-12-29 | 18273 | SHELL PIPELINE CORP | NO | 1992-11-27 | 900 | TX | HARRIS | PASADENA | NO |  | NO | INTERSECTION OF QUEENS AND ALLEN-GENOA RANCHO 24-INCH PIPELINE |  | LINE PIPE | GIRTH |  | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 784525.672 | 1582705.1629 | CRUDE OIL | 1 | 4500 | 4360 | NO | NO | 24 | 0.38 | 52000 | WELDED |  | 960 | 470 | YES | 3 | 960 | 1 | 53 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.R. HAVEY - MANAGER REGULATORY COMPLIANCE | 7132410132
2017-09-29 08:50 | YES | NO | 19920232 | 1993-01-12 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1992-12-14 | 1104 | MI | GOGEBIC |  | NO |  | YES | LAKEHEAD PIPE LINE'S OLD WAKEFIELD PUMP STATION (REMOVED). APPROX. 4 MILES SOUTHEAST OF WAKEFIELD, MI AND 1 MILE NE OF U.S. HWY 2 ON COUNTY RD. 398. LAKEHEAD'S |  | LINE PIPE | OTHER | 2" PRESSURE EQUALIZATION | 1992 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19613.1418 | 39567.6291 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | JON E STAUDOHAR - SECRETARY & GENERAL MANAGER CORPORATE SERV | 7153941404 | ON DECEMBER 14, 1992, AT APPROXIMATELY 11:04 MST. LAKEHEAD EXPERIENCED A LEAK ON IT'S LINE 5 PIPELINE NEAR WAKEFIELD, MI. CREWS HAD JUST COMPLETED MAINLINE WORK WHERE A STOPPLE BYPASS HAD BEEN INSTALLED AND WERE REMOVING THE STOPPLE TOWERS. AS THE TOWER WAS BEING REMOVED, THE RIGGING JUMPED SLIGHTLY AND STRUCK A HOSE LINE CONNECTED TO A 2" PRESSURE EQUALIZATION VALVE. THE VALVE WAS STRIPPED FROM THE THREADED FITTING CAUSING THE REPORTED RELEASE. LINE 5 WAS SHUTDOWN ON AN UNRELATED MATTER PRIOR TO THIS INCIDENT. ALL OIL WAS CONTAINED WITHIN THE EXCAVATION, HOWEVER, DUE TO THE STATIC PRESSURE IN THE LINE,REPAIRS COULD NOT BE INITIATED UNTIL PRESSURE WAS RELIEVED THROUGH DRAIN-UP. THE RELEASE WAS CONTROLLED AND ALLOWED TO DRAIN INTO THE OPEN EXCAVATION UNTIL PRESSURE WAS RELIEVED AND REPAIRS COULD BE MADE. APPROXIMATELY 100 BARRELS OF CRUDE OIL WERE RELEASED INTO THE OPEN EXCAVATION BEFORE VACUUM TRUCKS BEGAN RECOVERING THE OIL. AT NO TIME FOLLOWING DID THE VOLUME IN THE EXCAVATION INCREASE, HOWEVER, TOTAL DRAIN-UP VOLUME WAS APPROXIMATELY 850 BARRELS. THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 1308 MST, DECEMBER 14, AND THE MICHIGAN DEPARTMENT OF NATURAL RESOURCES WAS NOTIFIED AT 1313 MST, DECEMBER 14. AN INCIDENT UPDATE WAS PROVIDED TO MR. DONALD MOORE OF THE OFFICE OF PIPELINE SAFETY - CENTRAL REGION ON DECEMBER 15, 1992.
2017-09-29 08:50 | YES | YES | 19920233 | 1993-01-06 | 15490 | PHILLIPS PIPE LINE CO | YES | 1992-12-03 | 1215 | CO | ADAMS | AURORA | NO |  | NO | MCCULLOCH-BORGER LINE, MP 350A-26+83. NEAR NORTH SIDE OF I-70 IN AURORA, CO. APPROX. 1000' WEST OC CHAMBERS RD. |  | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 6 | 0 | 6 | 119500 | 93750.8178 | 189133.267 | L. P. G. | 2 | 1665 | 0 | NO | NO | 6.63 | 0.19 | 52000 | WELDED |  | 1577 | 795 | YES | 24 | 2379 | 9 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | B L THORMAN - MANAGER OF ENGIN. & TECHNICAL SERVICES | 9186614721 | CONTRACTOR WAS EXCAVATING THE PIPELINE IN PREPARATION FOR AN I-70 WIDENING PROJECT. HE HIT AND PUNCTURED THE PIPELINE RELEASING NGL. THE LINE HAD BEEN PREVIOUSLY LOCATED AND A PORTION ADJACENT TO THE PUNCTURE HAD BEEN EXPOSED. VAPORS WERE IGNITED. NO COMPANY EMPLOYEES OR CONTRACTOR EMPLOYEES WERE INJURED. INJURED PARTIES WERE PASSING BY. STOPPLES WERE SET. FUEL BURNED OUT AT APPROXIMATELY 17:30 CST.
2017-09-29 08:50 | YES | NO | 19920235 | 1993-01-05 | 809 | ARCO PIPE LINE CO | YES | 1992-12-21 | 730 | OK | CARTER |  | NO |  | NO | TWO MILES EAST OF RINGLING, OKLAHOMA ON HIGHWAY 70 |  | TANK FARM | OTHER | NON SPECIFIED | 1928 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1176.7885 | 2374.0577 | CRUDE OIL | 1 | 145 | 145 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G POLING - COMPLAINCE COORDINATOR | 7139865233 | ON DECEMBER 21, 1992, A TANK CONTAINING CRUDE OIL OVERFLOWED AT ARCO PIPE LINE COMPANY'S FACILITY. TWO MILES EAST OF RINGLING, OKLAHOMA. THE INCIDENT OCCURRED IN SECTION 32, TOWNSHIP 4 SOUTH, RANGE 3 WEST, JEFFERSON COUNTY. APPROXIMATELY 145 BARRELS SPILLED ON SOIL IN THE TANK DIKE AREA DUE TO A FAULTY TANK GAUGE. ARCO PIPE LINE COMPANY PROMPTLY REMOVED THE CRUDE OIL FROM THE AREA VIA VACUUM TRUCKS. CLEAN UP OF THE SPILL WAS COMPLETED ON DECEMBER 22, 1992. 145 BARRELS OF CRUDE OIL WERE RECOVERED. WATERWAYS WERE NOT AFFECTED BYTHE SPILL. ON THE SAME DAY, I REPORTED THE SPILL TO PETTY OFFICER STILLWAGON OF THE NATIONAL RESPONSE CENTER, WADEEN HAYS OF THE OKLAHOMA CORPORATION COMMISSION, AND MIKE SMITH OF THE OKLAHOMA DEPARTMENT OF POLLUTION CONTROL. ARCO PIPE LINE COMPANY WILL INVESTIGATE THE INCIDENT UTILIZING AN INTERNAL TEAM COMPRISED OF OPERATIONS, CONTROL CENTER, AND COMPLIANCE PERSONNEL TO HELP AVOID A SIMILAR INCIDENT IN THE FUTURE.
2017-09-29 08:50 | YES | NO | 19920236 | 1993-01-05 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1992-12-19 | 930 | OK | CREEK | DRUMRIGHT | NO |  | NO | FROM INTERSECTION OF SH99 & 33 GO 1.5 MILES NORTH IN SH99, EAST INTO SITE |  | LINE PIPE | PIPE |  | 1954 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 23535.7702 | 47481.1549 | CRUDE OIL | 1 | 325 | 310 | NO | NO | 12 | 0.25 | 0 | WELDED |  | 600 | 50 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E Y WOOTTEN - COMPLIANCE COORDINATOR | 9185866962 | PIPE FAILURE ADJACENT TO WELD. RELEASE SPREAD OVER 2 1/2 MILES OF CREEK BEFORE CONTAINMENT. LINE EXCAVATED AND CLAMPED 12/19/92 @ 4 PM. LINE PERMANENTLY REPAIRED 12/21/92 @ 9 PM. CLEANUP IS 90% COMPLETE AS OF 12/28/92.
2017-09-29 08:50 | NO | NO | 19920237 | 1992-12-31 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-03-30 | 1230 | CA | ALAMEDA | OAKLAND | NO |  | NO | PLMP 3.47 AT FALLON ST. BLOCK VALVE, APROX. 50 FEET FROM SPRR TRACKS AND 5 FEET FROM A BEACON STORAGE YARD |  | LINE PIPE | VALVE |  | 1969 | OTHER | PACKING FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 7060.731 | 14244.3465 | TURBINE FUEL | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SR. V.P. OPERATIONS & ENGINEERING | 2134867720 | AREA SUPERVISOR DAVE NORD DISCOVERED A PACKING GLAND SWEAT LEAK ON A 1-INCH VALVE AT FALLON STREET BLOCK VALVE. REPLACED WITH A NEW 1" VALVE. NOTE: INITIAL ESTIMATES OF THE TOTAL PROPERTY DAMAGE CAUSED BY THIS OCCURRENCE WERE LESS THAN $5,000 AND THEREFORE NO FORMAL REPORT WAS FILED. HOWEVER, SUBSEQUENT INVESTIGATION HAS RAISED THOSE ESTIMATES TO EXCEED $5,000 AND WE NOW SUBMITTHIS REPORT TO COMPLY WITH THE INTENT OF THE REGULATION.
2017-09-29 08:50 | YES | NO | 19930001 | 1993-01-15 | 12127 | MARATHON PIPE LINE CO | YES | 1992-12-19 | 1030 | WY | WASHAKIE | WYOMING | NO |  | NO | NW4 SECTION 20 T4SN R 94W . MPLC CHATHAM STATION, WASHAKIE COUNTY, WYOMING |  | PUMPING STATION | BOLTED FITTING |  | 1952 | OTHER | FAILURE OF LINER CAP BOLT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9414.3081 | 18992.462 | CRUDE OIL | 1 | 53 | 53 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A FISHER - REGULATORY COORDINATOR | 4194213201 | ON DECEMBER 19, 1992, AT APPROXIMATELY 1030 HOURS LOCAL TIME, ALL 8 BOLTS SECURING THE LINER CAP OF PUMP NO. 2 FAILED, RELEASING AS ESTIMATED 53 BBLS, OFCRUDE OIL. SPILLED OIL WAS COMPLETELY CONTAINED ON STATION PROPERTY. FIFTY-THREE BBLS. OF OIL WERE RECOVERED. THE NRC AND WY-DEQ WERE NOTIIFED BY TELEPHONE OF THE INCIDENT. WY-DEA WILL BE CONSULTED REGARDING SOIL DISPOSAL.
2017-09-29 08:50 | YES | NO | 19930002 | 1993-01-19 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1992-12-13 | 1015 | TX | SAN PATRICIO |  | NO |  | NO | FIVE (5) MILES WEST OF PORTLAND ON STATE HWY 893 & 1074 |  | LINE PIPE | PIPE |  | 1966 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 78452.5672 | 158270.5163 | NATURAL GAS LIQUID | 2 | 6 | 0 | NO | YES | 10.75 | 0.19 | 46000 | WELDED |  | 792 | 700 | YES | 8 | 991 | 2 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W D PARTLOW - ENVIRONMENTAL & SAFETY SUPERVISOR | 7138777370 | HOUSTON 10" LEAK OCCURRED AT 1015 HOURS ON 12/13/92 NEAR THE INTERSECTION OFSTATE HIGHWAYS 893 & 1074 IN SAN PATRICIO COUNTY. LEAK APPEARS TO HAVE BEENCAUSED BY A SEAM FAILURE ON THE PIPE. THERE WERE NO DEATHS OR INJURIES. LEAK OCCURRED ON PLOWED FARMLAND. AREA WAS SECURED FROM TRAFFIC FOR APPROXIMATELY 20 HOURS.
2017-09-29 08:50 | YES | NO | 19930003 | 1993-01-22 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1992-12-22 | 100 | CA | SAN BERNARDINO | BLOOMINGTON | NO |  | NO | WITHIN SFPP'S COLTON TERMINAL TANK FARM, LOCATED AT 2359 S RIVERSIDE AVENUE, BLOOMINGTON, CA |  | TANK FARM | OTHER | NON SPECIFIED | 1963 | OTHER | OVERFILLED TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 137291.9926 | 276973.4035 | GASOLINE | 3 | 2238 | 439 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENOIR V P - OPERATIONS & ENGINEERING | 2134867720 | OVERFILLED BREAKOUT TANK DURING DELIVERY. UPON DISCOVERY, PIPELINE FEEDING TANK WAS SHUT DOWN, INITIAL REPORTS MADE AND CLEANUP OPERATIONS INITIATED.
2017-09-29 08:50 | YES | NO | 19930004 | 1993-01-28 | 18718 | SUN PIPELINE CO | YES | 1992-12-31 | 50 | PA | CHESTER | WEST WHITELAND | NO |  | NO | ON LEFT, APPROX. 0.1 MILE WEST OF RT. 100, ON SHOEN RD. |  | LINE PIPE | GIRTH |  | 1931 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 588394.254 | 1187028.8721 | FUEL OIL | 1 | 645 | 539 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1100 | 940 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BUDDY J CURRENS - MANAGER - RISK MANAGEMENT & ENGINEERING | 2159755803 | LEAK WAS CAUSED BY THIRD PARTY DAMAGE. LINE WAS HIT BY LIGHT POLE AUGER. LINE MARKERS WERE IN PLACE AT TIME OF LEAK AND A COASTAL STATES CRUDE GATHERING COMPANY REPRESENTATIVE HAD LOCATED/STAKED LINE TEMPORARILY FOR THE LIGHT COMPANY AT THEIR REQUEST PRIOR TO EXCAVATION. REPLACED DAMAGED SECTION WITH 20 FEET OF NEW PIPE.
2017-09-29 08:50 | YES | NO | 19930005 | 1993-01-21 | 22907 | WYCO PIPE LINE CO | YES | 1992-12-26 | 930 | WY | LARAMIE | CHEYENNE | NO |  | NO |  |  | TANK FARM | VALVE | TANK | 0 | OTHER | WEATHER CONDITIONS - FROZ | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 470.7154 | 949.6231 | TRANSMIX (PART. REFINED PETRO) | 2 | 185 | 50 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RONALD A WENKE - FIELD SUPERVISOR | 3072373463 | TANK AT CHEYENNE TERMINAL WAS ISOLATED AND WAS FILLED WITH MIXTURE OF PETROLEUM PRODUCTS AND WATER. VALVE WHICH ISOLATED TANK FROM TERMINAL MANIFOLD FROZE AND CRACKED THIS VALVE, CAUSING WATER AND PRODUCT MIXTURE TO LEAK ONTO THEGROUND.
2017-09-29 08:50 | YES | NO | 19930007 | 1993-01-15 | 22183 | PINEY POINT INDUSTRIES, INC | YES | 1992-12-14 | 1530 | MD | PRINCE GEORGES |  | NO |  | NO | SUITLAND PARKWAY AT OLD MARLBORO PIKE |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 39226.2836 | 79135.2581 | JET FUEL | 2 | 40 | 40 | NO | NO | 8 | 0.25 | 0 | WELDED |  | 300 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA | NONE | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | WILLIAM E SCOTT - TERMINAL MANAGER | 3015996400 | UTILITY CONTRACTOR BORING ROAD CROSSING BENEATH SUITLAND PARKWAY FOR A 4" CONDUIT. MACHINE WAS OPERATING FROM NORTH SIDE OF ROADWAY, AUGER STRUCK LINE PIPE LOCATED ON SOUTH SIDE OF ROADWAY. "ONE-CALL" SYSTEM ADVISED OF PROJECTEDCONSTRUCTION ON 12/08/92, A MEETING WAS SCHEDULED BETWEEN OPERATOR/CONTRACTOR FOR 12/11/92, WHICH CONTRACTOR CANCELLED. THE MEETING NEVER OCCURRED PRIORTO THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19930008 | 1993-01-29 | 7161 | HAWIIAN INDEPENDENT REFINERY, INC (HIRI) | NO | 1993-01-14 | 728 | HI | OAHU | KAPOLEI | NO |  | NO | INCIDENT OCCURRED ABOUT 1.5 MI. N OF THE REFINERY, IN THE VICINITY OF THE KAPOLEI SHOPPING CENTER. PIPELINE WHERE INCIDENT OCCURRED IS APPROX 100 FT E OF MP3.0 |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 36757 | 28167.7705 | 56825.7705 | JET FUEL | 2 | 405 | 310 | NO | NO | 10 | 0.25 | 35000 | OTHER |  | 1472 | 250 | YES | 24 | 1866 | 5 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | DOT REGULATIONS | NO | NO | KENNARD S VANDERGRIFT, JR. - REFINERY ADMINSTRATIVE MANAGER | 8085473947 | AT ABOUT 7:30 AM ON JANUARY 14, 1993, THE 10" DIAMETER REFINED PRODUCTS PIPELINE WAS STRUCK BY A FRONT-END LOADER OPERATED BY FLETCHER PACIFIC CONSTRUCTION CO. LTD. MAKING A HOLE APPROXIMATELY 5" X 3". AT THE TIME OF THE IMPACT THERE WAS NO FLOW THROUGH THE PIPELINE, WHICH CONTAINED JP-8 AT A PRESSURE OF APPROXIMATELY 250 PSIG. APPROXIMATELY 17,000 GALLONS OF PRODUCT WAS RELEASED. APPROXIMATELY 13,000 GALLONS WERE RECOVERED AND RETURNED TO THE REFINERY.THE IMPACT OCCURRED APPROXIMATELY 100' EAST OF MP 3.0, SEVERAL HUNDRED FEET WEST OF A NEW SHOPPING CENTER THAT IS BEING BUILT IN THE AREA. DURING THE PRECEEDING WEEKS FLETCHER PACIFIC HAD UNDERTAKEN EXCAVATIONS IN THE AREA TO INSTALL A CONCRETE STORMWATER CULVERT 8' X 7'. THE CULVERT HAD BEEN COMPLETED AND LARGELY BACKFILLE, WITH ONLY THE LAST 50' STILL TO BE COVERED. THIS SECTION INCLUDED THE AREA WHERE THE 10" PIPELINE CROSSED OVER THE CULVERT. SOIL FROM THE EXCAVATION HAD BEEN STOCKPILED OVER THE AREA WHERE THE PIPELINE WAS STRUCK. ON JANUARY 14, 1993, FLETCHER PACIFIC EMPLOYEES WERE BACKFILLING AROUND THE LAST 50' OF THE CULVERT. A LARGE KOMATSU PC-44 EXCAVATOR WAS BEING USED TO RECLAIM SOIL FROM THE STOCKPILE WHEN THE INCIDENT OCCURRED. APPROXIMATELY 5' OF THE LINE CONTAINING THE DAMAGE PORTION HAD BEEN REPLACED.
2017-09-29 08:50 | YES | NO | 19930009 | 1993-01-15 | 10312 | GULF CENTRAL PIPELINE CO | YES | 1992-12-16 | 1145 | IL | JERSEY |  | NO |  | NO | SEC. 10, R10W, T7N MILEPOST 10-25 |  | LINE PIPE | PIPE |  | 1970 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 3138.1027 | 6330.8207 | ANHYDROUS AMMONIA | 2 | 6 | 0 | NO | NO | 8.63 | 0.2 | 1423 | WELDED |  | 1340 | 690 | YES | 26 | 1994 | 1 | 70 | EXTERNAL | Null | YES | OTHER | ELECTRO CHEMICAL | NO DATA |  | Null | NO DATA |  | Null | Null | JIM L NORVELL | 3144865788 | AT APPROXIMATELY 11:45AM, A COUNTY MAINTENANCE WORKER OBSERVED A STRONG SMELL OF ANHYDROUS AMMONIA AND VAPORS COMING FROM THE GROUND AT MILEPOST 10-15. HE CALLED OUR DISPATCHER IN WICHITA AND REPORTED HIS OBSERVATION. THE DISPATCHER NOTICED NO PRESSURE DROP ON THE SCADA SYSTEM. FIELD PERSONNEL WAS NOTIFIED AND PRESSURE REDUCED. A RELEASE WAS CONFIRMED AT 12:40. VALVES ON EACH SIDE OF THE RELEASE WERE CLOSED. PERSONNEL AND MATERAILS WERE GATHERED FOR REPAIR. CORROSION WAS FOUND ON THE PIPE CAUSED BY POOR TAPE. A TEN FOOT FULLEMCIRCLEMENT SLEEVE WAS INSTALLED ON THE PIPE AND THE LINE RETURNED TO SERVICE ON 12017-92. CONTAMINATION WAS RESTRICTED TO SOIL ONLY WITH NO INJURY TO PERSONNEL, LIVESTOCK, OR POLLUTION OF WATERS. NOTIFICATIONS WERE MADE ON 12-16-92 TO THE ILLINOIS DEPARTMENT OF EMERGENCY SERVICES ATT 13:10 (#923574) AND TO THE NRC AT 13:27 (#149454)
2017-09-29 08:50 | YES | NO | 19930010 | 1993-01-21 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1992-12-17 | 1140 | PA | HUNTINGDON |  | NO |  | NO |  |  | NO DATA | OTHER | THREADED FITTING INTO 2" | 1992 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 117678.8508 | 237405.7744 | GASOLINE | 3 | 35 | 12 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | DEAN R MOYER - REGULATORY COMPLAINCE ADMINSTRATOR | 2158208300 | A 2" BYPASS PIPING AROUND THE MAINLINE CHECK VALVE AT MILE POST 146.302 ON LAUREL PIPE LINE WAS INSTALLED. DURING BACKFILL OPERATIONS BY THE CONTRACTOR,EXCESSIVE OVERBURDEN LOADING CREATED STRESS ON THE 2" SCREWED VALVE AND FITTING CONNECTION. ON DECEMBER 17, 1992, A PRODUCT SPRAY WAS DISCOVERED EMANATING FRON THIS THREADED FITTING CONNECTION INTO THE 2" VALVE WHICH WAS LOCATED WITHIN A VALVE ENCLOSURE BELOW GRADE LEVEL. PERMANENT REPAIR COMPLETED SO THAT THREADED FITTING CONNECTION BECAME INOPERATIVE. THE RECOVERED PRODUCT WASRECYCLED AND CLEANUP OF AFFECTED AREA IS BEING CONDUCTED TO THE SATISFACTIONOF THE PENNSYLVANIA DEPARTMENT OF NATURAL RESOURCES.
2017-09-29 08:50 | NO | NO | 19930011 | 1993-02-16 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | Null | 1993-01-05 | 830 | CA | LOS ANGELES | CARSON | NO |  | NO | 20410 SOUTH WILMINGTON AVE. CARSON CA |  | TANK FARM | TANK | TANK W-3 | 1955 | OTHER | CRACK IN TANK FLOOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 45979.4387 | 92759.0997 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD, SENIOR VICE PRESIDENT - OPERATIONS & ENGINEERING | 2134867720 | CRACK IN TANK FLOOR CAUSED APPROXIMATELY 10 FEET X 4 INCHES WET SPOT ON GROUND. SOIL REMOVED AND PROPERLY DISPOSED. TANK EMPTIED AND REPAIRED.
2017-09-29 08:50 | YES | NO | 19930012 | 1993-02-08 | 24003 | YELLOWSTONE PIPELINE CO | YES | 1993-01-14 | 1100 | MT | SANDERS |  | NO |  | YES | SW18, T20N, R24W |  | LINE PIPE | PIPE |  | 1953 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 383161.9894 | 772992.4979 | GASOLINE | 3 | 72 | 10 | NO | NO | 10.75 | 0.31 | 42000 | WELDED |  | 1716 | 600 | YES | 0 | 0 | 1 | 54 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY BEGGS, COORDINATOR - REGULATORY COMPLIANCE | 3036494090 | ON JANUARY 14, 1993, A PIPELINE FAILURE OCCURRED ON THE YELLOWSTONE PIPELINEIN SANDERS COUNTY, MT, ON THE FLATHEAD INDIAN RESERVATION. THE RELEASE WAS DISCOVERED BY THE LANDOWNER WHO CALLED THE EMERGENCY PHONE NUMBER SHOWN ON ANADJACENT PIPELINE MARKER. THE SYSTEM WAS IMMEDIATELY SHUT DOWN REMOTELY BY CONOCO'S OPERATIONS CENTER. PETROLEUM PRODUCT ENTERED THE NEARBY CAMAS CREEK; SMALL POOLES OF PRODUCT WERE OBSERVED FOR APPROXIMATELY 1700 FEET DOWNSTREAM OF THE RELEASE SITE. CLEANUP HAS INCLUDED THE USE OF SIPHON DAMS, ABSORBENT MATERIALS AND SOIL EXCAVATION.
2017-09-29 08:50 | YES | NO | 19930013 | 1993-02-11 | 443 | AMOCO PIPELINE CO | YES | 1993-01-16 | 1045 | NM | LEA |  | NO |  | NO | 9 1/2 MILES NORTH AND 13 1/2 MILES WEST OF LOVINGTON, NEW MEXICO |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 185 | 160 | NO | NO | 8 | 0.19 | 0 | WELDED |  | 720 | 0 | YES | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM HOMER - P/L MAINT. FMN | 5053962817 | LEAK WAS DUE TO INTERNAL CORROSION-RECOVERED ALL OIL POSSIBLE WITH VACUUM TRUCK. LEAK SITE IS IN RANGE LAND.
2017-09-29 08:50 | YES | NO | 19930014 | 1993-02-25 | 19536 | TOTAL PIPELINE CORP | YES | 1993-01-21 | 1050 | OK | COTTON | DEVOL | NO |  | NO | NE 1/4 OF SECTION 20, TOWNSHIP 4 SOUTH, RANGE 13 WEST, COTTON COUNTY, OKLAHOMA FROM THE JCT. OF I-35 & HWY 70, 5 MILES W. 1 MILE N, 1/2 MILE W THEN S 1/4 MILE |  | LINE PIPE | PIPE | COLLAR COUPLING ON PIPE | 1940 | OTHER | 8" PIPE COLLAR COUPLING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 76632.3979 | 154598.4996 | CRUDE OIL | 1 | 1200 | 1150 | NO | NO | 8.63 | 0.32 | 29000 | COUPLED |  | 480 | 6 | YES | 8 | 900 | 7 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL J COOPER - MGR. REGULATORY COMPLIANCE | 4052291638 | ON THE AFTERNOON OF JANUARY 20, 1993 TOTAL'S 24 HR SCADA CONTROL CENTER NOTIFIFED THE BURKBURNETT FIELD OFFICE OF A POSSIBLE MEASUREMENT PROBLEM AT DEVOL STATION ON THE KADANE 8" INCOMING METER SKID. THE BURKBURNETT OPERATIONS MANAGER WENT TO THE SITE AND CHECKED OUT THE SITUATION. THE METERS, PRESSURE TRANSMITTERS, FLOW TRANSMITTES, BACK PRESSURE VALVES, & OVERPRESSURE RUPTURE DISK ASSEMBLY WERE CHECKED OUT TO SEE IF THERE WAS ANY MALFUNCTIONING EQUIPMENT. NONE WAS FOUND SO FURTHER CHECKS WEREMADE ON DOWN STREAM PUMPING STATIONS& UMMONITORED FIELD PUMPS TO SEE IF PROBLEMS EXISTED AT THESE POINTS. NONE WERE FOUND. BY THIS TIME IT WAS AFTER DARK AND A DECISION WAS MADE TO SHUT IN THE SYSTEM AND PERFORM FURTHER INVESTIGATION THE FOLLOWING MORING. THIS WAS NOT AN ALARMING CONDITION SINCE THERE HAD BEEN INSTANCES IN THE PAST WHERE EQUIPMENT HAD MALFUNCTIONED AND GIVEN ERRORS IN OUR MEASUREMENT CALCULATIONS. THE FOLLOWING MORNING MAINTENANCE PERSONNEL WERE DISPATCHED TO DEVOL STATION TO CHECK THE INTERNAL METER ELEMENT INCLUDING THE GEAR TRAIN & DRIVE LINK ASSEMBLY. THE BACK PRESSURE VALVE WAS ALSO CLEANED. THE GAUGER WORKED THE STATION THE MORNING OF JANUARY 21, 1993 AND FOUND THAT THERE WAS SHORTAGE OF APPROCIMATELY 1200 BARRELS AT THE STATION. AT THIS POINT MAINTENANCE EMPLOYEES BEGAN DRIVING OUT THE PIPELINE, CHECKING FOR A POSSIBLE LEAK. A LEAK WAS FOUND APPROXIMATELY 1 MILE SOUTH OF DEVOL STATION IN A WHEAT FIELD AT 10:30 A.M. THE OIL HAD TRAVELED SOUTHWARD AND COLLECTED IN TWO FARM PONDS & IN AN UNNAMED CREEK. EMERGENCY RESPONSE CREWS WERE DISPATCHED FROM THE BURKBURNETT &HEALDTON FIELD OFFICES IMMEDIATELY TO SET UP CONTAINMENT BOOMS TO PREVENT THE OIL FROM TRAVELING FURTHER DOWN THE CREEK. VACUUM TRUCKS WERE DISPATCHED TO THE SITE TO PICK UP THE OIL OFF OF THE FARM PONDS. PORTABLE TANKS WERE SETUP AT DEVOL STATION TO STORE THE OIL & WATER PICKED UP BY THE VACUUM TRUCKS.EMERGENCY CLEANUP CREWS WORKED AROUND THE CLOCK UNTIL THE MAJORITY OF THE OILWAS CLEANED UP. THE PIPELINE WAS REPAIRED JANUARY 21, 1993 AT APPROXIMATELY10:10 P.M. BY INSTALLING NEW PIPE IN THE AFFECTED AREA. THE LINE HAD PILLEDINTO AT AN 8" COLLAR COUPLING. THIS WAS ARRIBUTED TO THE GROUND SHIFTING DUE TO HEAVY RAINS. THE OIL THAT COULD NOT BE PICKED UP WITH VACUUM TRUCKS WAS CLEANED UP WITH ABSORBENT PADS, BOOMS, & MATERIALS. THE CREEK WAS FLUSHED WITH CLEAN WATER FROM THE FARM POND & THE WATER & OIL WAS PICKED UP WITH VACUUM TRUCKS. APPROXIMATELY 10 BARRELS OF OIL WAS BURNED ALONG WITH GRASS AND OTHER DEBRIS. ALL REMAINING OIL RESIDUE WAS BURNED BY SPREADING HAY OVER THE AREA & LIGHTING WITH A PROPANE TORCH.
2017-09-29 08:50 | YES | NO | 19930015 | 1993-02-23 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-01-21 | 1600 | NM | LEA |  | NO |  | NO | LINE 80-3 - TEXACO-EUNICE TO LINE 80-12 COUNTY ROAD 45, 2 MILES WEST OF HWY.18, LEA CO., NM |  | LINE PIPE | PIPE |  | 1943 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 27490 | 21066.2462 | 42499.1275 | NATURAL GAS LIQUID | 2 | 878 | 0 | NO | NO | 4 | 0.19 | 42000 | WELDED |  | 1440 | 650 | YES | 8 | 1945 | 10 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | B L THORMAN, MANAGER OF ENGINEERING AND TECHNICAL SERVICES | 9186614721 | AT 4:00 P.M. (CST) A ROAD GRADER STRUCK LINE 80-3 AT THE INTERSECTION OF LINE 80-3 AND COUNTY ROAD 45 IN LEA CO., NM. THE ROAD GRADER PUNCTURED THE PIPELINE CAUSING THE RELEASE OF 878 BBLS. OF NGL. THE ROAD GRADER HAD BEEN CUTTING THE ROAD AND BAR DITCHES IN PREPARATION FOR PAVING. THE PIPELINE WAS WELL MARKED ON BOTH SIDES OF THE ROAD. ONE-CALL NOTIFICATION WAS NOT MADE BY THE CONTRACTOR GRADING THE ROAD.
2017-09-29 08:50 | YES | NO | 19930016 | 1993-01-19 | 443 | AMOCO PIPELINE CO | YES | 1993-01-21 | 1045 | OK | PAYNE |  | NO |  | NO | AMOCO'S PENCE TANK FARM. SOUTHWEST QUARTER OF SECTION 12, TOWNSHIP 17 NORTH, RANGE 5 EAST |  | TANK FARM | PIPE | GIRTH WELD | 1975 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 459.7944 | 927.591 | CRUDE OIL | 1 | 200 | 199 | NO | NO | 12 | 0.38 | 0 | WELDED |  | 275 | 50 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | T.O. MC GEEEHAN - ACTING AREA MANAGER | 9182257271 | THE LEAK WAS CAUSED BY A LOCALIZED, INTERNAL CORROSION PIT. THE PIT WAS LOCATED ON THE BOTTOM OF THE PIPE IN A WELD. THE LINE WAS NOT OPERATING AT THE TIME OF THE LEAK.
2017-09-29 08:50 | YES | YES | 19930017 | 1993-01-23 | 10012 | KANEB PIPELINE CO | YES | 1993-01-22 | 715 | NE | MADISON |  | NO |  | NO | NW 1/4 SECTION 3 T24N R1W |  | PUMPING STATION | OTHER | INBOARD PUMP SEAL | 1988 | OTHER | INBOARD PUMP SEAL FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 100 | 76.6324 | 154.5985 | L. P. G. | 2 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L LEROY ANDERSON - MGR OF REGULATORY AFFAIRS | 3162621408 | THIS INCIDENT OCCURRED ON FRIDAY, JANUARY 22, 1993, HOWEVER, IT WAS NOT UNTIL MONDAY, JANUARY 25, 1993 THAT WE WERE INFORMED A COMPANY EMPLOYEE MAY HAVE BEEN INJURED BY COMING INTO CONTACT WITH LIQUID PROPANE. WE CONTACTED THE KANSAS CITY OFFICE OF PIPELINE SAFETY AT THAT TIME TO REQUEST GUIDANCE REGARDINGPROPER NOTIFICATION IN ORDER TO MAINTAIN COMPLIANCE WITH THE REGULATIONS. WE WERE ADVISED TO CONTACT THE NATIONAL RESPONSE CENTER AND REPORT THE POSSIBILITY OF AN INJURY OF AN EMPLOYEE DURING THIS INCIDENT. WE ARE NOW ABLE TO REPORT THAT A COMPANY EMPLOYEE DID SUSTAIN INJURY TO THREE TOES OF THE LEFT FOOT AND ONE TOE OF THE RIGHT FOOT. THE EMPLOYEE IS RECEIVING PROFESSIONAL MEDICAL TREATMENT FOR THIS INJURY AND FULL RECOVERY IS EXPECTED.
2017-09-29 08:50 | YES | NO | 19930018 | 1993-02-25 | 4906 | EXXON PIPELINE CO | YES | 1993-01-26 | 1530 | TX | HOUSTON |  | NO |  | NO | EXXON PIPELINE COMPANY SATSUMA STATION 9118 JACKRABBIT RD. HOUSTON, TX 77095 |  | TANK FARM | TANK |  | 1950 | OTHER | TANK BOTTOM FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 134106.6963 | 270547.3743 | CRUDE OIL | 1 | 1825 | 1800 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MGR -ENVIRON & REGULATORY COMPLAINCE DEPT | 7136565521 | TANK WAS OUT OF SERVICE (CONTAINING CRUDE OIL) WITH THE FLOATING ROOF RESTING ON ITS LEGS. CRUDE RELEASED THROUGH HOLE IN BOTTOM DUE TO EITHER CORROSIONOR DAMAGE TO BOTTOM FROM ROOF LEG.
2017-09-29 08:50 | NO | NO | 19930019 | 1993-01-09 | 15851 | PRIDE REFINING INC | YES | 1993-01-26 | 1150 | TX | MCLENNAN | LORENA | NO |  | NO | APPROX. 1 1/2 MILES NW OF CITY OF LORENA, TX, OFF XOUNTY ROAD #116 |  | LINE PIPE | PIPE | CRACK IN 12" PIPE COLLAR | 1925 | OTHER | COLLAR SEEP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1532.648 | 3091.97 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 12 | 0.38 | 25000 | THREADED |  | 664 | 333 | YES | 8 | 830 | 0 | 92 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON - PIPELINE MANAGER | 9156748231 | AT APPROXIMATELY 11:50 AM ON 1-26-93 LEAK WAS SPOTTED BY LANDOWNER CHARLIE MANTHEI. HE REPORTED THE SPILL BY TELEPHONE TO PRIDE'S EMERGENCY RESPONSE NUMBER. THE PIPELINE WAS SHUT DOWN AND PERSONNEL WERE DISPATCHED TO THE LEAK SITE. WE PLACED AN OIL CONTAINMENT BOOM ON THE CREEK TO CONTAIN THE SOIL. WE THEN NOTIFIED EMTECH ENVIRONMENTAL SERVICES TO RESPOND AND TO PROCEED WITH CLEAN-UP. THE REPAIRS WERE MADE AT APPROXIMATELY 11:30 PM ON 1-27-03 WITH A FULL ENCIRCLEMENT REPAIR SLEAVE.
2017-09-29 08:50 | NO | NO | 19930020 | 1993-02-11 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1993-01-28 | 830 | CA |  | CARSON | NO |  | NO | 223RD STREET AND WILMINGTON AVE |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 12 | 0.28 | 42000 | WELDED |  | 609 | 50 | YES | 4 | 760 | 8 | 92 | EXTERNAL | Null | YES | OTHER | PINHOLE CORROSION LEAK AT | NO DATA |  | Null | NO DATA |  | Null | Null | ARTHUR G DIEFENBACH - BUSINESS UNIT MANAGER | 3104289027 | LEAK OCCURRED IN SMALL SECTION OF UNCOATED PIPE (APPROX. 2') AND WAS FOUND AT 8:30AM LINE WAS SHUT DOWN AND CONTAMINATED SOIL WAS EXCAVATED AND REMOVED AND LINE WAS REPAIRED.
2017-09-29 08:50 | NO | NO | 19930021 | 1993-01-24 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1993-01-28 | 756 | AZ | PINAL |  | NO |  | Null | IN GILA RIVER |  | LINE PIPE | PIPE | UNKNOWN AT THIS TIME | 1985 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 0 | 0 | NO | NO | 6 | 0.28 | 3550 | WELDED |  | 0 | 0 | YES | 8 | 2578 | 10 | 85 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENOIR V.P. - OPERATIONS & ENGINEERING | 2134867720 | UPON INITIAL NOTIFICATION OF A POTENTIAL LEAK ON SFPP'S 6" PHOENIX-TUCSON PIPELINE, WE IMMEDIATELY SHUT DOWN OPERATIONS AND DRAINED BACK PRODUCT INTO PHOENIX TERMINAL AND DISPATCHED PERSONNEL TO CLOSE THE APPROPRIATE BLOCK VALVES.- SFPP WAS UNABLE TO VERIFY A DISCHARGE FROM THE PIPELINE. THE NEGATIVE PRESSURE TEST AND CONDITION OF THE PRODUCT REMOVED INDICATES THE LINE IS NOT PRESENTLY LEAKING, ALTHOUGH A SMALL PINHOLE LEAK AT HIGHER PRESSURE IS POSSIBLE. THE GASOLINE AT THE SITE HAS BEEN DISPLACED BY WATER. - SFPP WILL NOT BE ABLE TO INSPECT THE ORIGINAL GILA RIVER CROSSING UNTIL THE WATER LEVEL AND FLOWRATE ARE REDUCED. THEREFORE, SFPP HAS DECIDED TO LEAVE THE PIPELINE OUT OF SERVICE UNTIL A NEW PIPELINE CROSSING CAN BE INSTALLED.
2017-09-29 08:50 | NO | NO | 19930022 | 1993-03-01 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | Null | 1993-01-29 | 1030 | CA | LOS ANGELES | CARSON | NO |  | NO | SFPP WARSON STATION, 20410 S. WILMINGTON AVE., CARSON, CALIFORNIA |  | PUMPING STATION | OTHER | SUMP | 1971 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 15326.4796 | 30919.6999 | TURBINE FUEL | 3 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR V.P., OPERATIONS & ENGINEERING | 2134867720 | SUMP OVERFLOWED AT WATSON STATION SPILLING APPROXIMATELY 5 BARRELS OF TURBINE FUEL AND WATER. THE OVERFLOW OCCURRED DURING A TANK WATER BOTTOM DRAWING OPERATION. THE SMALL QUANTITY OF SOIL THAT CAME INTO CONTACT WITH THE PRODUCTWAS REMOVED AND WILL BE DISPOSED OF PROPERLY.
2017-09-29 08:50 | NO | NO | 19930023 | 1993-02-25 | 4906 | EXXON PIPELINE CO | YES | 1993-01-30 | 900 | TX | HEARNE |  | NO | N/A2 | NO | EXXON PIPELINE COMPANY HEARNE CRUDE STATION STATE HIGHWAY 6 1 MILE S OF HEARNE, ROBERTSON COUNTY, TX |  | PUMPING STATION | PIPE |  | 1981 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19158.0995 | 38649.6249 | TRANSMIX (PART. REFINED PETRO) | 1 | 10 | 9 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MGR - ENVIRONMENTAL AND REGULATORY COMPLIANCE DEP | 7136565521 | DEFECTIVE OF FAILED PIPE 3/8" TUBING SPLIT.
2017-09-29 08:50 | NO | NO | 19930024 | 1993-02-16 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-01-28 | 1415 | GA | CARROLL | BREMEN | NO |  | NO | TANK 41 - PLANTATION'S BREMEN TANK FARM LOCATED AT U.S. HWY 27, BREMEN, GA |  | TANK FARM | TANK |  | 1942 | OTHER | 1/4" HOLE BURNED TANK FLO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 4138.1495 | 8348.319 | JET FUEL | 3 | 5 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK, VICE PRESIDENT - OPERATIONS | 4043645916 | ON FRIDAY, JANUARY 22, 1993, WE REMOVED TANK 41 AT OUR BREMEN TANK FARM FROMSERVICE, CLEANED IT AND REPLACED THE ROOF DRAIN. ON WEDNESDAY, JANUARY 27, 1993, WE PLACED TANK 41 BACK IN SERVICE. OUR STANDARD PROCEDURE IS TO CHECK FOR LEAKS DURING THE FIRST TANK FILL AFTER PLACING A TANK BACK IN SERVICE. ONTHURSDAY, JANUARY 28, 1993, AT 14:15 EST, WHILE CHECKING FOR LEAKS IN TANK 41, WE DISCOVERED PRODUCT SEEPING FROM UNDER THE TANK. WE REMOVED THE TANK FROM SERVICE, CLEANED IT AND INSPECTED IT. OUR INSPECTION REVEALED A 1/4 INCH HOLE IN THE TANK FLOOR. APPARENTLY, THE HOLE RESULTED FROM A BURN THROUGH WHICH OCCURRED DURING THE REMOVAL OF A PIPE SUPPORT ASSOCIATED WITH THE DESIGN OF THE PREVIOUS ROOF DRAIN SYSTEM. WE REPAIRED THE TANK FLOOR BY WELDING A 12" X 12" STEEL PLATED OVER THE HOLE.
2017-09-29 08:50 | YES | NO | 19930025 | 1993-03-26 | 4906 | EXXON PIPELINE CO | NO | 1993-02-16 | 1645 | TX | HARRIS | HOUSTON | NO |  | NO | EPC SATUMA - PIERCE JUNCTION 12" CRUDE SYSTEM NEAR THE INTERSECTION OF HOLMES RD & ALMEDA RD IN SW HOUSTON HARRIS COUNTY, TX |  | PUMPING STATION | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | SUBSIDENCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 9500 | 7280.0778 | 14686.8575 | TRANSMIX (PART. REFINED PETRO) | 1 | 80 | 79 | NO | NO | 12 | 0.38 | 25000 | COUPLED |  | 620 | 197 | YES | 8 | 775 | 5 | 91 | NO DATA | Null | Null | NO DATA |  | SUBSIDENCE |  | Null | NO DATA |  | Null | Null | J B COX HOLT - MGR- ENVIRONMENTAL & REGULATORY COMPLIANCE | 7136565521 | SUBSIDENCE OF THE PIPE RESULTED IN A LEAK AT A COUPLING. AFTER DISCOVERY OFTHE LEAK, THE PIPELINE SYSTEM WAS SHUT DOWN. EPC AND CONTRACT PERSONNEL WEREDISPATCHED, AND ARRIVED ON-SCENE WITHIN 30 MINUTES. CRUDE OIL RELEASED (80 BARRELS) WAS CONTAINED IN A ROADSIDE DITCH. CONTAINMENT BOOM WAS DEPLOYED AND VACCUUM TRUCKS WERE UTILIZED TO RECOVER THE FREE OIL. SORBAEN MATERIALS WERE USED TO CLEAN UP RESIDUAL OIL. THE PIPELINE WAS REPAIRED BY WELDING THE COUPLING (COLLAR) AND THEN BY WELDING A FULL WRAP "PUMPKIN" OVER THE COUPLING. THE LINE WAS THEN RETURNED TO SERVICE THE FOLLOWING DAY.
2017-09-29 08:50 | YES | NO | 19930026 | 1993-03-23 | 4906 | EXXON PIPELINE CO | NO | 1993-02-25 | 1940 | TX | ELLIS |  | NO |  | NO | EPC MILFORD STATION- LOCATED APPROXIMATELY 4 MILES NORTH OF MILFORD, ELLIS COUNTY, TEXAS OFF OF FM 308. |  | PUMPING STATION | PUMP |  | 1967 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 30652.9592 | 61839.3998 | GASOLINE | 3 | 1 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | J B COLT - MGR - ENVIRONMENTAL & REG COMPLIANCE DEPT | 7136565521 | LUBRICATOR ON PUMP WAS SHOT WITH A FIREARM BY AN UNKNOWN PERSON(S). RESULTEDIN BEARING FAILURE DUE TO LOSS OF LUBRICATION AND ULTIMATELY IN PUMP INTERNAL DAMAGE. AUTOMATED STATION CONTROL SHUT-DOWN AND ISOLATED PUMP ON HIGH VIBRATION INDICATOR (FROM FAILED BEARING). HIGH VIBRATION AND FRICTION FROM FAILED BEARING IGNITED LUBRICATING OIL IN INBOARD BEARING AREA. UNKNOWN WHETHER TANDEM MECHANICAL SEALS FAILED OR WHETHER ANY PRODUCT WAS RELEASED. NO PRODUCT OBSERVED ON GROUND OR RECOVERED. SIGNIFICANT INTERNAL DAMAGE TO PUMP CONFIRMED ON MARCH 3, 1993 WHEN PUMP CASE OPENED. EXXON AND LOCAL AUTHORITIES CONTINUING VANDALISM INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19930027 | 1993-03-22 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-02-23 | 1655 | TX | BRAZORIA |  | NO |  | NO | SWEENY-PASADENA 12" LINE - MP 32X-9+80 APPROXIMATELY 0.8 MILE SOUTHEAST OF INTERSECTION OF FM 521 AND COUNTY ROAD 1462. SECTION 9, BLOCK A-236, HT&B SURVEY. |  | LINE PIPE | PIPE | SHOP FABRICATED BEND | 1956 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 344845.7905 | 695693.2481 | DIESEL FUEL | 3 | 951 | 708 | NO | NO | 12.75 | 0.25 | 46000 | WELDED |  | 1270 | 533 | YES | 24 | 1650 | 1 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B L THORMAN - MGR ENGINEERING & TECHNICAL SERVICES | 9186614721 | THE ALVIN OFFICE RECEIVED A REPORT AT 4:10 P.M. ON 3/23/93 OF AN ODOR BETWEEN FM 521 AND COUNTY ROAD 1462. COMPANY PERSONNEL WERE SENT TO THE AREA TO INVESTIGATE, AND THE PIPELINE WAS SHUT DOWN. AT 4:55 P.M., BECKY OHLER WITH THE TEXAS AIR CONTROL BOARD NOTIFIED THE PASADENA CONTROL CENTER THAT PRODUCT WAS FOUND ON THE GROUND. AT 5:10 P.M. PHILLIPS PERSONNEL ARRIVED ON SITE. THE LEAK WAS CAUSED BY A MANUFACTURING DEFECT IN A PIPE BEND.
2017-09-29 08:50 | YES | NO | 19930028 | 1993-03-23 | 2552 | COLONIAL PIPELINE CO | YES | 1991-04-18 | 920 | GA | FLOYD | CHATTOOGA | NO |  | NO | JOHN'S MOUNTAIN CHATOOGA/FLOYD COUNTY LINE |  | LINE PIPE | OTHER | FILLET WELD HEAT-AFFECTED | 1963 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 4018.6507 | 8107.2417 | GASOLINE | 2 | 40 | 15 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J A COX - MGR. TECHNICAL & REGULATORY | 4048412296 | THE COLONIAL PIPELINE COMPANY'S ATLANTA JUNCTION RECEIVED A CALL FROM MR. DAVID JACKSON AT 09:20 AM, EDT, ON APRIL 18, 1991, REPORTING THE ODOR OF PRODUCT AT DUNAWAY GAP, DRY CREEK VALLEY ROAD IN CHATTOOGA COUNTY, GEORGIA. MAINTENANCE PERSONNEL WERE DISPATCHED TO THE SCENE AND BEGAN TO SEARCH FOR THE SOURCE OF THE LEAK. THE PIPELINE WAS EXPOSED AROUND 3:00 PM, EDT, AND PRODUCT WAS EVIDENT BUT NOT LEAKING FROM THE PIPE. THE DECISION WAS MADE TO EXPOSE A 2" BLEEDER VALVE AT 4:OO PM, EDT, AND THE LEAK WAS ONLY DISCOVERED AFTER PRESSURE WAS PLACED ON THE PIPELINE. A THREE-INCH CRACK WAS DISCOVERED ALONG THE BASE OF A 2" COUPLET TO WHICH THE BLEEDER VALVE WAS ATTACHED. THE PIPELINE WAS DRAINED, AND THE WELD AROUND THE BASE OF THE COUPLET WAS REPAIRED BY WELDING. A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED OVER THE AREA REINFORCING THE INITIAL REPAIR. THE LEAK WAS REPORTED TO THE GEORGIA DEPARTMENT OF NATURAL RESOURCES AT 10:35 AM, EDT, ON APRIL 18, 1991. THE NATIONAL RESPONSE CENTER WASNOTIFIED OF THE LEAK AT 11:26 AM, EDT, ON THE SAME DAY. THE ENTIRE SECTION OF PIPELINE WAS REMOVED AT A LATER DATE DUE TO THE RESULTS OF AN INTERNAL INSPECTION SURVEY WHICH INDICATED CORROSION IN THE AREA OF THE BLEEDER VALVE. CURRENTLY, COLONIAL PIPELINE COMPANY IS MONITORING THE QUALITY OF AREA STREAMS AND THE DRINKING WATER SUPPLY OF NEARBY RESIDENTS AND MAINTAINING PRODUCT COLLECTION DEVICES, ALTHOUGH NO FREE PRODUCT HAS BEEN DETECTED AT THE SITE SINCEFEBRUARY, 1992.
2017-09-29 08:50 | YES | NO | 19930029 | 1993-03-22 | 22430 | WEST SHORE PIPE LINE CO | YES | 1993-03-06 | 752 | IL | LAKE |  | NO |  | NO | WEST SHORE PIPE LINE LINDENHURST STATION1 MILE WETS OF HIGHWAY 45 ON ROLLINS ROAD. |  | PUMPING STATION | PUMP | PACKING GLAND | 1961 | OTHER | PACKING GLAND FAILURE ON | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 383161.9894 | 772992.4979 | GASOLINE | 3 | 85 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | APRIL S MANLEY - AREA MANAGER - OPERATIONS | 7082573740 | AT APPROXUMATELY 07:52 HOURS ON 3/6/93, THE CONTROL CENTER RECEIVED A CALL FROM A NEARBY RESIDENT OF THE PUMP STATION REPORTING THAT PRODUCT WAS ESCAPINGTHE PUMP UNIT. PUMPS WERE IMMEDIATELY SHUT DOWN AND PERSONNEL DISPATCHED TOTHE SITE. NOTIFICATIONS WERE MADE TO THE LOCAL FIRE DEPARTMENT AT 8:13 HOURS AND ILLINOIS EPA(#930-558-ILEPA) AND NOTIONAL RESPONSE CENTER (NR160948) AT09:45 HOURS. CLEAN-UP ACTIVITIES BEGAN AT APPROXIMATELY 10:30-11:00 HOURS.PRODCUT MIGRATED A SHORT DISTANCE OFF THE PUMP STATION GROUNDS BUT DID NOT REACH ANY SURFACE WATER. CLEAN-UP ACTIVITIES CONTINUED UNTIL ALL FREE LIQUID WAS PICKED UP.
2017-09-29 08:50 | NO | NO | 19930030 | 1993-03-15 | 809 | ARCO PIPE LINE CO | NO | 1993-02-04 | 1230 |  |  |  | YES | LATITUDE 29-05-30&LONGITU | NO |  |  | LINE PIPE | GIRTH |  | 1975 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | PIN HOLE IN WELD | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2 | 0 | NO | NO | 10 | 0.37 | 440 | WELDED |  | 550 | 450 | YES | 1 | 900 | 2 | 93 | NO DATA | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G POLING - COMPLIANCE COORIDINATOR | 7139865233 | ON FEBRUARY 3, 1993 A SHEEN OF UNKNOWN ORIGIN WAS SPOTTED BY HELICOPTER IN SOUTH PASS 6, OFFSHORE LOUISIANA, ALTHOUGH ARCO PIPE LINE COMPANY HAS A PIPELINE IN THE AREA, NO NOTICEABLE REDUCTION IN PRESSURE REGISTERED ON METERING EQUIPMENT. IN ORDER TO PROPERLY INVESTIGATE, A FOUR-ANCHOR BOAT WAS DISPATCHEDTO THE TO THE AREA ON FEBRUARY 5, 1993. ON FEBRUARY 6, 1993, THE TEAM ABORAD THE BOAD CONFIRMED THAT THE PIPELINE WAS LEAKING A SMALL QUANTITY OF CRUDE OIL. DURING THE INVESTIGATION ACTIVITIES, ARCO PIPE LINE COMPANY AND ARCO OIL AND GAS COMPANY MOBILIZED BOOM TO THE LOWER DECK OF A NEARBY PLATFORM AND CONTACTED CLEAN GULF TO BE ON STAND-BY NOTICE. DEPLOYMENT OF THESE SERVICESWERE NOT REQUIRED DURING THE LEAK INVESTIGATION AND MITIGATION. BECAUSE OF THE MINUTE QUANITY OF CRUDE OIL ON THE WARER, THE CURRENT AND SOME WAVE ACTION WERE SUFFICIENT TO DISPERSE THE LIGHT SHEEN. IN ZERO WATER VISIBILITY, DIVERS WORKED AROUND THE CLOCK TO LOCATE AND CLAMP THE SOURCE OF THE LEAK. PRESSURE WAS MAINTAINED ON THE PIPELINE ON ORDER TO LOCATE THE LEAK POINT DUE SUCCESSFULLY COMPLETING A PRESSURE TEST ON THE LINE, THE LEAK WAS CONSIDERED STOPPED. NO EVIDENCE OF THE SHEEN REMAINED.
2017-09-29 08:50 | YES | NO | 19930031 | 1993-03-30 | 22907 | WYCO PIPE LINE CO | YES | 1993-02-14 | 718 | WY | PLATTE |  | NO |  | NO | SE/4 OF SECTION 6 T27N R68W PLATTE COUNTY, WY. WYCO'S BEARCREEK PUMP STATION |  | PUMPING STATION | OTHER | NIPPLE 1/2 INCH | 0 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5150 | 3946.5685 | 7961.8227 | GASOLINE | 3 | 75 | 60 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | NIPPLE FATIGUE | Null | NO DATA |  | Null | Null | RONALD A WENKE - FILED SUPERVISOR | 3072373463 | ON 2/14/93 A TECHNICIAN FROM CASPER WAS DISPATCHED BY OUR TULSA CONTROL CENTER TO INVESTIGATE THE REASON FOR OUR BEAR CREEK STATION FAILING TO START. BEAR CREEK STATION IS LOCATED APPROXIMATELY 10 MILES SOUTH OF GLENDO, WY NEAR THE CASSA EXIT ON INTERSTATE 25. UPON ARRIVING AT APPROXIMATELY 7:45AM, THE TECHNICIAN DISCOVERED A GASOLINE LEAK IN THE PUMP STATION'S YARD. APPROXIMATELY 80 TO 100 BARRELS OF GASOLINE HAD LEAKED FROM A THREAD-A-LET WELDED TO THE MAINLINE WITH 1/2-INCH NIPPLE, VALVE AND A PRESSURE GAUGE ATTACHED. METAL FATIGUE IS SUSPECTED AS THE CAUSE OF THE NIPPLE'S FAILURE. A VACUUM TRUCK RECOVERED APPROXIMATELY 60 BARRELS OF FREE PRODUCT. THE REMAINING PRODUCT WAS FROZEN AND BECAME MIXED WITH SNOW IN THE STATION YARD, WHICH WAS PICKED UP AND CONTAINED ON PLASTIC SHEETING. CLEAN UP OF THE REMAINING SNOW AND PRODUCT MIXTURE COMMENCED THE MORNING OF MARCH 1, 1993, AND WAS COMPLETED ON MARCH 4TH. THIS INCIDENT WAS VERBALLY REPORTED TO THE NRC (NATIONAL RESPONSE CENTER)AT 8:47AM, REPORT #158005, THE WYOMING DEQ AT 9:14AM, THE PLATTE COUNTY SHERIFF'S DEPARTMENT WHO IN TURN NOTIFIED THE WYOMING HIGHWAY PATROL, THE WHEATLAND FIRE DEPARTMENT AND WYCO'S CORPORATE OFFICES IN CHICAGO, IL.
2017-09-29 08:50 | YES | NO | 19930032 | 1993-03-15 | 12127 | MARATHON PIPE LINE CO | YES | 1993-02-16 | 1800 | WY | PARK |  | NO |  | YES | OREGON BASIN PIPELINE PUMP STATION, STATION 8, T51N, R100W, APPROXIMATELY 12 MILES SE OF CODY, WYOMING. |  | PUMPING STATION | PUMP |  | 0 | OTHER | CAUSE UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1149485.9683 | 2318977.4937 | CRUDE OIL | 1 | 3100 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W C BEAUCHAMP - ENVIRON & SAFETY COORDINATOR | 4194213587 | A FIRE WAS DISCOVERED AT THE REFERENCED LOCATION AT APPROXIMATELY 1800 HOURSMST ON FEBRUARY 16, 1993. ALL RELEASED CRUDE OIL WAS CONSUMED IN THE FIRE OR CONTAINED WITHIN STATION SPILL CONTAINMENT BERMS. NO WATER WERE AFFECTED.THE NRC, USBLM, WY-DEQ, AND THE CODY FIRE DEPARTMENT WERE PROMPTLY NOTIFIED OF THE EVENT. WY-DEQ WILL BE CONSULTED REGARDING OILED SOIL DISPOSAL. DNV, AN INDEPENDENT CONSULTING FIRM FROM HOUSTON, TEXAS, HAS BEEN RETAINED TO CONDUCT AN INVESTIGATION OF THE CAUSE OF THE FIRE. A FINAL INVESTIGATION REPORT IS EXPECTED ON OR BEFORE MARCH 19, 1993.
2017-09-29 08:50 | NO | NO | 19930033 | 1993-03-02 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1993-02-02 | 1100 | CA | RIVERSIDE |  | NO |  | NO | WEST OF I215, SOUTH OF EASTRIDGE AVENUE THOMAS BROS. PAGE 14, E-6 LS51, PLMP 12.59 |  | LINE PIPE | PIPE |  | 1990 | OTHER | LINE SPLASHED BACK DURING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 12261.1837 | 24735.7599 | JET FUEL | 3 | 4 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J M ABBOUD - SENIOR V.P. - OPERATIONS & ENGINEERING | 2134867720 | DURING PIPE REPLACEMENT APROX. 3-4 BARRELS OF JP-4 MILITARY JET FUEL WERE SPILLED. CONTAMINATED SOIL REMOVED AND WILL BE DISPOSED OF PROPERLY.
2017-09-29 08:50 | YES | NO | 19930034 | 1993-03-05 | 2552 | COLONIAL PIPELINE CO | YES | 1993-02-05 | 1015 | NC | GUILFORD |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S GREENSBORO JUNCTION. |  | TANK FARM | TANK |  | 1963 | OTHER | MECHANICAL FAILURE OF RUP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4597.9439 | 9275.91 | GASOLINE | 2 | 15 | 12 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J A COX - MGR, TECHNICAL & REGULATORY | 4048412296 | AT 1015 EST ON FEBRUARY 5, 1993, OPERATOR PERSONNEL, DURING A VISUAL INSPECTION AT THE GREENSBORO TANK FARM DISCOVERED GASOLINE LEAKING FROM THE "FOAM-MAKER" (AERATOR) LOCATED ADJACENT TO TANK 825. THIS AERATOR IS PART OF COLONIAL'S FIRE PROTECTION SYSTEM DESIGNED TO DELIVER FOAM TO THE TANK IN THE EVENT OF ROOF SEAL FIRES. THE LEAK WAS STOPPED BY CLOSING THE 4" FAOM LINE VALVE.COMPANY AND CONTRACTOR PERSONNEL ON SITE WERE ABLE TO CONTAIN THE GASOLINE IN THE TANK DIKE AND PREVENT THE PRODUCT FROM ENTERING THE STATION RETENTION POND. THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 156721) AT 1102 EST WHEN IT BECAME APPARENT THAT THE DAMAGE RELATED COSTS WOULD EXCEED $5,000.00. AS A COURTESY, THE SOUTHERN REGION OF THE OFFICE OF PIPELINE SAFETY AND THE NORTH CAROLINA DIVISION OF ENVIRONMENTAL MANAGEMENT (NCDEM) WERE NOTIFIEDOF THE LEAK. AN INVESTIGATION REVEALED THAT THE MECHANICAL FAILURE OF A RUPTURE DISK IN A " DIAMETER FIRE FOAM LINE CAUSED THE GASOLINE TO ENTER THE FIRE SYSTEM PIPING. APPROXIMATELY 15 BARRELS OF GASOLINE ESCAPED FROM TANK 825. OF THIS TOTAL, 12 BARRELS WERE RECOVERED AND RETURNED TO THE SYSTEM AND THEREMAINING 3 BARRELS WERE LOST OF EVAPORATION AND ABSORPTION. THE CONTAMINATED SOIL HAS BEEN STOCKPILED IN AN IMPERVIOUS ENVELOPE AND WAITS DISPOSAL.
2017-09-29 08:50 | YES | NO | 19930035 | 1993-03-04 | 443 | AMOCO PIPELINE CO | YES | 1993-02-09 | 750 | WY | PARK |  | NO |  | NO | SW 1/4, SECTION 15, R101W, T51N (TRACK 71, LOT1) |  | PUMPING STATION | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 383.162 | 772.9925 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 12.75 | 0.31 | 35000 | WELDED |  | 1237 | 800 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R E PETERSON | 3072662119 | THE SPILL OCCURRED 200' NORTHWEST OF AMOCO PIPELINE'S OREGON STATION ON PRIVATE PROPERTY LOCATED IN LOT 1, TRK. 71,T.51N R.101W IN PARK COUNTY. THE SPILLRAN 600' DOWN A DRAW WHERE A DAM WAS CONSTRUCTED, AND THE SPILL WAS CONTAINED. AN ESTIMATED 100 BARRELS WAS SPILLED AND ESTIMATED 90 BARRELS WAS RECOVERED. THE LEAK WAS CAUSED FROM INTERNAL CORROSION ON A 50' RUNAROUND OFF OF APL 12" ELK BASIN LINE. SUBSEQUENT TO THE LEAK, THE RUNAROUND HAS BEEN DISCONNECTED FROM THE 12" MAINLINE AND IS NO LONGER IN SERVICE.
2017-09-29 08:50 | YES | NO | 19930036 | 1993-03-08 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1993-02-03 | 1715 | MI | LAPEER | NORTH BRANCH | NO |  | NO | SITE IS APPROX 3.5 MI. NW OF TOWN OF NORTH BRANCH, MI, E BARNES RD/SIVERWOOD RD INTERSECTION. LAKEHEAD'S MILEPOST 1686.2 DOWNSTREAM(SE) OUR N BRANCH,MI PUMP STA |  | LINE PIPE | PIPE |  | 1953 | OTHER | 1/4" DEEP FLAT SPOT IN PI | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 153264.7958 | 309196.9992 | CRUDE OIL | 1 | 5 | 1 | NO | NO | 30 | 0.28 | 52000 | WELDED |  | 617 | 441 | YES | 4 | 771 | 10 | 66 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E STAUDOHAR - SECRETARY & GENERAL MANAGER CORPORATE SERV | 7153941404 | ON FEBRUARY 3, 1993, 17:15 MST, LAKEHEAD'S SUPERIOR CONTROL CENTER RECEIVED A CALL FROM A LANDOWNER REPORTING CRUDE OIL IN A DITCH NEAR OUR LINE 5, NORTHBRANCH, MI PUMP STATION. THE LINE WAS SHUTDOWN AT 17:16 MST AND COMPANY PERSONNEL WERE DISPATCHED TO THE AREA. THE LEAK WAS CONFIRMED AND WAS LOCATED JUST DOWNSTREAM OF THE PUMP STATION IN THE SILVERWOOD ROAD EAST DITCH. EXCAVATION REVEALED A 1/4" DEEP FLAT SPOT IN THE PIPE, APPROXIMATELY 12" X 12" CONTAINING A 4-3/4" CRACK RUNNING HORIZONTALLY WITH THE PIPE. NO EXTERNAL CORROSION WAS EVIDENT AND THE CAUSE OF THE ANOMALY IS UNKNOWN. THE LEAK WAS REPAIRED WITH A PLIDCO SLEEVE AND THE LINE RETURNED TO SERVICE ON FEBRUARY 4, 1993,08:45 MST. ON FEBRUARY 18, LAKEHEAD CHOSE TO CUT-OUT AND REPLACE THE JOINT OF PIPE AND ACCORDINGLY, TOTAL PROPERTY DAMAGES REFLECT THIS DECISION. THE NATIONAL RESPONSE CENTER WAS NOTIFIED ON FEBRUARY 3, AT 18:30 MST, AND THE MICHIGAN DEPARTMENT OF NATURAL RESOURCES WAS ALSO NOTIFIED AT 18:30, FEBRUARY 3.INCIDENT INFORMATION WAS PROVIDED TO MR. ROLAND MILLER OF THE OFFICE OF PIPELINE SAFETY - CENTRAL REGION ON THE MORNING OF FEBRUARY 4 ALONG WITH AN INCIDENT UPDATE THAT SAME AFTERNOON.
2017-09-29 08:50 | NO | NO | 19930037 | 1993-03-09 | 1682 | BP OIL PIPELINE CO | NO | 1993-02-08 | 1520 | LA | PLAQUEMINES | BAYOU CHALAND | NO |  | NO | EAST SIDE OF BAYOU CHALAND IN SMALL BAYOU |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | CRUDE OIL | 1 | 5 | 1 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 1100 | 500 | YES | 8 | 1378 | 1 | 89 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | L L OWEN - REGION SUPERINTENDENT | 5043926601 | ON FEBRUARY 8, 1993, AT APPROXIMATELY 1520 HOURS, J.J. O'CONNELL, BP OIL PIPELINE COMPANY SUPERVISOR WAS FLYING THE PIPELINE ROUTE AND SPOTTED AN OIL SHEEN NEAR BAYOU CHALAND. THE BP PIPELINE WAS IMMEDIATELY SHUTDOWN AND MAINTENANCE PERSONNEL SENT TO INVESTIGATE. IT WAS CONFIRMED AT APPROXIMATELY 1700 HRS. SHEEN WAS COMING FROM THE 12 INCH LOOP LINE. SORBENT PADS WERE DEPLOYED TO PICKUP THE SMALL QUANTITY OF FREE OIL POCKETED NEAR THE TENNESSEE GAS BULKHEAD. TEMPORARY REPAIRS WERE COMPLETED ON FEBRUARY 12 BY WELDING A FULL ENCIRCLEMENT ON THE PIPELINE. PERMANENT REPAIRS WERE COMPLETED FEBRUARY 16 BY REPLACING THE SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19930038 | 1993-03-08 | 443 | AMOCO PIPELINE CO | YES | 1993-02-17 | 1200 | TX | HOCKLEY |  | NO |  | NO | GO SOUTH OF SUNDOWN, TEXAS ON HIGHWAY 303 FOR 3 MILES, SLAUGTHER STATION IS ON NORTH SIDE OF HIGHWAY |  | TANK FARM | VALVE | RELIEF VALVE OUTAGE | 1944 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 4214.7819 | 8502.9175 | CRUDE OIL | 1 | 330 | 320 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 210 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALBERT L WOOD, JR. - PLMF | 8068977027 | REMOTELY ACTUATED UNATTENDED VALVE WAS INADVERTANTLY CLOSED AT STATION CLOSED AT STATION MANIFOLD. INCREASED IN PRESSURE DUE TO SHUT IN CAUSED A DOWNLINE RELIEF VALVE TO ACTUATE. UPON ACTUATION OIL WAS RELIEVED TO GROUND.
2017-09-29 08:50 | YES | NO | 19930039 | 1993-04-02 | 1248 | BELLE FOURCHE PIPELINE CO | YES | 1993-03-01 | 1130 | MT | CARTER |  | NO |  | YES | NE/4SE/44 SECTION 10, T8S-R57E |  | LINE PIPE | PIPE |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11494.8597 | 23189.7749 | CRUDE OIL | 1 | 50 | 40 | NO | NO | 8 | 0.19 | 42000 | WELDED |  | 600 | 450 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVE RIEGER - ENGINEER | 3072660235 | PIPE FAILED ALONG A LONGITUDINAL SEAM IN A JOINT OF PRE-1970 ERW PIPE. THE FAILURE OCCURRED UNDERGROUND APPROXIMATELY 35 FEET FROM A PIG LAUNCHER.
2017-09-29 08:50 | NO | NO | 19930040 | 1993-03-31 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-03-04 | 830 | AL | SHELBY | HELENA | NO |  | NO | TANK 26 - PLANTATION'S HELENA TANK FARM LOCATED OFF SHELBY COUNTY ROAD NO. 52, HELENA, ALBAMA. |  | TANK FARM | TANK |  | 1941 | OTHER | FIVE CRACKS IN THE FLOOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 19200 | 14713.4204 | 29682.9119 | GASOLINE | 3 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VICE PRESIDENT-OPERATIONS | 4043645916 | ON THE MORNING OF MARCH 4, 1993, WHILE DRAWING WATER OFF TANK 26, A PLANTATION UTILITY OPERATOR DISCOVERED A DISCOLORATION ON THE SKETCH PLATE. THE TANKWAS TAKEN OUT OF SERVICE, CLEANED AND INSPECTED. THE INSPECTION REVEALED FIVE CRACKS IN THE FLOOR PLATE ADJACENT TO THE SUMP. THE TANK WILL REMAIN OUT OF SERVICE UNTIL REPAIRS CAN BE SCHEDULED.
2017-09-29 08:50 | NO | NO | 19930041 | 1993-03-25 | 443 | AMOCO PIPELINE CO | YES | 1993-03-02 | 1630 | IL | WILL | MANHATTAN | NO |  | NO | 15600 BRUNS ROAD, MANHATTAN, IL 60442. 1/2 MILE SOUTH OF MANHATTAN ON HWY 52. 1/2 WEST OF HWY 52 ON BRUNS ROAD. |  | TANK FARM | OTHER | DRAIN TILES THAWED RELEAS | 1950 | OTHER | FAILURE OF A TANK ROOF DR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | CRUDE OIL | 1 | 20 | 15 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | P J MCGANNON - AREA MANAGER | 2197382384 | ON MARCH 2, 1993 AMOCO PIPELINE PERSONNEL, RESPONDING TO A NOTIFICATION, DISCOVERED A CRUDE OIL RELEASE INTO PRAIRIE CREEK. AT 1750 HRS NOTIFICATION WASMADE TO THE NRC, REPORT # 160395. THE ORIGIN OF THE RELEASE WAS DRAIN TILES, WHICH CARRY STORMWATER FROM AMOCO'S MANHATTAN TANKFARM, WHICH HAD THOWED RELEASING TRAPPED CRUDE OIL INTO THE NEARBY CREEK. UPON INVESTIGATION, IT WAS REVEALED A PREVIOUSLY UNDISCOVERED DRAIN TILE, PRESUMABLY INSTALLED BY A FARMER PRIOR TO THE TANK FARM'S CONSTRUCTION, HAD FILLED WITH CRUDE OIL AS A RESULT OF A TANK ROOF DRAIN LINE FAILURE WHICH HAD OCCURRED ON FEBRUARY 14, 1993.AT THIS TIME IT APPEARED THAT THE NON-DOT REPORTABLE RELEASE WAS CONTAINED WITH THE TANK DIKE AND CLEAN-UP WAS HANDLED ACCORDINGLY. SUBSEQUENT TO THE MARCH 2, 1993 DISCOVERY, DRAIN TILE WAS FOUND BENEATH THE TANK DIKE.
2017-09-29 08:50 | NO | NO | 19930042 | 1993-04-06 | 2190 | CENTRAL FLORIDA PIPELINE CORP | NO | 1993-03-12 | 937 | FL | OSCEOLA | LAKE ALFRED | NO |  | NO | LOCATION PARALLEL TO CSX MAIN LINE TRACK- 1/2 MILE W PIERCE ST ON OLD LAKE ALFRED RD AT LAKE ALFRED CITY LIMITS(CSX MP838). LOCATION ON SIDE OF TRACKS-COCACOLA |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 30652.9592 | 61839.3998 | DIESEL FUEL | 1 | 10 | 0 | NO | NO | 6.63 | 0.19 | 61200 | WELDED |  | 1200 | 1000 | YES | 24 | 1500 | 3 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | DAVID COFFEE - PIPELINE ENGINEER | 8132482148 | MARCH 12, 1993, AT 0937, OPERATOR FRANK DAVIS RECEIVED A CALL FROM FIRE CHIEF LARRY CLOUD OF THE LAKE ALFRED FIRE DEPARTMENT (813-956-3214) REPORTING A LEAK ON ONE OF OUR FUEL LINES. BOTH THE 6 AND 10 INCH PIPELINES WERE SHUT DOWN. ASSISTANT PIPELINE MANAGER, EDDIE FOSTER, RESPONDED IMMEDIATELY TO THE SCENE AND DETERMINED THAT THE LEAK WAS FROM THE 6 INCH DISTILLATE PIPELINE. EMERGENCY RESPONSE PERSONNEL AND EQUIPMENT WERE DISPATCHED IMMEDIATELY. A PIN HOLE APPROXIMATELY 1/16 INCH IN DIAMETER WAS FOUND. "JET A" FUEL SPRAYED AN AREA ABOUT 50 FOOT IN DIAMETER. THE CONTAMINATED SOIL WAS EXCAVATED ONTO VISQUENE AND COVERED. THE PIPE WITH THE HOLE WAS CUT OUT AND ASECTION OF PIPE APPROXIMATELY 11 FEET WAS WELDED INTO PLACE. THE NEW PIPE HAD PREVIOUSLY BEENPRESSURE TESTED. THE WELDS WERE X-RAYED. THE PIPE WAS PRIMED AND RE-COATED. THE PIPELINE WAS LOWERED AN ADDITIONAL 2 FEET AND BACKFILLED.
2017-09-29 08:50 | YES | NO | 19930044 | 1993-04-12 | 443 | AMOCO PIPELINE CO | YES | 1993-03-20 | 1445 | TX | KENT |  | NO |  | NO | GO APPRO 25 MILES N OF SNYDER TO JUSTICBURG. GO E ON LAKE ALAN HENRY RD TO DAM. ACCIDENTAL PUNCTURE IS 1/2 MILES E OF DAM. SECTION 56 H &G.N.R.R. CO. BLK.5 |  | LINE PIPE | NO DATA |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 383.162 | 772.9925 | CRUDE OIL | 1 | 1000 | 975 | NO | NO | 8 | 0.32 | 0 | WELDED |  | 860 | 150 | YES | 4 | 575 | 10 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | ANTHONY WOFFORD - PIPELINE MAINT. FOREMAN | 9155733589 | CONTRACTOR HAS BEEN WORKING IN AREA FOR A COUPLE OF YEARS CONSTRUCTING EARTHERN DAM. CONTRACTOR EMPLOYEE WAS MOVING DIRT IN THE AREA WHERE THE LINE WAS STRUCK. CONTRACTOR EMPLOYEE WAS AWARE OF LINE BUT JUST MISJUDGED DEPTH AND EXACT LOCATION.L MARKERS WERE CLEARLY VISIBLE ON BOTH SIDES OF WHERE LINE WASDAMAGED. THE AMOCO PIPELINE FACILITY INVOLVED IN THIS INCIDENT IS THE COGDELL TO POST PIPELINE.
2017-09-29 08:50 | YES | NO | 19930046 | 1993-04-30 | 22907 | WYCO PIPE LINE CO | YES | 1993-04-09 | 1620 | SD | PENNINGTON | RAPID CITY | NO |  | NO | WYCO PIPELINE'S RAPID CITY, S.D. TERMINAL 3225 EGLIN ST., RAPID CITY, S.D. NE 1/4, NW 1/4, SEC 33, TN 2N R8E |  | TANK FARM | OTHER | INTERNAL DRAIN LINE HOSE | 1962 | OTHER | TANK ROOF DRAIN LINE HOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5450 | 4176.4657 | 8425.6182 | GASOLINE | 3 | 300 | 250 | Null | Null | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RONALD A WENKE - FIELD SUPERVISOR | 3072373463 | ON APRIL 9, 1993 COMPANY PERSONNEL DISCOVERED A GASOLINE RELEASE AT OUR RAPID CITY TERMINAL FROM TANK #6 WITHIN THE TANK DIKE. AT APPROXIMATELY 5:18PM MDT TELEPHONIC NOTIFICATION WAS MADE TO THE NRC, REPORT #166711. THE ORIGIN OF THE RELEASE WAS THE TANK DRAIN LINE. THE RELEASE WAS MOSTLY CONFINED TO THE TANK DIKE AREA. A SMALL AMOUNT OF PRODUCT MIGRATED OFF SITE TO A STORM WATER POND ADJACENT TO OUR PROPERTY. OF THE 300 BARRELS RELEASED, 250 BARRELS WERE RECOVERED AND RETURNED TO STORAGE. THE SMALL AMOUNT THAT MIGRATED OFF OUR PROPERTY WAS ABSORBED AND COLLECTED AND CLEANED UP BY THE RAPID CITY HAZMATTEAM. THE DRAIN LINE VALVE AT THE TANK SHELL HAS BEEN FLANGED.
2017-09-29 08:50 | YES | NO | 19930047 | 1993-04-15 | 10313 | KOCH PIPELINE INC | YES | 1993-03-29 | 810 | MO | HARRISON |  | NO |  | NO | KOCH PIPELINES BETHANY TANK TERMINAL, TANK #33 |  | TANK FARM | TANK |  | 0 | OTHER | TANK OVER RUN CAUSED BY | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 114948.5968 | 231897.7494 | CRUDE OIL | 1 | 6600 | 6517 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK M MCCANN | 6124584860 | THE ACCIDENT WAS CAUSED BY MIXTURE OF CRUDE OIL AND NIRTOGEN GAS ENTERING TANK 33 DURING A 20" WOOD RIVER PIPELINE PURGING OPERATION. THE TANK WAS NEAR CAPACITY AT THE OF THE ACCIDENT. THE CRUDE OIL WAS FORCED OUT OF THE TANK THROUGH THE ROOF SEAL INTO SECONDARY CONTAINMENT.
2017-09-29 08:50 | YES | NO | 19930048 | 1993-04-14 | 26065 | NATIONAL COOP REFINERY ASSCO | YES | 1993-03-19 | 825 | IA | POTTAWATTAMIE |  | NO |  | NO | NCRA MILE POST NO. 227 - NORTH 410 FEET LOCATED IN THE NW1/4, SECTION 19, T74N, R44W, POTTAWATTAMIE COUNTY, IOWA. |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | GASOLINE | 1 | 365 | 365 | Null | Null | 6.63 | 0.25 | 35000 | WELDED |  | 560 | 23 | YES | 24 | 700 | 5 | 67 | NO DATA | Null | YES | NO DATA | DNA | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | DOUGLAS D. GRAUER, P.E. - PRODUCTS PIPELINE AND TERMINAL SUP | 9132267781 | ON FRIDAY, MARCH 19, 1993 AT 8:25 A.M., CLARENCE GRAHAM WORKING FOR HAVENS CONST. CO., INC. - (HAVENS), LIBERTY, MISSOURI, HIT THE SIX (6) INCH NCRA PRODUCTS PIPELINE WITH A CATERPILLAR 245B TRACKHOE. THE TRACKHOE BUCKET PUNCTURED A HOLE IN THE PIPELINE - 2IN. X 3 1/2 IN. AND ALSO DENTED THE PIPELINE IB THREE OTHER LOCATIONS. APPROXIMATELY THREE HUNDREDAND SIXTY-FIVE (365) BARRELS OF NO-LEAD GASOLINE ESCAPED INTO A FORTY-EIGHT (48) INCH DIAMETER SEWER MAIN AND THE THREE (3) FOOT GRAVEL BAS AT A BELL HOLE THAT WAS BEING EXCAVATED FOR THE INSTALLATION OF A MANHOLE. HAVENS HAD BEEN CONTRACTED BY THE CITY OF COUNCIL BLUFFS, IOWA TO INSTALL THE FORTY-EIGHT (48) INCH DIAMETER SEWER MAIN. THE NCRA PRODUCTS PIPELINE WAS CLEARLY MARKED WAS REQUIRED BY DOT 195.410 AND THE CLOSEST MARKER WAS EIGHTY (80) FEET NORTH OF THE ACCIDENT IN A NORTH-SOUTH FENCE LINE. THE CONSULTING ENGINEER, WELLS ENGINEERS ENVIRONMENTAL, INC. WHO DESIGNED THE PROJECT, AND THE CITY OF COUNCIL BLUFFS, IOWA WERE AWARE OF BOTH THE EXISTENCE AND THE LOCATION OF THE PIPELINE. NCRA PRODUCTS PIPELINE WAS NOT NOTIFIED, EITHER BY TELEPHONE OR VIA IOWA UNDERGROUND PLANT LOCATION SERVICE, INC. THAT THE FORTY-EIGHT (48) INCH DIAMETER SEWER MAIN WAS BEINGCONSTRUCTED IN THE VICINITY OF THE PRODUCTS PIPELINE. NCRA PRODUCTS PIPELINE WAS CONTACTED ABOUT THE ACCIDENT BY KENNY LESLIE, THE SUPERINTENDENT FOR HAVENS AT 8:35 A.M. THE PIPELINE WAS SHUT DOWN BY 8:41 A.M. THE MAINLINE BLOCKVALVES WERE CLOSED ON EACH SIDE OF THE ACCIDENT BY 9:12 A.M. THE DAMAGED SECTION OF LINE PIPE - ONE HUNDRED AND SISTEEN AND ONE-HALF (116 1/2) INCHES LONG WAS CUT OUT AND REPLACED WITH ANOTHER SECTION. THE NEW SECTION OF LINE PIPE SPECIFICATIONS ARE LISTED BELOW: OUTSIDE DIAMETER - 6.625 IN. WALL THICKNESS - .432 IN. API 5L GRADE B . SEAMLESS. HYDROSTATICALLY TESTED TO 1700 PSIG. ON MAY 5, 1981. THE WELDS WERE X-RAYED BY PROFESSIONAL SERVICE INDUSTRIES, INC. -(PSI) - OMAHA, NEBRASKA AND PASSED API 1104. THE SOMASTIC COATINGWAS REPLACED WITH ROYSTON PRIMER AND GREENLINE TAPE. THE NCRA PRODUCTS PIPELINE WAS STARTED BACK UP ON FIRDAY, MARCH 19, 1993 AT 11:52 P.M. CLEANUP OF THE NO-LEAD GASOLINE LOST BEGAN ON FRIDAY, MARCH 19, 1993 AT 10:15 A.M. AND WAS COMPLETED ON WEDNESDAY, MARCH 24, 1993 AT 12:00 P.M. A TOTAL OF THREE HUNDRED AND SIXTY-FIVE (365) BARRELS OF NO-LEAD GASOLINE WAS RECOVERED.
2017-09-29 08:50 | YES | NO | 19930049 | 1993-04-30 | 2552 | COLONIAL PIPELINE CO | YES | 1993-03-28 | 849 | VA | FAIRFAX |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000000 | 7663239.7888 | 15459849.9583 | FUEL OIL | 2 | 9708 | 8463 | NO | NO | 36 | 0.34 | 52000 | WELDED |  | 687 | 484 | YES | 24 | 858 | 10 | 80 | NO DATA | Null | Null | NO DATA |  | OTHER | UNDER INVESTIGATION | Null | NO DATA |  | Null | Null | J A COX - MGR. - TECHNICAL & REGULATORY | 4048412296 | AT 0849 EST ON MARCH 28, 1993, THE CONTROLLER OPERATING COLONIAL'S 36" LINE 03 OBSERVED A RAPID, SIGNIFICANT SUCTION PRESSURE DROP AT THE DORSEY JUNCTIONPUMP STATION LOCATED NEAR WOODBINE, MD WHICH INDICATED A POSSIBLE LEAK BETWEEN CHANTILLY PUMP STATION NEAR FAIRFAX, VA AND DORSEY JUNCTION. THE BALTIMORE AREA MANAGER WAS NOTIFIED AT 0851 EST AND IMMEDIATELY BEGAN THE PROCESS OF INSTITUTING COLONIAL'S EMERGENCY RESPONSE NOTIFICATION AND MOBILIZATION. AT 0927 EST THE ATLANTA CONTROL CENTER WAS NOTIFIED BY THE FAIRFAX, VA COUNTY POLICE THAT A LEAK EXISTED IN THE AREA ADJACENT TO THE RESTON HOSPITAL CENTER.COLONIAL PERSONNEL BEGAN ARRIVING AT THE LEAK SITE AT 0942 EST AND BEGAN INITIAL CONTAINMENT ACTIVITIES. AT 1004 EST NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER (REPORT NO. 164492). AT 1010 EST, NOTIFICATION WAS MADE TO THE EASTERN REGION, OFFICE OF PIPELINE SAFETY. AT 1020 EST, NOTIFICATION WAS MADE TO THE NATIONAL TRANSPORTATION SAFETY BOARD. IN ADDITION THE U.S. COAST GUARD, THE VIRGINIA DEPARTMENT OF ENVIRONMENTAL QUALITY AND THE MARYLAND DEPARTMENT OF THE ENVIRONMENT WERE ALSO ADVISED OF THE LEAK. CONTAINMENT BOOMS WERE DEPLOYED AT SEVERAL LOCATIONS ON THE SUGARLAND RUN, A TRIBUTARY OF THE POTOMAC RIVER TO CONTAIN THE 9,708 BARRELS OF FUEL OIL CALCULATED TO HAVE ESCAPED THROUGH FROM THE RUPTURE. AS OF 4/16/93, 8449 BARRELS OF PRODUCT HAVEBEEN RECOVERED. RECOVERY ACTIVITIES ARE CONTINUING. THE INVESTIGATION INTOTHE CAUSE OF THE INCIDENT IS CONTINUING. REPAIRS TO THE PIPELINE WERE MADE BY REMOVING THE DAMAGED PIPE AND INSTALLING 36" O.D., 0.344" W.T., X-52 GRADE PIPE THAT HAD PREVIOUSLY BEEN HYDORSTATICALLY TESTED.
2017-09-29 08:50 | YES | NO | 19930050 | 1993-04-14 | 4906 | EXXON PIPELINE CO | NO | 1993-03-10 | 1352 | TX | HARRIS | HOUSTON | NO |  | NO | APPROXIMATELY 3/4 MILE SW OF INTERSECTION OF HOLMES ROAD AND ALMEDA ROAD IN SOUTHWEST HOUSTON, HARRIS COUNTY, TEXAS |  | LINE PIPE | PIPE |  | 1928 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9195.8877 | 18551.8199 | CRUDE OIL | 1 | 61 | 60 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 908 | 161 | YES | 8 | 772 | 10 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J B HOLT, MANAGER ENVIRONMENTAL & REGULATORY COMP. DEPT | 7136565521 | THE PIPELINE WAS DAMAGED BY A DOZER GRADING A DITCH. RELEASED OIL WAS CONTAINED IN ROAD DITCHES BY THE CONSTRUCTION OF EARTHEN BERMS. THE OIL WAS THEN PULLED DIRECTLY BACK INTO THE PIPELINE BY RUNNING SYSTEM DOWNSTREAM PUMPING UNITS. THE DAMAGED PIPE WAS CUT OUT AND REPLACED WITH NEW PIPE. THE INCIDENTWAS REPORTED TO THE NRC AT 3:18 ON 3/10/93 TO PETTY OFFICE POMPILIO, NRC REPORT # 161622.
2017-09-29 08:50 | NO | NO | 19930051 | 1993-04-14 | 19226 | TEXACO PIPELINE INC | NO | 1993-03-16 | 1100 | TX | DALLAS | DALLAS | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1947 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | GASOLINE | 3 | 21 | 19 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 500 | 95 | YES | 0 | 1000 | 1 | 48 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | B L LEDNICKY - DISTRICT MGR | 7139534260 | AT 7:00 AM ON MARCH 16, 1993, THE HEARNE TO DALLAS 10" MAINLINE WAS SHUT DOWN AND STOPPLED TO TIE IN NEW 2 MILE SECTION OF 10" AT MP 140 AND REPLACE CORRODED RR CROSSING AT MP 142.5. THE LINE WAS COLD CUT PREMATURELY AT 10:45 AM WITH APPROXIMATELY 95 PSI OF NITROGEN AND GASOLINE RELEASED TO THE ATMOSPHERE.
2017-09-29 08:50 | YES | NO | 19930052 | 1993-04-19 | 22907 | WYCO PIPE LINE CO | YES | 1993-03-27 | 1751 | CO | EL PASO | FOUNTAIN | NO |  | NO | WYCO PIPE LINE CO - FOUNTAIN TERMINAL, 1004 S. SANTE FE STREET, FOUNTAIN, CO 80817-2047 |  | TANK FARM | OTHER | NON SPECIFIED | 1967 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 45979.4387 | 92759.0997 | DIESEL FUEL | 1 | 142 | 45 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  | 3032866400 | 3-27-93 16:49 CST CONTROLLER ON DUTY AT TULSA CONTROL CENTER RECEIVED SOFTWARE ALARM AT 36 FEET. 17:51 CST CONTROLLER RECIEVED HIGH-HIGH-ALARM, ACKNOWLEDGED ALARM BUT DID NOT SWITCH TO ANOTHER TANK. 18:55 CST TECHNICIAN CALLED OUT & CONFIRMED OUTAGE, OUTAGE CONTAINED WITHIN TANK DIKE. 23:30 CST VACCUM TRUCKS ARRIVED AT LOCATION. DELAYED DUE TO WHITEOUT SNOW CONDITIONS ON MONUMENT HILL OVERPASS. 3-28-93 01:00 CST COMPLETED RECOVERY OF PRODUCT IN LIQUID FORM. SOIL REMEDIATION WITHIN THE TANK DIKE IS PRESENTLY BEING PLANNED.
2017-09-29 08:50 | YES | NO | 19930053 | 1993-04-07 | 879 | CHEMOIL REFINING | NO | 1993-03-05 | 700 | CA | LOS ANGELES | LONG BEACH | NO |  | NO | PORT OF LONG BEACH - PIER J- BERTH 247 |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 34484.579 | 69569.3248 | FUEL OIL | 2 | 22 | 20 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MILO SOTO - PIPELINE SUPT. | 3104248515 | EARTH TECHNOLOGY CORPORATION, SUBCONTRACTOR TO GLOFON INCORPORATED, USING A HYDROLIC SAMPLER PUNCHED A ONE AND ONE HALF (1 1/2) INCH HOLE THROUGH THE 16 INCH PIPELINE ALLOWING SOME OF THE STATIC VOLUME OF THE PIPELINE TO ESCAPE. THE PIPELINE WAS NOT IN USE AT THE TIME. MAIN LINE BLOCK VALVES WERE CLOSED.
2017-09-29 08:50 | NO | NO | 19930054 | 1993-04-12 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1993-03-18 | 1245 | CA | LOS ANGELES | CARSON | NO |  | NO | 2160 SEPULEVA BLVD |  | NO DATA | OTHER | VACUUM TRUCK HOSE | 0 | OTHER | UNKNOWN - VACUUM TRUCK HO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 9962.2117 | 20097.8049 | CRUDE OIL | 1 | 5 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. KELLEY - SOUTHERN DISTRICT MANAGER | 8053270110 | FLUSHING LIGHT CRUDE FROM 8" PIPELINE INTO VACUUM TRUCK WITH WATER, AT APPROXIMATELY 10 PSI VACUUM TRUCK HOSE SPLIT. HOSE RATED FOR 150 PSI.
2017-09-29 08:50 | YES | NO | 19930055 | 1993-04-23 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1993-03-27 | 1730 | TX | HARRIS |  | NO |  | NO | DECKER DRIVE (LOOP 330) AT BAKER ROAD |  | TANK FARM | OTHER | TANK | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 42895 | 32871.4671 | 66315.0264 | GASOLINE | 1 | 7560 | 4634 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM - VICE PRESIDENT - OPERATIONS | 7137593615 | A MISCALCULATION OF THE ESTIMATED TIME OF FILL ON AN UNLEADED REGULAR GASOLINE TANK RESULTED IN THE OVERFILLING OF THE TANK. UPON DISCOVERY, THE OPERATOR IMMEDIATELY SHUT OFF FLOW TO THE TANK AND STOPPED THE OVERFLOW OF PRODUCT.ALL SPILLED PRODUCT WAS CONTAINED WITHIN THE TANK CONTAINMENT DIKE. THERE WERE 4,634 BBLS OF PRODUCT TRANSFERRED FROM THE CONTAINMENT DIKE TO ADJACENT STORAGE TANKS, 2,921 BBLS. WERE LOST TO EVAPORATION AND 5 BBLS. LOST TO ABSORPTION INTO THE SOIL IN CONTAINMENT DIKE AREA. THIS IS TO BE REMEDIATED IN-SITU
2017-09-29 08:50 | YES | NO | 19930056 | 1993-04-23 | 443 | AMOCO PIPELINE CO | YES | 1993-03-25 | 500 | IL | LIVINGSTON | PONTIAC | NO |  | NO | FLANAGAN STATION, ROUTE 23, 2 MILES N OF I-55 NEAR PONTIAC, ILLINOIS. |  | TANK FARM | OTHER | TANK ROOF DRAIN LINE ON # | 1960 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | FAILURE OF TANK ROOF DRAI | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | CRUDE OIL | 1 | 1000 | 990 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | P J MCGANNON - AREA MANAGER | 2197382384 | ON MARCH 25, 1993 AMOCO PIPELINE'S CONTROL CENTER NOTED A CHANGE IN TANK LEVEL OF A STATIC TANK. AMOCO PIPELINE PERSONNEL RESPONDED AND DISCOVERED CRUDEOIL IN THE DIKE OF FLANAGAN STATION TANK #1411. AT 0850 HOURS, NOTIFICATION EAS MADE TO THE NRC, REPORT #163991. UPON INVESTIGATION IT WAS REVEALED THATA TANK ROOF DRAIN RELEASED THE OIL TO THE DIKE. AT APPROXIMATELY 1700 HOURS, DURING THE COURSE OF CLEANUP, THE OIL IN THE DIKE AREA BEGAN TO DRAIN TO A PREVIOUSLY UNDISCOVERED DRAIN TILE BENEATH THE DIKE AREA. THE DRAIN TILE, WHICH WAS PRESUMABLY LAID BY A FARMER PRIOR TO THE TANK FARM'S CONSTRUCTION, CARRIED THE OIL OFF THE PROPERTY TO A DRAINAGE DITCH. AT 1930 HOURS, THE NRC WAS UPDATED REGARDING THIS DEVELOPMENT.
2017-09-29 08:50 | NO | NO | 19930057 | 1993-04-22 | 809 | ARCO PIPE LINE CO | NO | 1993-03-22 | 1330 | TX | GREGG |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 6 | 0.28 | 0 | NO DATA |  | 202 | 20 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G POLING - COMPLIANCE COORDINATOR | 7139865233 | ON MARCH 22, 1993, AN EXTERNAL CORROSION LEAK WAS DISCOVERED ON A SPAN THAT CROSSED RABBIT CREEK IN GREGG COUNTY. IMMEDIATELY, TWO SPILL BOOMS WITH SOCKBOOMS IN FRONT WERE PLACED ACROSS RABBIT CREEK. THE LEAK WAS CLAMPED WITH ATEMPORARY SADDLE. AFTER THE LEAK WAS STOPPED, REMAINING CRUDE OIL CLEAN UP
2017-09-29 08:50 | YES | NO | 19930058 | 1993-04-29 | 443 | AMOCO PIPELINE CO | YES | 1993-04-01 | 118 | IA | SIOUX |  | NO |  | NO | SECTION 15, T-95 N, R-48 W. PIPELINE SEGMENT: COUNCIL BLUFFS-SIOUX FALLS @ MP 134.6 |  | LINE PIPE | GIRTH |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8429.5638 | 17005.835 | GASOLINE | 2 | 390 | 0 | NO | NO | 6 | 0.25 | 35000 | WELDED |  | 1440 | 200 | YES | 24 | 1793 | 4 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES | WASHOUT | Null | NO DATA |  | Null | Null | MITCHELL B. WEISS - AREA MANAGER | 8168992214 | AT 1:18AM ON APRIL 1, 1993, AMOCO'S TULSA CONTROL CENTER NOTED A SUDDEN DROPIN PRESSURE AT OUR INACTIVE HAWARDEN PUMPING STATION. CONCURRENTLY, THE FLOW RATES INTO THE DOWNSTREAM SIOUX FALLS (SD) TERMINAL DROPPED DRAMATICALLY. THE CONTROLLER, IMMEDIATELY SHUT THE SYSTEM DOWN AND ACTIVATED OUR EMERGENCY RESPONSE PLAN. A HEAD PIPELINER LOCATED AT SIOUX CITY PROCEEDED NORTH TOWARDHAWARDEN ATTEMPTING TO IDENTIFY THE LEAK LOCATION WHILE CLOSING UPSTREAM VALVES IN THE PROCESS. A TERMINAL OPERATOR AT SIOUX FALLS WAS CALLED OUT TO INSPECT THAT FACILITY AND THEN FOLLOW THE LINE SOUTH OUT OF THAT LOCATION. THE NATIONAL RESPONSE CENTER WAS CONTACTED AND THE SUSPECTED LEAK WAS LOGGED AS REPORT NO. 165155 BY PETTY OFFICER MAULDIN AT 0426 EST. THE NEXT MORNING A PATROL PLANE WAS CONTRACTED TO FLY THE PIPELINE RIGHT-OF-WAY BETWEEN SIOUX FALLS AND SIOUX CITY. NOTHING WAS FOUND. AT ABOUT 2:30PM ON 4/1/93, AN AMOCO EMPLOYEE ON A GROUND SEARCH CONFIRMED THE LOCATION OF THE BREAK AT THE PIPELINECROSSING OF THE BIGG SIOUX RIVER JUST NORTH OF HAWARDEN, IA. AT THE TIME OFTHE DISCOVERY, THE BIG SIOUX WAS 6-1/2 FEET ABOVE FLOOD STAGE. ONLY MINIMALTRACES OF GASOLINE COULD BE FOUND. ON 4/2/93 THE RIVER CROSSING WAS EVACUATED, CUT, AND PHYSICALLY ISOLATED FROM THE BALANCE OF THE SYSTEM. ON 4/5/93 WHILE STILL ABOVE FLOOD STAGE, A DIVER WENT DOWN INTO THE BIG SIOUX. THE DIVER CONFIRMED THE LINE WAS BROKEN IN TWO ABOUT 45 FEET FROM THE SOUTH BANK ON THE IOWA SIDE OF THE RIVER. ON 4/22/93 A NEW CROSSING, USING THE DIRECTIONAL DRILLING METHOD, WAS COMPLETED AND THE LINE WAS RETURNED TO SERVICE FROM THE RIVER. IT WAS CONFIRMED THAT THE FAILURE INVOLVED A CLEAN BREAK AT A GIRTH WELD. WITH CONCURRENCE OF DOT, WHOSE PERSONNEL WERE ON SITE, THE PIPE WILL BESENT TO AMOCO'S NAPERVILLE, ILLINOIS RESEARCH CENTER FOR A DETAILED METALLURGICAL ANALYSIS. THE DIVER ALSO INDICATED THE LINE WAS PARTIALLY EXPOSED AS ARESULT OF SCOURING ALONG THE RIVER BED.
2017-09-29 08:50 | NO | NO | 19930059 | 1993-04-28 | 809 | ARCO PIPE LINE CO | NO | 1993-03-24 | 1130 | TX | GREGG |  | NO |  | Null |  |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 5 | 4 | NO | NO | 8 | 0.32 | 0 | NO DATA |  | 179 | 150 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G POLING | 7139865233 | THE LEAK FROM AN 8" PIPELINE WAS DISCOVERED BY AN AMOCO EMPLOYEE AT 11:30 A.M. CRUDE OIL LEAKED INTO A CREEK WITH NO NAME IN WM.H. CASTLEBERRY SURVEY; GREGG COUNTY, TEXAS. QUICKLY, ARCO PIPE LINE COMPANY WAS NOTIFIED ABOUT LEAK.QUICKLY, ARCO PIPE LINE EMPLOYEES CONTAINED THE SPILL BY PLACING A BOOM ACROSS THE CREEK. SIMULTANEOUSLY, A TEMPORARY SADDLE WAS PLACED ON THE 8" PIPELINE TO STOP THE LEAK. A VACUUM TRUCK WAS DISPATCHED TO RETRIEVE ANY REMAINING CRUDE OIL. DENNIS MITCHELL OF THE TEXAS RAILROAD COMMISSION VISITED THE SITE AND WAS SATISFIED WITH ARCO PIPE LINE COMPANY'S CLEANUP EFFORT.
2017-09-29 08:50 | YES | NO | 19930060 | 1993-04-28 | 443 | AMOCO PIPELINE CO | YES | 1993-04-29 | 800 | NM | EDDY |  | NO |  | NO | 12 MILES EAST AND 4 1/2 MILES S OF ARTESIA, NM AMOCO PIPELINES "ARTESIA STATION" |  | LINE PIPE | TANK |  | 1993 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 919.5888 | 1855.182 | CRUDE OIL | 1 | 2500 | 2440 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GREG COMPTON - RPLMF | 5053962817 | TEMPORARY TANKAGE, 550 BBL. FRAC. TANKS, WERE IN USE ON LOCATION WHILE MAIN TANK WAS UNDERGOING REPAIRS. CONTROL OF OIL IN FRAC. TANK WAS BY HYDROMOTOR AND ASSOCIATED CONTROL EQUIPMENT. HYDROMOTOR FAILED TO CLOSE, CAUSING LIQUIDTO CONTINUE TO BE PUMPED INTO TEMPORARY TANKS. TANKS OVERFLOWED. OIL WAS CONTAINED IN TANK DIKE.
2017-09-29 08:50 | YES | NO | 19930061 | 1991-10-30 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1991-02-26 | 810 | TX | UPTON | CRANE | NO |  | NO | 16 1/2 MI. NE OF MCCAMEY, TEXAS, AND 2 1/2 MI. SE OF FM 870 |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 803.7301 | 1621.4483 | CRUDE OIL | 1 | 70 | 0 | NO | NO | 10.75 | 0.31 | 35000 | WELDED |  | 1050 | 159 | YES | 12 | 1240 | 1 | 68 | EXTERNAL | Null | YES | OTHER | LOCALIZED CORROSION - PIT | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED - REGULATORY COMPLIANCE SUPV | 9152645414 | PIPELINE HAD BEEN IN OPERATION, AND HAD BEEN SHUT DOWN AT 0645 HRS AS A NORMAL OPERATIONAL PROCEDURE. AT 0810 HRS. THE PATROL PILOT, DURING A ROUTINE PATROL, REPORTED OIL OUT AT THE LEAK SITE. A MAINTANANCE/REPAIR CREW WAS IMMEDIATELY DISPATCHED TO THE SITE. TEMPORARY REPAIRS WERE MADE WITH THE USE OF A RUBBER CONE PLUG HELD IN PLACE BY A PIECE OF PIPE HALF WRAP BOLTED TO THE PIPE. WHEN OIL FLOW IS RESUMED IN THE PIPELINE, THE REPAIR WILL BE MADE PERMANENT BY THE USE OF WHOLE-WRAP. THERE WAS NO RECOVERY OF THE SPILLED OIL AS IT HAD SOAKED INTO THE GROUND. THE SOIL AT THE SITE WAS WELL MIXED TO PROMOTENATURAL BIODEGRADATION AND TO REDUCE THE POSSIBILITY OF THE SOIL POOLING ON THE SURFACE LATER, THEREBY CAUSING A POTENTIAL DANGER TO LIVESTOCK IN THE AREA. ALL SITE CLEAN-UP WAS COMPLETED BY MARCH 1, 1991. HOWEVER, PERMANENT REPAIRS HAD NOT BEEN MADE BECAUSE OIL FLOW IN THE PIPELINE HAD NOT YET RESUMED.
2017-09-29 08:50 | YES | NO | 19930062 | 1991-10-30 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1991-01-09 | 550 | TX |  |  | NO |  | NO | 4 MILES SE OF KINGVILLE, TEXAS. BANK OF THE SAN FERNANDO CREEK |  | LINE PIPE | PIPE |  | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 459 | 250 | NO | NO | 4.5 | 0.02 | 2912 | WELDED |  | 1240 | 0 | Null | 8 | 1550 | 5 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DC HUNT JR - AREA SUPERVISOR | 5122894701
2017-09-29 08:50 | NO | NO | 19930063 | 1991-10-30 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1991-01-01 | 0 | TX | SAN PATRICIO |  | NO |  | NO | FARM MKT RD 1074 & FARM MKT RD 893 - 1/4 MILE NORTH ON 893 - SO IN FIELD E OF 893 5 MI. S OF LAFTLEX |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 0 | 0 | NO | NO | 10.75 | 0.19 | 0 | WELDED |  | 1440 | 500 | YES | 0 | 0 |  |  | EXTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LYNN D NEAL | 5128873953
2017-09-29 08:50 | YES | NO | 19930064 | 1993-04-29 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1993-03-29 | 925 | NY | ONEIDA |  | NO |  | NO |  |  | TANK FARM | OTHER | FLANGE GASKET ON 3" TANK | 1959 | OTHER | FAILED FLANGE GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11494.8597 | 23189.7749 | TRANSMIX (PART. REFINED PETRO) | 3 | 950 | 950 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R MOYER - REGULATORY COMPLAINCE ADMINSTRATOR | 2158208300 | THE GASKET ON A 3-INCH, 150 #(ANSI) TANK DRAIN VALVE FAILED. THIS GASKET WAS ON THE TANK SHELL SIDE OF THE DRAIN VALVE. ALL OF THE RELEASE PRODUCT WAS CONTAINED IN THE TANK DIKE AND SUBSEQUENTLY RECOVERED. ALL REQUIRED NOTIFICATIONS WERE MADE IN A TIMELY MANNER. THE CLEANUP WAS CONDUCTED UNDER THE DIRECTION OF THE NEW YORK DEPARTMENT OF ENVIRONMENTAL CONSERVATION (DEC). THE FAILED GASKET WAS REPLACED AND THE TANK WAS THEN RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19930065 | 1993-05-03 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1993-04-06 | 145 | CA | KERN |  | NO |  | NO | 1.44 MILES SOUTH OF FCPL GRAPEVINE PUMP STATION, EAST SIDE OF NORTH BOUND 1-5 FRWY. 2,631 FEET SOUTH OF TRUCK RUNAWAY RAMP. |  | LINE PIPE | PIPE |  | 1950 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 3000000 | 2298971.9366 | 4637954.9875 | CRUDE OIL | 1 | 6200 | 3312 | NO | NO | 16 | 0.31 | 42000 | WELDED |  | 1264 | 325 | YES | 8 | 1587 | 3 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VP | 3104289217 | PIPELINE RUPTURED DUE TO AN APPARENT BUTT-WELD FAILURE IN THE LINE. LINE WAS THEN SHUT DOWN AND COMPANY PERSONNEL PROCEEDED TO PINPOINT THE SCENE OF THEACCIDENT (OCCURRED AT NIGHT IN A RURAL LOCATION) AND COMMENCED CLEANUP AND REPAIR OPERATIONS.
2017-09-29 08:50 | NO | NO | 19930066 | 1993-05-24 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1993-04-27 | 650 | AR | UNION |  | NO |  | NO | 1/2 MILE SOUTHEAST OF QUINN COMMUNITY, UNION COUNTY, SECTION 1, TOWNSHIP 175 |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OIL AND GASOLINE | 1 | 1 | 1 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 775 | 80 | YES | 8 | 1000 | 1 | 42 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | O H CUNNINGHAM - V.P. - OPERATIONS | 7137593615 | AT 0650 HOURS, APRIL 27, 1993, TEPPCO PERSONNEL RECEIVED A TELEPHONIC REPORTOF A STRONG PETROLEUM PRODUCT ODOR NEAR OUR 10" SYSTEM IN UNION COUNTY, ARKANSAS. THIS SYSTEM WAS DOWN AND SHUT IN AT THE TIME OF THE CALL. PERSONNEL WERE DISPATCHED IMMEDIATELY TO THE LEAK LOCATION AND VERIFIED A LEAK TELEPHONICALLY TO THE OPERATIONS PERSONNEL AT 0820 HOURS. UPON ISOLATION OF THE SITE, IT WAS DETERMINED EXTERNAL CORROSION HAD CAUSED A PIN-HOLE FAILURE IN THE PIPE. REMOVAL OF THIS SECTION OF PIPE AND INSTALLATION OF NEW PIPE WAS COMPLETEDON APRIL 30, 1993. CLEAN-UP OPERATIONS WERE CONCLUDED AND THE SYSTEM WAS RESTARTED APRIL 30, 1993.
2017-09-29 08:50 | YES | NO | 19930067 | 1993-05-17 | 2552 | COLONIAL PIPELINE CO | YES | 1993-04-13 | 1420 | GA | GWINNETT |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1978 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 360000 | 275876.6324 | 556554.5985 | OIL AND GASOLINE | 3 | 30 | 11 | NO | NO | 40 | 0.34 | 60000 | WELDED |  | 743 | 195 | YES | 24 | 972 | 8 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | J. A. COX MGR. TECHNICAL & REGULATORY | 4048412296 | AT APPROXIMATELY 1530 EDT ON APRIL 12, 1993, COLONIAL RECEIVED A REPORT OF APETROLEUM-LIKE ODOR NEAR ITS PIPELINE IN THE NORCROSS, GEORGIA AREA. A COMPANY REPRESENTATIVE WAS DISPATCHED TO THE AREA TO INVESTIGATE. EXCAVATIONS BEGAN ON 4/13/93 AND AT 1420 EDT A SMALL PIN HOLE LEAK WAS LOCATED IN THE 40", LINE 01 THAT RUNS FROM HOUSTON, TEXAS TO GREENSBORO, NORTH CAROLINA. AT 1544EDT ON 4/13/93, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 167276)THAT A REPORTABLE LEAK EXISTED. SIMULTANEOUSLY, A REPRESENTATIVE OF THE SOUTHERN REGION OF THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED AND INVITED TO THESITE. AT 1555 EST, THE GEORGIA ENVIRONMENTAL PROTECTION DIVISION WAS ADVISEDTHAT THE LEAK EXISTED. THE PIPELINE WAS REPAIRED BY INSTALLING A FULL-ENCIRCLEMENT, WELDED SPLIT SLEEVE OVER THE HOLE. COLOR PHOTOS WERE TAKEN OF THE ANOMALY AND FORWARDED TO AN INDEPENDENT METALLURGIST FOR ANALYSIS AND ALSO TO THE WASHINGTON, DC OFFICE OF PIPELINE SAFETY. A PRELIMINARY REPORT FROM THISMETALLURGIST, INDICATES THAT THE LEAK RESULTED FROM A SEVERE ELECTRICAL DISCHARGE FROM THE PIPELINE PROBABLY AS THE RESULT OF A LIGHTNING STRIKE. CLEAN-UP ACTIVITIES BEGAN ALMOST IMMEDIATELY AFTER THE DISCOVERY OF THE LEAK AND INCLUDE THE PLACEMENT OF ABSORBENT BOOMS AND PADS IN A NEARBY CREEK WHERE FREE PRODUCT WAS DISCOVERED. TEST HOLES HAVE BEEN DRILLED INTO THE WATER TABLE TODETERMINE THE EXTENT OF THE CONTAMINATION PRESENT. THROUGH 5/10/93, APPROXIMATELY 11 BARRELS OF GASOLINE HAVE BEEN RECOVERED AND RETURNED TO THE SYSTEM.CLEAN-UP AND SOIL REMEDIATION ACTIVITIES ARE CONTINUING. MARCH 9, 1994:COLONIAL HAS ROUTINELY MONITORED AND PERIODICALLY PICED UP PRODUCT AT ARECOVERY TRENCH INSTALLED AT THIS LEAK SITE. AN APPROXIMATE TOTAL OF 62BARRELS HAS BEEN RECOVERED. ON FEBRUARY 11, 1994, AND EMPLOYEE VISITED THESITE AFTER HEAVY RAINS AND NOTED THAT TRACES OF GASOLINE HAD RISEN TO THEGROUND SURFACE, AND A SLIGHT SHEEN GAD MIGRATED TO THE NEARBY CREEK. BECAUSETHE PRODUCT SHEEN WAS VISIBLE ON THEIS SMALL STREAM, COLONIAL NOTIFIED THENATIONAL RESPONSE CENTER (REPORT NO.221308). WHILE ONLY ONE GALLON OFGASOLINE WAS RECOVERED BY THE APPLICATION OF ABSORBANT PADS AT THE VISIT TOTHE SITE, COLONIAL'S ENVIRONMENTAL DEPARTMENT HAS CONTINUED TO TEST THE LEVELSOF CONTAMINATION AND NOW EXPECTS THAT AN UNDERTERMINED AMOUNT OFCONTAMINATION AND SOME PRODUCT STILL EXISTS IN THE GROUND. COLONIAL CONTINUESCLEAN-UP ACTIVITIES AT THE SITE.
2017-09-29 08:50 | NO | NO | 19930068 | 1993-05-06 | 7273 | HIGH ISLAND PIPELINE INC | YES | 1993-04-07 | 1410 | TX |  |  | YES | LAT.28DEG.17'45.65" LONG9 | YES | ON SUBSEA MANIFOLD OF 6" LINE TO 14" LINE IN H.I. BLK. A-462. |  | NO DATA | OTHER | SUBSEA MANIFOLD | 1984 | OTHER | DRIP LEAK ON SUBSEA MANIF | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 1620 | 450 | YES | 4 | 2460 | 7 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | HOWARD B SPALDING - SUPERVISOR - OPERATIONS | 4099483407 | SCATTERED "BLOSSOMS" WERE OBSERVED BY AMOCO PIPELINE EMPLOYEES AT ABOUT 2:10PM ON 4/7/93. THE ENTIRE SYSTEM WAS SHUT IN UNTIL THE SUBSEA "HOT TAP" VALVE ON THE 6-INCH LINE CONNECTING H.I.A-462 PLATFORM TO THE SYSTEM COULD BY CLOSED BY DIVERS. ALL PLATFORMS EXCEPT H.I.A.-462 RESUMED OPERATION ON 4/8/93.LEAK TESTS WERE PERFORMED UNDER VARIOUS PRESURE AND FLOW CONDITIONS. HOWEVER, DIVERS WERE UNABLE TO PINPOINT THE COMPONENT THAT HAD LEAKED. NO FURTHER "BLOSSOMS" WERE OBSERVED AND THE SYSTEM WAS RETURNED TO OPERATION AT APPROXIMATELY 1:05 AM ON 4/9/93.
2017-09-29 08:50 | NO | NO | 19930069 | 1993-05-06 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-04-06 | 1515 | KS | JOHNSON | LENEXA | NO |  | NO | PAOLA-KANSAS CITY 8" LINE - MP 33-16+70 1/8 MILE WEST OF I-35; NORTHWEST OF 95TH STREET AND WIDMER; LENEXA, KS. SEC. 33, T12S. R24E |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 44000 | 33718.2551 | 68023.3398 | KEROSENE | 3 | 1 | 0 | NO | NO | 8.63 | 0.19 | 40000 | WELDED |  | 960 | 300 | YES | 24 | 1250 | 10 | 94 | EXTERNAL | Null | YES | OTHER | PIT CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. THORMAN - MGR OF ENGINEERING AND TECHNICAL SERVICE | 9186614721 | LINE FLYER REPORTED DEAD SPOTS IN GRASS AT MP 33. PHILLIPS PIPE LINE PERSONNEL INVESTIGATED AND DISCOVERED AN OILY RESIDUE. THE 8" LINE WAS SHUT DOWN AND BLOCKED IN. EXCAVATION OF THE LINE BEGAN. THE LEAK WAS LOCATED AND CLAMPED. THE FAILED PIPE SECTION WAS REMOVED AND REPLACED.
2017-09-29 08:50 | YES | NO | 19930070 | 1993-05-23 | 22907 | WYCO PIPE LINE CO | YES | 1993-03-24 | 730 | WY | LARAMIE |  | NO |  | NO | WYCO PIPE LINE COMPANY'S CHEYENNE, WY TERMINAL TANK #6 SEC , T.3N, R W. LORAMIE COUNTY, WY. |  | TANK FARM | OTHER | ROOF DRAIN LINE HOSE | 1947 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3300 | 2528.8691 | 5101.7505 | KEROSENE | 1 | 75 | 10 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RONALD A WENKE | 3072373463 | ON MARCH 24, 1993 AT APPROXIMATELY 7:30AM, COMPANY PERSONNEL DISCOVERED A GASOLINE RELEASE AT CHEYENNE TERMINAL'S TANK #6 WITHIN THE TANK DIKE. AT 9:30AM MST, MR. DWAINE SHROYER OF OUR DUPONT, CO OFFICE NOTIFED THE NRC OF THE RELEASE, AND WAS GIVEN REPORT #163796. THE ORIGIN OF THE RELEASE WAS THE TANKDRAIN LINE. THE RELEASE WAS CONFINED TO THE TANK DIKE AREA. SIXTY-FIVE (65) BARRELS OF GASOLINE WERE RECOVERED AND RETURNED TO STORAGE. THE DRAIN LINEOPENING AT THE ROOF AND THE TANK SHELL HAVE BEEN PLUGGED AND/OR CLOSED. THE TANK IS SCHEDULED TO BE OUT OF SERVICE AND REPAIRED LATER THIS SUMMER.
2017-09-29 08:50 | NO | NO | 19930071 | 1993-06-18 | 4906 | EXXON PIPELINE CO | NO | 1993-05-06 | 1245 | TX | BRAZORIA |  | NO |  | NO | APPROX 10 MILES OF WEST COLUMBIA, BRAZORIA COUNTY, TEXAS, OFF (NORTH) OF FM 1301 |  | LINE PIPE | PIPE |  | 1968 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 13793.8316 | 27827.7299 | L. P. G. | 2 | 1 | 0 | NO | NO | 8 | 0.22 | 52000 | WELDED |  | 1900 | 1000 | YES | 24 | 2376 | 4 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J B HOLT - MGR ENVIRON & REGULATORY COMPLAINCE DEPT | 7136565521 | LEAK WAS CAUSED BY LAMINATION IN THE PIPE. ICE BALL FORMED AROUND PIPE ANDMINIMIZED AMOUNT OF PRODUCT RELEASED. AMOUNT RELEASED WAS BELOW REGULATORYTHRESHOLD FOR REPORTING (I.E., <5BBL HVL). IAR WAS LATER DETERMINED,HOWEVER, THAT COSTS OF REPAIR COULD EXCEED DOT'S $5,000 "PROPERTY DAMAGE"REPORT THRESHOLD. THE LEAK WAS REPORTED TO NRC WHEN IT WAS DETERMINED THATTHE $5,000 THRESHOLD MIGHT BE EXCEEDED. REPAIRS CONSISTED OF CUTTING OFCUTTING OUT AND REPLACING THE DAMAGE SECTION OF PIPE. ALL REPAIRS COMPLETEDAND PIPELINE RETURNED TO SERVICE 05/08/93. INCIDENT REPORTED TO NRC -5/7/93, 15:18 HOURS, REPORT NUMBER 172172
2017-09-29 08:50 | YES | NO | 19930072 | 1993-06-21 | 443 | AMOCO PIPELINE CO | YES | 1993-06-06 | 1200 | TX | HOCKLEY |  | NO |  | NO | AMOCO PIPELINES SLAUGHTER STATION LOCATED 2 MILES SOUTH OF AND 2 MILES EAST OF SUNDOWN, TEXAS |  | PUMPING STATION | OTHER | SUMP & 1/2 INCH VALVE | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1149.486 | 2318.9775 | CRUDE OIL | 1 | 110 | 100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALBERT WOOD JR. - PLMF | 8068977027 | ON JUNE 18, 1993, AT 12:00 CST, AMOC PIPELINE DISCOVERED A CRUDE OIL RELEASEAT ITS SLAUGHTER STATION. THE SOURCE OF THE RELEASE WAS A SUMP PUMP WHICHHAD OVERFLOWED. A 1/2 INCH VALVE, USED TO BLEED AIR FROM A SUCTION PUMP, WAS INADVERTANTLY LEFT OPEN. WITH THIS VALVE OPEN AND IT BEING CONNECTED TO THE SUMP, THE SUMP WAS UNABLE TO HANDLE THE VOLUME AND IT OVERFLOWED. AT 12:48P.M. CST, MR. JAMES LUTTER NOTIFIED THE NRC OF THE RELEASE AND WAS GIVEN REPORT # 178368. THE RELEASE WAS CONTAINED AT THE STATION, AND CLEANUP IS IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19930073 | 1993-06-21 | 18718 | SUN PIPELINE CO | YES | 1993-05-21 | 200 | OK | CREEK |  | NO |  | NO | FROM INTERSECTION OF HWY 99-33-&16, GO 1 MILE N, 1 MI EAST, 1/4 MI N. EAST INTO NW NE SW 27-18N-7E |  | PUMPING STATION | PUMP |  | 0 | OTHER | MECHANICAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | CRUDE OIL | 1 | 700 | 674 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EVELYN L WOOTTEN - COMPLIANCE COORDINATOR | 9185866962 | ON FRIDAY MORNING, 5-21-93, AT APPROXIMATELY 2:00 AM., THE ROD IN THE POWER END OF THE UNIT AT DRUMRIGHT STATION BROKE ALLOWING CRUDE OIL TO ESCAPE FROM THE FLUID END OF THE PUMP. APPROXIMATELY 700 BBLS. OF CRUDE OIL FLOWED THROUGH THE STATION MANIFOLD AND INTO A SMALL CREEK. THE OIL WAS QUICKLY CONTAINEDAND PICKED UP BY 6:OO P.M THE SAME DAY. THERE WERE NO INJURED AND RELATIVELY LITTLE IMPACT TO THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19930074 | 1993-06-21 | 809 | ARCO PIPE LINE CO | NO | 1993-05-18 | 2030 | TX | GONZALES |  | NO |  | NO | 9 MILES S OF GONZALES, TX ON HWY. 183, 1.5 MILES WEST ON GRAVEL ROAD, 1000 FT. SOUTH OF GRAVEL ROAD IN PASTURE. |  | LINE PIPE | PIPE |  | 1948 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 49811.0586 | 100489.0247 | GASOLINE | 3 | 813 | 230 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 775 | 745 | YES | 0 | 845 | 1 | 48 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY E GRAVES - MGR OPERATIONS COMPLAINCE - PRODUCTS B.U. | 7139865368
2017-09-29 08:50 | YES | NO | 19930075 | 1993-06-18 | 809 | ARCO PIPE LINE CO | YES | 1993-05-28 | 2045 | TX | HARRIS |  | NO |  | NO | ARCO PIPE LINE COMPNAY. 901 CLINTON DR. GALENA PARK. TX |  | LINE PIPE | BOLTED FITTING |  | 1993 | OTHER | FAILURE OF BOLTED INSULAT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | DIESEL FUEL | 3 | 357 | 236 | NO | NO | 10 | 0.37 | 35000 | FLANGED |  | 1220 | 1195 | YES | 4 | 1950 | 5 | 93 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY E GRAVES - MGR COMPLIANCE - PRODUCTS BUSINESS UNIT | 7139865368 | BOTTOM PORTION OF INSULATING FLANGE GASKET FAILED RESULTING IN A RELEASE FROM
2017-09-29 08:50 | YES | YES | 19930076 | 1993-06-21 | 10312 | GULF CENTRAL PIPELINE CO | YES | 1993-05-19 | 1430 | MO | TEXAS | MOUNTAIN VIEW | NO |  | NO | R7W, T27N, SEC 33 |  | LINE PIPE | VALVE | T.D. WILLIAMSON T101 TAPP | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 2 | 2 | 0 | 30000 | 22989.7194 | 46379.5499 | ANHYDROUS AMMONIA | 2 | 59 | 59 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM NORVELL - REGULATIONS COORDINATOR | 3144865488 | THE STOPPLE TECHNICIAN, ASSUMING THE 2" COMPLETION PLUG WAS SET INSIDE THE HILLCO NIPPLE, BEGAN RETRACTING THE T101 BORING BAR WITH THE INTENTION TO RETRACT THE FEED TUBE TO THE 6" INDICATION MARK. EITHER THE PLUG HAD ACTUALLY NEVER SEATED OR THE PLUG UNSCREWED FROM THE NIPPLE DURING RETRACTION. THE PRESUURIZED PRODUCT BELOW THE PLUG RELEASED THROUGH THE TAPPING VALVE CAUSING INJURY TO TWO COMPANY EMPLOYED PERSONNEL AND SOME DAMAGE TO THE SURROUNDING VEGETATION. THE AMMONIA VAPORS RELEASED STRAIGHT UP INTO THE ATMOSPHERE. THERE WAS NOT ANY LIQUID AMMONIA INVOLVED. USING THE NIPPLE AND VALVE CONFIGURATIONFROM THE PROJECT PLAN USED DURING THE ACCIDENT, IT WAS FOUND THROUGH RECREATING THE EVENT, THAT WITH THE FEED TUBE READING 6" THE PLUG WAS LOCATED INSIDETHE BALL OF THE TAPPING VALVE. THERE IS A STRONG POSSIBILITY THAT IF THE TAPPING VAVLE WAS PARTIALLY CLOSED, THE PLUG COULD BE COCKED INSIDE THE VALVE BALL FORMING A SEAL WHICH GAVE THE STOPPLE TECHNICIAN A "SET" CONDITION AFTER BLOWING DOWN PRESSURE BETWEEN THE PLUGGING MACHINE AND THE TOP OF THE VALVE.CONSEQUENTLY, WHEN THE NIPPLE WAS UNSCREWED FROM THE TOP OF THE VALVE, THEREWAS NO LONGER ANY DOWNWARD RESTRICTION FROM THE BORING BAR AND THE PRESSURIZED PRODUCT BELOW THE PLUG ALLOWING THE AMMONIA TO ESCAPE UPWARDS. WE INTENT SENDING THE T101 TAPPING MACHINE IN FOR EXAMINATION TO DETERMINE IF THE PLUG COULD ANGLE INSELF INSIDE THE VALVE BALL AND CAUSE A SEAL.
2017-09-29 08:50 | YES | NO | 19930077 | 1993-06-15 | 10012 | KANEB PIPELINE CO | YES | 1993-05-11 | 1230 | NE | FILLMORE |  | NO |  | NO | NW 1/4, NW 1/4, SECTION 30, T-7-N, R-2-W |  | TANK FARM | BOLTED FITTING |  | 1953 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 383.162 | 772.9925 | DIESEL FUEL | 1 | 87 | 78 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LEROY ANDERSON - MGR OF REGULATORY AFFAIRS | 3162621408 | THE RELEASE OCCURRED DURING A NORMAL PUMPING OPERATION. THE RELEASE WAS OBSERVED AND STOPPED WITHIN 2 -3 MINUTES OF ITS ACTUAL OCCURRENCE. THE RELEASE WAS COMPLETELY CONTAINED WITHIN THE DIKED ENCLOSURE SURROUNDING THE TANK. THE FITTINF INVOLVED IN THE INCIDENT IS A DRESSER 10" STYLE 38 REGULAR COUPLING, THE FITTING HAS BEEN REMOVED FROM SERVICE AND REPLACED. FACILITY PERSONNEL ARE INSPECTING ALL OTHER COUPLINGS OF THIS STYLE TO DETERMINE THEIR SERVICEABILITY. GASKETS THAT SHOW SIGNS OF DETERIORATION WILL BE REPLACED.
2017-09-29 08:50 | YES | NO | 19930078 | 1993-06-15 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-05-05 | 1130 | TX | NUECES |  | NO |  | NO | TWO 2 MILES EAST OF BANQUETE, TEXAS; 200 YARDS EAST OF COUNTY ROAD 81 AND 300 YARDS SOUTH OF COUNTY ROAD 42. |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | CRUDE OIL | 1 | 50 | 0 | NO | NO | 8 | 0 | 0 | WELDED |  | 550 | 400 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W D PARTLOW - ENVIRONMENTAL & SAFETY SUPERVISOR | 7138777370 | WHILE LINE WAS IN SERVICE, NOTICED SHORTAGE ON MORNING OF 5/05/93. SHUT LINE DOWN TO LOOK FOR LEAK. LEAK WAS DISCOVERED AT 1130 HRS. WELDED BALF WRAP ON PIPE UNTIL SECTION CAN BE REPLACED.
2017-09-29 08:50 | NO | NO | 19930079 | 1993-06-15 | 15485 | PHILLIPS 66 CO | NO | 1993-04-28 | 2000 | TX | BRAZORIA |  | NO |  | NO | APPROX. 1/2 MILE EAST OF THE CITY OF JONES CREEK, TEXAS, INSIDE PEACH POINT WILDLIFE RESERVE |  | LINE PIPE | PIPE |  | 1949 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9195.8877 | 18551.8199 | JET FUEL | 3 | 2 | 1 | NO | NO | 8 | 0.19 | 35000 | WELDED |  | 870 | 450 | YES | 8 | 1093 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G I TRAYER - PRODUCT MANAGER | 4094912200 | A REPORT OF A SPOT OF DEAD VEGETATION ON THE PIPELINE RIGHT OF WAY WAS CALLED IN BY THE PIPELINE AERIAL PATROL. THE PIPELINE WALKING PATROL VERIFIED THAT A HYDROCARBON SMELL AND RESIDENCE WERE APPARENT AT A LOCATION NEAR JONES CREEK, TEXAS INSIDE PEACH POINT WILDLIFE PRESERVE. THE WALKING PATROL INFORMEDTHE REFINERY STOCK DISPATCHER OF THE FINDINGS. ALTHOUGH THE LEAK WAS STRONGLY SUSPECTED TO BE ON THE #3 PRODUCTS PIPELINE, WHICH HAD LAST CARRIED BASE AVIATION GASOLINE, ALL THREE FINISHED PRODUCTS PIPELINES IN THE RIGHT OF WAY WERE SHUTDOWN AS A PRECAUTION UNTIL LAB ANALYSIS COULD VERIFY THE LINE INVOLVED. THE STOCK DISPATCHER CALLED THE REFINERY TECHNICAL ASSISTANT WHO ARRIVED ONSITE AT APPROXIMATELY 8:00 PM. A SAMPLE OF THE HYDROCARBON AT THE LEAK SITE WAS TAKEN AND TRANSPORTED TO PHILLIPS 66 COMPANY LABORATORY FOR ANALYSIS. LABORATORY ANALYSIS CONFIRMED THAT THE LINE INVOLVED WAS THE #3 PRODUCTS PIPELINE. THE REFINERY TECHNICAL ASSISTANT BEGAN NOTIFICATION OF COMPANY PERSONNEL, ENVIRONMENTAL PERSONNEL, AND REPAIR CREWS. OUTSIDE AGENCIES WERE CONTACTED INCLUDING THE TEXAS RAILRAOD COMMISSION, TEXAS WATER COMMISSION, THE NATIONAL RESPONSE CENTER, AND TEXAS PARKS AND WILDLIFE. SINCE THE LEAK SITE WAS RELATIVELY SMALL AND ISOLATED, THE PIPELINE WAS DOWN BLOCKED, THE HOUR WAS LATE, REPAIR CREWS WERE LINED UP TO ARRIVE FIRST LIGHT ON THURSDAY, APRIL 29, 1993. REPAIR CREWS ARRIVED AT THE SITE AT APPROXIMATELY 7:15 AM. THE LEAK SITE WAS EXCAVATED AND THE LEAK LOCATION WAS FOUND. THE LEAK ON THE LINE WAS ONTHE BOTTOM OF THE PIPE WHICH APPEARED TO BE IN THE CENTER OF A SMALL INDENTATION IN THE PIPE. THE ORIGINAL COATING ON THE PIPE WAS STILL INTACT. NO SIGNS OF CURRENT EXCAVATIONS IN THE AREA WERE FOUND. A PIPELINE REPAIR CLAMP WAS INSTALLED OVER THE PIPE AND INDENTATION. THE LINE WAS STARTED BACK UP TO VERIFY THE INTEGRITY OF THE REPAIR. NO PROBLEMS WERE FOUND. PLANS ARE TO REMOVE THE SECTION OF LINE CONTAINING THE CLAMP BY SEPTEMBER, 1993 SO THAT THE PIPE SECTION IN QUESTION MAY BE EVALUATED BY METALLURGICAL EXAMINATION. THE ESTIMATED COST OF REMOVING THIS SECTION OF PIPE IS INCLUDED IN THE ESTIMATED TOTAL PROPERTY DAMAGE. A PLAN FOR CLEANUP OF THE LEAK REPAIR SITE HAS BEEN FILED WITH THE TEXAS WATER COMMISSION.
2017-09-29 08:50 | NO | NO | 19930081 | 1993-06-14 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1993-05-12 | 1200 | MN | KITTSON | DONALDSON | NO |  | NO | IMMEDIATELY DOWNSTREAM OF LAKEHEAD'S DONALSON PUMP STATION. APPROX. 1 3/4 MILE EAST OF DONALDSON. MN ON COUNTY ROAD 11. |  | LINE PIPE | PIPE |  | 1954 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22989.7194 | 46379.5499 | CRUDE OIL | 1 | 2 | 0 | Null | Null | 26 | 0.28 | 52000 | WELDED |  | 709 | 500 | YES | 24 | 886 | 8 | 74 | NO DATA | Null | Null | NO DATA |  | OTHER | DENT CAUSED - UNIDENTIFIE | Null | NO DATA |  | Null | Null | JON E STAUDOHAR - SECRETARY & DIRECTOR, CORPORATE SERVICES | 7153941404 | LAKEHEAD PERSONNEL BASED AT OUR DONALDSON, MN PUMP STATION WERE NOTIFIED AT 12:00 MST, MAY 12, 1993 OF A SPOT OF OILED SOIL JUST OUTSIDE OF THE STATION BY A TENANT/LANDOWNER. LAKEHEAD EMPLOYEES CONFIRMED THE REPORT AND INITIATED AN IMMEDIATE LINE SHUTDOWN OF ALL THREE LINES. AFTER THE AREA WAS EXCAVATED, A 1 1/2" DIAMETER X 1/4" DEEP DENT WITH A 3/8" CRACK IN THE BOTTOM WAS DISCOVERED ON LAKEHEAD'S 26" LINE 2. A PLIDCO REPAIR SLEEVE WAS INSTALLED OVER THELEAK AND THE LINE WAS RETURNED TO SERVICE AT 18:30 MST, MAY 12, 1993.
2017-09-29 08:50 | YES | NO | 19930082 | 1993-06-11 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1993-05-09 | 345 | TX | EL PASO | EL PASO | NO |  | NO | 200 FEET W OF SHELL STR & CARNEGIE STR INTERSECTION IN THE MIDDLE OF CARNEGIE STR, OUR PLMP 4.36 |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 57474.2984 | 115948.8747 | DIESEL FUEL | 3 | 400 | 0 | NO | NO | 12 | 0.19 | 52000 | NO DATA |  | 0 | 0 | Null | 0 | 1530 | 12 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | STANDARD PIPELINE MARKERS | Null | Null | J M ABBOUD - SENIOR VICE PRESIDENT - OPERATIONS & ENGINEERIN | 2134867720 | THE EL PASO TO TUCSON 12-INCH LINE WAS SHUT DOWN AT 0345, 5-9-93, DUE TO A LINE BREAK AT PLMP 4.4, APPROXIMATELY FOUR MILES WEST OF EL PASO STATION NEAR THE EL PAS AIRPORT. THE 8-INCH LINE WAS SHUT DOWN AT 0601, 5-9-93, DUE TO ITS PROMIXITY TO THE 12-INCH LINE. THE 12-INCH LINE HAD RUPTURED ON THE BOTTOMOF THE PIPE. EVIDENCE AT THE SCENE REVEALED THE PIPELINE HAD BEEN DAMAGED AT SOME POINT IN THE PAST BY UNKNOWN PARTIES AND COVERED BACK UP WITHOUT ANY NOTIFICATION OF THE LINE DAMAGE. COATING ON THE 8-INCH PIPELINE HAD BEEN DAMAGED AND THE LINE SCRAPED AS WELL. A SIX-FOOT SECTION OF 12-INCH PIPE WAS REPLACED AND REPAIRS WERE COMPLETED AS OF 0700, 5-10-93. A 10-FOOT SECTION OF 12-INCH PIPE WAS REPLACED AND REPAIRS WERE COMPLETED AS OF 0700, 5-10-93. A 10-FOOT SLEEVE WAS WELDED ON THE 8-INCH LINE AT PLMP 4.36 ON 5-12-93.
2017-09-29 08:50 | YES | NO | 19930083 | 1993-06-01 | 10312 | GULF CENTRAL PIPELINE CO | YES | 1993-05-04 | 215 | IA | FRANKLIN | ALEXANDER | NO |  | NO | T93N, R22W, SEC. 15, MILEPOST 211.15 |  | LINE PIPE | PIPE |  | 1970 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 134106.6963 | 270547.3743 | ANHYDROUS AMMONIA | 2 | 5692 | 0 | NO | NO | 8.63 | 0.2 | 1423 | OTHER |  | 1420 | 935 | YES | 72 | 1995 | 9 | 70 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | PUBLIC AWARENESS | Null | NO | JIM L NORVELL - REGULATIONS COORDINATOR | 3144865488 | 5/4/93 - 02:15 CONTROL CENTER IN WICHITA NOTICED GRADUAL PRESSURE DROP IN AREA AFTER THE MAINLINE PUMP AT ELDORA, IA. WENT DOWN AT 01:55. 02:20 - CLOSED BLOCK VALVE REMOTELY AT ELDORA, IA AND NOTIFIED INJECTION TO S/D. REMOTELY CLOSED BLOCK VALVE AT BLAIR, NE PUMP STATION. BEGAN CALLING COMPANY PERSONNEL TO RESPOND. 02:29 - MS. PRESTON CRUIS (515-358-6267) CALLED CONTROL CENTERTO REPORT A VAPOR CLOUD 4 MI. NORTH AND 2.5 MI. EAST OF ALEXANDER, IA. SHEHAD CALLED SHERIFF. 02:53 - CONTROL CENTER RECEIVED CALL FROM SHERIFF DEPT.REPORTING THE LEAK AND ASKING FOR INSTRUCTIONS. 03:15 - NOTIFIED IOWA/DNR BY TELEPHONE (#05043-KL-0330) OF RELEASE. 03:20 - SHERIFF CALLED CONTROL CENTER TO REPORT EVACUATION OF ALEXANDER. 03:40 - NOTIFIED NRC (171302) OF RELEASE AND EVACUATION. 04:29 - VALVE 6-33 CLOSED MANUALLY. 05:16 - VALVE 6-34 CLOSED MANUALLY. BEGAN SETTING UP PROPANE BURNERS TO BURN VAPORS IN PREPARATION FOR STOPPLE AND REPAIR UPON ARRIVAL OF EQUIPMENT . 13:10 - LOCAL DISASTER AGENCIES LIFTED EVACUATION BAN. AIR SAMPLES BY IOWA/DNR SHOWED 5 PPM IN APPROX. 1 MILE RADIUS DOWNWIND. 22:00 - STOPPLE SET AND LEAK UNDER CONTROL. 5/5/93 - 20:00 - SECTION OF PIPE CUT OUT AND REPLACED. FIELD TILE WAS DOUNS ONTOP OF PIPELINE DURING EXCAVATION INDICATING POSSIBLE THIRD PARTY DAMAGE. 5/6/93 - LINE RETURNED TO SERVICE AT 17:30. PARTIALLY BACK-FILLED UNTIL SITE REMEDIATION PERFORMED. SOIL SAMPLES HAVE BEEN TAKEN AND WE ARE WORKING WITH IOWA/DNR FOR REMEDIATION OF SITE.
2017-09-29 08:50 | YES | NO | 19930084 | 1993-06-01 | 809 | ARCO PIPE LINE CO | YES | 1993-05-14 | 1550 | TX | HARRIS |  | NO |  | NO | GREENSPOINT MALL, 12300 NORTH FREEWAY, HOUSTON, TEXAS. ADJACENT TO NORTHBOUND SERVICE ROAD BETWEEN HELTWAY 8 AND GREENS ROAD. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 15326.4796 | 30919.6999 | JET FUEL | 3 | 142 | 56 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1220 | 600 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | LARRY E GRAVES - MGR OPERATIONS COMPLAINCE - PRODUCTS B.U | 7139865368 | CONTRACTOR WAS INSTALLING DRAINAGE TILE FOR A NEW STORM SEWER SYSTEM WHEN PIPELINE WAS DAMAGED. CONTRACTOR WAS AWARE OF PIPELINE LOCATION.
2017-09-29 08:50 | NO | NO | 19930085 | 1993-06-02 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-05-10 | 730 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | TANK 13 - PLANTATION'S BATON ROUGE TANK FARM LOCATED OFF BLOUNT ROAD IN BATON ROUGE, LOUISIANA. |  | TANK FARM | TANK |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 26000 | 19924.4235 | 40195.6099 | GASOLINE | 3 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | CREVICE CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VP - OPERATIONS | 4043645916 | ON THE MORNING OF MAY, 1993, WHILE GAUGING TANK 13 AT PLANTATION'S BATON ROUGE TANK FARM, A UTILITY OPERATOR DISCOVERED A DISCOLORATION ON THE SKETCH PLATE. THE TANK WAS TAKEN OUT OF SERVICE, CLEANED AND INSPECTED. THE INSPECTION REVEALED A CRACK (DUE TO CREVICE CORROSION), APPROXIMATELY 2" FROM WHERE THE FLOOR ATTACHES TO THE TOP OF THE SUMP LIP. THE TANK WAS REPAIRED BY REMOVING APPROXIMATELY 24" OF FLOOR PLATE AROUND THE ENTIRE SUMP AND REPLACING IT WITH 1/4" - THICK STEEL PLATE.
2017-09-29 08:50 | YES | NO | 19930086 | 1993-06-08 | 809 | ARCO PIPE LINE CO | NO | 1993-05-20 | 2030 | TX | GONZALES |  | NO |  | NO | 9 MILES SOUTH OF GONZALES, TX ON HWY 183, 1.5 MILES WEST ON GRAVEL ROAD, 1000 FT. SOUTH GRAVEL ROAD IN PASTURE. |  | LINE PIPE | PIPE |  | 1948 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 49811.0586 | 100489.0247 | GASOLINE | 3 | 813 | 230 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 775 | 745 | YES | 0 | 845 | 1 | 48 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY E GRAVES - MGR OPERATIONS COMPLIANCE - PRODUCTS. | 7139865368 | A SEVERE THUNDER STORM WAS PASSING THROUGH THE AREA. LIGHTNING CAUSED DAMAGE TO AN ELECTRICAL COIL ALLOWING THE CONTROL VALVE TO IMMEDIATELY CYCLE TO THE OPEN POSITION CAUSING EXCESS OPERATING PRESSURE ON THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19930087 | 1993-06-03 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-05-04 | 1245 | NM | EDDY |  | NO |  | NO | LINE 80-110 EXT. - ARTESIA TO LEE SEC. 27, T17S, R30E ONE MILE SOUTH AND ONE MILE EAST OF LOCO HILLS, NM |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 27000 | 20690.7474 | 41741.5949 | NATURAL GAS LIQUID | 2 | 80 | 0 | NO | NO | 3.5 | 0.13 | 35000 | WELDED |  | 1350 | 640 | YES | 8 | 1900 | 11 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B L THORMAN - MGR OF ENGINEERING & TECHNICAL SERVICES | 9186614721 | A SMALL DITCHING MACHINE STRUCK LINE 80-11 EXT. ABOUT 1.4 MILES SOUTHEAST OFLOCO HILLS, NM, RELEASING APPROXIMATELY 80 BARRELS OF NGL TO THE ATMOSPHERE. AN ADDITIONAL 790 BARRELS WERE VENTED TO COMPLETE THE REPAIR. THE CONTRACTOR FAILED TO MAKE ONE-CALL NOTIFICATION. THE LINE WAS MARKED IN THE AREA OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19930088 | 1993-06-08 | 443 | AMOCO PIPELINE CO | YES | 1993-05-31 | 630 | NM | EDDY |  | NO |  | NO | 12 MILES EAST OF ARTESIA, NEW MEXICO AND 4 MILES SOUTH |  | PUMPING STATION | TANK |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 280 | 265 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES HOMER - PLMF | 5053962817 | HIGH TANK SHUT DOWN FAILED, ALLOWING TANKS TO OVER FLOW.
2017-09-29 08:50 | YES | YES | 19930090 | 1993-06-08 | 2330 | CHEVRON PIPELINE CO | NO | 1993-05-06 | 1230 | TX | CULBERSON | WINK | NO |  | NO | SEC 17, BLOCK 61 SURVEY TSP2 MILE POST 123 |  | LINE PIPE | PIPE |  | 1956 | INCORRECT OPERATION BY OPERATOR PERSONNEL | FAILURE TO FOLLOW MAINTEN | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 2 | 2 | 0 | 1250 | 957.905 | 1932.4812 | CRUDE OIL | 1 | 1 | 0 | YES | NO | 20 | 0.25 | 0 | WELDED |  | 900 | 350 | NO | 0 | 0 | 1 | 76 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L J DELANEY - SYSTEM TEAM LEADER | 7133637126 | THE MAINTENANCE CREW RESPONDED TO A ONE BARREL LEAK REPORTED BY THE AIR PATROL PILOT. THE PIPE WAS EXPOSED BY THE BACKHOE AND A PLUG INSTALLED TO STOP THE FLOW OF OIL. A WELDER AND WELDER'S HELPER PROCEEDED TO INSTALL A TWO FOOTSECTION OF FULL WRAP. A COMBINATION OF THE BACKHOE UNCOVERING OILY SOIL ANDA DECREASE IN THE WIND ALLOWED VAPORS TO BUILD IN THE DITCH WHICH WERE SUBSEQUENTLY IGNITED BY THE WELDING TORCH. THE RESULTING FLASH FIRE BURNED THE WELDER AND WELDER'S HELPER BUT WAS EXTINGIUSHED IMMEDIATELY BY THE FIRE WATCH USING AN ANSUL 30 LB. FIRE EXTINGUISHER. THE INJURED EMPLOYEES WERE TAKEN TOGUALALUPE MEDICAL CENTER IN CARLSBAD, NEW MEXICO WHERE THE FIRST EMPLOYEE WAS CLASSIFIED AS RECEIVING 5% FIRST AND 10% SECOND DEGREE BURNS ON THE LEGS, SIED AND FACE. THE OTHER EMPLOYEE WAS CLASSIFIED AS RECEIVING 5% FIRST DEGREEBURNS ON THE ARMS, STOMACH AND NOSE.
2017-09-29 08:50 | YES | NO | 19930091 | 1993-06-03 | 18718 | SUN PIPELINE CO | YES | 1993-05-03 | 1305 | OK | CREEK |  | NO |  | NO | COUNTY RD - SE4 SEC 9-17N-7E CREEK COUNTY |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 766.324 | 1545.985 | JET FUEL | 1 | 72 | 71 | NO | NO | 8 | 0.2 | 35000 | NO DATA |  | 1075 | 50 | YES | 10 | 1399 | 4 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | EDITH F COEN , DISTRICT SUPERVISOR | 9183524363 | COUNTY ROAD GRADER HIT LINE CAUSING LEAK. LINE WAS WELL MARKED WITH MARKERSON EITHER SIDE OF THE ROAD. LINE WAS 18" DEEP IN BAR DITCH. LINE HAS BEEN REPAIRED AND LOWERED.
2017-09-29 08:50 | YES | NO | 19930092 | 1993-06-03 | 18273 | SHELL PIPELINE CORP | YES | 1993-05-04 | 800 | MS | CARROLL | BLACK HAWK | NO |  | NO | CAPLINE/CARROLLTON STATION 2-INCH SECTION 36, T-18-N, R-2-E; SIX MILES SOUTH OF CARROLLTON |  | PUMPING STATION | PIPE |  | 1968 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19158.0995 | 38649.6249 | CRUDE OIL | 1 | 130 | 130 | NO | NO | 2 | 0.22 | 35000 | WELDED |  | 615 | 500 | YES | 24 | 894 | 1 | 73 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A R HAVEY MGR REGULATORY COMPLAINCE | 7132410132
2017-09-29 08:50 | YES | NO | 19930093 | 1993-06-03 | 737 | ASHLAND PIPELINE CO | YES | 1993-05-01 | 802 | IL | MARION | PATOKA | NO |  | NO | 1/4 MILE WEST OF SEVEN HILLS RD. ON CONSERVATION RD., THEN 200' NORTH IN A FIELD. SECTION 14, TOWNSHIP 4N, RANGE 1E |  | LINE PIPE | LONGITUDINAL WELD |  | 1968 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 229897.1937 | 463795.4987 | CRUDE OIL | 1 | 5016 | 5016 | NO | NO | 20 | 0.23 | 52000 | WELDED |  | 861 | 856 | YES | 24 | 1168 | 8 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM SIMPSON - DIVISION SUPERINTENDENT | 5026832485 | THE INCIDENT OCCURRED ON ASHLAND'S PATOKA, ILLINOIS TO OWENSBORO, KENTUCKY 20" CRUDE OIL PIPELINE SYSTEM, WHICH WAS OPERATING NORMALLY UNTIL 8:02 AM (CDT), SATURDAY, MAY 1, 1993 WHEN A SUDDEN THRUPUT INCREASE AT PATOKA STATION, THE LINE ORIGINATING STATION, ACCOMPANIED BY A DRASTIC PRESSURE REDUCTION ON THE LINE, RESULTED IN THE ACTIVATION OF THE LOW-PRESSURE STATION SHUTDOWN DEVICES. THE PIPELINE CONTROL CENTER IN ASHLAND, KENTUCKY RECEIVED INSTANTANEOUS INDICATION OF THE SYSTEM UPSET AND IMMEDIATELY INITIATED FULL SHUTDOWN PROCEDURES, AND BEGAN NOTIFICATION OF RESPONSIBLE COMPANY AUTHORITIES. UPON INVESTIGATION, IT WAS DETERMINED THAT A FAILURE IN THE PIPE, APPROXIMATELY 1.5 MILES FROM PATOKA STATION, HAD RESULTED IN A RELEASE OF APPROXIMATELY 5,000 BARRELS OF CRUDE OIL. THE SPILL WAS CONTAINED IN A DRY FARM POND ON THE AFFECTED PROPERTY, AND ALL FREE OIL WAS PICKED UP BY VACUUM TRUCKS AND RETURNED TO TANKAGE AT PATOKA. THE REMAINING OILY DIRTY AND CLEAN-UP MATERIALS WAS REMOVED AND DISPOSED OF AT AN AUTHORIZED LANDFILL. THE OPERATING PRESSURE ON THE LINE HAS BEEN REDUCED 20%, FROM THAT WHICH EXISTED AT THE TIME OF FAILURE, BY U.S. DOT OFFICIALS, PENDING RESULTS OF PIPE FAILURE TESTING BEING CONDUCTED BY KIEFNER & ASSOCIATES OF COLUMBUS, OH. THE PIPELINE WAS REPAIRED WITH A NEW SECTION OF PRE-TESTED 20" PIPE AND WAS RETURNED TO SERVICE AT APPROXIMATELY 6:49 PM (CDT), SUNDAY, MAY 2, 1993.
2017-09-29 08:50 | NO | NO | 19930094 | 1993-06-03 | 2552 | COLONIAL PIPELINE CO | YES | 1993-05-04 | 1930 | TN | KNOX | KNOXVILLE | NO |  | NO | COLONIAL PIPELINE COMPANY'S EAST KNOXVILLE DELIVERY FACILITY |  | NO DATA | VALVE |  | 1978 | OTHER | PROVER LOOP VENT VALVE NO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | FUEL OIL | 2 | 2 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J A COX - MGR - TECHNICAL & REGULATORY | 4048412296 | AT 1930 EST ON 5-4-93, COLONIAL PERSONNEL AT KNOXVILLE DELIVERY WERE NOTIFIED BY A THIRD PARTY THAT PRODUCT WAS SPRAYING FROM PIPING AT THE EAST KNOXVILLE DELIVERY FACILITY (AN UNMANNED FACILITY). THE DELIVERY OF FUEL OIL WAS IMMEDIATELY SHUT DOWN BY THE OPERATOR AT KNOVILLE. THE CHIEF OPERATOR IN CHARGEOF EAST KNOXVILLE ARRIVED AT 1930 EST AND NOTED A STRONG FUEL OIL ODOR. THEKNOX COUNTY FIRE DEPARTMENT WAS CALLED TO THE FACILITY. WITH FIRE DEPARTMENT APPROVAL, THE LINE WAS RESTARTED TO LOCATE THE SOURCE OF THE LEAK. PRODUCTWAS FOUND TO BE ESCAPING FROM A PROVER LOOP VENT VALVE THAT HAD NOT BEEN CLOSED COMPLETELY. IT IS ESTIMATED THAT 2 BARRELS OF PRODUCT ESCAPED INTO THE FACILITY YARD. CLEAN UP HAS RESULTED IN THE COLLECTION AND RETURN TO THE SYSTEM OF 1 BARREL OF FUEL OIL. ON 5-6-93, IT BECAME APPARENT THAT CLEAN-UP COSTS WOULD EXCEED $5,000, AND AT 1400 EST THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 171867). SIMULTANEOUSLY, THE SOUTHERN REGION OF THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED OF THE INCIDENT.
2017-09-29 08:50 | NO | NO | 19930095 | 1993-06-02 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-05-10 | 530 | SC | SPARTANBURG |  | NO |  | NO | PLANTATION'S SPARTANBURG PUMP STATION AND DELIVERY TERMINAL. |  | PUMPING STATION | VALVE |  | 1968 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 15326.4796 | 30919.6999 | GASOLINE | 3 | 35 | 15 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M CROOK - VP. OPERATIONS | 4043645916 | ON MAY 10, 1993, THE RELIEF TANK AT PLANTATION'S SPARTANBURG DELIVERY TERMINAL OVERFLOWED RELEASING APPROXIMATELY 35 BARRELS OF GASOLINE AS A RESULT OF AN EQUIPMENT MALFUNCTION. DURING DELIVERY TO A LOCAL SHIPPER, AN IMPROPER VALVE ALIGNMENT BY THE SHIPPER CAUSED PLANTATION TO EXPERIENCE A HIGH DEILVERY MANIFOLD PRESSURE. A VALVE OPENED TO THE RELIEF TANK TO RELIEVE THE HIGH MANIFOLD PRESSURE. UPON FLOW TO THE RELIEF TANK, A TERMINAL LOCKOUT OCCURRED INVOLVING THE CLOSING OF THE INCOMING PRESSURE REDUCING VALVE TO PLANTATION'S TERMINAL. HOWEVER, DUE TO THE FAILURE OF AN "O" RING IN THE PRESSURE REDUCING VALVE, THE VALVE DID NOT CLOSE COMPLETELY, THUS ALLOWING PRODUCT TO CONTINUE TO FLOW TO THE RELIEF TANK. BY RECEIVING BOTH A HIGH RELIEF TANK ALARM AND EXPLOSIVE ATMOSPHERE ALARMS, THE OPERATOR REALIZED THAT AN EQUIPMENT MALFUNCTION WAS OCCURRING. THE OPERATOR IMMEDIATELY CLOSED A TAKE-OFF VALVE THAT ISOLATED THE TERMINAL. AN EMERGENCY RESPONSE WAS INITIATED BY PLANTATION WITH ALL PRODUCT BEING CONTAINED EITHER ON PLANTATION OR ADJACENT PROPERTY. THE SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL WAS ADVISED OF THERELEASE AND WITNESSED CLEAN-UP ACTIVITIES.
2017-09-29 08:50 | NO | NO | 19930096 | 1993-07-06 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-06-01 | 1840 | TX | SAN PATRICIO |  | NO |  | NO | 5 MILES NORTH OF MIDWAY STATION. .2 MILES NORTH OF COUNTY ROADS 98 & 79 INTERSECTION |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | JET FUEL | 3 | 35 | 0 | NO | NO | 12.75 | 0.2 | 52000 | WELDED |  | 1193 | 929 | YES | 4 | 1492 | 2 | 89 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W D PARTLOW | 7138777370 | LEAK OCCURRED INSIDE OF 16" ROAD CASING ON PIPELINE ROAD CROSSING. REPLACEDWITH 200' OF NEW PIPE.
2017-09-29 08:50 | YES | NO | 19930097 | 1993-07-07 | 4430 | EMERALD PIPE LINE CORP | YES | 1993-06-04 | 1500 | KS | SEWARD |  | NO |  | NO | TOWNSHIP 34 SOUTH, RANGE 31 WEST, SECTION 34. 13 1/2 MILES EAST AND 3/4 MILE NORTH OF THE CITY OF LIBERAL, KANSAS |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 57474.2984 | 115948.8747 | L. P. G. | 2 | 5277 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | COMPANY PROGRAM | NO | NO | GERALD CHILDERS MANAGER, PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APPROXIMATELY 1500 HOURS ON JUNE 4, 1993, AN EMPLOYEE OF THE SEWARD COUNTY ROAD DEPARTMENT, WHILE OPERATING A MAINTAINER STRUCK AND RUPTURED OUR 6" OKAN LATERAL. THE EXCAVCATOR DID NOT CALL FOR A LOCATE THERE FOR IT WAS NOT TEMPORARILY MARKED; HOWEVER, THE PIPELINE WAS STRUCK WITHIN 15 FEET OF OUR AERIAL MARKER AND WARNING SIGN. THE LINE WAS VISIBLY MARKED ON BOTH SIDES OF THEROAD. THE ACCIDENT ALLOWDED 5,277 BARRELS OF PROPANE TO ESCAPE, OF WHICH NONE WAS SUBSEQUENTLY RECOVERED. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING 3 FEETOF LINE WITH PRE-TESTED PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19930098 | 1993-07-13 | 10313 | KOCH PIPELINE INC | YES | 1993-06-22 | 1730 | WI | WOOD |  | NO |  | NO | 3/4 OF A MILE SOUTH U.S. HIGHWAY 10, NEAR BLOCK VALVE 106, WOOD COUNTY, WISCONSIN |  | LINE PIPE | VALVE |  | 1987 | OTHER | THE PIPING IN QUESTION HA | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 91958.8775 | 185518.1995 | GASOLINE | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK M MCCANN | 6124584860 | A HYROCARBON ODOR WAS NOTICED WITHIN THE SOIL BY A KOCH EMPLOYEE DURING A MAINTENANCE ACTIVITY ON AN ADJACENT PIPELINE NEAR BLOCK VALVE 106. THE PIPELINE SEGMENT IN QUESTION WAS EXCAVATED AND REPLACED. SOURCE UNKNOWN AT THIS TIME. CAUSE : THE PIPING IN QUESTION HAD BEEN REMOVE AND TAKEN TO A METALURGIST FOR ANALYSIS.
2017-09-29 08:50 | YES | NO | 19930099 | 1993-07-13 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1993-06-16 | 900 | NE | GAGE |  | NO |  | NO | INCIDENT OCCURRED APPROXIMATELY 100' NORTH OF THE C/L OF STATE HWY 136, 7 MILES EAST OF BEATRICE, NE. |  | LINE PIPE | OTHER | STOPPLE FITTING | 1993 | OTHER | STOPPLE SEALING ELEMENT F | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9195.8877 | 18551.8199 | L. P. G. | 2 | 1560 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G A ROOD - V.P. | 7138537876 | A PIPELINE RELOCATION WAS UNDERWAY (UTILIZING THIRD PARTY CONTRACTORS) AT CROSSING OF NEBRASKA HIGHWAY 136 TO ALLOW FOR ROAD IMPROVEMENTS. STOPPLE TEES WERE WELDED ON THE PIPE AND COUPONS CUT FROM THE PIPE ON BOTH SIDES OF THE ROAD ON JUNE 15, 1993. THE FOLLOWING EVENTS TOOK PLACE ON JUNE 16, 1993: 1) ON JUNE 16, 1993 MAINLINE BLOCK VALVE NOS. 12 LOCATED SOUTH OF HIGHWAY 136, AND 13 LOCATED NORTH OF HIGHWAY 136 ON PIPELINE 102 WERE CLOSED AND CHAIN LOCKED. 2) BETWEEN 0730 AND 0800 HOURS BOTH STOPPLE SEALING ELEMENTS WERE SET. 3) THE SECTION OF PIPE BETWEEN THE STOPPLES WAS BLOWN DOWN (25 BBLS OF ETHANE). 4) A TEN FOOT SECTION OF PIPE WAS REMOVED FROM THE SOUTH SIDE OF HIGHWAY. 5) MOVED TO NORTH SIDE OF HIGHWAY TO REMOVE TWENTY FOOT SECTION OF PIPE. DURING THE REMOVAL OF THIS SECTION OF PIPE THE NORTH STOPPLE SEALING ELEMENT FAILED, RELEASING ETHANE LIQUID INTO THE TIE-IN BELL HOLE AT 0900 HOURS. 6) FOUR CONTRACTOR PERSONNEL WERE IN THE BELL HOLE. ONE INDIVIDUAL RECEIVED MINOR FIRST AID ON THE JOB SITE AND ONE WAS TAKEN TO THE NEBRASKA CITY HOSPITAL FOR PRECAUTIONARY X-RAYS, TREATED FOR SCRAPES AND ABRASIONS, RELEASED AND RETURNED TO WORK ON JUNE 18, 1993. 7) THE SHERIFF, FIRE MARSHALL AND LOCAL FIRE DEPARTMENT RESPONDED TO THE SITE. THERE WAS NO FIRE OR EXPLOSION. 8) THE PIPELINE BETWEEN THE RELEASE SITE AND VALVE NO. 13 WAS COMPLETELY BLOWN DOWN BY 1500 HOURS. A NEW SEALING ELEMENT WAS INSTALLED AND THE TIE-IN WORK COMPLETED BY 1900 HOURS.
2017-09-29 08:50 | YES | NO | 19930100 | 1993-06-29 | 450 | AMOCO PRODUCTION CO | NO | 1993-06-17 | 2215 |  |  |  | YES | LONG28 34'LAT.90 24'032.2 | YES | D.O.T. PIPELINE SEGMENT #22 (MMS). THE PIPELINE FROM OCS-G-1248, ST161 SSTI (CHEVERON SUSEA TIE-IN 10 3/4") TO OCS-G-1248, ST161-A PRODUCTION PLATFORM (AMOCO) |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 983000 | 753296.4712 | 1519703.2509 | CONDENSATE | 1 | 50 | 0 | NO | NO | 4 | 0.24 | 1440 | WELDED |  | 1440 | 100 | YES | 4 | 2200 | 4 | 87 | NO DATA | Null | Null | NO DATA |  | SHIP ANCHOR |  | Null | NO DATA |  | NO | NO | E L MEDLEY | 5045866413 | CAUSE: CONTRACT SIESMIC BOAT ANCHORED OVER THE LINE. WHEN THE BOAT ATTEMPTED TO RETRIEVE THE ANCHOR, THE LINE WAS SEVERED. THE BOAT CAPTAIN NOTICED THE SHEEN ON THE WATER AND NOTIFIED THE AMOCO FOREMAN. THE PLATFORM AUTOMATICALLY SHUT-IN PRODUCTION ON THE PIPELINE'S PRESSURE SAFETY LOW SIGNAL (PSL). REMARKS: THE CGA ID BOAT, WHICH IS EQUIPPED WITH A G.T. 185 SKIMMER AND AN ADDITIONAL BOAT WITH A FAST RESPONSE UNIT (FRU) WERE DISPATCHED TO THE SCENE. SEA CONDITIONS WERE TOO ROUGH TO SAFELY CONDUCT SKIMMING OPERATIONS. ANOTHERBOAT WAS ON STAND-BY AT OUR FOUCHON BASE, WITH A SECOND FRU.
2017-09-29 08:50 | NO | NO | 19930101 | 1993-07-01 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1993-05-31 | 900 | MI | OAKLAND | NOVI TOWNSHIP | NO |  | NO |  |  | LINE PIPE | OTHER | SUPPORT SLEEVE | 1972 | FAILED WELD | FAILED WELD IN SUPPORT SL | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 45979.4387 | 92759.0997 | GASOLINE | 3 | 5 | 5 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 1305 | 1050 | YES | 24 | 1753 |  | 72 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER - REGULATORY COMPLIANCE ADMINISTRATOR | 2158208300 | A SHEEN ON A SMALL WATER PUDDLE IN A ROAD DRAINAGE DITCH WAS REPORTED TO THELOCAL EMERGENCY CENTER. THE EMERGENCY CENTER CONTACTED THE LOCAL FIRE DEPARTMENT. THE LOCAL FIRE DEPARTMENT, HAVING RECENTLY ATTENDED A BUCKEY PUBLIC AWARENESS PROGRAM, ASKED THE EMERGENCY CENTER TO CONTACT BUCKEYE. ALL REQUIRED NOTIFICATIONS WERE MADE IN A TIMELY MANNER. INVESTIGATION OF THE INCIDENT REVEALED THE CAUSE TO BE A FAILED LONGITUDINAL WELD ON A SUPPORT SLEEVE USED TO REINFORCE A TD WILLIAMSON 101 2" THREAD-O-RING NIPPLE.THE SUPPORT SLEEVE WAS REMOVED. REPAIRS WERE MADE BY INSTALLING A CERTIFIED SEGMENT OF PRETESTED 12" .250X-52 PIPE. THIS REPLACEMENT PIPE SEGMENT WAS COATED AFTER THE TIE IN WELDS WERE SUCCESSFULLY X-RAYED. ANY AFFECTED SOIL WAS REMOVED AND THE SITE CLEANUP WAS COMPLETED TO THE SATISFACTION OF THE MICHIGAN DEPARTMENT OF NATURAL RESOURCES. THE FAILED WELD IN THE SUPPORT SLEEVE HAS BEEN SENT TO AN OUTSIDE FIRM FOR FUTHER ANALYSIS.
2017-09-29 08:50 | NO | NO | 19930102 | 1993-06-29 | 809 | ARCO PIPE LINE CO | NO | 1993-04-28 | 1400 | TX | RUSK |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1935 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 4 | 0.24 | 0 | NO DATA |  | 80 | 10 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G POLING | 7139865233 | THE LEAK FROM THE 4" GRAVITY PIPELINE WAS DISCOVERED BY A RAILROAD COMMISIONOF TEXAS EMPLOYEE AT APPROXIMATELY 2:00 P.M. CRUDE OIL LEAKED INTO A NORMALLY DRY CREEK BED. ARCO PIPE LINE COMPANY EMPLOYEES CONTAINED THE SPILL BY PLACING A BOOM ACROSS THE CREEK. A TEMPORARY SADDLE WAS PLACED ON THE 4" PIPELINE TO STOP THE LEAK. ALSO, A VACUUM TRUCK WAS DISPACTCHED TO RETRIEVE THE SPILLED CRUDE OIL.
2017-09-29 08:50 | YES | NO | 19930103 | 1993-06-29 | 19536 | TOTAL PIPELINE CORP | NO | 1993-05-27 | 800 | OK | COTTON |  | NO |  | NO | SW1/4, SECTIN 18, 4S, 12W, COTTON COUNTY, OKLAHOMA |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2298.9719 | 4637.955 | CRUDE OIL | 1 | 60 | 30 | NO | NO | 8.63 | 0.32 | 35000 | COUPLED |  | 596 | 500 | YES | 8 | 745 | 4 | 86 | EXTERNAL | Null | YES | OTHER | ISOLATION CORROSION PIT D | NO DATA |  | Null | NO DATA |  | Null | Null | MICHEAL JOHN COOPER | 4052291638 | ON THE AFTERNOON OF 5/26/93 TOTAL'S SCADA CONTROL OPERATOR STARTED PUMPING PETROLEUM CRUDE OIL FROM TOTAL'S DEVOL STATION TO TOTAL'S DUNDEE (1191) STATION. INTEGRITY CALCULATIONS SHOWED A DIFFERENCE OF 50 BARRELS PER HOUR BETWEENMETERING POINTS. THE SYSTEM WAS SHUT DOWN AND EMERGENCY CREWS WERE CALLED IN TO CHECK OUT THE PIPELINE SEGMENT. AIR PATROL & VEHICLE PATROL OF THE LINEWAS MADE AND NO LEAKS WERE DISCOVERED. THE SEGMENT WAS SHUT DOWN AND MAINLINE VALVES CLOSED. THE FOLLOWING MORNING AIR PATROL AND A TOTAL EMPLOYEE DISCOVERED A LEAK ALONG SIDE A DIRT SECTION LINE ROAD. EMERGENCY CREWS RESPONDED TO THE SITE, CLEANUP PROCEDURES WERE INITIATED, AND TEMPORARY REPAIRS WERE MADE TO THE PIPELINE. THE LEAK SITE WAS CLEANED UP TO THE SATISFACTION OF OCC PIPELINE SAFETY & OCC OIL & GAS INSPECTORS. PERMANENT REPAIRS TO THE PIPELINE WILL BE SCHEDULED IN JUNE OR JULY 1993. THIS LEAK WAS INITIALLY REPORTEDAS 268 BARRELS, BUT WAS LATER DETERMINED TO BE 60 BARRELS DUE TO PROBLEMS WITH A METER AT DUNDEE (1191) STATION WHICH WAS CHANGED OUT AND REPAIRED 5/26/93
2017-09-29 08:50 | YES | NO | 19930104 | 1993-06-30 | 19234 | TEXAS EASTERN CORP | YES | 1993-05-29 | 1857 | OH | BUTLER |  | NO |  | NO | INTERSECTION OF YANKEE RD AND TODHUNTER RD., 0.4 MI FROM. INTERSECTION OF TODHUNTER RD. AND STATE HIGHWAY 4. |  | LINE PIPE | PIPE | NON-REGULATED < 20% SMYS | 1993 | OTHER | FAILURE OF 2" 90 ELL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 23000 | 17625.4515 | 35557.6549 | L. P. G. | 2 | 148 | 148 | YES | NO | 2 | 0.15 | 35000 | THREADED |  | 300 | 140 | YES | 0 | 125 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O H CUNNINGHAM | 7137593615 | AT 1857 HOURS CST, MAY 29, 1993 A RELEASE OF BUTANE RESULTED IN A FIRE AT THE TODHUNTER TERMINAL. TERMINAL PERSONNEL IMMDIATELY ENACTED EMERGENCY PROCEDURES AND BEGAN ISOLATING THE SECTION OF PIPING WHICH FAILED. THE RELEASE OCCURRED WHEN A 2" LINE FAILED AT A 90 DEGREE ELL. THE FIRE WAS PERMITTED TO EXTINGUISH ITSELF UNDER A SUPERVISED CONTROLLED BURN. THE TERMINAL OPERATIONS WERE RESTARTED AT APPROXIMATELY 2200 HRS. CST.
2017-09-29 08:50 | YES | NO | 19930105 | 1993-06-30 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-05-19 | 1445 | TX | SAN PATRICIO |  | NO |  | NO | FM 1074 & FM 893 INTERSECTION: 1/4 MI. NORTH OF FM 893 - 50' TO THE EAST. |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | L. P. G. | 2 | 156 | 0 | NO | NO | 10.75 | 0.19 | 46000 | WELDED |  | 792 | 500 | YES | 8 | 991 | 2 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W D PARTLOW | 7138777370 | HOUSTON 10" LEAK OCCURRED AT 1445 HOURS ON 5/19/93 1/4 MILE NORTH OF THE INTERSECTION OF STATE HIGHWAY 589 & 1074 OFF OF S.H. 893 IN SAN PATRICIO COUNTY. LEAK WAS CAUSED BY EXTERNAL CORROSION. THERE WERE NO DEATHS OR INJURIES.LEAK WAS INITALLY REPORTED BY THE SAN PATRICIO COUNTY SHERRIFF'S DEPARTMENT WAS OBSERVING NO VAPORS BUT "JUST BUBBLES IN THE STANDING WATER" OVER THE FIELD. A TEMPORARY CLAMP WAS INSTALLED.
2017-09-29 08:50 | NO | NO | 19930106 | 1993-07-07 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1993-06-14 | 740 | CA | LOS ANGELES | LONG BEACH | NO |  | NO | WEST HYNES PUMP STATION/TANK FARM, 5900 CHERRY AVENUE, LONG BEACH, CA 90805 |  | TANK FARM | OTHER | GASKET BETWEEN FLANGE & M | 1983 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9195.8877 | 18551.8199 | CRUDE OIL | 1 | 22 | 22 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | DANIEL C REYNEVELD | 3104289217 | CONTRACTOR EMPLOYEE BACKED VEHICLE INTO A JUNCTION BOX CONTAINING CONTROL SYSTEM WIRING WHICH WAS THEN DAMAGED. AUTOMATIC VALVES THEN CLOSED CAUSING A PRESSURE SURGE IN THE SYSTEM. A FLANGE GASKET AT A TANK FILL VALVE FAILED RESULTING IN THE SPILL. SYSTEM WAS SHUT DOWN AND SPILL CLEANED UP. THE GASKETWAS REPLACED AND FACILITY RETURNED TO SERVICE AFTER REPAIRS WERE MADE TO CONTROL SYSTEMS.
2017-09-29 08:50 | YES | NO | 19930107 | 1993-06-30 | 934 | OXYCHEM PIPELINE OPERATIONS | NO | 1993-05-21 | 215 | TX |  | CORPUS CHRISTI | NO |  | NO | MCKINZIE ROAD CROSSING JUST SOUTH OF THE OXYCHEM CORPUS CHRISTI PLANT ENTRANCE |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1149485.9683 | 2318977.4937 | NOT GIVEN | 3 | 1 | 1 | NO | NO | 6 | 0.22 | 42000 | WELDED |  | 720 | 300 | YES | 24 | 1050 | 9 | 79 | EXTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | SAM C. HSIEH | 7139971000 | A PLANT OFF-SITE OPERATOR DISCOVERED BENZENE BEING RELEASED THROUGH CASING VENTS AT THE MCKINZIE ROAD CROSSING. THE PRECISE TIME THAT THE RELEASE BEGAN IS
2017-09-29 08:50 | YES | NO | 19930108 | 1993-07-02 | 26149 | ALYESKA PIPELINE SERVICE CO | NO | 1993-06-01 | 800 | AK | FAIRBANKS NORTH STAR |  | NO |  | NO | NORTH POLE METERING CONNECTION. SEC 13, T2S-R2E FAIRBANKS MERIDIAN, NORTH POLE, AK |  | LINE PIPE | VALVE |  | 1976 | OTHER | VENTED PLUG ON VALVE STEM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 383161.9894 | 772992.4979 | CRUDE OIL | 1 | 2 | 1 | NO | NO | 6 | 0.43 | 35000 | WELDED |  | 901 | 432 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN S DAYTON | 9072658923 | DURING A ROUTINE PIPELINE CORROSION INSPECTION, A LEAK WAS DISCOVERED ON VALVE V700 ON THE 6" RESID RETURN LINE FROM THE NORTH POLE METERING STATION, THE VENTED PLUG ON THIS VAVLE WAS LEAKING AND WAS REPLACED WITH A SOLID PLUG. THE VALVE ITSELF WAS REPLACED AFTER A SMALL WEEP WAS OBSERVED IN THE VICINITYOF A FACTORY WELD. THE GENERAL AREA AROUND THE SITE HAS BEEN CLEANED UP. MAJOR CONTAMINATED SOIL HAS BEEN REMOVED TO DATE (120 CY). MINOR CONTAMINATION IS BEING ADDRESSED AT THIS TIME. FIVE MONITORING WELLS WERE INSTALLED AROUND THE SITE WITH NO DETECTION OF NAY HYDROCARBONS. CLEAN UP IS BEING MONITORED BY THE ALASKA DEPARTMENT OF ENVIROMENTAL CONSERVATION.
2017-09-29 08:50 | NO | NO | 19930109 | 1993-07-16 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-06-04 | 1345 | ND | CASS |  | NO |  | NO | NEW INTERSECTION OF BENDER LANE AND MAIN ST. HARWOOD, NORTH DAKOTA |  | LINE PIPE | PIPE |  | 1946 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | FUEL OIL | 3 | 5 | 3 | NO | NO | 6 | 0.19 | 35000 | WELDED |  | 950 | 400 | YES | 8 | 1450 | 10 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - SR. VICE PRESIDENT AND GENERAL MANGER | 9185883850 | ON JUNE 4, 1993, A SLIGHT SEEPING LEAK WAS DISCOVERED AT M. P. 111+46 WHEN EVIDENCE OF FUEL OIL BEGAN SHOWING UP IN A SANITARY SEWER. THE LEAK WAS SO SMALL THAT AT 400 PSI IT WAS DISCOVERED ONLY AFTER WIPING THE EXCAVATED PIPE COMPLETELY DRY AND COMING BACK TO FIND A DARK,DAMP SPOT ON THE PIPE.METALLURGICAL ANALYSIS REVEALED THE LEAK TO BE THE RESULT OF A NON-WELDED DARK SPOT IN THE ERW SEAM. IT HAD SURVIVED THE HYDROSTATIC TEST IN 1987. THIS LEAK WAS ORIGINALLY ESTIMATED TO HAVE COST $4,000 AND THEREFORE NOT REQUIRING A 7000-1 REPORT, HOWEVER, REMEDIATION ULTIMATELY REQUIRED REMOVING 8 TRUCK LOADS OF SOIL THAT RAN THE TOTAL COST UP ABOVE $5,000.
2017-09-29 08:50 | YES | NO | 19930111 | 1993-07-26 | 15851 | PRIDE REFINING INC | YES | 1993-07-14 | 800 | NM | EDDY |  | NO |  | NO | APX.8 MILES EAST OF LOVING NEW MEXICO ON HWY 21 TO REFINERY ROAD TURN NORTH APX. 2 MILES ON RIGHT SIDE OF HWY. |  | PUMPING STATION | PUMP |  | 1992 | OUTSIDE FORCE DAMAGE | RODS PARTED ON PIPELINE | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 383.162 | 772.9925 | CRUDE OIL | 1 | 59 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | JOHN T. MACON - PIPELINE TERMINAL MANAGER | 9156748231 | DUE TO A MECHANICAL FAILURE OF THE PIPELINE PUMPING UNIT OIL SPILLED FROM ITAND RAN APPROXIMATELY 1500'X2' CAUSING NO DAMAGE TO ANY WATER WAYS. AREA WAS DRY DIRTED AND ANY OIL STANDING WAS REMOVED. SPILL #186570.
2017-09-29 08:50 | NO | NO | 19930112 | 1993-06-28 | 26149 | ALYESKA PIPELINE SERVICE CO | NO | 1993-05-28 | 1700 | AK | NORTH SLOPE |  | NO |  | YES | CHECK VALVE 29A, PIPELINE MILEPOST 161.5,NEAR JAMES DALTON HIGHWAY MP 253 SEC. 32,T14S,R12E UMIAT MERIDIAN |  | LINE PIPE | VALVE |  | 1991 | OTHER | LOOSE GREASE FITTING CAP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 4 | 4 | NO | NO | 48 | 0.56 | 70000 | WELDED |  | 970 | 656 | YES | 8 | 1500 | 6 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN S. DAYTON - VICE PRESIDENT,OPERATIONS | 9072658923 | THE LEAK WAS DISCOVERD MAY 28,1993, IN A CONCRETE VAULT SURROUNDING CHECK VALVE 29A SOUTH OF PUMP STATION 4 AT PIPELINE MILE POST 161.5. ABOUT 150 GALLONS OF CRUDE OIL WERE FOUND ON TOP OF THE THREE FEET OF WATER WITHIN THE VAULT.EQUIPMENT WAS USED TO REMOVE THE OIL/WATER MIXTURE IN THE VAULT TO ENABLE A CLOSER EXAMINATION. A LOOSE GREASE FITTING CAP WAS FOUND TO BE THE CAUSE. AFTERE-TIGHTENING THE CAP, THE LEAK STOPPED. ENVIRONMENTAL SURVEILLANCE REPORTEDNO INDICATION OF OIL OUTSIDE THE VAULT. NO OIL SHEENS WERE FOUND ON THE NEARBY ATIGUN RIVER. NO DAMAGE TO ANIMALS, BIRDS OR THE SURROUNDING ENVIRONMENT WAS REPORTED.
2017-09-29 08:50 | YES | NO | 19930113 | 1993-07-23 | 443 | AMOCO PIPELINE CO | YES | 1993-06-22 | 730 | WY | GOSHEN |  | NO |  | NO | FT. LARAMIE STATION,LOCATED IN S/E 1/4 OF S/W 1/4 SECTION 23, TOWNSHIP 26N,RANGE 64W. |  | TANK FARM | TANK |  | 1949 | OTHER | TANK BOTTOM FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3700 | 2835.3987 | 5720.1445 | CRUDE OIL | 1 | 620 | 20 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL E. LINK - FIELD SUPERVISOR | 3078372121 | ON JUNE 22,1993,AT 0730 MST, AMOCO PIPELINE DISCOVERED A CRUDE OIL CONDENSATE RELEASE AT ITS FT. LARAMIE STATION. THE SOURCE OF THE RELEASE WAS FROM UNDER TANK #6940. A 3' X10' STAIN WAS DISCOVERED ADJACENT TO THE WEST SIDE OF THETANK; EXCAVATION TO A 2' DEPTH DISCLOSED SEEPAGE FROM UNDER THE TANK. UPON VERIFICATION THAT A SPILL HAD OCCURRED, D.A. SHROYER, APL AREA MANAGER IN DENVER, WAS NOTIFIED , AND HE IN TURN MADE VERBAL NOTIFICATION TO THE EMERGENCY RESPONSE CENTER AND THE WYOMING DEQ. THE TANK HAD BEEN PUMPED TO A LIQUID LEVEL OF 1FT. (895 BBLS) ON JUNE 18TH IN PREPARATION FOR NORMAL MAINTENANCE CLEANING AND REPAIRS. MEASUREMENT OF THE LIQUID LEVEL REMAINING IN THE TANK AFTER THE SPILL WAS DISCOVERED INDICATED A LOSS OF 620 BBLS HAD OCCURRED. 20 BBLS FREE LIQUID WERE RECOVERED FROM AN EXCAVATED PIT WHER THE SEEPAGE WAS OCCURRING AND 200 BBLS OF LIQUID REMAINING IN THE TANK WERE REMOVED. AFTER THE RECOVERY OF 20 BBLS FROM THE PIT, SEEPAGE STOPPED, WITH AN ESTIMATED LOSS OF 600 BBLS BENEATH THE TANK NOT RECOVERED TO DATE.REMEDIATION HAS BEGUN, WORKING WITHIN PARAMETERS DEFINED BY THE WYOMING DEPARTMENT OF ENVIRONMENTAL QUALITY. UNTIL THE TANK HAS BEEN CLEANED OF REMAINING SOLID MATERIALS ON THE TANK FLOOR TO ALLOW ENTRY, INVESTIGATION OF THE CAUSE OF THE TANK BOTTOM FAILURE IS PENDING.
2017-09-29 08:50 | YES | NO | 19930114 | 1993-07-26 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-07-03 | 1000 | IA | SIOUX |  | NO |  | NO | LOCATED IN THE BIG SIOUX RIVER IN THE NORTHEAST 1/4 OF SECTION 15 T95N, R48W NEAR HIGHWAY 10 NORTH OF HAWARDEN, IOWA IN SIOUX COUNTY. |  | LINE PIPE | OTHER | NONE SPECIFIED | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 30652.9592 | 61839.3998 | L. P. G. | 2 | 227 | 0 | NO | NO | 6 | 0.38 | 35000 | WELDED |  | 1450 | 476 | YES | 8 | 1920 | 8 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - SR.VICE PRESIDENT & GENERAL MANAGER | 9185883850 | AT 1450 HOURS ON JULY 3, 1993, A PASSERBY REPORTED SOMETHING BUBBLING UP INTHE BIG SIOUX RIVER. INVESTIGATION REVEALED THE RIVER CROSSING WAS LEAKING AND HAD BEGAN AT 1000 HOURS. THE CROSSING VALVES WERE CLOSED ANT EH RIVER CROSSING LINE FILL WAS FLARED OFF. THE WINDS PREVENTED ANY VAPOR CLOUD FROM FORMING. THE RIVER CROSSING WAS BLINDED OFF ONCE THE LINE FILL WAS FLARED OFF. THELEAK OCCURRED DURING SEVERE FLOODING WHICH HAS PREVENTED INSPECTION AND REPAIR UNTIL THE FLOOD WATERS RECEDE. IT IS SPECULATED THAT A TREE OR OBJECT BEING CARRIED BY THE FLOOD WATERS STRUCK AND DAMAGED THE LINE. A SUPPLEMENTAL REPORT WILL BE FILED WHEN THE ACTUAL LEAK CAUSE CAN BE DETERMINED SAFELY.
2017-09-29 08:50 | YES | NO | 19930115 | 1993-07-26 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-06-19 | 845 | TX | VICTORIA |  | NO |  | NO | APPROXIMATELY .8 MI. SOUTH OF GARCITAS CREEK AND 300 YDS. SOUTHEAST OF FM 616 ON THE KEERAN RANCH. |  | LINE PIPE | OTHER | NONE SPECIFIED | 1943 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 15326.4796 | 30919.6999 | L. P. G. | 2 | 174 | 0 | NO | NO | 8.63 | 0.32 | 0 | WELDED |  | 750 | 677 | YES | 8 | 960 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW - ENVIRONMENTAL & SAFETY SUPV | 7138777370 | LEAK WAS ORIGINALLY REPORTED AS BEING ON THE BUTANE SHUTTLE SYSTEM. LATER IDENTIFIED AS BEING ON HOUSTON 8" LPG SYSTEM. LEAK WAS CAUSED BY A PINHOLE IN AWELD ON THE BOTTOM OF PIPE. LEAK WAS REPAIRED AND LINE WAS BACK IN SERVICE AT 0400 HRS. ON 6/20/93.
2017-09-29 08:50 | NO | NO | 19930116 | 1993-07-19 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1993-06-19 | 910 | TX | HARRIS | BAYTOWN | NO |  | NO | CORNER OF DECKER DRIVE AND BAKER STREET |  | TANK FARM | OTHER | PRESSURE HOSE | 1993 | OTHER | FAILURE OF PRESSURE HOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4597.9439 | 9275.91 | DIESEL FUEL | 1 | 42 | 41 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM - VICE PRESIDENT - OPERATIONS | 7137593615 | AT 0910 HOURS, CST, JUNE 19,1993, THE FAILURE OF A PRESSURE HOSE CONNECTOR RESULTED IN THE RELEASE OF APPROXIMATELY 42 BARRELS OF DIESEL FUEL. ALL SPILLED PRODUCT WAS CONTAINED WITHIN A TANK CONTAINMENT DIKE. APPROXIMATELY 41 BARRELS WERE TRANSFERED FROM THE CONTAINMENT DIKE TO A STORAGE TANK WITH APPROXIMATELY ONE BARREL OF PRODUCT LOST TO ABSORPTION INTO THE SOIL INSIDE THE CONTAINMENT DIKE. THIS HAS BEEN SUBJECTED TO IN-SITU REMEDIATION.
2017-09-29 08:50 | YES | NO | 19930117 | 1993-07-12 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-06-11 | 945 | TX | NUECES | CORPUS CHRISTI | NO |  | NO | WEST SIDE OF HUNTER LANE;1 BLOCK EAST OF SUNTIDE ROAD; NORTH SIDE OF I-37. |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 153264.7958 | 309196.9992 | CRUDE OIL | 1 | 385 | 350 | NO | NO | 8.63 | 0.3 | 0 | WELDED |  | 550 | 0 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW - ENVIRONMENTAL & SAFETY SUPERVISOR | 7138777370 | LEAK WAS REPORTED BY EXXON PIPELINE PATROL PILOT WHO NOTICED OIL FLOWING FROM A DRAINAGE DITCH INTO TULE LAKE BASIN AT UPRIVER ROAD. INITIAL RESPONSE EFFECTS LIMITED THE FLOW OF OIL INTO THE BASIN TO LESS THAN 5 BBLS.BY 6/13/94, APPROXIMATELY 350BBLS. OF OIL HAD BEEN RECOVERED. A HEAVY RAIN THAT NIGHT BURST THE CONTAINMENT DIKE AT HUNTER AND UPRIVER ROAD ALLOWING APPROXIMATELY 10 BBLS OF OIL FLOW INTO TULE LAKE. BECAUSE OF HEAVY RUN-0FF, OIL WAS UNABLE TO BE CONTAINED UNTIL IT REACHED THE MOUTH OF TULE LAKE AT CITGO DOCK #3. ADDITIONAL RECCOVERY EFFORTS WERE MADE ON THE MORNING OF 6/14/1993. THE LEAK WAS CAUSED BY EXTERNAL CORROSION AND A TEMPORARY CLAMP WAS INSTALLED ON THE LINE.
2017-09-29 08:50 | YES | NO | 19930118 | 1993-07-19 | 12127 | MARATHON PIPE LINE CO | YES | 1993-06-19 | 354 | IL | MACON |  | NO |  | NO | T14N - R3E SECTION 4. 1/2 MILE SOUTH OF NTERSECTION OF COUNTY ROADS 300N AND 1750E ON EAST SIDE OF ROAD APPROXIMATELY 85' FROM CENTER LINE OF ROAD 1750E. |  | LINE PIPE | PIPE |  | 1958 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 591000 | 452897.4715 | 913677.1325 | GASOLINE | 1 | 970 | 119 | NO | NO | 12 | 0.25 | 46000 | WELDED |  | 1300 | 1210 | YES | 8 | 1668 | 0 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER - SR. ENVIRONMENTAL & SAFETY ENGINEER | 4194213201 | AT APPROXIMATELY 03:54 CDT ON JUNE 19,1993, A LOW SUCTION SWITCH AT THE WABASH MACON STATION, CAUSED THE PUMP UNITS, AT THAT STATION, TO BE SHUT DOWN. THE REMAINING THREE PUMPS RUNNING ON THE WOOD RIVER TO CHAMPAIGN LEG OF THE WABASH SYSTEM WERE SHUT DOWN AT 03:58 CDT BY AN ANALYST, AT THE FINDLAY OPERATIONS CENTER, AND THE WOOD RIVER OPERATOR. AT 03:59 THE FINDLAY OPERATIONS CENTERANALYST NOTIFIED THE AREA FOREMAN OF THE INCIDENT. THE AREA FOREMAN DISPATCHED PERSONNEL TO THE AREA TO INVESTIGATE AND CLOSE THE MAINLINE BLOCK VALVES.MPLC AND CONTRACT EMERGENCY RESPONSE PERSONNEL WERE PUT ON ALERT. SHERIFFS IN FIVE COUNTIES, IN THE POTENTIALLY AFFECTED AREA, AND THE ILLINOIS EMERGENCYMANAGEMENT AGENCY WERE NOTIFIED OF THE POSSIBILIYT OF A PIPELINE LEAK. THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 07:08 CDT OF THE LEAK. AT 07:15 CDT, THE RELEASE LOCATION WAS DISCOVERED IN A CORN FIELD APPROXIMATELY 3 MILES DOWN STREAM OF MACON PUMP STATION. THE RELEASED PRODUCT ENTERED FINLEY CREEK ANDWAS CONTAINED THERE BY A SYSTEM OF CONTAINMENT DAMS. A 50 FOOT JOINT OF 12" PIPE WAS FOUND TO HAVE A SEAM FAILURE. THE JOINT OF PIPE CONTAINING THE FAILURE WAS REMOVED FROM THE PIPELINE AND FORWARDED TO AN INDEPENDENT LABORATORY FOR ANALYSIS. A REPLACEMENT JOINT OF PIPE, WHICH HAD BEEN PREVIOUSLY HYDROSTATICALLY TESTED, WAS INSTALLED IN THE PIPELINEL CLEAN UP AND DISPOSAL OF CONTAMINATED EARTH IS BEING COORDINATED WITH THE ILLINOIS EPA, OFFICE OF CHEMICAL SAFETY, EMERGENCY RESPONSE UNIT.
2017-09-29 08:50 | NO | NO | 19930119 | 1993-08-24 | 2552 | COLONIAL PIPELINE CO | YES | 1993-07-20 | 1101 | MD | BALTIMORE |  | NO |  | NO | LEAK SITE 8INCH LINE 36 STATION 382+68 |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | GASOLINE | 1 | 1 | 1 | NO | NO | 8.63 | 0.22 | 42000 | WELDED |  | 1535 | 888 | YES | 24 | 1513 | 3 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | JAMES L. GAMBRELL - ADMINISTRATOR | 4048412402 | AT 1101 EDT ON JULY 20,1993, COLONIAL PERSONNEL WERE NOTIFIED BY A THIRD PARTY OF THE PRESENCE OF A GASOLINE ODOR AND A SHEEN ON A TRIBUTARY OF LONG GREENCREEK NEAR HYDES, MARYLAND. COLONIA'S LINE 36 FROM ABERDEEN JUNCTION TO NORTH BALTIMORE DELIVERY TRAVERSED THIS AREA,AND AT 1121 EDT THE LINE WAS SHUT DOWN. AN INVESTIGATOR WAS DISPATCHED TO THE SCENE AND FOUND SMALL BUBBLES OF GASOLINE LEAKING INTO THE CREEK. EMERGENCY RESPONSE PERSONNEL, INCLUDING A LOCAL SPILL CONTRACTOR, WERE IMMEDIATELY DISPATCHED TO THE THE SCEN TO BEGIN CONTAINMENT AND CLEAN-UP ACTIVITIES. A CONTAINMENT DAM DOWNSTREAM OF THE LEAK ANDABSORBENT DIAPERS WERE INSTALLED TO ASSIST THE RECOVERY OF PRODUCT. LOCAL FIRE AND POLICE DEPARTMENTS WERE CALLED TO THE SITE AND AT 1250 EDT THE NATIONAL RESPONSE CENTER WAS NOTIFIED OF THE INCIDENT (REPORT NO. 187501). AT 1300 EDT THE STATE OF MARYLAND DEPARTMENT OF THE ENVIRONMENT WAS NOTIFIED OF THE INCIDENT. EXCAVATION OF THE PIPELINE REVEALED PRODUCT WAS LEAKING FROM A SMALL CRACK IN A GOUGE. THIS GOUGE APPEARED TO BE THE RESULT OF THIRD PARTY MECHANICAL DAMAGE. THE DAMAGED SECTION WAS REMOVED AND REPLACED WITH PREHYDROSTATICALLY TESTED PIPE. THE SECTION OF THE PIPE CONTAINING THE DAMAGE HAS BEEN FORWARDED TO AN INDEPENDENT METALLURGIST FOR ANALYSIS. THE ENVIRONMENTAL DEPARTMENTHAS IMPACT STUDIES AND AR MONITORING CONTINUING CLEAN-UP ACTIVITIES. IT IS ESTIMATED THAT LESS THAN 20 GALLONS OF GASOLINE ESCAPED FROM THE SYSTEM AND 5GALLONS OF GASOLINE ESCAPED FROM THE SYSTEM AND 5 GALLONS WERE RECOVERED.
2017-09-29 08:50 | YES | NO | 19930120 | 1993-08-24 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-07-29 | 1315 | KS | BROWN |  | NO |  | NO | SW1/4,SE1/4,SECTION 24,T1S,R17E,BROWN COUNTY KANSAS |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | GASOLINE | 3 | 330 | 315 | NO | NO | 8.63 | 0.2 | 35000 | WELDED |  | 1150 | 500 | YES | 8 | 1579 | 6 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | STEVEN S. BALL - SR. VICE PRESIDENT & GENERAL | 9185883850 | THE WPL #3-8" PIPELINE WAS STRUCK AND PUNCTURED AT MILE POST 80+24 BY A PADONIA TOWNSHIP OWNED AND OPERATED RADER. THE GRADER WAS BEING USED T REBUILD LOW SPOTS IN THE ROAD. THERE WAS NO ONE CALL NOTIFCATION. THE LINE DEPTH HAD BEEN REDUCED TO APPROXIMATELY 10 INCHES THROUGH SIGNIFICANT EROSION. THE PIPELINE WARNING SIGNS WERE IN PLACE ON BOTHE SIDES OF THE ROAD WITH NEAREST MARKER 8 FEET AWAY. THEY WERE NOT OBSTRUCTED AND WERE CLEARLY VISIBLE. THE PIPELINEWAS PUMPING GASOLINE AT THE TIME. THE LINE WAS SHUTDOWN WITHIN 2 OR 3 MINUTES. THE OPERATIONS CONTROL CENTER RECEIVED AN EXCESS FLOW ALARM AND ALMOST IMMEDIATELY FOLLOWING RECEIVED A PHONE CALL FROM THE LEAK SITE. THE PRODUCT WAS CONTAINED WITHIN THE DITCH WHICH WAS PROMPTLY DAMMED UP BY THE ROAD GRADER.
2017-09-29 08:50 | YES | YES | 19930121 | 1993-08-06 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1993-07-14 | 1705 | TX | GAINES |  | NO |  | NO | BLOCK AX, SECTION 24, RGNG R.R. CO SURVEY GAINES COUNTY, TX |  | PUMPING STATION | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 1 | 0 | 1546 | 1184.7369 | 2390.0928 | L. P. G. | 2 | 157 | 0 | NO | NO | 10.75 | 0.19 | 52000 | WELDED |  | 1310 | 920 | YES | 8 | 1798 | 11 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL | PIPELINE WARNING SIGNS | Null | Null | R.T. CRONK - SENIOR VICE PRESIDENT | 9185811800 | THE EQUIPMENT OPERATOR WAS EXCAVATING A DECOMMISSIONED PIPELINE. AN UNEXPOSEDPIPELINE ADJACENT TO THE EXCAVATION RUPTURED. THE FAILED POTION OF THE PIPEHAS BEEN SUBMITTED TO A METALLURGICAL CONSULTANT FOR EVALUATION OF CAUSE. THEFAILED PORTION OF PIPE SHOWED INDICATIONS OF PRIOR MECHANICAL DAMAGE. THEFAILED PORTION WAS SUBMITTED TO A METALLURGICAL CONSULTANT FOR EVALUATION OFCAUSE. THE METALLURGICAL REPORT DETERMINED THE FAILURE WAS CAUSED BYMECHANICAL DAMAGE TO THE PIPE AND IT IS PROBABLE THE DAMAGE THAT CAUSED THEFILURE OCCURRED AT THE TIME OF THE FAILURE.
2017-09-29 08:50 | YES | NO | 19930122 | 1993-08-02 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1993-07-04 | 1405 | NM | LEA |  | NO |  | NO | SECTION 5, RANGE 36-E,TOWNSHIP 17-S.,LEA COUNTY,NEW MEXICO |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2273 | 1741.8544 | 3514.0239 | NATURAL GAS LIQUID | 2 | 197 | 0 | NO | NO | 6.63 | 0.16 | 42000 | WELDED |  | 1424 | 500 | YES | 24 | 1869 | 38 | 8 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | PIPELINE WARNING SIGNS | NO | NO | R. T. CRONK - SENIOR VICE PRESIDENT | 9185811800 | THIRD PARTY DOING EXCAVATION WORK STRUCK PIPELINE WITH BACKHOE. LINE WAS SHUT DOWN, REPAIRED AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19930123 | 1993-08-04 | 809 | ARCO PIPE LINE CO | YES | 1993-07-12 | 807 | TX | TARRANT |  | NO |  | NO | CITGO PETROLEUM CORP 301 TERMINAL RD P.O. BOX 4307, FT. WORTH, TX 76106 |  | TANK FARM | TANK |  | 1965 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | MECHANICAL FAILURE OF A | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22989.7194 | 46379.5499 | DIESEL FUEL | 3 | 422 | 93 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHANDRA L. BADEN - COMPLIANCE COORDINATOR | 7139865356 | FAILURE OF A MECHANICAL TANK GAUGE RESULTED IN AN OVER DELIVERY OF #2 FUEL OIL.
2017-09-29 08:50 | YES | NO | 19930124 | 1993-08-06 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-07-08 | 907 | TN | KNOX | KNOXVILLE | NO |  | NO | 428 FEET NORTHEAST OF PETERS ROAD CROSSING,BENEATH TENNESSEE VALLEY AUTHORITY'S HIGH VOLTAGE TRANSMISSION LINES, SEE ATTACHED DRAWING A-DOT-47-0. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 498110.5863 | 1004890.2473 | DIESEL FUEL | 3 | 903 | 843 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1450 | 235 | YES | 9 | 2200 | 6 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ROY M. CROOK - VICE PRESIDENT -OPERATIONS | 4043645916 | PLANTATION OWNS AND OPERATES AN 8-INCH DIAMETER PIPELINE THAT CARRIES REFINED PETROLEUM PRODUCTS FROM BREMEN, GEORGIA TO KNOXVILLE, TN. ON THE MORING OF JULY 8,1993, AN EMPLOYEE OF SAM C. FRANKLIN & SON, INC. WAS REMOVING SOIL BENEATH TVA HIGH-VOLTAGE POWER LINES USING A LARGE EARTH MOVER. AFTER REMOVING APPROXIMATELY FIVE TO SIX FEET OF COVER, THE OPERATOR STRUCK THE PIPELINE, PUNCTURING A 2.-1/2" X 8" OPENING IN THE SIDE AND TOP OF THE PIPE. DIESEL FUEL WAS BEING TRANSPORTED IN THE PIPELINE AT THE TIME OF THE ACCIDENT. PLANTATIONWAS NOT NOTIFIED OF THE EXCAVATION PRIOR TO THE RUPTURE.
2017-09-29 08:50 | YES | NO | 19930125 | 1993-08-02 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-07-14 | 1510 | KS | BARBER |  | NO |  | NO | HARDTNER PUMP STATION - P169-2+80,APPROXIMATELY 225' WEST OF CENTERLINE OF ROAD. NE/4 OF SECTION 29,R15W,T43S,BARBER CO., KS |  | PUMPING STATION | OTHER | 1/2" COLLAR, NIPPLE, VALV | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15175 | 11628.9664 | 23460.3223 | L. P. G. | 2 | 25 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | D.R. DUBOIS - MANAGER OF ENG & TECHNICAL SERVICES | 9186616267 | WHILE REMOVING ABANDONED PIPING AT OLD PMP STATION, A BACKHOE BROKE1/2" NIPPLE, VALVE AND PLUG OUT OF A 1/2" COLLAR WELDED TO THE TOP OF THE PIPELINE. THE PIPELINE AND FITTINGS WERE BURIED, AND PART OF AN IN-SERVICE PIPELINE.
2017-09-29 08:50 | NO | NO | 19930126 | 1993-07-23 | 809 | ARCO PIPE LINE CO | YES | 1993-07-03 | 720 | TX | HARRIS |  | NO |  | NO | .10 OF A MILE SOUTH OF THE I-45 AND GREENS ROAD. JUNCTION ON THE WEST SIDE OF I-45, ADJACENT OT 12325 NORTH FREEWAY, HOUSTON, TX 77060 |  | LINE PIPE | OTHER | SUMP TANK | 1981 | OTHER | LEAKING DRAIN VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 6130.5918 | 12367.88 | GASOLINE | 3 | 5 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHANDRA L. BRADEN. COMPLIANCE COORDINATOR | 7139655356 | A 2-INCH DRAIN VALVE ON THE METER PROVER LEAKED, CAUSING THE SUMP TANK TO OVERFLOW
2017-09-29 08:50 | YES | NO | 19930127 | 1993-07-28 | 4906 | EXXON PIPELINE CO | YES | 1993-06-27 | 1935 | LA | ST JAMES |  | NO |  | NO | FROM THE INTERSECTION OF HIGHWAY 70 AND HIGHWAY 912 IN ST. JAMES PARISH, LA GO SOUTH ON HIGHWAY 912 APPROXIMATELY 8.1 MILES T BURTON RD. TAKE RIGHT ON BURTON RD |  | PUMPING STATION | PUMP | 1/2INCH SEAL COOLING LINE | 1992 | OTHER | 1/2 INCH COOLING LINE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 57474.2984 | 115948.8747 | CRUDE OIL | 1 | 25 | 24 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.B. HOLT - MANAGER OF ENVIRONMENTAL & REGULATORY COMPLIANCE | 7136565521 | EXXON PIPELINE COMPANY (EPC) RECEIVED A REPORT AT 19:35 OF A CRUDE OIL RELEASE AT A CRUDE OIL PUMPING STATION. THE STATION WAS SECURED AT 19:38.EPC AREA OIL SPILL RSPONSE TEAM AND CONTRACTORS WERE DISPATCHED TO THE LOCATION TO FURTHER CONTAIN THE OIL BEGIN CLEAN-UP OPERATIONS. APPROXIMATELY 25 BARRELS OF CRUDE OIL WERE RELEASED FROM THE STATION WHEN A 1/2 INCH COOLING LINE TO THE DISCHARGE END OF A CRUDE OIL PUMP FAILED. THE CRUDE OIL WAS CONTAINED AT THE STATION AND IN A ROAD-SIDE DITCH ( APPROXIMATELY 24 BARRELS WERE RECOVERED). THER WERE NO INJURIES WITH THIS EVENT.
2017-09-29 08:50 | NO | NO | 19930128 | 1993-08-24 | 18273 | SHELL PIPELINE CORP | YES | 1993-07-20 | 10 | IL | WILLIAMSON | MARION | NO |  | NO | CAPLINE 40-INCH BLOCK VALVE 549 NW 1/4, NW 1/4, SECTION 35, T-10-S, R-2-E |  | LINE PIPE | OTHER | 3/8 INCH STAINLESS STEEL | 1967 | OTHER | SEE BACK OF FORM (PARK K | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11494.8597 | 23189.7749 | CRUDE OIL | 1 | 10 | 0 | NO | NO | 8 | 0.09 | 0 | OTHER |  | 584 | 150 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.R. HAVEY - MANAGER REGULATORY COMPLIANCE | 7132410132 | THE 3/8" STAINLESS STEEL TUBING WAS LYING DIRECTLY ON TOP OF AND IN CONTACT WITH THE CONDUIT. DUE TO THE GROUND VIBRATION FROM TRAINS NEARBY, THE TUBING RUBBED A HOLE IN THE CONDUIT CAUSING THE RELEASE.
2017-09-29 08:50 | YES | NO | 19930129 | 1993-08-12 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-07-13 | 230 | TX | YOAKUM |  | NO |  | NO | WEEMS TATION (MP80), SEC. 837, BLK D. , JOHN H. GIBSON SURVEY 9 MILES WEST (HWY. 83, 2 MILES NORTH OF DENVER CITY, TX. |  | TANK FARM | BOLTED FITTING |  | 1993 | OTHER | MECHANICAL FAILURE OF BOL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4300 | 3295.1931 | 6647.7355 | CRUDE OIL | 1 | 470 | 420 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS - MANAGER OF ENG & TECHNICAL SERVICE | 9186616267 | A BOLT ON THE TOP COUPLING OF A PUMP SUCTION VIBRATION DAMPENER FAILED CAUSING CRUDE OIL TO BE RELEASED. THE SPILL WAS CONTAINED. A TOTAL OF 470 BARRELS WERE ESTIMATED TO HAVE SPILLED, WITH 420 BARRELS BEING RECOVERED.
2017-09-29 08:50 | NO | NO | 19930130 | 1993-07-26 | 26127 | CHEVRON PIPELINE CO | NO | 1993-07-08 | 1530 | CA |  |  | NO |  | NO | WEST OF TRACY BLVD BETWEEN CORRAL HOLLOW RD AND RACY BLVD. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 35 | 30 | NO | NO | 18 | 0.25 | 45000 | WELDED |  | 960 | 300 | YES | 4 | 1100 | 5 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | DOUGLAS TAM - TEAM LEADER | 5106803612 | CONTRACTOR BACK-FILLING HIS PIPELINE PROJECT HIT OUR CRUDE OIL WITH THE CORNER OF LOADER BUCKET. CONTRACTOR WAS NOT SUPPOSED TO BE WORKING AROUND OUR PIPELINE WITHOUT COMPANY PERSONNEL ON SITE.
2017-09-29 08:50 | NO | NO | 19930131 | 1993-07-28 | 12555 | MINNESOTA PIPELINE CO | YES | 1993-07-13 | 1330 | MN | CLEARWATER |  | NO |  | NO | CLEARBROOK PIPELINE TERMINAL, STATE HIGHWAY 92 AND 1/2 MILE EAST ON COUNTY ROAD 74 |  | TANK FARM | PIPE |  | 1968 | OTHER | CAUSE WILL BE DETERMINED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11494.8597 | 23189.7749 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK M. MCCANN | 6124584860 | AN ESTIMATED 1 2 GALLONS OF CRUDE OIL WAS DISCOVERED IN THE SECONDARY CONTAINMENT AREA AROUND TANK 3 PIPING. CONTRACTORS WERE CALLED IN, THE PIPING IN QUESTION WAS REMOVED AND REPLACED. IT WILL BE SENT TO A METALLURGICAL CONSULTANT
2017-09-29 08:50 | YES | NO | 19930132 | 1993-09-10 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-07-30 | 845 | TX | DUVAL |  | NO |  | NO | 1.5 MILES NORTH OF HWY 44 ON COUNTY ROAD 109 WEST SIDE OF SAN DIEGO NEAR LANDFILL |  | LINE PIPE | OTHER | UNKNOWN | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | CRUDE OIL | 1 | 50 | 30 | NO | NO | 5.5 | 0 | 0 | WELDED |  | 660 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | NO | NO | W.D. PARTLOW - ENVIRONMENTAL & SAFETY SUPERVISOR | 7138777370 | LEAK WAS CAUSED BY THIRD PARTY DAMAGE. THE PIPELINE WAS HIT/SEVERED BY A TRENCHING MACHINE WHILE LAYING A PHONE CABLE. A PERMANENT LINE MARKER WAS IN PLACE WITHIN A FEW FEET FROM WHERE THE LEAK OCCURRED. REPLACED WITH 40' SECTION OF NEW PIPE.
2017-09-29 08:50 | YES | NO | 19930133 | 1993-09-08 | 2337 | CHEVRON PIPELINE CO | YES | 1993-08-07 | 820 | LA | PLAQUEMINES | EMPIRE | NO |  | NO | THE LEAK WAS WITHIN FIREWALL AT CHEVRON PIPE LINES, W. DELTA 30 TANK BATTERY AT COORDINATES X255309.1 & Y-222584.7 |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19158.0995 | 38649.6249 | CRUDE OIL | 1 | 50 | 50 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 660 | 200 | YES | 0 | 2160 | 0 | 66 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | NO | NO | ALBERT S. BANTA - NATURAL TEAM LEADER | 5045927516 | WHILE CONTRACTOR WAS EXCAVATING WITHIN THE FIREWALL OF THE FACILITY HE STRUCK OUR PIPELINE.
2017-09-29 08:50 | YES | NO | 19930134 | 1993-08-08 | 19226 | TEXACO PIPELINE INC | NO | 1993-08-13 | 1648 | OK | OKLAHOMA | OKLAHOMA | NO |  | NO | 3/4 MILE EAST OF I-35 ON 15TH STREET IN EDMOND, OKLAHOMA, THEN 2/5 MILE SOUTH TO LOCATION |  | LINE PIPE | PIPE |  | 1918 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 567.0797 | 1144.0289 | CRUDE OIL | 1 | 150 | 120 | NO | NO | 8 | 0.25 | 2535 | WELDED |  | 600 | 18 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | BOYD VRATIL - AREA MANAGER | 9182253469 | CONTRACTOR WAS CONSTRUCTING ROAD FOR HOUSING ADDITION USING LARGE EARTH MOVING EQUIPMENT. DURING CONSTRUCTION A DIRT SCRAPER STRUCK LINE WHILE MAKING PASS, PUNCTURING LINE. EQUIPMENT OPERATOR SHUT DOWN EQUIPMENT AND FOUND LINE MARKER AT FIRST ROAD CROSSING.TEXACO PIPELINE PERSONNEL RECEIVED CALL AND DISPATCHED EMPLOYEES TO SHUT BLOCK VALVES AND CONTAIN SPILL. PIPELINE WAS IDLE AT TIME OF INCIDENT. NOTE: IN REFERENCE TO PART J, QUESTION #5; THE LINE WAS FLAGGED AT A LOCATION 150 YARDS SUTH OF LEAK SITE, BUT NOT AT THE ACTUAL LOCATIONWHERE LINE WAS HIT. THIS WAS DUE TO A COMMUNICATION ERROR BETWEEN TPLI PERSONNEL AND CONTRACTOR.
2017-09-29 08:50 | YES | NO | 19930135 | 1993-08-20 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-07-19 | 1736 | TX | DUVAL |  | NO |  | NO | 3.5 MI. EAST OF ROSITA STATION - ON THE TOBIN RANCH. BETWEEN FREER AND SAN DIEGO, TEXAS. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | CRUDE OIL | 1 | 209 | 50 | NO | NO | 5.5 | 0 | 0 | WELDED |  | 660 | 300 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS ON R.O.W | NO | NO | W.D. PARTLOW - ENVIRONMENTAL & SAFETY SUPV | 7138777370 | LEAK WAS CAUSED BY THIRD PARTY DAMAGE. THE PIPELINE WAS CUT/SEVERED BY A CHISEL PLOW BEING PULLED BY A BULLDOZER. OPERATOR OF BULLDOZER IMMEDIATELY REPORTED INCIDENT TO COASTAL STATES CRUDE GATHERING DISPATCHEING. REPLACED WITH 20' SECTION OF NEW PIPE.
2017-09-29 08:50 | YES | NO | 19930136 | 1993-08-27 | 30661 | NORCO PIPELINE, INC | YES | 1993-08-06 | 1200 | IL | MARSHALL | TOLUCA | NO |  | NO | 322 EAST SANTA FE ROAD, TOLUCA, ILLINOIS T29N-R1E, SECTION 5, MARSHALL COUNTY ILLINOIS |  | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 105000 | 80464.0178 | 162328.4246 | GASOLINE | 3 | 35 | 31 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 795 | 255 | YES | 50 | 925 | 7 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RON WEAKS - OPERATIONS & MAINTENANCE MANAGER | 2196988218 | AT 10:55 AM ON FRIDAY, AUGUST 6, LOU DURHAM CALLED AND REPORTED THERE WAS GASOLINE COMING OUT A VENT PIPE AT 322 E. SANTA FE ROAD IN TOLUCA, IL. OPERATIONS SUPERVISOR LEFT IMMEDIATLEY TO VERIFY IT WAS OUR LEAK. BY 12:00 NOON HE CONTACTED MAZON OFFICE AND CONTRACTORS WERE CONTACTED AND NORCO EMPLOYEES LEFT FOR LEAK SITE. VAC TRUCK WAS CALLED TO REMOVE PRODUCT, CASING WAS REMOVED UNTIL LEAK WAS LOCATED, NEW TESTED PIPE WAS INSTALLED TO REPLACE CORRODED PIPE.
2017-09-29 08:50 | YES | NO | 19930137 | 1993-08-30 | 10313 | KOCH PIPELINE INC | NO | 1993-08-01 | 1532 | OK | CREEK |  | NO |  | NO | SEC 1 T18N, R11E CREEK COUNTY,OKLAHOMA 6795 SOUTH 97TH WEST AVENUE NEAR SAND SPRINGS,OK |  | LINE PIPE | PIPE |  | 1955 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 61305.9183 | 123678.7997 | NATURAL GAS LIQUID | 2 | 4089 | 711 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 587 | 889 | YES | 8 | 875 | 10 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | JAMES H. ELMORE - VICE PRESIDENT | 4053952377 | OVERPRESSURE OF THE PIPELINE DUE TO THERMAL/TEMPERATURE BUILD-UP AND POSSIBLE OPERATOR ERROR.
2017-09-29 08:50 | YES | NO | 19930138 | 1993-08-26 | 809 | ARCO PIPE LINE CO | YES | 1993-07-26 | 1555 | TX | MONTGOMERY |  | NO |  | NO | WILLIS PUMP STATION, MILE POST 89.9, STATION NO. 4746+90,8 MILES WEST OF WILLIS, TEXAS ON F.M.1097. |  | PUMPING STATION | OTHER | 1" THREADED PIPE FITTING | 1980 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 36000 | 27587.6632 | 55655.4598 | CRUDE OIL | 1 | 350 | 90 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | CO REP ON SITE ST DRAWING | Null | YES | STEVEN G. POLING - COMPLIANCE COORDINATOR | 7139865233 | ON JULY 26,1993, A CONTRACTOR WORKING FOR ARCO PIPE LINE COMPANY WAS EXCAVATING NEAR THE 20" TRUNK PIPELINE AT WILLIS PUMP STATION. AT 3:55 PM, A BACKHOEOPERATED BY THE CONTRACTOR HIT AND BROKE A 1" THREADED PIPE FITTING ON THE 20" TRUNK PIPELINE. THE ARCO PIPE LINE COMPANY CONTROL CENTER SHUT DOWN THE PIPELINE. VACUUM TRUCKS WERE DISPATCHED TO THE SCENE IN ORDER TO REMOVE FREE STANDING CRUDE OIL. THE BROKEN 1" THREADED PIPE FITTINGS WAS REMOVED AND REPLACED WITH A 1" PIPE PLUG. CRUDE CONTAMINATED SOIL, TREES, AND OTHER VEGETATION WERE COLLECTED IN ROLL-OFF BINS FOR OFF-SITE DISPOSAL. ONCE SILL DEBRIS WAS REMOVED FROM THE SITE, GRASS WAS PLANTED ALONG THE RIGHT OF WAY. KEN ORSBURN OF THE RAILROAD COMMISSION OF TEXAS AND SAM PARKS OF THE TEXAS HIGHWAY DEPARTMENT WERE SATISFIED WITH ARCO PIPE LINE COMPANY'S CLEANUP EFFORT.
2017-09-29 08:50 | NO | NO | 19930140 | 1993-09-13 | 8166 | INTERSTATE ENERGY CO | NO | 1993-08-23 | 1030 | PA | PHILADELPHIA | LINWOOD | NO |  | NO |  |  | PUMPING STATION | OTHER | NITROGEN VENTING AT STA. | 1976 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | STA. BLOCK VALVE LEAKED | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11494.8597 | 23189.7749 | NOT GIVEN | 1 | 25 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.C. SPARKMAN - GENERAL MANAGER | 2153275325 | PIPELINE WAS DISPLACED WITH NITROGEN FOR TOTAL LENGTH (85 MILES). A SHORT ONTHE CATHODIC PROTECTION WAS OBSERVED ACROSS AND INSULATED FLANGE. TO CLEAR THE SHORT THE NITROGEN WAS TO BE VENTED BETWEEN THE PUMP STATION (ORIGIN) AND THE FIRST PIPELINE BLOCK VALVE (MILEPOST 9.53). DURING THE VENTING OPERATION A SLUG OF OIL (APPROX. 10 GALLONS) ESCAPED INTO THE ATMOSPHERE AS A RESULT OFA SUSPECTED LEAK ACROSS THE STATION BLOCK VALVE. THE OIL ATOMIZED AND FELL ON ADJACENT HOMES (APPROXIMATELY 12) AND VEHICLES (45, TO DATE). CLEAN UP OF PROPERTIES AND VEHICLES ARE ESTIMATED TO BE COMPLETED IN 2-3 WEEKS.
2017-09-29 08:50 | YES | NO | 19930141 | 1993-09-08 | 2552 | COLONIAL PIPELINE CO | YES | 1993-07-28 | 1720 | NC | CABARRUS | CONCORD | NO |  | NO | COLONIAL PIPELINE COMPANY'S KANNAPOLIS PUMPIING STATION. APPROX 4 MILES TO KANNAPOLIS BM 651 |  | PUMPING STATION | OTHER | 3/8" PRESSURE SWITCH TUB | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22989.7194 | 46379.5499 | FUEL OIL | 2 | 5 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | VICTOR A. YARBOROUGH - DIRECTOR OF ENGINEERING | 4048412304 | DURING A DAILY CHECK AT COLONIAL PIPELINE COMPANY'S KANNAPOLIS NO.2 PUMP STATION, A COMPANY EMPLOYEE FOUND PRODUCT LEAKING FROM TUBING LOCATED IN AN ACCESS WELL. THE CONTROL CENTER IN ATLANTA WAS NOTIFIED, AND THE STATION WAS IMMEDIATELY SHUT DOWN. A CONTRACTOR WAS CALLED TO THE STATION TO ASSIST IN CLEAN UP AND REPAIRS. AT 1817, EST, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO 189313) WHEN IT BECAME APPARENT THAT CLEANUP COSTS WOULD EXCEED $5,000.THE NORTH CAROLINA DIVISION OF ENVIRONMENTAL MANAGEMENT WAS ALSO INFORMED OFTHE INCIDENT. AN ESTIMATED FIVE BARRELS OF FUEL OIL LEAKED INTO THE SURROUNDING SOIL; ONE BARREL WAS RECOVERED. THE CONTAMINATED SOIL HAS BEEN EXCAVATED AND PLACED IN A PLASTIC ENVELOPE FOR REMEDIATION. THE CAUSE OF THE LEAK WAS FOUND TO BE A HOLE IN A CORROSION PIT IN THE 3/8" STEEL TUBING CONNECTING THE NO.1 PUMP UNIT AND THE STATION DISCHARGE PRESSURE SWITCH.
2017-09-29 08:50 | YES | NO | 19930142 | 1993-08-30 | 443 | AMOCO PIPELINE CO | YES | 1993-07-29 | 1100 | KS | ALLEN | HUMBOLDT | NO |  | NO | SEC 10 T26S R18E, ALLEN COUNTY, KS |  | TANK FARM | PIPE |  | 1959 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 383.162 | 772.9925 | CRUDE OIL | 1 | 200 | 190 | NO | NO | 24 | 0.25 | 0 | NO DATA |  | 125 | 30 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. CARICO - AREA MANAGER CUSHING OPERATIONS | 9182257271 | PIT DEVELOPED ON BOTTOM SIDE OF PIPE, IN A LOW AREA OF THE LINE. POSSIBLE SALT-WATER CORROSION.
2017-09-29 08:50 | NO | NO | 19930143 | 1993-08-12 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1993-06-30 | 2237 | PA | BERKS | MUHLENBERG TOWNSHIP | NO |  | NO |  |  | LINE PIPE | OTHER | TRANSMIX TANK | 1977 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 8500 | 6513.7538 | 13140.8725 | GASOLINE | 3 | 3 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER - REGULATORY COMPLIANCE ADMINISTRATOR | 2158208300 | PRIOR TO ARRIVAL OF A FUEL OIL, THE BUCKEYE EMPLOYEE FLUSHED THE GASOLINE OUT OF THE MANIFOLD, VIA A 2-INCH VALVE TO THE TRANSMIX TANK. THE EMPLOYEE FORGOT TO CLOSE TH4E 2-INCH VALVE. WHEN THE EMPLOYEE OBSERVED PRODUCT COMING FROMTHE TANK VENT, THE 2-INCH VALVE WAS CLOSED IMMEDIATELY. THE RELEASED PRODUCTWAS CONTAINED IN THE TANK DIKE. AFFECTED SOIL WAS REMOVED AND SITE CLEANUP WAS COMPLETED TO THE SATISFACTION OF THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENT
2017-09-29 08:50 | NO | NO | 19930144 | 1993-08-26 | 809 | ARCO PIPE LINE CO | NO | 1993-06-26 | 1130 | TX | GREGG |  | NO |  | NO | 15+39 NE WATSON TIE-IN,1/2MILE NORTH OF KILGORE, TEXAS |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 4 | 2 | NO | NO | 6 | 0.28 | 0 | NO DATA |  | 202 | 20 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G. POLING - COMPLIANCE COORDINATOR | 7139865233 | THE LEAK FROM A 6" PIPELINE OCCURRED ON JUNE 26,1993. CRUDE OIL LEAKED INTO RABBIT CREEK IN JOHN CARITHER SURVEY, GREGG COUNTY, TEXAS. AFTER NOTIFICATION, ARCO PIPE LINE COMPANY IMMEDIATELY DISPATCHED A VACUUM TRUCK TO RETRIEVE FREE STANDING CRUDE OIL. SIMULTANEOUSLY, A TEMPORARY SADLE WAS PLACED ON THE 6"PIPELINE TO STOP THE LEAK. CRUDE CONTAMINATED DEBRIS WAS REMOVED FROM THE SPILL SITE.
2017-09-29 08:50 | NO | NO | 19930145 | 1993-08-27 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1993-07-27 | 640 | OH | ALLEN | SHAWNEE TOWNSHIP | NO |  | NO |  |  | PUMPING STATION | OTHER | BASKET STRAINER | 1982 | OTHER | TUBE TURN CLOSURE "O-RING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | OIL AND GASOLINE | 3 | 5 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER - REGULATORY COMPLIANCE ADMINISTRATOR | 2158208300 | GAS OIL WAS RELEASED FROM A BASKET STRAINER CLOSURE. THE PIIPELINE WAS IMMEDIATELY SHUT DOWN. ALL REQUIRED NOTIFICATIONS WERE MADE IN A TIMELY MANNER. CLEANUP WAS COMPLETED TO THE SATISFACTION OF THE OHIO ENVIRONMENTAL PROTECTION AGENCY. THE O-RING WAS REPLACED AND THE PIPELINE SYSTEM WAS RETURNED TO SERVIC
2017-09-29 08:50 | YES | NO | 19930146 | 1993-08-24 | 443 | AMOCO PIPELINE CO | YES | 1993-08-03 | 1407 | WY | NATRONA |  | NO |  | NO | SPILL OCCURRED IN THE SECTION 6 TOWNSHIP 33N 79W NATRONA COUNTY, WYOMING AT AMOCO PIPELINE'S CASPER STATION FACILITY, CASPER, WYOMING. |  | PUMPING STATION | OTHER | 1/2"LINE ON A GRAVITOMETE | 1960 | OTHER | 1/2"LINE ON A GRAVITOMETE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 766.324 | 1545.985 | CRUDE OIL | 1 | 70 | 69 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. PETERSON - CASPER OPERATING AREA MANAGER | 3072662119 | ON AUGUST 03, 1993, AT 14:07 MST, AMOCO PIPELINE COMPANY DISCOVERED A CRUDE OIL RELEASE AT ITS CASPER STATION, CASPER, WYOMING. THE SOURCE OF THE RELEASEWAS 1/2" LINE TO A GRAVITOMETER UNIT. AN AMOCO PIPELINE BACKHOE WAS CONDUCTIN MAINTENANCE IN THE AREA AND STRUCK THE 1/2" LINE. AT 16:36 MST, PETTY OFFICER EASON OF THE NRC WAS NOTIFIED OF THE RELEASE, REPORT #190498. AN ESTIMATED70 BARRELS OF CRUDE OIL WAS RELEASED AND APPROXIMATELY 60 BARRELS WERE RECOVERED. THE RELEASE WAS CONFINED TO THE AMOCO'S STATION PROPERTY AND NO CRUDE OIL REACHED ANY SURFACE OR GROUND WATERS.
2017-09-29 08:50 | YES | NO | 19930147 | 1993-09-28 | 443 | AMOCO PIPELINE CO | YES | 1993-08-25 | 1117 | IL | KNOX |  | NO |  | NO | SECTION 10 T 10N R1E, KNOX, COUNTY, ILLINOIS PIPE SEGMENT: MANHATTAN - FREEMAN AT MILE POST 355. |  | LINE PIPE | PIPE |  | 1936 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2000 | 1900 | NO | NO | 12 | 0.34 | 35000 | WELDED |  | 576 | 14 | YES | 8 | 900 | 0 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | PIPELINE MARKERS IN GROUN | NO | NO | PAT MCGANNON - AREA MANAGER | 2197382359 | OTTOM PORTION OF A 90 DEGREE ELBOW WHICH WAS REPLACED.
2017-09-29 08:50 | NO | NO | 19930148 | 1993-09-28 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1993-08-31 | 830 | CA | LOS ANGELES | PORT OF LONG BEACH | NO |  | NO | HARBOR SCENIC DRIVE - 170' SOUTH OF OCEAN BOULEVARD |  | LINE PIPE | OTHER | 90 ELL | 1989 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 13027.5076 | 26281.7449 | CRUDE OIL | 1 | 30 | 8 | NO | NO | 6 | 0.28 | 37440 | WELDED |  | 1500 | 350 | YES | 8 | 1900 | 6 | 89 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. KELLEY - SOUTHERN DISTRICT MANAGER | 8053270110 | LUBBOCK COUNTY ROAD GRADER PUNCTURED PIPELINE WHILE DEEP GRADING BAR-DITCH.
2017-09-29 08:50 | NO | NO | 19930149 | 1993-10-15 | 809 | ARCO PIPE LINE CO | YES | 1993-10-05 | 1540 | OK | LINCOLN |  | NO |  | NO | ONE MILE EAST OF SPARKS,OKLAHOMA ON HWY.18B |  | LINE PIPE | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | DIESEL FUEL | 3 | 2 | 1 | NO | NO | 8.65 | 0.32 | 35000 | WELDED |  | 650 | 300 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | CHANDRA L. BRADEN - COMPLIANCE COORDINATOR | 7139865356 | THE RELEASE OCCURRED WHEN THE LINCOLN COUNTY DISTRICT #2 HIT THE PIPELINE WITH A ROAD GRADER WHILE DOING ROAD REPAIRS.
2017-09-29 08:50 | NO | NO | 19930150 | 1993-10-14 | 809 | ARCO PIPE LINE CO | YES | 1993-10-05 | 1400 | MO | CHARITON |  | NO |  | NO | NEAR TEST POINT 23.1 AT STA.1220+92, SOUTH EDGE OF MENDON, MO ON HWY.11. |  | LINE PIPE | PIPE | IN CASING | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9195.8877 | 18551.8199 | GASOLINE | 3 | 7 | 6 | NO | NO | 8.65 | 0.32 | 35000 | WELDED |  | 495 | 150 | YES | 24 | 804 | 10 | 70 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | CHANDRA L. BRADEN - COMPLIANCE COORDINATOR PRODUCTS B.U. | 7139865356 | D VALVE. THIS OCCURRED DURING A SCHEDULED START UP TO TOLEDO, OHIO. THE PUMPSTATION AT HARTSDALE, INDIANA AND GOSHEN, INDIANA WERE BOTHE STARTED CAUSINGSURGE PRESSURE IN THE PIPE. THE RESULTING PRESSURE EXCEEDED THE STRENGTH OF THE PIPE CAUSING A LONGITUDINAL STRESS FRACTURE OF PIPE.
2017-09-29 08:50 | YES | NO | 19930151 | 1993-10-25 | 19326 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1993-10-01 | 2200 | TX | MIDLAND |  | NO |  | NO | SECTION 33, BLOCK 39,T-2-S,T&P RR COMPANY SURVEY 5 MILES SOUTH OF MIDLAND, TEXAS |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5100 | 3908.2523 | 7884.5235 | CRUDE OIL | 3 | 60 | 0 | NO | NO | 10.75 | 0.37 | 25000 | WELDED |  | 765 | 350 | YES | 8 | 1105 | 10 | 90 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWIN H. GRIPP - DISTRICT MANAGER | 9159497019 | THE LEAK WAS REPORTED AT 2200 ON OCTOBER 1, 1993. THE LINE WAS IMMEDIATELY SHUT DOWN. LEAK WAS DUG OUT AND CLAMPED OFF BY 0100 ON OCTOBER 2, 1993. PERMANENT REPAIRS WERE COMPLETED OCTOBER 4, 1993. REMEDIATION OF OIL SOAKED AREA IS UNDER WAY.
2017-09-29 08:50 | YES | NO | 19930152 | 1993-10-14 | 30661 | NORCO PIPELINE INC. | YES | 1993-09-15 | 621 | IN | DE KALB |  | NO |  | NO | ONE QUARTER MILE WEST OF COUNTY ROADS 18AND 75 INTERSECTION |  | LINE PIPE | PIPE |  | 1944 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 153264.7958 | 309196.9992 | FUEL OIL | 3 | 676 | 344 | NO | NO | 8 | 0.32 | 0 | WELDED |  | 602 | 900 | YES | 8 | 790 | 8 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICK H. HOOD - SAFETY & ENVIRONMENTAL REPRESENTATIVE | 5014443507
2017-09-29 08:50 | NO | NO | 19930153 | 1993-10-25 | 30661 | NORCO PIPELINE INC. | YES | 1993-09-15 | 0 | OH | WILLIAMS |  | NO |  | NO | NEAR U.S. HIGHWAY 6 ON THE OHIO/INDIANA STATE LINE, IN WILLIAMS COUNTY, OH ACCORDING TO THE OPERATOR, NORCO PIPELINE, INC. |  | LINE PIPE | PIPE |  | 0 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 0 | 0 | Null | Null | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E. DALE YOUNGBERG - MANAGER OPERATION ARCO PIPE LINE CO. | 7139865394 | UNDER CONTRACT WITH THE OWNER/OPERATOR, NORCO PIPELINE, INC. ARCO PIPE LINE COMPANY PROVIDES CERTAIN PIPELINE SERVICES ON THE CHICAGO-TOLEDO HARTSDALE EAST PIPELINE. THEREFORE, IT BECAME AWARE OF A DISCHARGE OF DIESEL FUEL FROM THE PIPELINE ON OR ABOUT SEPTEMBER 15,1993. WITHOUT ADMITTING ANY LIABILITY FORTHE DISCHARGE, OR THE EXISTENCE OF ANY REPORTING OBLIGATION ON ITS PART , ARCO PIPE LINE COMPANY TELEPHONICALLY CONFIRMED THAT THE OPERATOR, NORCO PIPELINE, INC. HAD REPORTED THE EXISTENCE OF THIS SPILL TO THE NRC AND THERFORE IS SUBMITTING THIS FOLLOW-UP REPORT. HOWEVER, BECAUSE IT IS NOT THE OWNER OR OPERATOR OF THE PIPELINE, ARCO PIPE LINE COMPANY DOES NOT POSSESS THOSE FACTS NECESSARY TO RESPOND TO MOST OF THE INQUIRIES ON THE FORM. THEREFORE, ITS RESPONSE TO MOST ITEMS NECESSARILY IS "UNKNOWN." THE NORCO REPORT NUMBER IS 197889
2017-09-29 08:50 | NO | NO | 19930154 | 1993-11-04 | 809 | ARCO PIPE LINE CO | YES | 1993-10-18 | 700 | MO | MACON |  | NO |  | NO | AT NORTHA EDGE OF ELMER, MISSOURI, AT STATION #3230+32. ELMER IS LOCATED NORTH OF 36 HWY. ON HWY.3, THEN WEST ON "J" BLACKTOP. |  | LINE PIPE | PIPE | IN CASING | 1938 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 45979.4387 | 92759.0997 | GASOLINE | 3 | 7 | 5 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 495 | 160 | YES | 24 | 804 | 10 | 70 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | CHANDRA L. BRADEN - COMPLIANCE COORDINATOR | 7139865356 | RELEASE CAUSED BY EXTERNAL CORROSION INSIDE CASING.
2017-09-29 08:50 | YES | NO | 19930155 | 1993-09-27 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1993-08-30 | 840 | CA | SAN BERNARDINO |  | NO |  | NO | SECTION 13, T6N,R6E, , SBB & M, SAN BERNARDINO COUNTY, CALIFORNIA AT MILE-POST 202.9 OF FCPL LINE 90. |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 68969.1581 | 139138.6496 | CRUDE OIL | 1 | 20 | 0 | NO | NO | 16 | 0.03 | 52 | WELDED |  | 1170 | 170 | YES | 4 | 1520 | 9 | 77 | EXTERNAL | Null | YES | OTHER | SMALL PIT HOLE | NO DATA |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | LINE WAS NOT OPERATING AT THE TIME THE LEAK WAS DISCOVERED. REPAIR PERSONNELTHEN EXCAVATED AREA AND PROCEEDED TO REPAIR THE LINE. OIL-LADEN SOIL WAS REMOVED, AND A NEW 40 FOOT SECITON OF PIPE WAS INSTALLED TO PERMIT LINE TO BE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19930156 | 1993-11-08 | 2271 | CHASE TRANSPORTATION CO | YES | 1993-10-08 | 1720 | KS | RENO |  | NO |  | NO | NW NW1/4 SEC. 1 T26S R7W RENO COUNTY, KANSAS |  | PUMPING STATION | OTHER | UNKNOWN | 1977 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 76632.3979 | 154598.4996 | GASOLINE | 1 | 25 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHUCK JOHNSON - VICE PRESIDENT | 3148327484
2017-09-29 08:50 | YES | NO | 19930157 | 1993-11-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1993-09-28 | 852 | TX | GAINES |  | NO |  | NO | SECTION 48, TRACT 1-T-GA-12 BLOCK AX, GAINES COUNTY, TEXAS |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5383 | 4125.122 | 8322.0372 | NATURAL GAS LIQUID | 2 | 397 | 0 | NO | NO | 8 | 0.22 | 52000 | WELDED |  | 1440 | 660 | YES | 24 | 2430 | 10 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | GARY R. SMETHERS - GENERAL MANAGER OPERATIONS SUPPORT | 9185811800 | THE LINE WAS STRUCK BY A THIRD PARTY USING AN AUGER MACHINE TO INSTALL ANCHORS AT A WELL SITE.
2017-09-29 08:50 | NO | NO | 19930159 | 1993-11-12 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-10-16 | 810 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | TANK 14 PLANTATION'S BATON ROUGE TANK FARM LOCATED OFF BLOUNT ROAD IN BATON ROUGE, LOUISIANA. |  | TANK FARM | TANK |  | 1942 | OTHER | CRACK IN THE FLOOR TO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8429.5638 | 17005.835 | GASOLINE | 3 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK - VICE PRESIDENT -OPERATIONS | 4043645916 | ON THE MORNING OF OCTOBER 16, 1993, WHILE DRAWING WATER OFF TANK 14 AT PLANTATION'S BATON ROUGE TANK FARM, A PLANTATION TERMINAL OPERATOR DISCOVERED A DISCOLORATION ON THE SKETCH PLATE. THE TANK WAS TAKEN OUT OF SERVICE, CLEANED AND INSPECTED. THE INSPECTION REVEALED A CRACK IN THE SHELL TO FLOOR FILLET WELD. THE CRACK WILL BE REPAIRED BY REPLACING THE SKETCH PLATE WITH NEW PLATE. PART D - CAUSE OF ACCIDENT- SHELL FILLET WELD
2017-09-29 08:50 | YES | NO | 19930160 | 1993-11-15 | 12628 | MOBIL PIPELINE CO | NO | 1993-10-17 | 800 | TX | HENDERSON |  | NO |  | NO | ATHENS, TEXAS ON B&J RANCH AT OR NEAR INTERSECTION OF HIGHWAY 317 AND HIGHWAY 607 |  | LINE PIPE | OTHER | PIN HOLE IN WELD | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2298.9719 | 4637.955 | CRUDE OIL | 1 | 75 | 65 | NO | NO | 12.75 | 0.25 | 1180 | WELDED |  | 250 | 40 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | T.P. MURPHY - SAFETY & HEALTH COMPLIANCE ADVISOR | 2146583869 | E DISPATCHED AND INITIATED RECOVERY AND CLEAN-UP OPERATIONS. CRUDE OIL ENTERED A TRIBUTARY TO FLAT CREEK. CONTAINMENT BOOMS WERE SET, ABSORBMENT PADS ANDVACUUM TRUCKS WERE UTILIZED. 65 BBLS. WERE RECOVERED. NO CRUDE OIL ENTERED COASTAL WATERS.
2017-09-29 08:50 | YES | NO | 19930161 | 1993-11-08 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1993-09-30 | 1520 | OK | OKLAHOMA | OKLAHOMA CITY | NO |  | NO | SW/4 SECTION 30-12N-2W.FROM I-35, GO 1/4 MILE E. ON NE 10TH ST. TO BRYANT AVE, THEN TURN N.ON BRYANT APPR. 1/4 MILE. STATION ON E. SIDE OF BRYANT(1400 N. BRYANT |  | PUMPING STATION | VALVE |  | 1984 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 153264.7958 | 309196.9992 | CRUDE OIL | 1 | 350 | 200 | NO | NO | 0 | 0 | 0 | FLANGED |  | 500 | 453 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E.L. WOOTEN - COMPLIANCE COORDINATOR | 9185866962 | FAILURE OF CHECK VALVE COVER DUE TO EXCESSIVE PRESSURE.
2017-09-29 08:50 | YES | NO | 19930162 | 1993-11-09 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-10-10 | 830 | OK | CUSTER |  | NO |  | NO | BUXTON-BORGER LINE - MP 135-22+25;NW/4 SEC.13,T12N,R18W,CUSTER CO.,OK:1 MILE SOUTH,3.4 MILES EAST,.3MILE SOUTH INTO PASTURE. |  | LINE PIPE | LONGITUDINAL WELD |  | 1951 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 76632.3979 | 154598.4996 | CRUDE OIL | 1 | 1900 | 540 | NO | NO | 10.75 | 0.2 | 42000 | WELDED |  | 1142 | 937 | YES | 24 | 1434 | 9 | 78 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS - MANAGER OF ENGINEERING & TEDCHANICAL SERVICES | 9186616267 | THE LEAK WAS DISCOVERED AT 8:30 AAM ON OCTOBER 10, 199 DURING THE INVESTIGATION OF AN ABNORMAL PRESSURE CONDITION. THE PIPE FAILED DUE TO A DEFECTIVE PRE-1970 ERW LONGITUDINAL SEAM.
2017-09-29 08:50 | YES | NO | 19930163 | 1993-11-09 | 15490 | PHILLIPS PIPE LINE CO | YES | 1993-10-09 | 1130 | TX | BRAZORIA |  | NO |  | NO | SWEENY PUMP STATION, OLD OCEAN, TEXAS |  | PUMPING STATION | OTHER | RELIEF VALVE | 1979 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 9962.2117 | 20097.8049 | GASOLINE | 3 | 90 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS - MANAGE OF ENGINEERING & TECH. SERVICES | 9186616267 | NITROGEN SUPPLY MAINTAINING SET PRESSURE ON FLEX-FLOW RELIEF VALVE FAILED CAUSING RELIEF VALVE TO OPEN
2017-09-29 08:50 | NO | NO | 19930164 | 1993-11-09 | 12125 | MARATHON OIL CO | NO | 1993-10-16 | 420 | LA |  |  | YES | LAT.28 O4'22" LONG.92 3 | NO | VR 386B FLATFORM GULF OF MEXICO OUTER CONFINENTAL SHELF VERMILION BLOCK 386 OCS - G -2278 |  | LINE PIPE | PIPE | LEAK OCCURED IN THE | 1980 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 15326.4796 | 30919.6999 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 3.5 | 0.32 | 36000 | WELDED |  | 2880 | 1650 | YES | 24 | 3600 | 10 | 81 | EXTERNAL | Null | YES | OTHER | EXTERNAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | BILL FAMRER - PRODUCTION FORMAN | 3182338240 | THE OIL PIPELIN, DEPARTING VR386B DEVELOPED A SMALL LEAL + 8' ABOVE THE WATER LINE. A VERY MINUTE AMOUNT OF OIL WAS RELEASED INTO THE GULF. THE PLATFORM WAS SHUT-IN AND SECURE. PREPARATION ARE BEING MADE FOR REPAIR WORK. PART C - PIPELINE RISER SECTION AT APPROX. 8" ABOVE THE WATER LINE.
2017-09-29 08:50 | NO | NO | 19930165 | 1993-10-25 | 809 | ARCO PIPE LINE CO | NO | 1993-09-22 | 1430 | TX | ANDERSON |  | NO |  | NO | NORTH OF SLOCUM TEXAS, TO FM 2022, TAKE THE FIRST COUNTY ROAD THE LEFT, AND FOLLOW TO OLD WOODEN BRIDGE, THE LEAK SITE WAS N. OF THE WOODEN BRIDGE. |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 10 | 9 | NO | NO | 8 | 0.32 | 0 | NO DATA |  | 179 | 200 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G. POLING - COMPLIANCE COORDINATOR | 7139865233 | THE LEAK FROM A 8" PIPELINE WAS DISCOVERED BY EDDIE LAWLER AT 2:30 P.M. CRUDE OIL LEAKED INTO SQUIRREL CREEK IN J. CRAWFORD A-189, ANDERSON COUNTY, TEXAS. AFTER NOTIFICATION, ARCO PIPE LINE COMPANY IMMEDIATELY DISPATCHED PERSONNELTO PLACE BOOM ACROSS SQUIRREL CREEK. NEXT, VACUUM TRUCKS WERE DISPATCHED TO RETRIEVE FREE STANDING CRUDE OIL. SIMULTANEOUSLY, PERSONNEL WASHED THE BANKS OF THE CREEK TO REMOVE ANY CRUDE OIL. THE LEAK WAS REPAIRED WITH A GASO LEAK CLAMP WITH PLATE.
2017-09-29 08:50 | YES | NO | 19930166 | 1993-11-09 | 809 | ARCO PIPE LINE CO | NO | 1993-10-07 | 1430 | TX | RUSK |  | NO |  | NO | APPROXIMATELY,698 +45 - 1/5 MILES SOUTH OF LARID HILL ROBERT W. SMITH SURVEY. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 700 | 612 | NO | NO | 12 | 0.38 | 0 | NO DATA |  | 178 | 125 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | EXTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN G. POLING - COMPLIANCE COORDINATOR | 7139865233 | THE LEAK FROM THE 12" PIPELINE WAS DISCOVERED BY BILLY VERNON OF MCMURREY PIPE LINE AT 2:30 P.M. CRUDE OIL LEAKED INTO RABBIT CREEK IN ROBERT W. SMITH SURVEY, RUSK COUNTY, TEXAS. AFTER NOTIFICATION, ARCO PIPE LINE COMPANY (APL) IMMEDIATELY DISPATCHED PERSONNEL TO BUILD DAMS WITH FLUME PIPE AND PLACE BOOM ACROSS THE CREEK. ONCE THE SPILL HAD BEEN CONTAINED, PERSONNEL WASHED THE CREEK AND PICKED UP THE CRUDE OIL WITH VACUUM TRUCKS. ALSO, CRUDE AFFECTED SOIL WAS REMOVED AND REPLACED WITH FRESH TOP SOIL. A TEMPORARY SADDLE WAS PLACED ONTHE 12" PIPELINE UNTIL PERMANENT REPAIRS COULD BE MADE. THE EPA AND RRC GAVEAPPROVAL OF APL'S FINAL CLEAN-UP EFFORTS.
2017-09-29 08:50 | NO | NO | 19930170 | 1993-10-28 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-09-29 | 800 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | TANK 16 - PLANTATION'S BATON ROUGE TANK FARM LOCATED OFF BLOUNT ROAD IN BATON ROUGE, LOUISIANA. |  | TANK FARM | TANK |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 9195.8877 | 18551.8199 | GASOLINE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | CREVICE CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK - VICE PRESIDENT - OPERATIONS | 4043645916 | ON THE MORNING OF SEPTEMBER 29, 1993, WHILE GAUGING TANK 16 AT PLANTATION'S BATON ROUGE TANK FARM, A UTILITY OPERATOR DISCOVERED A SISCOLORATION ON THE SKETCH PLATE. THE TANK WAS TAKEN OUT OF SERVICE, CLEANED AND INSPECTED. THE INSPECTION REVEALED A CRACK (DUE TO CREVICE CORROSION), APPROXIMATELY 2" FROM WHERE THE FLOOR ATTACHES TO THE TOP OF THE SUMP LIP. THE TANK WAS REPAIRED BY REMOVING APPROXIMATELY 24" OF FLOOR PLATE AROUND THE ENTIRE SUMP AND REPLACING IT WITH 1/4" THICK STEEL PLATE.
2017-09-29 08:50 | YES | NO | 19930171 | 1993-10-28 | 19536 | TOTAL PIPELINE CORP | NO | 1993-09-27 | 800 | OK | CARTER | HEALDTON | NO |  | NO | NW NW NW 17-4S-R3W |  | TANK FARM | OTHER | MAJOR HEAD SWITCH USED | 1986 | OTHER | DIAPHRAGM ON LEVEL GAUGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 766.324 | 1545.985 | CRUDE OIL | 1 | 130 | 130 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL J. COOPER - MANAGER OF REGULATORY COMPLIANCE | 4052291638 | STATION OPERATOR ARRIVED AT STATION AT 0800 HOURS TO GAUGE STORAGE TANK. WHEN HE APPROACHED TANK HE NOTICED OIL IN DIKE AREA. HE DETERMINED SOURCE AND SHUT VALVE ON MAJOR HEAD SWITCH. EMERGENCY CREW WAS CALLED IN AND ALL OF OIL WAS PICKED UP WITH VACCUM TRUCKS. OIL STAIN WAS PICKED UP WITH ABSORBENT MATERIALS. EVIDENTALY THE DIAPHRAGM HAD RUPTURED EARLIER IN THE MORNING PRIOR TO THE STATION OPERATOR'S ARRIVAL. THE TANK SWITCH HAS BEEN REMOVED AND THE VALVE PLUGGED SINCE NEWER MORE SOPHISTICATED EQUIPMENT HAS BEEN INSTALLED.
2017-09-29 08:50 | YES | NO | 19930172 | 1993-10-20 | 2552 | COLONIAL PIPELINE CO | YES | 1993-09-06 | 1245 | NC | MECKLENBURG |  | NO |  | NO | COLONIAL PIPELINE COMPANY"S CHARLOTTE DELIVERY FACILITY |  | TANK FARM | OTHER | 1/2 INCH NIPPLE | 0 | OTHER | DEFECTIVE PIPING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 216000 | 165525.9794 | 333932.7591 | GASOLINE | 1 | 20 | 16 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR TECHNICAL & REGULATORY | 4048412402 | ON SEPTEMBER 6, 1993, GASOLINE WAS DISCOVERED SEEPING INTO A SMALL CREEK LOCATED ON COLONIAL PIPELINE COMPANYS CHARLOTTE DELIVERY PROPERTY. COMPANY PERSONNEL IMMEDIATELY DEPLOYED BOOMS ON THE CREEK AND SUCCESSFULLY CONTAINED THE PRODUCT, PREVENTING IT FROM ENTERING THE STATION RETENTION POND. THREE GALLONS OF GASOLINE WERE RECOVERED. BECAUSE THE PRODUCT ENTERED THE SMALL STREAM, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 196511) OF THE INCIDENT AT 1605 EST ON SEPTEMBER 6. THE NORTH CAROLINA DEPARTMENT OF ENVIRONMENTAL, HEALTH, AND NATURAL RESOURCES WAS ALSO NOTIFIED OF THE INCIDENT. AT THE PRESENT TIME, AN INVESTIGATION CONTINUES TO DETERMINE IF THIS PRODUCT RESULTED FROMAN ACTIVE LEAK OR IS RESIDUAL PRODUCT FROM AN EARLIER INCIDENT. ACTIONS TAKEN TO DATE INCLUDE THE INSTALLATION OF A MONITORING WELL, RECOVERY TRENCHES, AND LIMITED EXCAVATION OF STATION MANIFOLD PIPING. THIS REPORT WILL BE AMENDED AS SOON AS THE INVESTIGATION DETERMINES THE EXACT CAUSE OF THE INCIDENT.
2017-09-29 08:50 | YES | NO | 19930173 | 1993-10-20 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1993-09-20 | 1058 | CA | CONTRA COSTA | BRENTWOOD | NO |  | NO | APPROXIMATELY 30 FEET SOUTH OF INTERSECTION OF BALFOUR ROAD AND FAIRVIEW AVENUE (PLMP 23.0). |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 102000 | 78165.0458 | 157690.4696 | DIESEL FUEL | 3 | 230 | 230 | NO | NO | 10.75 | 0.25 | 0 | WELDED |  | 1360 | 0 | YES | 24 | 1700 | 11 | 57 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | INSPECTOR ON SITE AND | YES | YES | J.M. ABBOUD - SENIOR V.PRESIDENT -OPERATIONS & ENGINEERING | 2134867720 | LINE WAS HIT IN THE SIDE THROUGH APPROXIMATELY 6 INCHES OF SOIL WHILE CONTRACTOR WAS COPACTING EXISTING EXCAVATION. LINE WAS WELL MARKED, BUT NOT DAYLIGHT
2017-09-29 08:50 | NO | NO | 19930174 | 1993-11-15 | 2552 | COLONIAL PIPELINE CO | YES | 1993-08-30 | 1515 | LA | JEFFERSON DAVIS |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 4138.1495 | 8348.319 | GASOLINE | 1 | 0 | 0 | NO | NO | 40 | 0.31 | 52000 | WELDED |  | 584 | 100 | YES | 24 | 731 |  | 76 | NO DATA | Null | Null | NO DATA |  | OTHER | UNDETERMINED SOURCE | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR TECHNICAL & REGULATORY | 4048412402 | ON AUGUST 30, 1993, COLONIAL MAINTENANCE PERSONNEL WERE EXCAVATING THE 40" LINE 01 NEAR BAYOU NEZPIQUE IN LOUISIANA TO INVESTIGATE AN INDICATION RECORDEDBY AN INTERNAL MAGNETIC INSPECTION TOOL. DURING THE EXCAVATION, GASOLINE FUMES WERE DISCOVERD. AFTER THE PIPE WAS EXPOSED, AN 8 FOOT LONG, LONGITUDINAL INDENTATION WAS FOUND ON THE PIP IN THE 7 TO 9 O'CLOCK POSITION. UPON CLOSER EXAMINATION, 1 1.5" CRACK WAS FOUND IN THE INDENTATION, BUT NO PRODUCT WAS FOUND LEAKING FROM THE CRACK AND ONLY WHEN THE LINE PRESSURE WAS HIGHER THAN THE 100 PSIG. THE LINE WAS OPERATING AT DURING THE EXCAVATION. AT 1605 CDT THE NATIONAL RESPONSE CENTER (REPORT NO. 195396) WAS NOTIFIED OF THE INCIDNET. TELEPHONIC NOTIFIECATION OF THE INCIDENT WAS ALSO MADE TO THE LOCAL SHERIFF'S DEPARTMENT, THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY, AND AS A COURTESY, THE SOUTHWEST REGION OF THE OFFICE OF PIPELINE SAFETY. REPAIR TO THE PIPELINE WAS MADE BY THE INSTALLATION OF A FOOT LONG, FULL ENCIRCLEMENT SLEEVE. ALL SLEEVE WELDS WERE INSPECTED BY MAGNETIC PARTICLE EXAMINATION AND THE SLEEVE WAS COATED WITH PRIMER AND POLYKEN TAPE. THE SOURCE OF THE OUTSIDE FORCE DAMAGE THAT CAUSED THE INDENTATION CANNOT CONCLUSIVELY BE DETERMINED.
2017-09-29 08:50 | YES | NO | 19930175 | 1993-10-14 | 10012 | KANEB PIPELINE CO | YES | 1993-09-09 | 1813 | KS | MCPHERSON |  | NO |  | NO | NW 1/4, SECTION 33, T-19-S, R-4-W |  | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | L. P. G. | 2 | 2525 | 0 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 720 | 221 | YES | 24 | 980 | 11 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | L. LEROY ANDERSON - MANAGER OF REGULATORY AFFAIRS | 3162621408 | BRB CONTRACTORS, INC. A FIRM FROM TOPEKA, KANSAS, WAS IN THE PROCESS OF REMOVING A TEMPORARY ACCESS ROAD THEY HAD BUILT FOR A CONSTRUCTION PROJECT IN THEIMMEDIATE AREA, WHEN OUR PIPELINE WAS DAMAGED. THEIR BACKHOE OPERATOR WAS REMOVING A DRAINAGE CULVERT WHEN HE PUNCTURED OUR PIPELINE. THIS SAME BACKHOE OPERATOR WAS AWARE OF OUR PIPELINE'SLOCATION BECAUSE HE OBSERVED OUR PERSONNEL CLEARLY MARK THE PIPELINE'S LOCATION FOR THE INITIAL CONSTRUCTION ACTIVITY.IN FACT, ONE OF OUR MARKING FLAGS WAS WITHIN 10 FEET OF ONE SIDE OF THE BACKHOE AND ANOTHER FLAG WAS LOCATED WITHIN 40 FEET OF THE OTHER SIDE OF THE BACKHOE. BRB CONTRACTORS, INC. PERSONNEL NEGLECTED TO CONTACT US PRIOR TO THE REMOVAL OF THE DRAINAGE CULVERT. IF WE HAD BEEN CONTACTED, WE WOULD OF BEEN ABLETO HAVE OUR PERSONNEL ON SITE, AND THIS ACCIDENT WOULD HAVE BEEN AVOIDED.
2017-09-29 08:50 | NO | NO | 19930176 | 1993-10-14 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | YES | 1993-09-20 | 1245 | MO | MONTGOMERY |  | NO |  | NO | NE OF THE SE 1/4, SECTION 17, T50N, R4W PRAIRIE TOWNSHIP, MONTGOMERY COUNTYMISSOURI |  | LINE PIPE | VALVE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK M. MCCANN - DIVISION MANAGER | 6124584860 | A SMALL AMOUNT OF STAINED SOIL WAS OBSERVED BY A KOCH EMPLOYEE BY A BLOCK VALVE LOCATION ON THE 20" SEGMENT OF WOOD RIVER PIPELINE. AFTER THE EXCAVATION WAS COMPLETED, THE VALVE BODY WAS CLEANED FOR VISUAL INSPECTION. A SMALL AMOUNT OF SEEPAGE WAS NOTICED TO BE OCCURRING AROUND THE THREAD OF A PLUG WHICH WAS LOCATED ON THE VALVE BODY. THE PLUG WAS REMOVED AND REPLACED.
2017-09-29 08:50 | NO | NO | 19930177 | 1993-10-14 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | YES | 1993-09-08 | 1613 | MO | HARRISON |  | NO |  | NO | KOCH PIPELINES, INC. BETHANY TERMINAL, TANK 33 |  | TANK FARM | TANK |  | 1981 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | BACTERIA | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK M. MCCANN - DIVISION MANAGER | 6124584860 | OIL AND WATER WAS OBSERVED AT THE EDGE OF THE TANK. OIL WAS CONTAINED AT THIS TIME. TANDK WAS EMPTIED AND INSPECTED, OBSERVED SMALL PIT ON TANK FLOOR. TANK WAS REPAIRED BY CBI.
2017-09-29 08:50 | NO | NO | 19930178 | 1993-10-14 | 18718 | SUN PIPELINE CO | YES | 1993-09-14 | 2020 | OK | SEMINOLE | SEMINOLE | NO |  | NO | SW 1/4, SEC 24-9N-6E-300' NORTH OF STROTHERS ROAD, 1.5 MILES EAST OF HARVEY ROAD. |  | LINE PIPE | PIPE |  | 1933 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4597.9439 | 9275.91 | GASOLINE | 1 | 7 | 5 | NO | NO | 6.63 | 0.28 | 35000 | WELDED |  | 980 | 228 | YES | 12 | 1225 |  | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. CHRISTENSEN JR - MAINT. SUPERVISOR | 4053820626 | GENE SMITH, LANDOWNER, REPORTED LEAK TO DISPATCHER, THEY NOTIFIED LEE COKELEY WHO TOOK CONTROL OF INCIDENT AND CALLED OUT NECESSARY PERSONNEL AND EQUIPMENT. CONTAINMENT AND VACUMING OPERATIONS WERE IMPLEMENTED. A TEMPORARY CLAMP WAS INSTALLED TO STOP LEAKAGE.
2017-09-29 08:50 | YES | NO | 19930179 | 1993-10-04 | 395 | AMOCO OIL CO | YES | 1993-09-03 | 1000 | IL | LIVINGSTON | PONTIAC | NO |  | NO | FLANAGAN STATION, ROUTE 23, 2 MILES NORTH OF I-55 NEAR PONTIAC, ILLINOIS |  | TANK FARM | OTHER | TANK ROOF DRAIN LINE ON | 1960 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | FAILURE OF TANK ROOF | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | P.J. MCGANNON - AREA MANAGER | 2197382384 | ON SEPTEMBER 3, 1993 AT APPROXIMATELY 10 A.M. , A SHEEN WAS DISCOVERED ON A STREAM NEAR FLANAGAN STATION. AMOCO PIPELINE PERSONNEL VERIFIED THAT THERE WAS NOT A PIPELINE LEAK AND TRACED THE SOURCE OF THE CRUDE OIL TO STORAGE TANK #1411'S ROOF DRAIN. AT 10:20 HOURS, NOTIFICATION WAS MADE TO THE NRC, REPORT #195990. AT APPROXIMATELY 1530 HOURS, DURING THE COURSE OF CLEANUP, THE ILLINOIS EPA IN CONJUNCTION WITH THE PONTIAC, IL FIRE DEPARTMENT, GRANTED APPROVALFOR A CONTROLLED BURN-OFF. THE BURN-OFF IN A NEARBY DITCH AND CREEK WAS SUCCESSFUL IN CLEANING UP AT A MINIMUM 80% OF THE CRUDE OIL. THE REMAINING 20% OFTHE CRUDE OIL WAS CLEANED UP WITH SKIMMERS.
2017-09-29 08:50 | YES | NO | 19930180 | 1993-10-05 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1993-07-26 | 10 | NE | LANCASTER |  | NO |  | NO | TOWNSHIP 11 NORTH, RANGE 8 EAST, SECTION 1 OF LANCASTER COUNTY, NEBRASKA |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 152184 | 116622.2484 | 235274.1806 | ANHYDROUS AMMONIA | 2 | 2203 | 0 | NO | NO | 6.63 | 0.16 | 46000 | WELDED |  | 1130 | 256 | YES | 24 | 1550 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL | PIPELINE WARNING SIGNS | Null | Null | G.R. SMETHERS - GENERAL MANAGER -OPERATIONS SUPPORT | 9185811800 | THE PIPELINE HAD BEEN EXPOSED BY EROSION OF THE CREEK BED AND BANKS DURING RECENT FLOODING. THE PIPELINE WAS HIT BY DEBRIS CARRIED BY FLOOD WATERS IN THEFLOODED CREEK. THE LINE RUPTURED DUE TO CONTACT WITH DEBRIS.THE CREEK CROSSING WAS REPLACED BY DIRECTIONAL DRILLING AND RETURNED TO SERVICE
2017-09-29 08:50 | YES | NO | 19930181 | 1993-10-05 | 22430 | WEST SHORE PIPE LINE CO | YES | 1993-08-27 | 630 | WI |  | MILWAUKEE | NO |  | NO | WEST SHORE PIPE LINE GRANVILLE STATION 11115 WEST COUNTY LINE ROAD MILWAUKEE, WISCONSIN 53224 |  | TANK FARM | OTHER | SUMP TANK | 1961 | OTHER | CHECK VALVE TO SUMP DID | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | NOT GIVEN | 3 | 180 | 130 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | APRIL S. MANLEY - AREA MANAGER - OPERATIONS | 7082573740 | ON AUGUST 27, 1993 COMPANY PERSONNEL DISCOVERED A REFINED PRODUCT RELEASE ATWEST SHORE PIPELINE'S GRANVILLE STATION. CONTAINMENT AND CLEAN-UP PROCEDURESWERE STARTED IMMEDIATELY AND NOTIFICATIONS WERE MADE TO THE NATIONAL RESPONSE CENTER (VERBEL REPORT #197895) AND THE WISCONSIN DEPARTMENT OF MILITARY AFFAIRS, DIVISION OF EMERGENCY GOVERNMENT AT 09:36 CST. THE ORIGIN OF THE RELEASE WAS A SUMP TANK. PRODUCT WAS CONTAINED WITHIN THE STATION BERMS. CLEAN-UP ACTIVITIES CONTINUED UNTIL ALL FREE LIQUID WAS RECOVERED.
2017-09-29 08:50 | YES | NO | 19930182 | 1993-10-05 | 19536 | TOTAL PIPELINE CORP | NO | 1993-08-23 | 1700 | OK | JEFFERSON | RINGLING | NO |  | NO | SECTION 36, TOWNSHIP 5S, RANGE 4W, JEFFERSON COUNTY, OKLAHOMA |  | LINE PIPE | OTHER | COLLAR COUPLING | 1930 | OTHER | COLLAR COUPLING BROKE OUT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 766.324 | 1545.985 | CRUDE OIL | 1 | 260 | 258 | NO | NO | 6.63 | 0.28 | 0 | COUPLED |  | 550 | 300 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | MICHAEL J. COOPER - MGR REGULATORY COMPLIANCE | 4052291638 | 8/23/93 OUTSIDE CONTRACTOR WAS REPLACING APPROXIMATELY 2600' OF 6" COUPLED PIPE WITH NEW 6" 5LX42.188 WT. EPOXY COATED PIPE. THE OLD PIPE HAD BEEN UNCOVERED AND A DEEPER DITCH DUG BESIDE TO PLACE NEW PIPE INTO (SEE DIAGRAM). THE WASLL COLLAPSED BENEATHE THE OLD SECTION OF 6" PIPE CAUSING IT TO FALL INTO THE DEEPER DITCH. A COLLAR COUPLING PULLED INTO SPILLING PETROLEUM CRUDE OIL INTO DITCH. EMERGENCY CREWS WERE CALLED AND ALL OIL WAS PICKED UP BY VACUUM TRUCK. OIL WAS CONTAINED IN DITCH LINE. LINE WAS COMPLETELY DRAINED AND ALL STATIONS SHUT DOWN AND LOCKED OUT. SECITON WAS ISOLATED BY MAINLINE VALVES UNTIL REPAIR WAS COMPLETED.PART D - CAUSE OF ACCIDENT- WHEN PIPE FELL INTO DITCH DURING REPAIR.
2017-09-29 08:50 | YES | YES | 19930183 | 1993-10-05 | 12105 | MAPCO AMMONIA PIPELINE INC | YES | 1993-08-20 | 725 | OK | OSAGE |  | NO |  | NO | TOWNSHIP 21 NORTH, RANGE 12 EAST, SECTION 20 OF OSAGE COUNTY, OKLAHOMA |  | LINE PIPE | PIPE |  | 1977 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 4 | 0 | 4 | 21119 | 16183.9961 | 32649.6571 | ANHYDROUS AMMONIA | 2 | 1446 | 0 | NO | NO | 6.63 | 0.14 | 46000 | WELDED |  | 1410 | 1110 | YES | 24 | 1927 | 4 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL | PIPELINE WARNING SIGNS | Null | Null | R.T. CRONK, SENIOR VICE PRESIDENT | 9185811800 | THE DAMAGED PIPE WAS REMOVED AND REPLACED WITH TESTED PIPE. UPON INVESTIGATION IT WAS DISCOVERD THAT THE PIPE HAD BEEN MECHANICALLY DAMAGED PRIOR TO THE INCIDENT. THE PIPE SECTION IS CURRENTLY BEING METALLURGICALLY EVALUTED.
2017-09-29 08:50 | YES | NO | 19930184 | 1993-10-01 | 19226 | TEXACO PIPELINE INC | YES | 1993-09-23 | 1440 | TX | WICHITA |  | NO |  | NO | 2110 HARDING STREET, WICHITA FALLS, TEXAS |  | TANK FARM | TANK |  | 1949 | OTHER | TANK CAUGHT ON FIRE WHILE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID R. SEATON - DISTRICT MANAGER | 8177230761 | WORKERS WERE REPLACING SEAL ON CRUDE OIL STORAGE TANK NO 1263. AT APPROXIMATELY 2:40 PM WHILE USING AN AIR DRILL TO BORE THROUGH THE STAINLESS STEEL SHOE OF THE EXTERNAL FLOATING ROOF, A FIRE STARTED IN THE SPACE BETWEEN THE TANKSHOE AND THE RIM PLATE OF THE ROOF. WICHITA FALLS FIRE DEPARTMENT EXTINGUISHED THE FIRE A T APPROXIMATELY 6:10 PM USING FOAM THAT WAS SUPPLIED BY SHEPPARD AIR FORCE BASE. PART D CAUSE OF ACCIDENT- WORKERS WERE REPLACING SEAL MATERIAL CAUSE IS STILL UNDER INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19930185 | 1993-10-05 | 18706 | SUN PIPELINE CO | YES | 1993-09-02 | 802 | PA | ADAMS | BERWICK TOWNSHIP | NO |  | NO | NEAR THE INTERSECTION OF BLAIR AND LOBELL ROADS APPROXIMATELY TWO MILES SOUTHWEST OF ABBOTSTOWN PA. |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 766323.9789 | 1545984.9958 | GASOLINE | 3 | 625 | 100 | NO | NO | 6 | 0.28 | 30000 | WELDED |  | 1200 | 950 | YES | 24 | 1400 | 0 | 59 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | BOB ARNET - MANAGER, RISK MANAGEMENT | 2159755823 | THIRD PARTY OPERATING DITCHING EQUIPMENT, WHILE INSTALLING DRAIN LINES ON A GOLF COURSE, HIT SUN PIPE LINE COMPANY'S 6" ICEDALE-TO-ALLEGHENY PIPELINE.
2017-09-29 08:50 | YES | NO | 19930186 | 1993-09-27 | 2527 | COASTAL STATES GAS TRANSMISSION CO | NO | 1993-08-12 | 2100 | TX | HIDALGO |  | NO |  | NO | .5 MI. SOUTH OF SHELL MCALLEN STATION - (F.M. 1017) |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | GASOLINE | 3 | 150 | 0 | NO | NO | 4.5 | 0.16 | 42000 | WELDED |  | 1050 | 1000 | YES | 0 | 0 | 0 | 66 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS, ETC | NO | NO | W.D. PARTLOW - ENVIRON. & SAFETY SUPV. | 7138777370 | LEAK WAS CAUSED BY THIRD PARY DAMAGE, IT APPEARED NOT TO HAVE BEEN HIT RECENTLY. SEVERAL OTHER PIPELINES ARE LOCATED WITHIN CLOSE PROXIMITY TO COASTAL R.O.W.. NEW PIPE WAS INSTALLED WHER THE LEAK OCCURRED.
2017-09-29 08:50 | YES | NO | 19930187 | 1993-09-27 | 18706 | SUN PIPELINE CO | YES | 1993-08-23 | 1000 | TX | GREGG |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | CORROSION, EXTERNAL | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 122.6118 | 247.3576 | CRUDE OIL | 3 | 525 | 480 | NO | NO | 10.75 | 0.31 | 1999 | WELDED |  | 1065 | 60 | YES | 8 | 1440 | 11 | 90 | EXTERNAL | Null | YES | OTHER | UNKNOWN | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | W.L. CRISP - DISTRICT SUPERVISOR | 4092873006 | INDEPENDENT CONTRACTOR WAS DIGGING A POND ON PRIVATE PROPERTY AND STRUCK SPL'S GRISSOM/MID-VALLEY ET-10"M.L. OIL WAS CONTAINED IN THE POND AND WAS RECOVERED BY VACUUM TRUCKS. THE DAMAGED SECTION OF PIPE WAS REMOVED AND REPLACED WITH PRE-TESTED PIPE.
2017-09-29 08:50 | YES | NO | 19930188 | 1993-09-27 | 2552 | COLONIAL PIPELINE CO | YES | 1993-08-26 | 1445 | TN | GRUNDY | COALMONT | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22989.7194 | 46379.5499 | FUEL OIL | 1 | 200 | 184 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1318 | 54 | YES | 8 | 1390 | 12 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.L. GAMBRELL - ADMINISTRATOR | 4048412402 | AT 1341 EST ON AUGUST 26, 1993, A HIGHWAY CONTRACTOR NOTIFIED COLONIAL'S CONTROL CENTER IN ATLANTA, GA THAT HIS EQUIPMENT HAD RUPTURED AN 8-INCH PIPELINEAT HIGHWAY 108 NEAR COALMONT, TN. THE CONTROL CENTER SHIFT SUPERVISOR IMMEDIATELY NOTIFIED THE CHATTANOOGA AREA OFFICE OF THE INCIDENT. EMERGENCY RESPONSE PERSONNEL INCLUDING SPILL CONTRACTORS WERE DISPATCHED TO THE SCENE AND THE NATIONL RESPONSE CENTER WAS NOTIFIED OF THE INCIDENT AT 1350 EST (REPORT NO.194776). WHEN COMPANY PERSONNEL ARRIVED AT THE SCENE AT 1545 EST. THE HIGHWAYCONTRACTOR HAD ALREADY CONSTRUCTED A SMALL POND AND CONTAINED FUEL OIL ESCAPED FROM THE RUPTURED PIPELINE WHICH RUNS FRON ATLANTA, GA TO NASHVILLE, TN. THE AMOUNT OF PRODUCT RELEASED WHEN THE CONTRACTORS RIPPER HIT THE PIPELINE WAS MINIMAL BECAUSE THIS SEGMENT OF THE LINE WAS SHUT DOWN AT THE TIME OF THE INCIDENT. CLEAN-UP OPERATIONS RECOVERED 184 BARRELLS OF PRODUCT. THE LINE WAS REPAIRED BY INSTALLING 6 FEET OF PREHYDROSTATICALLY TESTED 8.625" OD PIPE.THE TIE-IN WELDS WERE RADIOGRAPHED AND THE LINE RETURNED TO SERVICE. AN INVESTIGATION OF THE INCIDENT DETERMINED THAT THE CONTRACTOR HAD NOT MADE A "ONE-CALL" NOTICE BEFORE BEGINNING THE ROAD WORK. THE CONSTRUCTION SHOULD HAVE BEEN OFF RIGHT-OF-WAY, BUT THE TRACTOR OPERATOR MISTAKENLY ENTERED THE RIGHT-OF-WAY. THE CONTAMINATED SOIL HAS BEEN EXCAVATED AND PLACED IN A PLASTIC LINED PIT AND WILL DISPOSED OF.
2017-09-29 08:50 | YES | NO | 19930189 | 1993-09-21 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-08-15 | 1425 | WI | CLARK |  | NO |  | NO | NE 1/4 OF NE 1/4, SECTION 16, T 28N - R4W, CLARK COUNTY WISCONSIN |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 76632.3979 | 154598.4996 | FUEL OIL | 3 | 1234 | 1015 | NO | NO | 8.63 | 0.17 | 52000 | WELDED |  | 1450 | 485 | YES | 24 | 1960 | 7 | 87 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | STEVEN S. BALL - SR. VP & GENERAL MANAGER | 9185883850 | ON SUNDAY AFTERNOON AT APPROXIMATELY 1425,M AUGUST 15,1993, THE #1-8" LINE BETWEEN BATEMAN AND WAUSAU WAS STRUCK BY A BULLDOZER AT MP 108+30. THE BULLDOZER WAS BEING USED TO OBTAIN FILL MATERIAL FOR A BASEMENT BEING EXCAVATED. THEOPERATOR WAS AWARE OF THE PRESENCE OF OUR LINE BUT DID NOT MAKE A ONE CALL NOTIFICATION BECAUSE HE THOUGHT THE PIPELINE WAS DEEPER. PIPELINE MARKERS WERE PRESENT WITHIN 100' OF THE LEAK SITE AND UNOBSTRUCTED. THE DEPTH OF THE PIPEAT THE LEAK SITE WAS APPROXIMATELY 3.5'. AT THE TIME OF THE ACCIDENT, THE LINE WAS SHUT DOWN IN #2 FUEL OIL WAS A STATIC PRESSURE OF 300 PSI. ONCE THE LINE WAS HIT, THE BULLDOZER OPERATOR CALLED THE NUMBER LISTED ON THE PIPELINE MARKERS AND WITHIN 45 MINUTES WPL WAS ON SITE CLOSING THE NEAREST MAINLINE BLOCK VALVES ON EITHER SIDE OF THE LEAK SITE TO ISOLATE THE PUNCTURED LINE.
2017-09-29 08:50 | NO | NO | 19930190 | 1993-09-16 | 2552 | COLONIAL PIPELINE CO | YES | 1993-08-16 | 930 | AL | SUMTER | EPES | NO |  | NO | COLONIAL PIPELINE COMPANY'S EPES PUMP STATION. |  | PUMPING STATION | VALVE |  | 1967 | OTHER | CHECK VALVE SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | GASOLINE | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.A. COX - MANAGER TECHNICAL & REGULATORY | 4048412296 | ON SUNDAY, AUGUST 15K 1993, OPERATOR PERSONNEL, DURING A ROUTINE STATION CHECK OF EPES PUMP STATION, NOTICED THAT A SMALL AMOUNT OF GASOLINE HAD ENTERED A LEAK DETECTION BOX AT THE NO.2 UNIT ON LINE 01. THE FOLLOWING DAY, AUGUST 16, MAINTENANCE PERSONNEL EXCAVATED THE SOIL AROUND THE CHECK VALVE AND DISCOVERED THAT THE GASOLINE HAD BEEN RELEASED FROM THE INBOARD CHECK VALVE SPRING HOUSING COVER.AT 1015 CST ON AUGUST 16 IT BECAME APPARENT THAT DAMAGE RELATEDCOSTS WOULD EXCEED $5000, AND THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO.192640) OF THE LEAK. THE ALABAMA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT WAS ALSO NOTIFIED OF THE INCIDENT. ON AUGUST 19, THE STATION WAS SHUT DOWN AND REPAIRS WERE MADE TO THE CHECK VALVE. IT IS ESTIMATED THAT 10 GALLONS OF GASOLINE WERE RELEASED INTO THE SURROUNDING SOIL, OF WHICH, 4 GALLONS WERE RECOVERED. THE CONTAMINATED SOIL HAS BEEN EXCAVATED AND PLACED IN A PLASTIC ENELOPE AND AWAITS DISPOASL.
2017-09-29 08:50 | YES | NO | 19930191 | 1993-09-16 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1993-08-05 | 823 | CA | SAN BERNARDINO | RIALTO | NO |  | NO | COLTON TERMINAL, RIALTO, CALIFORNIA |  | PUMPING STATION | OTHER | 24" PROVER (BLOWN GASKET) | 1981 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 160000 | 122611.8366 | 247357.5993 | GASOLINE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR V. PRESIDENT - OPERATIONS & ENGINEERING | 2134867720 | A MANIFOLD VALVE FAILED TO OPEN CAUSING A HIGH PRESSURE CONDITION BLOWING OUT PROVER GASKET.
2017-09-29 08:50 | NO | NO | 19930192 | 1993-09-16 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1993-08-04 | 930 | CA | SOLANO | MARTINEZ | NO |  | NO | MARTINEZ BOOSTER STATION, ON RAILROAD RIGHT OF WAY, OUR MILE POST .05 |  | PUMPING STATION | BOLTED FITTING |  | 1967 | OTHER | GASKET LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19158.0995 | 38649.6249 | NOT GIVEN | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR V. PRESIDENT - OPERATIONS & ENGINEERING | 2134867720 | TECHNICIAN REPORTED WET SPOT DURING ROUTINE MAINTENANCE ON MARTINEZ BOOSTER.CREW WAS CALLED OUT TO REPAIR AND FOUND THE BURIED FLANGE GASKET ON BOOSTER WAS LEAKING. TIGHTENED FLANGE TO STOP LEAK AND WILL REPAIR AND REPLACE.
2017-09-29 08:50 | YES | NO | 19930194 | 1993-09-21 | 18718 | SUN PIPELINE CO | YES | 1993-08-03 | 1715 | OK | OKFUSKEE |  | NO |  | NO | FROM JUNCTION OF HIGWAY 48 AND 5MILE WEST, 1 MILE SOUTH, WEST INTO |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | CORROSION, EXTERNAL | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 150 | 120 | NO | NO | 8.63 | 0.2 | 0 | WELDED |  | 0 | 540 | YES | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | UNKNOWN | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.S. CHRISTENSEN JR. - MAINTENANCE SUPERVISOR | 4053820626 | BERN BROTHERS CONSTRUCTION WAS CLEANING OUT DRAINAGE DITCHES FOR LANDOWNER AND RAN AN EARTH MOVER INTO THE LINE, TEARING OUT THE TOP .5 OF THE PIPE. THE CONTROL CENTER SAW AN IMMEDIATE LOSS OF PRESSURE ON THE LINE SEGMENT AND SHUTIT DOWN. THEY THEN NOTIFIED LEE COKELY, OPER. SUPERVISOR WENT TO SEMINOLE OFFICE AND TOOK CONTROL OF COMMUNICATIONS AND DISPATCHING. THE MAINT. SUPERVISOR BEGAN CALLING OUT PERSONNEL AND STARTED CLOSING BLOCK VALVES TO ISOLATE THEAREA. VACUUM TRUCKS BEGAN PICKING UP PRODUCT AND DRAINING THE LINE. MOST OF THE SPILLED PRODUCT HAD BEEN PICKED UP WHEN EFFORTS WERE CEASED DUE TO AN ELECTRICAL STORM ARRIVING AT THE LOCATION. REPAIRS WERE MADE 8/14/1993. CLEAN UPIS STILL UNDER WAY.
2017-09-29 08:50 | YES | NO | 19930195 | 1993-09-02 | 12105 | MAPCO AMMONIA PIPELINE INC | YES | 1993-07-30 | 37 | OK | GARFIELD |  | NO |  | NO | TOWNSHIP 24 NORTH, RANGE 6 WEST, SECTION 13, GARFIELD COUNTY, OKLAHOMA |  | LINE PIPE | PIPE |  | 1974 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 46073 | 35306.8447 | 71228.1667 | ANHYDROUS AMMONIA | 2 | 3058 | 0 | NO | NO | 8.63 | 0.19 | 46000 | WELDED |  | 1440 | 1350 | YES | 24 | 1985 | 3 | 74 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | PIPELINE WARNING SIGNS | NO | NO | GARY SMETHERS - GENERAL MANAGER - OPERATION SUPPORT | 9185811800 | DISPATCHER ATTEMPTED TO START PUMPING PRODUCT ON THIS SECTION OF THE LINE. THE LINE RUPTURED JUST AFTER STARTING MAINLINE UNIT. FURTHER INVESTIGATION OF THE INCIDENT SHOWED THAT A CONTRACTOR WORKING ON ANOTHER PIPELINE HAD DAMAGEDTHE PIPELINE WITH A BACKHOE WHILE WORKING NEAR THE LINE. THE CONTRACTOR FAILED TO MAKE CONTACT WITH MAPCO AMMONIA PIPELINE INC.
2017-09-29 08:50 | NO | NO | 19930196 | 1993-11-04 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-10-07 | 800 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | TANK 84 - PLANTATION'S BATON ROUGE TANK FARM LOCATED OFF BLOUNT ROAD IN BATON ROUGE, LOUISIANA. |  | TANK FARM | TANK |  | 1952 | OTHER | CORROSION, INTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 9962.2117 | 20097.8049 | GASOLINE | 3 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | GALVANIC CORROSION IN THE | NO DATA |  | Null | NO DATA |  | Null | Null | RAY M. CROOK - VICE PRESIDENT - OPERATIONS | 4043645916 | ON THE MORNING OF OCTOBER 7, 1993, WHILE DRAWING WATER OFF TANK 84 AT PLANTATION'S BATON ROUGE TANK FARM, A PLANTATION UTILITY OPERATOR DISCOVERD A DISCOLORATION ON THE SKETCH PLATE. THE TANK WAS TAKEN OUT OF SERVICE, CLEANED AND INSPECTED. THE INSPECTION REVEALED A FIVE-INCH CRACK (DUE TO GALVANIC CORROSION) IN THE HEAT AFFECTED ZONE OF THE FLOOR TO SHELL WELD. THE CRACK WILL BE REPAIRED BY REPLACING THE SKETCH PLATE WITH NEW PLATE.
2017-09-29 08:50 | YES | NO | 19930197 | 1993-11-27 | 443 | AMOCO PIPELINE CO | YES | 1993-11-03 | 1610 | TX | MONTAGUE |  | NO |  | NO | 9 MILES NORTH OF BOWIE ON U.S. HWY 81, EAST ON F.M.RD 1806 TO PIPELINE R-O-W, NORTH ALONG PIPELINE R-O-W APPROXIMATELY 2 MILES |  | LINE PIPE | OTHER | NON-SPECIFIED | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1532.648 | 3091.97 | CRUDE OIL | 1 | 215 | 210 | NO | NO | 12 | 0.28 | 35000 | WELDED |  | 885 | 15 | YES | 24 | 1275 | 0 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | P.J. MCGANNON | 9037597131 | AT 1610 HOURS ON NOVEMBER 3, AMOCO PIPELINE COMPANY CONFIRMED AN OUTAGE ATTRIBUTED TO AN EXTERNAL CORROSION ON ITS 12-INCH BOWIE-NOCONA PIPELINE IN MONTAGUE CO. TX. THE OUTAGE WAS READILY CONTAINED AND PROMPTLY CLEANED UP. THE NRC WAS NOTIFIED AT 1930 HOURS. REPORT WAS MADE TO P.O. WILKERSON, AND ASSIGNEDREPORT NUMBER 206254.
2017-09-29 08:50 | YES | NO | 19930198 | 1993-11-20 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-10-18 | 821 | KS | MONTGOMERY | COFFEYVILLE | NO |  | NO | LOCATED APPR. 650'E. OF THE BLOCK VALVE AT MP 4+14 IN THE S.W. QUARTER OF TH N.W. QUARTER OF SECTION33, TOWNSHIP 34S, RANGE 16 E. IN MONTGOMERY COUNTY, KS |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 191580.9947 | 386496.249 | GASOLINE | 1 | 215 | 89 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 600 | 545 | YES | 8 | 845 |  | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - SR. VICE PRESIDENT & GENERAL MANAGER | 9185883850 | AT APPROXIMATELY 08:21 HOURS ON 10/18/93 MR. JOHN GARNER CONTACTED THE WILLIAMS PIPE LINE COMPANY OPERATIONS CONTROL CENTER AND REPORTED THAT HE SMELLED GASOLINE NEAR THE INTERSECTION OF FIRST STREET AND ENGLEWOOD STREET IN COFFEYVILLE, KANSAS. THE OPERATIONS CONTROL DEPARTMENT IMMEDIATELY SHUT DOWN OPERATIONS ON THE #2-8" COFFEYVILLE- CANEY JUNCTION PIPELINE AND CONTACTED THE WPL SOUTHERN REGION OFFICE. THE SOUTHERN REGION OFFICE IMMEDIATELY DISPATCHED EMERGENCY RESPONSE PERSONNEL TO INVESTIGATE THE REPORT. AT APPROX. 20:30 HOURS ON 10/18/93 A LEAK WAS FOUND. AT 21:00 HOURS THE LEAK WAS PLUGGED AND ARRESTED. THE CAUSE OF THE SPILL WAS DETERMINED TO BE AN EXTERNAL CORROSION PIT IN THE PIPELINE. THE PIPELINE WAS REPAIRED BY REPLACING A SECTION OF THE PIPE. APPROXIMATELY 215 BARRELS OF UNLEADED GASOLINE WERE SPILLED WITH 89 BARRELS RECOVERED. WPL COORDINATED THE CLEAN-UP EFFORTS WITH THE KANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT.
2017-09-29 08:50 | NO | NO | 19930199 | 1993-11-22 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1993-10-26 | 1100 | AR | UNION |  | NO |  | NO | UNION COUNTY, AR SECTION 23, TOWNSHIP 18S, RANGE 16 W - APPROXIMATELY ONE MILE SOUTHWEST OF PARKER'SCHAPEL, AR. |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 1 | 1 | NO | NO | 4 | 0.24 | 1986 | WELDED |  | 900 | 30 | YES | 8 | 1162 | 6 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | O. HORTON CUNNINGHAM - VICE PRESIDENT OPERATION | 7137593755 | AT APPROXIMATELY 1100 HURS CST, OCTOBER 26, 1993, A TEPPCO EMPLOYEE NOTICED A STRONG PETROLEUM ODOR NEAR OUR 4" SYSTEM IN UNION COUNTY, ARKANSAS. ADDITIONAL PERSONNEL WERE DISPATCHED IMMEDIATELY TO THE LEAK LOCATION. UPON ISOLATION OF THE SITE, IT WAS DETERMINED EXTERNAL CORROSION HAD CAUSED A PIN-HOLE FAILURE IN THE PIPE. REMOVAL OF THIS SECTION OF PIPE AND INSTALLATION OF NEW PIPE WAS COMPLETED ON NOVEMBER 2, 1993. CLEAN UP OPERATIONS WERE CONCLUDED AND THE SYSTEM RESTARTED NOVEMBER 2, 1993.
2017-09-29 08:50 | NO | NO | 19930200 | 1993-11-22 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-11-02 | 1630 | MS | COVINGTON | COLLINS | NO |  | NO | TANK 148- PLANTAITON'S COLLINS TANK FARM LOCATED OFF MISSISSIPPI HIGHWAY 588 IN COLLINS, MS. |  | TANK FARM | TANK |  | 1976 | OTHER | STRESS CRACK IN THE COLUM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 6130.5918 | 12367.88 | DIESEL FUEL | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK - VICE PRESIDENT-OPERATION | 4043645916 | ON THE AFTERNOON OF NOVEMBER 2, 1993, PLANTATION'S TANK INSPECTOR DISCOVEREDA DISCOLORATION ON THE SKETCH PLATE OF TANK 148 WHILE PERFORMING MAINTENANCEON AN ADJACENT TANK. TANK 148 WAS TAKEN OUT OF SERVICE, CLEANED AND INSPECTED. THE INSPECTION REVEALED A THREE INCH STRESS CRACK IN THE COLUMN REINFORCEMENT PLATE TO FLOOR WELD, THE CRACK WILL BE REPAIRED BY REPLACING THE COLUMN REINFORCEMENT PAD.
2017-09-29 08:50 | YES | NO | 19930201 | 1993-11-28 | 3012 | D - S PIPE LINE CORP | NO | 1993-10-21 | 1300 | TX | HASKELL |  | NO |  | NO | SECTION 1, BLOCK 50 GEORGE HARRIS SURVEY5 MILES WEST ON HIGHWAY 6 AND 2 MILES NORTH OF THE CITY OF OF STAMFORD, TEXAS |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 15326.4796 | 30919.6999 | OIL AND GASOLINE | 3 | 175 | 0 | NO | NO | 10.75 | 0.37 | 25000 | THREADED |  | 480 | 190 | YES | 24 | 600 | 5 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS - MANAGER | 8063783583 | AT APPROXIMATELY 1300 HOURS ON OCTOBER 21, 1993, OUR 10" HAWLEY TO DIXON CRUDE OIL PIPELINE EXPERIENCED A LEAK DUE TO EXTERNAL CORROSION. THE ACCIDENT ALLOWED 175 BARRELS OF GAS OIL TO ESCAPE, OF WHICH NONE WAS SUBSEQUENTLY RECOVERD. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY WELDING A 10" DIAMETER X 3/8" THICK FULL ENCIRCLEMENT SLEEVE ONTO THE LINE PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19930202 | 1993-11-28 | 443 | AMOCO PIPELINE CO | NO | 1993-10-21 | 1845 | TX | LIMESTONE | CITY OF MEXIA | NO |  | NO | WEST OF US 84, SOUTH ON FM 2705, MEXIA, TX 76667 |  | PUMPING STATION | OTHER | UNKNOWN | 1993 | OTHER | FAILURE OF TEMPORARY CONN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 613.0592 | 1236.788 | CRUDE OIL | 1 | 81 | 76 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G E SEHAN - DISTRICT MANAGER | 4099386901 | AT 1845 HURS ON OCTOBER 21, 1993, THE FAILURE OF A TEMPORARY CONNECTION BETWEEN PUMP AND PIPING AT AMOCO PIELINE COMPANY'S MEXIA STATION, IN MEXIA, TX, CAUSED AN 81 BARREL SPILL WHICH WAS CONTAINED ON APL PROPERTY. NRC WAS VERBALLY NOTIFIED AT 2122 HRS. REPORT MADE TO P.O. DEEGAN AND REPORT NUMBER 204186 ASSIGNED. PART D CAUSE OF ACCIDENT - CONNECTION BETWEEN PUMP AND PIPING.
2017-09-29 08:50 | YES | NO | 19930203 | 1993-11-27 | 12628 | MOBIL PIPELINE CO | YES | 1993-10-27 | 910 | PA | LEHIGH | ALLENTOWN | NO |  | NO | LOCATION 1800'E. AND 200' S. OF THE INTERSECTION OF ROUTE 987 (AIRPORT RD) AND THE CORP. LINE BETWEEN THE CITY OF ALLENTOWN AND HANOVER TOWNSHIP AND LOCATED IN |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | GASOLINE | 2 | 300 | 50 | NO | NO | 6.63 | 0.28 | 35000 | WELDED |  | 1440 | 800 | YES | 2 | 1590 | 12 | 68 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | T.P. MURPHY | 2146583869 | AT APPROXIMATELY 09:10 ON OCTOBER 27, 1993, OLSHAN DEMOLISHING CO. WAS REMOVING OLD PIPING FROM EXXON ABANDONED TANK FARM IN LEHIGH CO. CITY OF ALLENTOWN, PA. COMPANY WAS USING A KAMOTSU PC 400 LC EXCAVATOR WITH A HYDRALIC SHEER ATTACHMENT AND REMOVING UNDERGROUND PIPING AT THE FACILITY. PIPING WAS NOT BEING EXCAVATED BEFORE SHEERING AND REMOVING PIPE. CONTRACTOR STARTED TO REMOVE MOBIL'S INSERVICE 6" LINE RUPTURING THE PIPE CAUSING THE SPILL. THE UNLEADED GASOLINE VAPORIZED, CAUSING THE POPULATION AROUND THE LEAK SITE TO BE EVACUATED. PART B. SPECIFIC LOCATION - IN THE CITY OF ALLENTOWN .
2017-09-29 08:50 | YES | NO | 19930204 | 1993-12-03 | 13131 | CONOCO INC | YES | 1993-11-12 | 823 | MO | NEWTON |  | NO |  | NO | 2.5 MILES S.W. OF DIAMOND, MISSOURI SEC 19, T26N R31W NEWTON COUNTY, MISSOURI MP 201.5 |  | LINE PIPE | PIPE |  | 1930 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1532.648 | 3091.97 | FUEL OIL | 3 | 200 | 0 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 880 | 852 | YES | 4 | 1097 | 8 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY F. CLYNCH - REGIONAL TRANSPORTATION MANAGER | 4057676352 | AT 00:10 HRS. ON 11/12/93, CONOCO PIPE LINE OIL MOVEMENTS PERSONNEL IN HOUSTON OBSERVED A PRESSURE DROP ON CONOCO'S NO. 1 WOOD RIVER LINE. ACTIONS WERE TAKEN AT THAT TIME TO SHUT DOWN THE LINE AND ISOLATE THE SUSPECTED RELEASE. FIELD PERSONNEL WERE IMMEDIATELY NOTIFIED OF THE SUSPECTED RELEASE AND WERE DISPATCHED TO THE AREA TO BEGIN WALING THE LINE TO LOCATED AND CONFIRM IF THERE WAS ACTUALLY A RELEASE. (AERIAL RECONNAISSANCE WAS NOT POSSIBLE BECAUSE OF THE LACK OF VISIBILITY, LOW LIGHT AND RAIN). THE RELEASE WAS LOCATED AND CONFIRMED AT APPROXIMATELY 08:30 HRS ON 11/12/93. FIELD PERSONNEL BEGAN CONTAINMENTAND CLEAN-UP PROCEDURES AT THAT TIME. THE RELEASED MATERIAL (A COMBINATION OF NO.1 AND NO. 2 FUEL OIL) SPRAYED AN AREA APPROXIMATELY 200'X 200'. THE MAJORITY OF THE RELEASED MATERIAL THEN TRAVELED APPROXIMATELY 400' FROM ITS INITAL RELEASE POINT INTO A CONTAINMENT BASIN WHER RECOVERY OPERATIONS WERE SET UP. DURING CONTAINMENT AND RECOVERY OPERATIONS, THE LINE WAS EXCAVATED REVVEALING AN ANOMALY IN THE PIPE APPROXIMATELY 6" LONG AND 2" WIDE. THE RUPTURE WAS LOCATED IN A PIECE OF PIPE APPROXIMATELY 13 FEET IN LENGTH. THE 13" JOINT ALSO APPEARED TO HAVE A SLIGHT OVERBEND IN IT, SUGGESTING THAT THIS MAY HAVE BEENA TIE-IN POINT DURING THE ORIGINAL CONSTRUCTION. A 20 FOOT SECTION OF LINE CONTAINING THE FAILURE WAS PRESERVED FOR METALLURGICAL EXAMINATION AND REMOVEDFROM THE RELEASE SITE. THE REMOVED SECTION OF LINE WAS REPLACED AND OPERATIONS WERE RESUMED AT A REDUCED OPERATING PRESSURE, PER DIRECTIONS FROM THE KANSAS CITY REGIONAL OFFICE OF PIPELINE SAFETY.
2017-09-29 08:50 | YES | NO | 19930205 | 1993-12-03 | 4906 | EXXON PIPELINE CO | YES | 1993-10-21 | 602 | LA | WEST BATON ROUGE |  | YES | LA | NO | W. BATON ROUGE PARISH: T-10S S15 R-4E. FRM I-10 AND LOUISIANA HIGHWAY 1 GO SOUTH APPROXIMATELY 10 MILES TO LA HWY 1148. ON HWY 1148 GO IN WESTERLY DIR. APPR. 4 |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 76632.3979 | 154598.4996 | CRUDE OIL | 1 | 318 | 315 | NO | NO | 16 | 0.22 | 42000 | WELDED |  | 827 | 480 | YES | 8 | 1000 | 0 | 54 | EXTERNAL | Null | YES | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | G.G. PERSYN - MANAGER OF ENVIR. & REG. COMPLIANCE DEPARTMENT | 7136565521 | LOW PRESSURE WAS DETECTED AT EXXON PIPELINE COMPANY CRUDE OIL TERMINAL AT 06:02. THE LINE WAS SHUT-IN BY 06:12. EXXON PIPELINE COMPANY ASSOCIATES WERE DISPATCHED TO THE PIPELINE SYSTEM TO INVESTIGATE. ALSO, EXXON PIPELINE ASSOCIATES WERE PLACED ON STANDBY FOR POSSIBLE SPILL. LINE FLYERS WERE ALSO DIPATCHEDTO FLY THE LINE. THE LEAK WAS DISCOVERED BY A LINE FLYER. IMMEDIATELY, THE MOBILIZED EXXON PIPELINE OIL SPILL RESPONSE TEAM AND CONTRACTORS WERE DISPATCHED TO THE LOCATION. THE OIL WAS CONTAINED IN APPROXIMATELY A 200 FOOT RADIUS FROM THE PIPELINE, WHERE THE OIL WAS RECOVERED. THERE WERE NO INJURIES OR FIRES AS A RESULT OF THIS EVENT.PART B - SPECIFIC LOCATION - MILES TO PIPELINE RIGHT-OF-WAY, THEN NORTH APPROXIMATELY 300 YARDS TO SITE.
2017-09-29 08:50 | YES | NO | 19930207 | 1993-12-03 | 2552 | COLONIAL PIPELINE CO | YES | 1993-11-01 | 2056 | MS | PIKE | MAGNOLIA | NO |  | NO | COLONIAL PIPELINE COMPANY'S MCCOMB STATION. |  | PUMPING STATION | VALVE |  | 1963 | OTHER | CHECK VALVE SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | GASOLINE | 1 | 50 | 38 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR TECHNICAL & REGULATORY | 4048412402 | AT 1850 EST ON NOVEMBER 1, 1993, THE LINE NO 1 CONTROLLER RECEIVED A HIGH SUMP ALARM AT THE MCCOMB PUMP STATION. A TECHNICIAN WAS DISPATCHED TO INVESTIGATE AND UPON ARRIVAL AT 2056 EST DISCOVERED GASOLINE ON THE GROUND NEAR THE NO.1 UNIT. WHEN IT BECAME APPARENT THAT THE INCIDENT WOULD QUALIFY AS A D.O.T. REPORTABLE LEAK, THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 2232 EST (REPORT NO. 205883). OTHER AGENCIES NOTIFIED INCLUDE THE MISSISSIPPI EMERGENCY MANAGEMENT AGENCY AND EPA REGION IV. ON NOVEMBER 2, EXCAVATION OF THE STATION PIPING REVEALED THE SOURCE OF THE LEAK TO BE A SEAL FAILURE ON THE INBOARD SPRINGCOVER OF THE NO.2 UNIT CHECK VALVE. REPAIRS TO THE CHECK VALVE WERE MADE BY INSTALLING NEW PACKING AND REPLACING THE PACKING GLAND PLATES AND VALVE SPRINGCOVERS WITH IMPROVED DESIGNS. IT IS ESTIMATED THAT 50 BARRELS OF GASOLINE WERE RELEASED INTO THE SURROUNDING SOIL AND TO DATE, 38 BARRELS HAVE BEEN RECOVERED AND RETURNED TO THE SYSTEM. THE CONTAMINATED SOIL IS CURRENTLY BEING STORED IN A PLASTIC ENVELOPE FOR REMEDIATION.
2017-09-29 08:50 | YES | NO | 19930208 | 1993-11-22 | 2271 | CHASE TRANSPORTATION CO | YES | 1993-10-28 | 1300 | CO | LINCOLN |  | NO |  | NO | FROM ARRIBA, COLORADO - 1 MILE EAST, 1 MILE NORTH AND 2.5 MILES EAST ON THE SOUTH SIDE OF THE ROAD |  | LINE PIPE | OTHER | UNKNOWN | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | GASOLINE | 1 | 3384 | 285 | NO | NO | 10.75 | 0.19 | 0 | NO DATA |  | 1640 | 545 | YES | 24 | 1934 | 7 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | CHUCK JOHNSON - VICE PRESIDENT | 3168327484 | HENKLES & MCCOY CONSTRUCTION WAS LAYING A TELEPHONE CABEL FOR EASTERN SLOPE TELEPHONE COMPANY. THEY CALLED THE UTILITIES NOTIFICATION CENTER OF COLORADO ON 10/27/93, TO SET UP A MEETING AT THE LOCATION FOR A LINE LOCATE ON 10/28/93 AT 12:17 PM MDT. HENKLES & MCCOY STRUCK OUR PIPELINE AT 10:37 A.M. MDT, BEFORE WE WERE TO MEET WITH THEM TO LOCATE THE PIPELINE. A CHASE EMPLOYEE WAS ONHIS WAY TO MEET WITH THEM WHEN THE ACCIDENT HAPPENED.
2017-09-29 08:50 | YES | NO | 19930210 | 1993-11-22 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1993-10-18 | 420 | IA | CASS |  | NO |  | NO | THE MASSENA PUMP STATION IS LOCATED EAST OF MESSENA, IOWA, 2 MILES NORTH AND 3/4 MILES EAST OF THE JUNCTION OF HIGHWAY #92 AND #148. |  | PUMPING STATION | OTHER | 5/8" S S TUBING | 1992 | OTHER | 5/8" S S TUBING BROKE AT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 257.4849 | 519.451 | NATURAL GAS LIQUID | 2 | 20 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GEORGE A. ROOD - VICE PRESIDENT OPERATIONS | 7138537876 | ON OCTOBER 18, 1993 AT 04:20 HRS. THE CONTROL CENTER IN HOUSTON, TEXAS RECEIVED AN ALARM INDICATING THAT THERE WAS A SEAL LEAK AT THE MASSENA PUMP STATION. THE PUMP STATION MECHANIC WAS NOTIFIED AND RESPONDED. HE ARRIVED AT THE PUMP STATION AT 04:30 HRS. AND FOUND A BROKEN SEAL FLUSH LINE, 5/8" STAINLESS STEEL TUBING, RELEASING NORMAL BUTANE INTO THE ATMOSPHERE. THE MECHANIC CLOSEDTHE VALVE TO THE SEAL FLUSH WHICH STOPPED THE RELEASE OF NORMAL BUTANE INTO THE ATMOSPHERE. THE ALARM CLEARED AND THE STATION WAS READY FOR SERVICE AT 04:45 HRS. CALCCULATIONS INDICATE THAT APPROXIMATELY 20 BARRELS OF NORMAL BUTANE WAS RELEASED INTO THE ATMOSPHERE. THE SUCTION VALVE TO THE PUMP, A 6" GAS OPERATED BALL VALVE DID NOT COMPLETELY CLOSE CONTRIBUTING TO THE QUANTITY BEING RELEASED. PART D - CAUSE OF ACCIDENT - AT FERRELL NUT.
2017-09-29 08:50 | YES | NO | 19930211 | 1993-12-16 | 809 | ARCO PIPE LINE CO | NO | 1993-11-16 | 600 | OK | CARTER | RINGLING | NO |  | NO | INSIDE RINGLING STATION, 3 MILES EAST AND 1 MILE SOUTH OF RINGLING, OKLAHOMA OFF HWY 70. |  | PUMPING STATION | BOLTED FITTING |  | 1993 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | GASKET FAILURE | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | CRUDE OIL | 1 | 630 | 610 | NO | NO | 16 | 0.38 | 35000 | FLANGED |  | 1440 | 1535 | YES | 8 | 1800 | 10 | 93 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVE POLING - COMPLIANCE COORDINATOR | 7139865233 | POOL STATION, THE PUMP STATION IMMEDIATELY DOWN STREAM FROM RINGLING STATION, WENT DOWN DUE TO A POWER FAILURE. ALL LINE SURGE CONTROL EQUIPMENT FUNCTIONED AS DESIGNED HOWEVER, THE PRESSURE BETWEEN THE PUMP DISCHARGE AND THE OUTGING LINE CONTROLLER AT RINGLING STATION CAUSED A GASKET IN A BOLTED FITTING TOFAIL. SINCE THIS FAILURE OCCURED AT LESS THAN 110% OF THE MOP, AN INVESTIGATION IS UNDERWAY TO DETERMINE THE CAUSE OF PREMATURE FAILURE.
2017-09-29 08:50 | YES | NO | 19930212 | 1993-01-03 | 879 | CHEMOIL REFINING | NO | 1993-12-01 | 1100 | CA | PORT OF LONG BEACH | LONG BEACH | NO |  | NO | PIER "F" BERTH 3 SPOT #1050 |  | LINE PIPE | PIPE |  | 1972 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 134106.6963 | 270547.3743 | FUEL OIL | 1 | 20 | 18 | NO | NO | 12 | 0.25 | 35000 | WELDED |  | 522 | 430 | YES | 4 | 900 | 10 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID J. DRAGT - REFINERY MANAGER | 3109213581
2017-09-29 08:50 | NO | NO | 19930214 | 1993-12-08 | 2552 | COLONIAL PIPELINE CO | YES | 1993-11-06 | 620 | MD | HARFORD | FOREST HILL | NO |  | NO | COLONIAL PIPELINE COMPANY'S ABERDEEN JUNCTION 806 W. JARRETTSVILLE ROAD FOREST HILL, MD 21050 |  | TANK FARM | VALVE |  | 1965 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | GASOLINE | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR TECHNICAL & REGULATORY | 4048412402
2017-09-29 08:50 | NO | NO | 19930215 | 1993-12-08 | 15674 | PLANTATION PIPE LINE CO | YES | 1993-11-08 | 1345 | MS | COVINGTON | COLLINS | NO |  | NO | TANK 110- PLANTATION'S COLLINS TANK FARM LOCATED OFF MISSISSIPPI HIGHWAY 588 IN COLLINS, MISSISSIPPI |  | TANK FARM | TANK |  | 1963 | OTHER | PIN HOLE IN THE FLOOR FIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 11300 | 8659.461 | 17469.6305 | KEROSENE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK - VICE PRESIDENT - OPERATIONS | 4043645916
2017-09-29 08:50 | NO | NO | 19930216 | 1993-12-08 | 4906 | EXXON PIPELINE CO | YES | 1993-10-04 | 1500 | MS | PRENTISS |  | NO |  | NO | JEFFERSON DAVIS COUNTY, MS. T9N-R18W-S10. FROM PRENTISS MS GO IN NORTHERLY DIRECTION ON HWY 13 APPROX 9 MILES TO BLACK TOP ROAD. TURN RIGHT ON ROAD GO 5.5 MI |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5928 | 4542.7685 | 9164.5991 | NOT GIVEN | 1 | 2 | 2 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 727 | 0 | YES | 8 | 909 | 0 | 54 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | ONE CALL |  | Null | YES |  | 7136565521
2017-09-29 08:50 | YES | NO | 19930217 | 1993-12-08 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-11-04 | 1445 | OK | ROGERS |  | NO |  | NO | SOUTHEAST 1/4, OF THE SOUTHEAST 1/4 OF SECTION 11, TOWNSHIP 22 NORTH, RANGE 14 EAST IN ROGERS COUNTY, OKLAHOMA |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19158.0995 | 38649.6249 | GASOLINE | 3 | 142 | 142 | NO | NO | 12.75 | 0.3 | 30000 | WELDED |  | 750 | 250 | YES | 8 | 968 | 7 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - SR. VICE PRESIDENT & GENERAL MANAGER | 9185883850
2017-09-29 08:50 | YES | NO | 19930218 | 1993-12-08 | 4906 | EXXON PIPELINE CO | NO | 1993-10-23 | 900 | TX | ECTOR |  | NO |  | NO | EPC ECTOR STATION APPROXIMATELY 15 MILES NW OF ODESSA, ECTOR CO., TX (APPROX 1 MI NORTH OF HWY 158/HWY 1936 INTERSECTION |  | PUMPING STATION | VALVE |  | 1991 | OTHER | UNEXPLAINED OPEN VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 766.324 | 1545.985 | CRUDE OIL | 1 | 90 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.G. PERSYN - MANAGER | 7136565521
2017-09-29 08:50 | NO | NO | 19930219 | 1993-12-08 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1993-11-08 | 1020 | OH | UNION | LIBERTY TOWNSHIP | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19158.0995 | 38649.6249 | GASOLINE | 3 | 3 | 1 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1325 | 810 | YES | 24 | 1662 | 9 | 74 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DEAN R. MOYER - REGULATORY COMPLIANCE ADMINISTRATOR | 2158208300
2017-09-29 08:50 | YES | NO | 19930220 | 1993-12-10 | 809 | ARCO PIPE LINE CO | YES | 1993-11-06 | 2200 | TX | WICHITA | WICHITA FALLS | NO |  | NO | 2420' SOUTHEAST OF HWY 82 ROAD CROSSING AT STATION 137 +73 WITHIN THE CITY LIMITS OF WICHITA FALLS, TEXAS. |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 310 | 305 | NO | NO | 12 | 0.38 | 30000 | WELDED |  | 992 | 650 | YES | 8 | 1570 | 0 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | STEVEN G. POLING - COMPLIANCE COORDINATOR | 7139865233
2017-09-29 08:50 | NO | NO | 19930221 | 1993-12-10 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1993-11-02 | 1607 | AZ | PIMA | TUCSON | NO |  | NO | 6702 SOUTH WILMOT & SPRR RIGHT OF WAY PLMP 298.79 RRMP 993.5 |  | LINE PIPE | OTHER | FILTER HOUSING ON REMOTE | 1974 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | GASOLINE | 3 | 13 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | ACCUMULATION OF WATER IN | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT OPERATIONS & ENGINEERING | 2134867720 | TUCSON FIRE DEPT. CONTACTED THE LOS ANGELES SCHEDULER AND ADVISED HIM OF AN UNKNOWN HAZARDOUS SUBSTANCE AT 6702 S. WILMOT ROAD X VALENCIA, SOUTH OF RAILROAD. SCHEDULER ADVISED TUCSON AND FRANK FRENCH EN ROUTE TO INVESTIGATE. FOUNDLEAK IN REMOTE GRAVITOMETER. SHUT DOWN LINE AND DRAINED IN. CLOSED MAINLINEBLOCK VALVE AND ISOLATED GRAVITOMETER FOR REPAIRS. FIRE DEPT. WAS ON SITE ANDHAD FOAMED DOWN AREA. INTERNAL CORROSION OF GRAVITOMETER FILTER CAUSED A1/4" X 3/8" HOLE WHICH ALLOWED APPROXIMATELY 13 BARRELS OF UNLEADED REGULARGASOLINE TO ESCAPE ONTO THE GROUND. FILTER UNIT NOT REQUIRED FOR PROPEROPERATION OF GRAV ITOMETER AND WAS NOT REINSTALLED. PART C - GRAVITOMETEREP-TU 12" LINE PART D - ON REMOTE GRAVITOMETER
2017-09-29 08:50 | YES | NO | 19930222 | 1993-12-09 | 12127 | MARATHON PIPE LINE CO | YES | 1993-11-10 | 826 | OH | MERCER |  | NO |  | NO | SECTION 19, T5S, R3E, TWO MILES NORTH OF CELINA, OHIO, APPROXIMATELY 600 FT. EAST OF STATE HIGHWAY 127. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 306529.5916 | 618393.9983 | GASOLINE | 3 | 855 | 618 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1440 | 42 | YES | 8 | 1837 | 9 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JOSEPH A. FISHER - SR. ENVIRONMENTAL & SAFETY ENGINEER | 4194213201
2017-09-29 08:50 | YES | NO | 19930223 | 1993-12-16 | 15851 | PRIDE REFINING INC | YES | 1993-11-29 | 1600 | TX | NOLAN |  | NO |  | NO | APPROXIMATELY 3 MILES NORTHWEST OF BLACKWELL, TEXAS ON HWY 70. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 3 | 0.22 | 25000 | WELDED |  | 0 | 5 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | OTHER | UNKNOWN | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON - PIPELINE MANAGER | 9156748231
2017-09-29 08:50 | YES | NO | 19930224 | 1993-12-09 | 12628 | MOBIL PIPELINE CO | NO | 1993-10-31 | 1630 | TX | MIDLAND |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1970 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 229.8972 | 463.7955 | CRUDE OIL | 1 | 295 | 7 | NO | NO | 10 | 0.2 | 42000 | WELDED |  | 909 | 280 | YES | 2 | 1000 | 4 | 70 | INTERNAL | Null | YES | OTHER | SRB-SULFATE REDUCING BAC | NO DATA |  | Null | NO DATA |  | Null | Null | T.P. MURPHY - SAFETY & HEALTH COMPLIANCE ADVISOR | 2146583869
2017-09-29 08:50 | YES | NO | 19930225 | 1993-12-16 | 808 | ARCO TERMINAL SERVICES CORP | NO | 1993-10-13 | 430 | CA |  | SIGNAL HILL | NO |  | NO | INTERSECTION OF CHERRY AVENUE AND SPRINGSTREET. |  | LINE PIPE | SCRAPER TRAP |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 68969.1581 | 139138.6496 | DIESEL FUEL | 2 | 1 | 0 | NO | NO | 6 | 0.38 | 42 | WELDED |  | 720 | 100 | YES | 4 | 900 | 6 | 92 | EXTERNAL | Null | YES | OTHER | PINHOLE CORROSION LEAK | NO DATA |  | Null | NO DATA |  | Null | Null | EILEEN J.THRASHER - BUSINESS UNIT MANAGER | 3104289300
2017-09-29 08:50 | YES | NO | 19930226 | 1993-12-16 | 18273 | SHELL PIPELINE CORP | YES | 1993-11-20 | 919 | OK | PAYNE | CUSHING | NO |  | NO | CUSHING TANK FARM 26-INCH PIPE |  | TANK FARM | PIPE |  | 1949 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9500 | 7280.0778 | 14686.8575 | CRUDE OIL | 1 | 147 | 145 | NO | NO | 26 | 0.29 | 0 | WELDED |  | 275 | 20 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | A.R. HAVEY - MANAGER REGULATORY COMPLIANCE | 7132410132
2017-09-29 08:50 | NO | NO | 19930227 | 1993-12-15 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1993-11-10 | 1035 | CA | SACRAMENTO | SACRAMENTO | NO |  | NO | SACRAMENTO STATION, 1570 SOUTH RIVER ROAD, WEST SACRAMENTO, CA |  | TANK FARM | GIRTH |  | 1967 | OTHER | OPERATIONAL ERROR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | GASOLINE | 3 | 30 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT | 2134867720
2017-09-29 08:50 | YES | NO | 19930228 | 1993-12-08 | 15490 | PHILLIPS PIPE LINE CO | NO | 1993-11-09 | 1012 | TX | CHAMBERS | MONT BELVIEU | NO |  | NO | MONT BELVIEU PUMP STATION, MP 90-52+50, W.M. BLOODGOOD, A-4, CHAMBERS CO., TX. EAST OF HOUSTON ON I-1-10 TO S.H. 146 (MONT BELVIEU), NORTH ON S.H. 146 TO SUN |  | PUMPING STATION | PUMP |  | 1977 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 766.324 | 1545.985 | L. P. G. | 2 | 49 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS - MANAGER OF ENGINEERING & TECHNICAL SERVICES | 9186616267
2017-09-29 08:50 | YES | NO | 19930229 | 1993-10-05 | 30658 | KERN OIL AND REFINING CO. | NO | 1993-09-08 | 1315 | CA | KERN | BAKERSFIELD | NO |  | NO | NORTH SIDE OF PANAMA LANE, 0.2 MILES WEST OF STINE ROAD, SECTION 22, TOWNSHIP 30S., RANGE 27E |  | LINE PIPE | OTHER | THREADED FITTING | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1149.486 | 2318.9775 | CRUDE OIL | 1 | 116 | 96 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | THOMAS L. EVELAND - VICE PRESIDENT | 8058450761 | THE PIPELINE WAS BEING UNCOVERED WITH A BACKHOE TO INSPECT THE CATHODIC PROTECTION SYSTEM. THE BACKHOE STRUK A 2 INCH VALVE THAT WAS CONNECTED TO THE 6 INCH PIPELINE BY A THREADED NIPPLE. THE FORCE OF THE BACKHOE STRIKING THE VALVE KNOCKED THE 2 INCH NIPPLE LOOSE. TO REPAIR THE LINE, A BULL PLUG WAS THREADED INTO THE COLLAR AND SEAL WELDED WHERE THE 2 INCH NIPPLE HAD BEEN.
2017-09-29 08:50 | YES | NO | 19940001 | 1994-01-07 | 19237 | TEXAS EASTERN PRODUCT PIPELINE | YES | 1993-12-26 | 245 | TX | HARRIS | BAYTOWN | NO |  | NO | FACILITY LOCATED NEAR THE INTERSECTION OF DECKER DRIVE AT BAKER ROAD |  | TANK FARM | TANK |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 30800 | 23602.7785 | 47616.3379 | GASOLINE | 3 | 3696 | 1682 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM - VICE PRESIDENT | 7137593615 | OF A PREMIUM UNLEADED GASOLINE TANK. UPON DISCOVERY, THE OPERATOR IMMEDIATELY SHUT OFF FLOW TO THE TANK AND STOPPED THE OVERFLOW OF PRODUCT. THERE WERE 1,682 BBLS. OF PRODUCT TRANSFERED FROM THE CONTAINMENT DIKE TO AN ADJACENT STORGE TANK, APPROXIMATELY 2,000 BBLS. WERE LOST TO EVAPORATION AND APPROXIMATELY 10 BBLS. TO LOST TO ABSORPTION INTO THE CONTAINMENT DIKE AREA. THIS AREA IS
2017-09-29 08:50 | NO | NO | 19940002 | 1994-01-05 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1993-12-06 | 1207 | TX | CHAMBERS |  | NO |  | NO | 1/8 MILE SOUTH OF STATE HIGHWAY FM 194 |  | TANK FARM | PUMP |  | 1992 | OTHER | PUMP SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 3 | 8 | 7 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON DECEMBER 6, 1993, AT APPROXIMATELY 1207 HRS, CST A SPILL CAUSED BY A FAILED SEAL ON A TANK PUMP WAS DETECTED BY TEXAS EASTERN PRODUCTS PIPELINE COMPANY PERSONNEL AT THE MT. BELVIEU NORTH TERMINAL LOCATED IN CHAMBERS COUNTY, TEXAS. IMMEDIATELY, CONTINGENCY PROCEDURES WERE INITIATED. AN ESTIMATED 8 BARRELS OF NATURAL GASOLINE WEE SPILLED AND MIGRATED TO A DRAINAGE DITCH IN THE IMMEDIATE VICINITY. APPROXIMATELY 7 BARRELS OF PRODUCT WERE RECOVERED DURING CLEAN-UP.
2017-09-29 08:50 | YES | NO | 19940003 | 1993-12-24 | 2026 | CALNEV PIPELINE CO | YES | 1993-11-21 | 900 | CA | SAN BERNARDINO | RIALTO | NO |  | NO | APPROXIMATELY MILE POST 9.0, NEAR SUNWEST MATRIALS NORTH OF RIVERSIDE AVENUE AND LYTLE CREEK. RESPONSE ZONE 890. |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | JET FUEL | 2 | 108 | 5 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1330 | 1275 | YES | 24 | 2105 | 8 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | DAVID ANDRIES, P.E. - MANAGER OF ENGINEERING | 9098887771 | AN UNKNOWN INDIVIDUAL ATTEMPTED TO CUT OR DRILL INTO THE PIPELINE. A SMAL HOLE WAS MADE (APPROXIMATELY 1/8"), INITIATING RELEASED OF PRODUCT. A REPAIR WAS ATTEMPTED BY (PRESUMABLY) THE SAME INDIVIDUAL, USING HOSE CLAMPS AND A PIECE OF RUBBER TIRE. THE ADJACENT PROPERTY OWNER (SUNWEST MATERIALS) NOTICED THE SPRAY AND CONTACTED LOCAL AGENCIES, WHO CONTACTED CALNEV. CALNEV SHUT DOWN AND INITIATED EMERGENCY PROCEDURES. A 9.5 FOOT SEGMENT OF PIPE WAS REMOVED AND REPLACED WITH TESTED PIPE. THE LINE WAS RESTARTED AT APPROXIMATELY 2200 HOURS THAT EVENING.
2017-09-29 08:50 | YES | NO | 19940004 | 1993-12-24 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1993-11-15 | 1100 | TX | HIDALGO |  | NO |  | NO | 5 MI. LINE AND ABRAHAM ROADS-NORTHE BETWEEN TOWNS OF MISSION ND LAJOYA; 5 MI N. OF MISSION. |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | GASOLINE | 3 | 123 | 43 | NO | NO | 4.5 | 0.16 | 42000 | WELDED |  | 1050 | 500 | YES | 0 | 0 | 0 | 66 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS PUBLIC EDUCA | YES | YES |  | 7138777370
2017-09-29 08:50 | YES | NO | 19940005 | 1993-12-31 | 13131 | CONOCO INC | YES | 1993-12-01 | 2230 | MO | FRANKLIN | WASHINGTON | NO |  | NO | 300 YARDS WEST OF THE INTERSECTION OF S. POINT RD AND OLD HIGHWAY 100 IN THE TOWN OF WASHINGTON MO SECTION 25, T44N, R1W, FRANKLIN COUNTY, MISSOURI. |  | LINE PIPE | GIRTH |  | 1930 | FAILED WELD | SUBSIDENCE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 45979.4387 | 92759.0997 | GASOLINE | 2 | 200 | 124 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 900 | 696 | YES | 4 | 1219 | 8 | 90 | NO DATA | Null | Null | NO DATA |  | SUBSIDENCE |  | Null | NO DATA |  | Null | Null | VANCE WEBB - DIRECTOR OF REGULATORY COMPLIANCE | 4057674845 | AT APPROXIMATELY 21:16 HOURS ON DECEMBER 1, 1993, CONOCO PIPE LINE OIL MOVEMENTS GROUP IN HOUSTON OBSERVED A PRESSURE DEVIATION INDICATING A POSSIBLE RELEASE DOWNSTREAM OF WASHINGTON STATION ON THE NO.2 WOOD RIVER LINE. SHUT DOWN PROCEDURES WERE IMPLEMENTED AND THE REMOTELY OPERATED VALVE AT WASHINGTON STATION WAS CLOSED TO ISOLATE THE SUSPECTED RELEASE. FIELD PERSONNEL WERE IMMEDIATELY CONTACTED AND DISPATCHD TO THE POSSIBLE RELEASE SITE. UPON ARRIVING AT THE LOCATION FIELD PERSONNEL ALSO CLOSED THE MANUAL BLOCK VALVE IMMEDIATELY DOWNSTREAM OF THE RELEASE SITE. THE RELEASE WAS LOCATED IN THE 1600 BLOCK OF SOUTH POINT ROAD BETWEEN OLD HIGHWAY 100 AND DUBOIS CREEK CONTAINMENT BOOMS WEREDEPLOYED AT THREE LOCATIONS ON DUBOIS CREEK TO MINIMIZE CONTAMINATION OF THEMISSOURI RIVER, LOCATED DOWNSTREAM APPROXIMATELY 1/4 OF A MILE. VISUAL INSPECTION OF THE PIPE REVEALED A BREAK IN THE ACETYLENE WELD. APPROXIMATELY 35 FEET OF PIPE WAS REPLACED ON THE #2 LINE. WELD BANDS WERE PLACED ON BOTH THE ROAD CROSSING TIE-IN WELDS AND THE CREEK CROSSING TIE-IN WELDS ON BOTH THE NO.1 AND NO.2 LINES. THE BREAK APPEARS TO BE THE RESULT OF SEVERE SUBSIDENCE MAGNIFIED BY THREE FACTORS 1). LOCAL FLOODING LOOSENING THE SOIL, AS THIS AREA WAS SUBMERGED DURING THE FLOODING OF 93. 2). SETTLEMENT OF THE DITCHLINE OF FOEIGN PIPELINE CROSSING WHICH RUNS PARALLEL TO OLD HIGHWAY 100 AND IS LOCATED ALMOST DIRECTLY OVER THE BREAK AND 3). HEAVY TRAFFIC ON OLD HIGHWAY 100 DURING WEAKENED ROADBED CONDITIONS SETTLEMENT IN THE ROADBED WAS CLEARLY VISIBLE.
2017-09-29 08:50 | YES | NO | 19940006 | 1994-01-07 | 15774 | PORTAL PIPELINE CO | YES | 1993-12-15 | 1605 | ND | WARD |  | NO |  | NO | NE 1/4, SECTION 21, T156N, R87W |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10768 | 8251.7766 | 16647.1664 | CRUDE OIL | 1 | 150 | 140 | NO | NO | 12.75 | 0.22 | 52000 | WELDED |  | 1286 | 50 | YES | 8 | 1608 | 0 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PUBLIC EDUCATION | NO | NO | WALTER E. THOMPSON - GENERAL MANAGER OF OPERATION | 7018521087 | A LOCAL FARMER WS CLEANING OUT LOW ELEVATION AREAS IN HIS FIELD TO IMPROVE DRAINAGE. AS A RESULT, A SCRAPER REMOVED THE PIPE OVERBURDEN AND DAMAGED A 12"O.D. CRUDE OIL PIPELINE.
2017-09-29 08:50 | YES | NO | 19940007 | 1994-01-12 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1993-11-30 | 1630 | CA | SOLANO | DIXON | NO |  | NO | 1650 FEET UPSTREAM OF PLMP 34.43 (IE,PLMP 34.12) 50 FEET FROM RAILWAY AND 1660 FEET FROM FOX ROAD |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11494.8597 | 23189.7749 | GASOLINE | 3 | 600 | 600 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 1030 | YES | 24 | 1464 | 12 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT OPERATIONS & ENGINEERING | 2134867720 | SFPP EMPLOYEE WALKING ALONG RIGHT -OF-WAY SAW PRODUCT ON THE GROUND (10" DIAMETER WET SPOT). EMPLOYEE USED MOBILE TELEPHONE TO CALL IN AND REPORT. PIPELINE WAS SHUT DOWN IMMEDIATELY. WET SPOT DISAPPEARED. PIPELINE DRAINED INTO SACRAMENTO INSPECTION REVEALED SEVERAL PINHOLES WITHIN A 1" AREA. PIPELINE REPAIRED BY WELDING ON A THREE-FOOT SLEEVE.
2017-09-29 08:50 | NO | NO | 19940008 | 1994-01-12 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1993-12-03 | 1710 | CA | YOLO | WEST SACRAMENTO | NO |  | NO | 1570 SOUTH RIVER ROAD WEST SACRAMENTO CA |  | PUMPING STATION | LONGITUDINAL WELD | BOOSTER ST SCRAPER LAUNCH | 1987 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | GASOLINE | 3 | 40 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT OPERATIONS & ENGINEERING | 2134867720 | AT APPROX. 1612, 12/3/93, THE PROGRAMMABLE LOGIC CONTROLLER AT SACRAMENTO STATION MALFUNCTIONED AND CAUSED THE MOTOR-OLPERATED VALVES (MOV'S) TO ROCKLIN TO CLOSE AND THE MOTOR-OPERATED VALVE TO THE SCRAPER LAUNCHER TO OPEN. THE SCHEDULER ON DUTY IMMEDIATELY TOOK ACTION OT OPEN THE MOV'S TO ROCKLIN AND CLOSE THE MOV TO THE SCRAPER LAUNCHER. THE COMMAND TO CLOSE THE SCRAPER LAUNCHERMOV WAS NOT EXECUTED BY THE PLC, EVEN THOUGH IT WAS SENT REPEATEDLY. THE PIPELINE WAS SHUT DOWN AND LOCAL OPERATING PERSONNEL WERE NOTIFIED IMMEDIATELY. WHEN THEY ARRIVED AT THE SITE, IT WAS DETERMINED THAT DUE TO THE SCAPER LAUCHER VALVE OPENING, PRODUCT WAS SPILLED THROUGH THE SCRAPER LAUNCHER VENT. THE SCRAPER LAUNCHER MOV WAS LOCKED OUT SO THAT IT CAN ONLY BE OPERATED LOCALLY WHILE PERSONNEL ARE ON SITE. THE CENTRAL PROCESING UNIT (CPU) OF THE PLC WAS RE
2017-09-29 08:50 | YES | NO | 19940009 | 1994-01-10 | 2767 | COOK INLET PIPELINE CO | NO | 1993-12-28 | 1300 | AK | KENAI PENISULA BOROUGH |  | NO |  | NO | DRIFT RIVER TERMINAL - TANK #4 |  | TANK FARM | TANK |  | 1989 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11494.8597 | 23189.7749 | CRUDE OIL | 1 | 380 | 300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | R.H. GREENE - TERMINAL SUPERVISOR | 9075620197 | DUE TO RAIN AND ABNORMAL WARM SPELL, ICE FELL FROM THE ROOF OF TANK #4 ONTO A 1/2" NIPPLE CONNECTED TO THE BUTTERWORTH SYSTEM. THE NIPPLE CRACKED CAUSINGCRUDE OIL TO LEAK FROM THE TANK. APPROXIMATELY 380 BBLS. LEAKED OUT AND APPROXIMATELY 300 BBLS. WERE RECOVERED. CRUDE OIL CONTAIMINATED SNOW AND SOIL IS CONTAINED IN LINED AND COVERED CELLS (OF WHICH THERE ARE THREE) AND WILL BE MONITORED THOUGHOUT THE REMAINDER OF THE WINTER. CONTENTS OF THE CELLS WILL BEINJECTED BACK INTO THE SYSTEM AS SOON AS WEATHER CONDITIONS ALLOW THE CONTAINED SNOW TO MELT.
2017-09-29 08:50 | YES | NO | 19940010 | 1994-01-10 | 18214 | SHAMROCK PIPE LINE CORP | YES | 1993-12-07 | 845 | TX | WISE |  | NO |  | NO | ABSTRACT 858, A. VASQUEZ SURVEY, WISE COUNTY, TEXAS 7 MILES SOUTHEAST OF THE CITY OF DECATUR, TEXAS ON U.S. HIGHWAY 287. |  | LINE PIPE | PIPE |  | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 247600 | 189741.8172 | 382785.885 | GASOLINE | 3 | 1260 | 443 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1440 | 1369 | YES | 24 | 1778 | 10 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GERALD CHILDERS - MANAGER PIPELINE SAFETY AND REGULATIONS | 8063783583 | AT APPROXIMATELY 0845 HOURS ON DECEMBER 7, 1993, OUR 8 5/8" SOUTHLAKE PRODUCTS PIPELINE RUPTURED NEAR U.S. HIGHWAY 287 IN WISE COUNTY APPROXIMATELY 7 MILES SOUTHEAST OF DECATUR, TEXAS. UPON INVESTIGATION IT WAS DISCOVERED THE PIPEHAD BEEN STRUCK BY A DRILLING MACHINE OPERATED BY A SEISMIC CREW IN THE AREAABOUT SEPTEMBER 1993. THE ACCIDENT ALLOWED 1260 BARRELS OF UNLEADED GASOLINETO ESCAPE, OF WHICH 443 BARRELS WAS SUBSEQUENTLY RECOVERED. THE PRODUCT DID NVICE UPON INVESTIGATION IT WAS DISCOVERED THE PIPE HAD BEEN STRUCK BY A DRILLING MACHINE OPERATED BY A SEISMIC CREW IN THE AREA ABOUT.
2017-09-29 08:50 | NO | NO | 19940011 | 1994-01-12 | 3345 | DEVON ENERGY CORP | NO | 1994-01-12 | 1115 | WV | GILMER |  | NO |  | NO | WEST OF GILMER COUNTY ROUTE 26, NEAR INTERSECTION WITH GILMER COUNTY ROUTE 28, NEAR THE COMMUNITY OF LINN |  | LINE PIPE | PIPE |  | 1981 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 2 | 0.22 | 80 | OTHER |  | 0 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNKNOWN | Null | Null | GERALD W. DAVIS - WEST VIRGINA AREA FORMAN | 3044627389 | AN INTERMITTENTLY USED 2" GRAVITY OIL LINE FROM A WELL SITE WAS APPARENTLY PREVIOUSLY AND UNNOWN TO US DAMAGED BY A FIRE EXPOSURE. THE LINE SUBSEQUENTLY FAILED UPON USE AND SPILLED APPROXIMATELY ONE BARREL OF OIL WHICH HAS BEEN CLEANED UP TO THE BEST OF OUR ABILITY. ANY REMAINING SPILL CONTAMINATION IS BEING PRESENTLY REMEDIATED IN PLACE. THE SPILL WAS REPORTED TO THE NATIONAL CENTER ON 01/12/94 APPROX. 12:45 P.M. THE CALL WAS TAKEN BY PETTY OFFICER MAULDIN, AND WE WERE GIVEN A CONFIRMATION NUMBER OF 216345. THE SPILL WAS ALSO REPORTED TO THE WEST VIRGINIA SPILL HOT LINE AND THE WV DEPARTMENT OF ENVIRONMENTAL PROTECTION ON THIS SAME DATE WE ALSO PERSONALLY CALLED THE WVDOE FIELD INSPECTOR FOR THIS AREA AND HE ADVISED US THAT HE WOULD VISIT THE SITE AND FILE HIS NECESSARY REPORTS WITH THE STATE OF WEST VIRGINIA.
2017-09-29 08:50 | YES | NO | 19940012 | 1992-01-12 | 2330 | CHEVRON PIPELINE CO | YES | 1993-12-29 | 930 | ID | TWIN FALLS | MURTAUGH | NO |  | NO | FARMLAND |  | LINE PIPE | PIPE |  | 1949 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 14820 | 11356.9214 | 22911.4976 | JET FUEL | 3 | 92 | 92 | NO | NO | 8.63 | 0.25 | 42000 | WELDED |  | 1526 | 1440 | YES | 19 | 2039 | 12 | 87 | EXTERNAL | Null | YES | OTHER | NOT GIVEN | NO DATA |  | Null | NO DATA |  | Null | Null | L.T. JESTER III - BUSINESS UNIT MANAGER | 8012685300 | AT 0931 A.M.., DEC 29, 1993 THE CPL PUMP STATION AT GLENNS FERRY, IDAHO WAS SHUT DOWN TO ALLOW PASSAGE OF A SMART PIG. THE CONTROLLER NOTICED ALARMS OUTSIDE OF THOSE EXPECTED UNDER THE CIRCUMSTANCES. AT 098\38, THE PUMP AT THE MURTAUGH PUMP STATION DOWNSTRAM OF GLENNS FERRY SHUT DOWN. UNEXPECTED ALARMS CONTINUED TO BE RECEIVED AT THE CONTROL CENTER. AT 0940 THE CONTROLLER SHUT DOWN ANOTHER PUMP DOWNSTREAM. AT 0948 HE CONTACTED FIELD PERSONNEL IN TWO AREAS,SUSPECTIN THAT A LEAK MAY HAVE OCCURRED IN A SEGMENT OF LINE BETWEEN MURTAUGH & GLENN FERRY. BY 0951 THE ENTIRE WAS SHUT DOWN AND THE BLOCK VALVE AT MURTAUGH WAS CLOSED. THE LEAK WAS FOUND AT 1300 P.M. AND A CREW WAS SENT TO THE SCENE.
2017-09-29 08:50 | YES | NO | 19940013 | 1994-01-25 | 19226 | TEXACO PIPELINE INC | NO | 1994-01-24 | 148 | LA | VERMILION | ERATH | NO |  | NO | ERATH STATION - NORTH (OLD) TANK FARM LAT 29 53' 52" LONG 92 04'18" |  | TANK FARM | TANK |  | 1944 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | CRUDE OIL | 1 | 1537 | 1537 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E.D. LEWIS - DISTRICT MANAGER | 5048765645 | TANK OVERFLOWED DUE TO HUMAN ERROR.
2017-09-29 08:50 | NO | NO | 19940014 | 1994-02-02 | 12555 | MINNESOTA PIPELINE CO | YES | 1994-01-19 | 1700 | MN | WASHINGTON | COTTAGE GROVE | NO |  | NO | COTTAGE GROVE TERMINAL 6483 85TH STREET SOUTH COTTAGE GROVE MN |  | PUMPING STATION | OTHER | ST. RELIEF FLOW LINE | 1954 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | CRUDE OIL | 1 | 3 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | NOT GIVEN | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK M. MCCANN | 6124592424 | THE RELEASE WAS DISCOVERED AT THE STATION METERING BUILDING. THE PIPELINE SYSTEM WAS SHUTDOWN AND ISOLATED AT TIME OF DISCOVERY. COMPANY EMPLOYEES PERFORMED INITIAL RESPONSE AND CONTRACTORS ASSISTED WITH CLEANUP AND REPAIR. THE STATION PIPING IN QUESTION HAS BEEN SLEEVED, ISOLATED FROM OTHER STATION PIPING AND WILL BE TAKEN OUT OF SERVICE ON A PERMANENT BASIS.
2017-09-29 08:50 | YES | NO | 19940015 | 1994-02-02 | 19536 | TOTAL PIPELINE CORP | YES | 1994-01-05 | 750 | OK | PAYNE |  | NO |  | NO | NE/4 SEC. 27, T20N- R3E, PAYNE CITY, OK |  | PUMPING STATION | SCRAPER TRAP |  | 1968 | OTHER | PUMP SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5999.7281 | 12103.8749 | CRUDE OIL | 1 | 350 | 300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GARY A. STRACK - MANAGER OF REGULATORY COMPLIANCE | 3164425100 | 7:50 A.M. CALL FROM OUTSIDER CAME IN TO OUR 24-HOUR SCADA OPERATOR WHO IMMEDIATELY SHUT SYSTEM DOWN. 8:30 A.M. FIELD OPERATOR ARRIVED AND SECURED STATION. 9:OO A.M. FIRST TANK TRUCK ARRIVED AND CLEAN-UP BEGAN
2017-09-29 08:50 | YES | NO | 19940016 | 1994-01-14 | 12628 | MOBIL PIPELINE CO | NO | 1994-01-10 | 1115 | TX | TERRY |  | NO |  | NO | 2-1/2 MILES SOUTH OF TOKIO TEXAS AND 1/1/4 MILES EAST OF STATE F.M. RD. 1780 |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5624.7451 | 11347.3827 | CRUDE OIL | 1 | 260 | 135 | NO | NO | 8 | 0.25 | 0 | WELDED |  | 832 | 607 | YES | 2 | 915 | 5 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.D. HOGUE - OPERATIONS SUPERVISOR | 8062297431 | JANUARY 10,1994 AT 11:15 A.M. THE MOBIL PIPELINE PATROL PLANE REPORTED A LEAK ON THE MALLETT TO SEMINOLE 8" MAINLINE OT THE CLERK AT SEMINOLE OFFICE. AT 11:20 A.M. SEMINOLE PERSONNEL CALLED THE MPLCO DISPATCHER IN DALLAS AND HAD THE PUMP STATION AT MALLETT SHUT DOWN. AT 11:25 A.M. FIELD PERSONNEL WERE DISPATCHED TO THE LEAK SITE AT M.P. 18.8. THE BLOCK VALVE AT M.P. 14.17 WAS CLOSED AT 12:00 NOON AND THE LINE WAS ALLOWED TO DRAIN INTO SEMINOLE STATION A BACKHOE AND TOW VACUUM TRUCKS WERE DISPATCHED TO THE LEAK SITE AND BEGAN CLEAN UP OF THE LEAK SITE UPON DIGGING UP THE PIPE AT THE LEAK SITE IT WAS DISCOVERED THAT EXTERNAL CORROSION WAS THE CAUSE OF THE LEAK. THE BAD PIPE WAS REPLACED WITH NEW PIPE. THIS LEAK OCCURED IN A CUULTIVATED FIELD BUT NO CROPS WERE PLANTED A THE TIME. AT NO TIME WAS THE LEAK A DANGER TO THE PUBLIC.
2017-09-29 08:50 | NO | NO | 19940017 | 1993-12-30 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-11-27 | 745 | ND | FARGO |  | NO |  | NO | FARGO TERMINAL #218 |  | TANK FARM | TANK |  | 1946 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 23000 | 17625.4515 | 35557.6549 | FUEL OIL | 3 | 37 | 37 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | IMPRESSED CURRENT | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL - SENIOR VICE PRESIDENT & GENERAL MANAGER | 9185883850 | ON NOVEMBER 27, 1993, AT 0745 HOURS, FARGO OPERATING PERSONNEL FOUND FUEL OIL SURROUNDING THE CHIME AREA AT TANK 567 LOCATED WITHIN THE FARGO TANK FARM. UPON FURTHER INSPECTION PRODUCT WAS DISCOVERED BUBBLING FROM UNDER THE TANK BETWEEN THE SUCTION/RECEIVE LINES ON THE NORTH SIDE OF THE TANK.. AT THE TIME THE LEAK WAS DISCOVERED, THE TANK CONTAINED APPROXIMATELY 7800 BARRELS OF FUEL OIL. THE PROPER AUTHORITIES WERE IMMEDIATELY NOTIFIED AND THE TANK WAS PUMPED OUT. THE ALEXANDRIA MAINTENANCE CREW AND LOCAL HAZWOOPER CONTRACTOR ARRIVED EARLY THAT AFTERNOON, AND BY 1700 HOURS HAD COLLECTED 1587 GALLONS OF FREE PRODUCT AND HAULED ALL CONTAMINATED SNOW AND DIRT TO AS SURFACE IMPOUNDMENT AREA. ON NOVEMBER 30, 1993, A CONTRACTOR ARRIVED AT THE SITE TO CLEAN AND INSPECT THE TANK. APPROXIMATELY EIGHT (8) CORROSION HOLES WERE DISCOVERD IN THE TANK FLOOR. THE NECESSARY REPAIRS WERE MADE TO PUT THE TANK BACK IN SERVICE.
2017-09-29 08:50 | YES | NO | 19940018 | 1993-12-31 | 26304 | UNOCAL PIPELINE CO - WESTERN REGION | NO | 1993-12-16 | 2000 | CA | SAN LUIS OBISPO |  | NO |  | NO | IN THE TANK 80616 BASIN AT UNOCAL'S AVILA PUMP STATION LOCATED AT 10 SAN RAFAEL, AVILA BEACH CA. |  | TANK FARM | VALVE |  | 1960 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2298.9719 | 4637.955 | OIL AND GASOLINE | 1 | 100 | 100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | P.A. ARMSTRONG - DISTRICT SUPERINTENDENT | 8055437600 | A THERMAL RELIEF VALVE AT THE TANK 80616 GATE VALVE ACTUATED AND RELEASED 100 BARRELS OF A SEMI-REFINED GAS -OIL PRODUCT INTO THE TANK BASIN. THE RELATEDDEBRIS. THE PROUDCT WAS CONTAINED WITHIN THE TANK BASIN AND PROMPTLY RECOVERED WITH VACUUM TRUCKS.
2017-09-29 08:50 | YES | NO | 19940019 | 1993-12-31 | 17321 | RICHARDSON, SID CARBON & GAS CO | NO | 1993-12-12 | 850 | TX | NOLAN |  | NO |  | NO | 4 MI NORTHWEST OF TRENT TEXAS OFF OF NOLAN COUNTY ROAD 110 |  | LINE PIPE | PIPE |  | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 12261.1837 | 24735.7599 | L. P. G. | 2 | 512 | 0 | NO | NO | 4.63 | 0.19 | 42000 | WELDED |  | 1440 | 900 | YES | 12 | 2160 | 8 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | WARNING SIGNS POSTED | NO | NO | ROBERT GAWLIK - WEST TEXAS AREA SAFETY MANAGER | 9153672867 | CONSTRUCTION COMPANY WAS SALVAGING AN OLD ABANDONED BURIED TELEPHONE CABLE. THE COMPANY WAS DOING A PRE-RIP PRIOR TO PULLIN GHE CABLE FROM THE GROUND. THEY WER PRE-RIPPING AT A DEPTH OF 4'. OUR HVL PRODUCT LINE IS BURIED AT A 4"DEATH. WE WERE NOT NOTIFIED PRIOR TO THIS WORK SO THAT WE COULD SPOT OUR LINES FOR THEM. SIGNS WERE POSTED AT ALL FENCE CROSSINGS INCIDENT OCCURRED IN THE MIDDLE OF CULTIVATD FARM LAND.
2017-09-29 08:50 | NO | NO | 19940020 | 1994-01-09 | 12624 | MOBIL OIL CORP | NO | 1993-12-16 | 330 | TX | YOAKUM |  | NO |  | NO | 3 MILES NORTH OF DENVER CITY TEXAS ON HWY #214 |  | LINE PIPE | WELDING FITTING |  | 1993 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 7054 | 5405.6493 | 10905.3782 | NOT GIVEN | 3 | 3 | 0 | NO | NO | 4 | 0.24 | 35000 | WELDED |  | 2130 | 1920 | YES | 12 | 2860 | 7 | 93 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.D. HOGUE - OPERATIONS SUPERVISOR | 8062297431 | A 4" WELD ON AN ABOVE GROUND BLLOW DOWN RISER CRACKED THUS CAUSING CO2 TO LEAK FROM THE PIPELINE. EMPLOYEES AT THE SHELL GAS PLANT NORTH OF DENVER CITY TEXAS DISCOVERED THE LEAK ON OUR ESTE CO2 PIPELINE AND CALLEDF THE MOBIL DISPATCHER AT 3:30 AM DEC 16TH. THE DISPATCHER CALLED FIELD PERSONNEL AT 3:33 AM.THEY ARRIVED AT THE LEAK SITE AT 4:45 AM AND ISOLATED THE SECTION OF LINE THAT THE LEAK WAS ON AND BEGAN VENTING THE LINE PRESSURE TO ATMOSPHERE, TO ALLOW FOR REPAIRS TO BE MADE. IT WAS IMMEDIATLY DETERMINED THAT NO THREAT TO SAFETY OR THE ENVIRONMENT EXISTED.
2017-09-29 08:50 | NO | NO | 19940021 | 1994-01-27 | 808 | ARCO TERMINAL SERVICES CORP | YES | 1993-12-25 | 130 | CA | CARSON |  | NO |  | NO | ARCO'S LOS ANGELES REFINERY, 1801 EAST SEPULVEDA BLVD CARSON, CALIFORNIA 90745 |  | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38316.1989 | 77299.2498 | GASOLINE | 2 | 2 | 0 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 720 | 100 | YES | 4 | 900 | 10 | 83 | EXTERNAL | Null | YES | OTHER | PINHOLE CORROSION LEAK | NO DATA |  | Null | NO DATA |  | Null | Null | EILEEN J. THRASHER - BUSINESS UNIT MANAGER | 3104289300 | LEAK OCCURRED IN SMALL SECTION OF UNCOATED PIPE AT ARCO'S LOS ANGELES REFINERY AND WAS FOUND AT 3:OO PM. LINE WAS SHUT DOWN AND CONTAMINATED SOIL WAS EXCAVATED AND REMOVED AND LINE WAS REPAIRED. PART I CAUSED BY CORROSION- AT COATING BREAK.
2017-09-29 08:50 | NO | NO | 19940022 | 1994-01-14 | 2552 | COLONIAL PIPELINE CO | YES | 1993-11-15 | 1140 | NJ | MIDDLESEX | WOODBRIDGE | NO |  | NO | COLONIAL PIPELINE COMPANY'S LINDEN JUNCION 400 BLAIR ROAD WOODBRIDGE, NJ 07095 |  | TANK FARM | TANK |  | 1964 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | FUEL OIL | 3 | 15 | 9 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR TECHNICAL & REGULATORY | 4048412402 | ON NOVEMBER 15, 1993, A CONTRACTOR ENTERED TANK 1475 AT LINDEN JUNCTION TO PERFORM SCHEDULED MAINTENANCE. THE CONTRACTOR REMOVED A PLATE NEAR THE SUMP ANDFOUND PRODUCT UNDER THE TANK AT 1153 EST ON NOVEMBER 15, NEW JERSEYN DEPARTMENT OF ENVIRONMENTAL PROTECTION AND ENERGY WAS ADVISED OF THE INCIDENT. APPROXIMATELY 9 BARRELS OF PRODUCT WERE RECOVERED AND RETURNED TO THE SYSTEM. ASSESSMENT OF THE DAMAGES INCLUDE THE INSTALLATION OF MONITORING WELLS TO DETERMINE IF ANY GROUND WATER CONTAMINATION IS PRESENT AND TESTING FOR ANY SOIL CONTAMINATION. ON DECEMBER 18, 1993, IT BECAME APPARENT THAT HIS ENVIRONMENTAL TESTING WOULD CAUSE PROPERTY DAMAGES TO EXCEED $5,000, AND THE NATIONAL RESPONSECENTER WAS NOTIFIED ( REPORT NO 213014). AS A COURTESY, MR. BILL GUTE OF THEEASTERN REGION OF THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED OF THE INCIDENTA RADIOGRAPHIC EXAMINATION DETERMINED THAT A CRACK EXISTED IN THE WELD WHERETHE TANK LINE WAS ATTACHED TO THE TANK SUMP. AN EXAMINATION OF THE TANK BOTTOM FOUND NO OTHER POSSIBLE SOURCE FOR THE LEAKING PRODUCT, THEREFORE IT IS DETERMINED THAT THIS CRACK IN THE WELD IS THE SOURCE OF THIS LEAK.
2017-09-29 08:50 | YES | NO | 19940023 | 1994-01-14 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1993-12-09 | 430 | CA | LOS ANGELES |  | NO |  | NO | 26185 W. MCBEAN PARKWAY - SANTA CLARITA |  | TANK FARM | OTHER | NOT GIVEN | 0 | OTHER | POWER FAIL- TANK RAN OVER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 19158.0995 | 38649.6249 | CRUDE OIL | 1 | 200 | 195 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. KELLEY | 8053282331 | POWER TURNED OFF BY POWER COMPANY DOING POWER LINE WORK. TEXACO TRADING AND TRANSPORTATION INC WAS NOT NOTIFIED IN ADVANCE OF THIS PLANNED WORK. TTTI CONTROLLER RECEIVED A COMMUNICATION FAIL ALARM. CONTROLLER DELAYED NOTIFICATION OF APPROPRIATE FIELD PERSONNEL AND TANK RAN OVER.
2017-09-29 08:50 | YES | NO | 19940024 | 1994-01-09 | 18718 | SUN PIPELINE CO | YES | 1993-12-08 | 1310 | PA | LANCASTER |  | NO |  | NO | IMMEDIATELY WEST OF THE CONESTOGA VALLEY INDUSTRIAL CENTER LOCATED ALONG HORSESHOE ROAD IN UPPER LEACOCK TOWNSHIP, PA. |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1600 | 1226.1184 | 2473.576 | GASOLINE | 1 | 2369 | 450 | NO | NO | 6.63 | 0.28 | 2540 | WELDED |  | 1200 | 638 | YES | 8 | 1100 | 5 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KEVIN D. FULMER - SR. ENVIONMENTAL SPECIALIST | 2159755920 | IN RESPONSE TO OPERATIONAL INFORMATION WHICH SUGGESTED THE POSSIBILITY OF A LEAK, THE 6 INCH ICEDALE TO ALLEGHENY LINE WAS SHUT DOWN ON 12/08/93 AT 1310 HOURS. A PRESSURE CHECK IMMEDIATELY FOLLOWED IN TANDEM WITH LINE ISOLATING ACTIVITIES WHICH INDICATED A POTENTIAL LEAK WITHIN AN APPROXIMATE TEN MILE SEGMENT. ONCE THE APPROXIMATE 10 MILE SEGMENT WAS IDENTIFIED, LINE WALKERS AND HELICOPTER OVERFLIGHTS WERE IMMEDIATELY DISPATCHED TO CONFIRM/DENY A LEAK. NO EVIDENCE OF A LEAK WS DISCOVERED. FUTHER LINE ISOLATION ACTIVITIES WERE PERFORMED WHICH IDENTIFIED A SUSPECT TWO MILE SEGMENT. ENVIRONMENTAL CONSULTANTS AND TWO SOIL GAS CONTRACTORS WEE HIRED TO ASSIST IN LOCATING THE LEAK. ON 12/13/1993 THE LEAK WAS DISCOVERED IN A FARMERS FIELD JUST WEST OF THE CONESTOGA VALLEY INDUSTRIAL CENTER. THERE WAS NO SURFICIAL EVIDENCE OF ANY PETROLEUM PRODUCTS AT THIS LOCATION. ALL PRODUCT ENTERED THE SUBSURFACE VIA SHALLOW BEDROCKWHICH WAS LOCATED IMMEDIATELY ADJACENT TO THE LINE. UPON EXCAVATION, IT WAS OBSERVED THAT THE PIPELINE WAS STRUCK IN NUMEROUS LOCATIONS BY A THIRD PARTY.
2017-09-29 08:50 | NO | NO | 19940025 | 1994-02-02 | 12628 | MOBIL PIPELINE CO | NO | 1994-01-03 | 730 | TX | YOAKUM |  | NO |  | NO | 3 MILES NORTH OF DENVER CITY TEXAS ON HWY #214 |  | LINE PIPE | WELDING FITTING |  | 1993 | FAILED WELD | OTHER | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 29096 | 21821.011 | 44021.7931 | CARBON DIOXIDE | 3 | 6 | 0 | NO | NO | 2 | 0.15 | 35000 | WELDED |  | 2130 | 1903 | YES | 12 | 2660 | 7 | 93 | NO DATA | Null | Null | NO DATA |  | OTHER | VIBRATION | Null | NO DATA |  | Null | Null | J.D. HOGUE - OPERATIONS SUPERVISOR | 8062297431 | AT 7:30 A.M. JAN. 03. 1994 I RECEIVED A PHONE CALL FROM A SHELL/CORTEZ PIPELINE EMPLOYEE, TELLING ME THAT WE HAD A LEAK ON OUR ESTE PIPEL INE AT THE ABOVE GROUND VALVE SITE NEAR DENVER CITY, TX. I CALLED THE MPLCO DISPATCHER AND ASKED HIM TO CLOSE THE AUTOMATIC VALVE AT BRAVO PIPE LINE AT DENVER CITY. I ARRIVED AT THE LEAK SITE AT 8:30 A.M. AND DISCOVERED A CRACKED WELD IN A 2" WELD CONNECTING A MAINLINE VALVE BY PASSLINE. I CALLED THE MPLCO DISPATCHER AND INFORMED HIM OF THE PROBLEM AND HAD HIM SHUT CORTEZ PIPELINE DOWN SO THAT THEDAMAGED SECTON OF LINE COULD BE ISOLATED. AT 8:40 AM LINE ISOLATION WAS COMPLETED AND LINE BLOW DOWN BEGAN. IT WAS DETERMINED THAT NO THREAT TO SAFETY OR THE ENVIRONMENT EXISTED.
2017-09-29 08:50 | NO | NO | 19940026 | 1993-12-21 | 18386 | BP OIL PIPELINE CO | NO | 1993-10-26 | 2208 | OH | LUCAS |  | NO |  | NO | AT INTERSECTION OF SEAMEN & LALLENDORF ROADS |  | LINE PIPE | PIPE |  | 1955 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7663.2398 | 15459.85 | FUEL OIL | 3 | 45 | 43 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1200 | 1000 | YES | 24 | 1800 | 0 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.A. DEBROCK - REGION SUPERINTENDENT | 2163514777 | A CORROSION LEAK ON THE BOTTOM OF A 10" PIPELINE ALLOWED THE RELEASE OF FUELOIL. THE FUEL OIL ENTERED AN ADJACENT STOM SEWER WHICH DRAINED INTO AMOLSCH DITCH WHERE THE PRODUCT WAS BOOMED OFF. THE PIPE WAS IMMEDIATELY CLAMPED IN THE AREA OF THE LEAK AND THE PIPE WAS REPLACED ON NOVEMBER 16, ALL FREE PRODUCT WAS PICKED UP AND CONTAMINATED SOIL WAS REMOVED FROM THE SITE.
2017-09-29 08:50 | NO | NO | 19940027 | 1993-01-04 | 808 | ARCO TERMINAL SERVICES CORP | YES | 1993-12-05 | 800 | CA | CARSON |  | NO |  | NO | ARCO'S LOS ANGELES REFINERY, 1801 EAST SEPULVEDA BLVD. CARSON, CALIFORNIA 90745 |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22989.7194 | 46379.5499 | FUEL OIL | 1 | 3 | 0 | NO | NO | 12 | 0.31 | 42000 | WELDED |  | 720 | 150 | YES | 4 | 900 | 11 | 90 | EXTERNAL | Null | YES | OTHER | PINHOLE CORR. LEAK AT COA | NO DATA |  | Null | NO DATA |  | Null | Null | EILEEN J. THRASHER - BUSINESS UNIT MANAGER | 3104289300 | LEAK OCCURRED IN SMALL SECTION OF UNCOATED PIPE NEAR TANK 101 AT ARCO'S LOS ANGELES REFINERY AND WAS FOUND AT 8:00 AM. LINE WAS SHUT DOWN AND CONTAMINATED SOIL WAS EXCAVATED AND REMOVED AND LINE WAS REPARIED. PART I - AT COATING BREAK.
2017-09-29 08:50 | YES | NO | 19940028 | 1993-12-24 | 22907 | WYCO PIPE LINE CO | YES | 1993-12-19 | 700 | CO | ADAMS | DUPONT | NO |  | NO | DUPONT TERMINAL TANK 17 SEC 29,TS-2S, R767W ADAMS COUNTY, COLORADO DUPONT, CO 80024 |  | TANK FARM | PIPE |  | 0 | OTHER | WATER LINE FROZE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NOT GIVEN | 1 | 256 | 30 | NO | NO | 8 | 0 | 0 | FLANGED |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. ADAMS - FIELD SUPERVISOR | 3032866401 | AT 0730 I WAS NOTIFIED BY DICK LOCKMAN THAT WE HAD A PROBLEM AT THE DUPONT TERMINAL. THE DISCHARGE LINE OFF OF TANK 17 HAD FROZEN AND RUPTURED 3 GASKETS AND WE HAD WATER DRAINING ON THE GROUND. AT 0735 I CONTACTED AL PAPROSKI, RUBEN RIOS, AND PAT DANIELS (LEED TOOL), INFORMING THEM WHAT WAS GOING ON. I ASKED PAT TO GET HOLD OF SCOTT FARNER BECAUSE WE WOULD BE NEEDING THE VAC TRUCK TO PICK UP THE WATER. AT 0740 I NOTIFIED THE CDH (ANSWERING SERVICE) THAT WE HAD A WATER LEAK. THIS WAS DONE FROM MY CELLULAR PHONE. I INFORMED THEM THAT I WOULD UPDATE THEM AS SOON AS I WAS ON SCENE. I ARRIVED ON THE SCENE AT 0815AND FOUND WE HAD A SMALL LEAK FROM THREE PLACES AND OVER THE COURSE OF TIME HAD LOST ABOUT 256 BARRELS OF WATER FROM THE TANK. THIS WAS 1 FOOT OF LEVEL. IN THE TANK WE HAD 6 FEET OF WATER AND ON TOP OF THAT HAD 1.5 FEET OF OFF-SPEC PRODUCT. I HAD RUBEN TAKE AN LEL ON WHAT WAS COMING OUT OF THE TANK AND IT WAS ZERO. AT 0818 I CONTACTED THE NRC AND INFORMED THEM OF WHAT WE HAD GOING ON. I TALKED TO PETTY OFFICER MANGONI AND HE GAVE ME AN INCIDENT NUMBER OF 213208. AT 0830 I GOT A CALL BACK FROM TAMMIE OTTMER (CDH) AND EXPLAINED WHAT WAS GOING ON. SHE ASKED ME IF I HAD CONTACTED ANY OTHER AGENCY. I TOLD HER THENRC AND GAVE HER THE INCIDENT NUMBER. SHE ALSO WANTED ME TO CALL THE STATE OIL INSPECTOR (289-5643). I TRIED, THIS IS THE WRONG PHONE NUMBER. AT 0850 I CALLED THE ADAMS COAUNTY LEPC AND TALKED TO AN OFFICER LUCERO. HE TOOK THE REPORT AND SAID HE WOULD PASS IT ON TO THE POLICE AND FIRE DEPTS. AT 0910 SOUTH ADAMS COUNTY FIRE DEPT. CALLED AND I TOLD THEM WHAT WE HAD. HE SAID HE MAY HAVE SOMEONE GIVE US A CALL. AT 0915 THE LEAKING FLANGE WAS SECURED. 0915 I CONTACTED THE AMOCO NOTIFICATION CENTER AND PASSED ON TO THEM ALL OF THE INFORMATION THAT WE HAVE AND WHO I CONTACTED. AT 0924 RON LAPENTA CALLED AND I TOLD HIM WHAT WE HAD, HE SAID HE MAY COME OUT AND TAKE A LOOK IN A WHILE. AT 0935 I CALLED ALAN PITNEY AT HOME AND TOLD HIM ABOUT WHAT AS GOING ON, WHO I'D TALKED TO AND THAT HE NEED NOT BOTHER COMING OUT, EVERYTHING WAS UNDER CONTROL. CLEAN-UP STARTED AT 0930 WITH THE VAC TRUCK PICKING UP WHAT IS NOT FROZEN. MOST OF THE WATER IS IN THE FORM OF ICE AND THE COLOR IS CLEAR. 1010 PROCEEDINGTO FILL OUT REPORT FORMS. PART D - RUPTURING FLANGE GASKETS (3)
2017-09-29 08:50 | NO | NO | 19940029 | 1994-03-09 | 2552 | COLONIAL PIPELINE CO | YES | 1994-02-02 | 1657 | NJ | GLOUCESTER | WEST DEPTFORD TOWNSHIP | NO |  | NO | COLONIAL PIPELINE COMPANY'S WOODBURY TANK FARM MANTUA GROVE ROAD WOODBURY, NJ 08096 |  | TANK FARM | TANK | TANK ROOF DRAIN LINE | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 27500 | 20624.0653 | 41607.07 | KEROSENE | 3 | 5 | 4 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR -TECHNICAL & REGULATORY | 4048412402 | SHORTLY AFTER BEGINNING A DELIVERY OF AVIATION KEROSINE INTO TANK 1251 AT WOODBURY JUNCTION ON FEBRUARY 2, 1994, AN EMPLOYEE CHECKED THE TANK AND AT 1657EST, DISCOVERED PRODUCT FLOWING INTO THE TANK DIKE FROM THE TANK ROOF DRAIN.THE EMPLOYEE IMMEDIATELY CLOSED THE THREE-WAY VALVE ON THE DRAIN LINE AND STOPPED THE ESCAPE OF PRODUCT. AFTER DETERMINING THAT APPROXIMATELY 5 BARRELS OFKEROSINE HAD ESCAPED AND WAS CONTAINED WITHIN THE TANK DIKE, TELEPHONIC NOTICE WAS MADE TO THE NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION AND ENERGY AT 1724 EST. COMPANY PERSONNEL AND LOCAL RESPONSE CONTRACTORS WERE CALLEDTO THE SITE AND RECOVERED APPROXIMATELY 4 BARRELS OF PRODUCT. CONTAMINATED SOIL HAS BEEN PLACED IN AN IMPERVIOUS ENEVELOPE AND WILL BE DISPOSED OF AT A LATER DATE. ON FEBRUARY 4, 1994, IT WAS DETERMINED THAT THE DAMAGE AND REPAIR COSTS OF THE INCIDENT WOULD EXCEED $5,000 AND THE NATIONAL RESPONSE CENTER WASNOTIFIED AT 1115 EST (REPORT NO. 220140). THIS TANK HAS BEEN TAKEN OUT OF SERVICE AND THE DRAIN LINE WILL BE EXAMINED TO DETERMINE THE EXACT CAUSE OF THEFAILURE. SUPPLEMENTAL REPORT 2/15/95 STATES: AN INVESTIGATION REVEALED THATEXTREMLEY LOW TEMPERATURES IN THE REGION CAUSED WATER TRAPPED IN THE DRAINLINE TO FREEZE, THE PIPING SUBSEQUENTLY SPLIT RELEASING THE PRODUCT.
2017-09-29 08:50 | NO | NO | 19940030 | 1994-01-10 | 30687 | ASSOCIATED TRANSPORT & TRADING CO | YES | 1994-01-07 | 1730 | OK | JEFFERSON |  | NO |  | NO | SW 1/4 SEC 9 T6S R7W |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1124.949 | 2269.4765 | CRUDE OIL | 1 | 45 | 40 | NO | NO | 16 | 0.32 | 0 | FLANGED |  | 350 | 120 | YES | 2 | 640 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | NOT GIVEN | Null | ONE CALL |  | NO | NO | STEVEN C. BAGLEY - PIPELINE MANAGER | 4052397191 | AT APPROXIMATELY 17:30, ATTCO WAS NOTIFIED BY KOCH OIL THAT AN ANONYMOUS CALL WAS RECEIVED REPORTING A PIPELINE LEAK ON OUR LINE, UPON THE ARRIVAL AT THELOCATION, ATTCO PERSONNEL SHUT DOWN THE LINE AND BEGAN CLEAN-UP OPERATIONS AND MAKING REPAIRS. THE HOLE WAS AT 9:00, AND WAS DETERMINED AS A RIFLE BULLETHOLE. CRUDE OIL TRAVELED 200 YARDS DOWN A CREEK BED (CREEK WAS NOT FLOWING) THAT HAD A SMALL AMOUNT OF WATER IN IT, WASHED DOWN CREEK BANKS, AND WAS VACCUMED UP.
2017-09-29 08:50 | YES | NO | 19940031 | 1994-02-18 | 4493 | ENTERPRISE PRODUCTS CO | YES | 1994-01-19 | 1015 | TX | ORANGE |  | NO |  | NO | 0.66 MILE EAST OF NECHES RIVER OR 0.18 MILE EAST OF BAIRDS CANAL |  | LINE PIPE | PIPE |  | 1938 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 337484.7043 | 680842.964 | NOT GIVEN | 2 | 462 | 0 | NO | NO | 6.63 | 0.22 | 2777 | OTHER |  | 700 | 450 | YES | 24 | 900 | 0 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | ENTERPRISE INSPEC ON SITE | YES | YES | DONALD R. SCOTT - PIPELINE SUPERINTENDENT | 7133854383 | PIPE WAS PROBABLY DAMAGED IN OCTOBER, 1992 BY A CONTRACTOR LAYING TWO 6" PIPELINES IN A MARSHY AREA. THE NEW LINES CROSSED UNDER A CORRIDOR CONTAINING ONE ENTERPRISE AND THREE OTHER PIPELINES. AN ENTERPRISE INSPECTOR WAS ON SITE WHEN THE DITCH FOR THE NEW LINES WAS DUG, AND NO DAMAGE WAS OBSERVED. THE INSPECTOR WAS NOT PRESENT WHEN THE NEW LINES WERE LAID BECAUSE THE CONTRACTOR DIDNOT CONTACT HIM OR ENTERPRISE BEFORE STARTING BY THE CONTRACTOR, BUT THE LEAK OCCURRED AND DAMAGED PIPE WAS FOUND AT THE CROSSING POINT. PART J.- IF CALLED BY EXCAVATOR.
2017-09-29 08:50 | NO | NO | 19940032 | 1994-03-09 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-02-23 | 100 | CA | LOS ANGELES |  | NO |  | NO | LOCATED IN A CHRISTMAS TREE FARM N. OF MAGIC MOUNTAIN PKWY E. OF I-5, S. OF SANTA CLARA RIVER W. OFTHE CITY BOUNDARY-SANTA CLARITA (SEC 21,T4N,R16W)FCPL -LINE1 |  | LINE PIPE | PIPE |  | 1925 | FAILED WELD | EARTHQUAKE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | CRUDE OIL | 1 | 4 | 0 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 638 | 30 | YES | 4 | 797 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | ONE CALL |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | FAILURE OF GIRTH WELD DURING NORTHRIDGE EARTHQUAKE (1/17/94). DISCOVERED DURING GAS TESTING OF LINE PRIOR TO RESTORING SERVICE.
2017-09-29 08:50 | YES | NO | 19940033 | 1993-11-23 | 22610 | WILLIAMS PIPELINE CO | YES | 1993-10-17 | 1330 | IA | POLK | DES MOINES | NO |  | NO | TANK 777 IN WPL DES MOINES, IOWA, TANK FARM LOCATED IN SE QUARTER OF SECT 17, TOWNSHIP 78N, RANGE 23W ON THE EAST SIDE OF HIGHWAY 46 |  | TANK FARM | PUMP |  | 1955 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 383.162 | 772.9925 | GASOLINE | 1 | 75 | 75 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | TANK PUMP MECH FAILURE | Null | NO DATA |  | Null | Null | STEVEN S. BALL, SR. VP & GENERAL MANAGER | 9185883850 | DURING THE INSPECTION OF THE TANK FARM, THE OPERATOR SMELLED THE PRESENCE OFGASOLINE AND DISCOVERED THE PRODUCT ON THE SURFACE OF GROUNDWATER PRESENT INTHE TANK DIKE. AT THAT TIME THE SOURCE OF THE SPILL WAS FOUND TO BE FROM THETANK PUMP. THE LEAK WAS IMMEDIATELY ISOLATED. THE WATER WAS SKIMMED AND THE PRODUCT WAS VACUMMED UP AND DISCHARGED INTO THE TANK FARM SEPARATOR. THE PUMPWAS REMOVED AND SENT FOR REPAIR.
2017-09-29 08:50 | YES | NO | 19940034 | 1994-03-02 | 12628 | MOBIL PIPELINE CO | NO | 1994-01-28 | 930 | TX | NAVARRO | POWELL | NO |  | NO | EAST ON HWY 31 TO POWELL, TEXAS. RIGHT ON FARM ROAD 633. APPX. 2 MI ON FM 633 ON RIGHT. |  | LINE PIPE | PIPE |  | 1987 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 26000 | 19499.1162 | 39337.5935 | CRUDE OIL | 1 | 150 | 148 | NO | NO | 12.75 | 0.03 | 1370 | WELDED |  | 250 | 40 | YES | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | NOT AVAILABLE | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT - FIELD LOGISTICS MANAGER | 9036545321 | 7:30 AM CORSICANA HAD RECEIVED INFORMATION THAT THE EAST TEXAS CRUDE LINE WAS SHORT FOR THE TOTAL BARRELS PUMPED. LINE FLYER REPORT POSSIBLE LEAK NEAR MP.95 NEAR CORSICANA. HAWTHORNE CHECKED OUT LEAK SITE AT MP 95 AND FOUND OIL LEAKING NEAR MOBIL LINE AND ALSO DISCOVERED A 2" PLASTIC FLOW LINE THAT CROSSEDMOBIL LINE AT THE SAME LOCATION OF THE LEAK. REPORTED TO DALLAS THAT HAD POSSIBLE LEAK AND WANTED TO SHUT DOWN EAST TEXAS SYSTEM. DALLAS HAS SHUT THE LINE DOWN WHEN SHORTAGE WAS DISCOVERED. CLOSED GATE VALVES AT MP 81 AND MP 95 FOREIGN LINE WAS LATER FOUND TO BE A 2" WATER LINE. LEAK WAS MOBIL CRUDE. BOOMSWERE INSTALLED ON PIT IN PIPE AND LEAK WAS SECURED OFF. CREW BEGAN CLEAN UP AND LOCATING LAND OWNER OF PROPERTY AND ESTIMATE OF CRUDE BEING ASSESSED. CREEK HAD TO BE WALKED AND CHECKED FROM LEAK SITE TO END OF CREEK WHICH WAS ABOUT .5 MILES. PART I - REDUCING BACTERIA
2017-09-29 08:50 | YES | YES | 19940036 | 1994-03-09 | 10318 | KOCH REFINING CO | YES | 1994-02-15 | 940 | WI | EAU CLAIRE |  | NO |  | NO | PROPANE TRUCK TERMINAL INTERSECTION OF HWY 93 AND SPRUCE ROAD |  | NO DATA | LONGITUDINAL WELD | PIPELINE SCRAPER TRAP APP | 1992 | OTHER | SEE PART K | ALL OTHER CAUSES | MISCELLANEOUS | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK M. MCCANN - DIVISON MANAGER | 6124584860 | AT APPROXIMATELY 9:40 A.M ON FEBRUARY 14, 1994 A TRUCK DRIVER AT THE KOCH REFINING COMPANY EAU CLAIRE, WI PROPANE TERMINAL DISCOVERED THE BODY OF KOCH EMPLOYEE, MR. ROBERT N. SHAFFER IN A SAMPLING BUILDING ADJACENT TO OPERATORS PIPELINE. THE DRIVER NOTED THAT A SMALL VALVE ON THE 1/4 INCH SAMPLING TUBING WAS IN THE OPEN POSITION, ALLOWING PROPANE TO ESCAPE INTO THE SAMPLING BUILDING. THE VALVE WAS COLOSED BY THE DRIVER WITHOUT DIFFICULTY. THE DRIVER WAS TAKEN TO A LOCAL HOSPITAL FOR OBSERVATION AND WAS RELEASED THE SAME DAY. NO DEFECTS IN THE SAMPLING TUBING OR VALVE WERE FOUND. THERE WAS NO EVIDENCE THAT MR. SHAFFER WAS IN THE PROCESS OF PERFORMING SAMPLING. MR. SHAFFER WAS AN EXPERIENCED OPERATOR. INVESTIGATION IS CONTINUING TO DETERMINE IF AN UNRELATED MEDICAL EMERGENCY PRECIPITATED THE OPENING OF THE VALVE OR THE FAILURE TO CLOSE THE VALVE. PART C - APPERTUNANCE (1/4 INCH SS TUBING IN SAMPLING BLDG).
2017-09-29 08:50 | YES | NO | 19940037 | 1994-03-07 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-02-08 | 858 | NM |  | SAN JUAN | NO |  | NO | TOWNSHIP 28 N., RANGE 11 W., SECTION 13 OF SAN JUAN COUNTY, NEW MEXICO |  | NO DATA | OTHER | RETRACTABLE SAMPLE PROBE | 1992 | OTHER | RETRACTABLE SAMPLE PROBE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2954 | 2215.3996 | 4469.3558 | NATURAL GAS LIQUID | 2 | 65 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH - MANAGER OPERATIONS SUPPORT | 9185811800 | THE RETRACTABLE SAMPLE PROBE RETAINING MECHANISM APPARENTLY FAILED, ALLOWINGPRODUCT TO BE RELEASED TO THE ATMOSPHERE FOR FOURTEEN MINUTES. THE CAUSE OFTHE PROBE RETAINING MECHANISM FAILURE IS BEING EVALUATED IN COOPERATION WITHPROBE MANUFACTURER. PART D - CAME LOOSE OR BROKE. SUPPLEMENTAL REPORT 5/24/94INDICATED THAT RESULTS FROM AN EVALUATION OF THE SAMPLING PROBE HAVE BEENRECEIVED. CAUSE FOR THE FAILURE WAS DETERMINED TO BE EITHER IMPROPER ASSEMBLYOF THE PROBE BY THE MANUFACTURER OR A DEFECTIVE SNAP RING. A SURVEY OF THESYSTEM HAS CONCLUDED THAT NO SIMILAR UNITS ARE IN OPERATION. THE PROBE VENDORHAS BEEN NOTIFIED OF THE PROBLEM.
2017-09-29 08:50 | NO | NO | 19940038 | 1994-03-16 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1994-02-14 | 1430 | CA | ORANGE | ORANGE | NO |  | NO | ORANGE TERMINAL 1350 N. MAIN ORANGE, CA 92667 |  | PUMPING STATION | VALVE | ORANGE BY PASS VALVE | 1962 | OTHER | VALVE SEAL LEAKED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | NOT GIVEN | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT - OPERATIONS & ENG | 2134867720 | A STAIN WAS NOTED AT ORANGE TERMINAL NEXT TO THE SAMPLE SHED. THE AREA WAS EXCAVATED AND CAUSE OF STAIN WAS FOUND TO BE A SEAL LEAK ON AN UNDERGROUND BY-PASS VALVE. SEAL WAS REPLACED. OUR ENVIRONMENTAL DEPARTMENT IS CURRENTLY WORKING ON CLEANING UP THE SITE, AND THE AMOUNT OF PRODUCT INVOLVED IS UNKNOWN AT
2017-09-29 08:50 | YES | NO | 19940039 | 1994-03-04 | 22830 | WOLVERINE PIPELINE CO | YES | 1994-01-20 | 1330 | MI | JACKSON | BLACKMAN TOWNSHIP | NO |  | NO | 2101 MORRILL ROAD, JACKSON MI |  | NO DATA | OTHER | GRAVITOMETER ATTACHED TO | 1972 | OTHER | FAILED O-RING IN GRAVITOM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 38000 | 28498.7084 | 57493.4058 | GASOLINE | 3 | 100 | 63 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.C. COLE - VICE-PRESIDENT/MANAGER | 6163232491 | AT 13:30 HOURS, JANUARY 20, 1994, THE OPERATOR OF SHELL'S JACKSONS PRODUCTS TERMINAL INFORMED WOLVERINE PIPE LINE CO. THAT A SMALL PUDDLE OF GASOLINE HADBEEN DISCOVERED NEAR A TANK DIKE ON SHELL'S PROPERTY. THE GASOLINE PUDDLE WAS LOCATED AT THE END OF A FIELD TILE DRAINAGE PIPE WHERE THE PIPE EXITTED THEGROUND. INSPECTION OF WOLVERINE PIPE LINE CO'S FACILITIES REVEALED A SMALL STREAM OF GASOLINE LEAKING FROM A GRAVITOMETER. THE GRAVITOMETER WAS REMOVED AND REPLACED WITH A FLANGE BLIND THUS STOPING THE LEAK. A FAILED O-RING IN THEGRAVITOMETER WAS THE CAUSE OF THE LEAK. ALL OF THE LEAKED GASOLINE HAD MIGRATED THROUGH THE SOIL AND ENTERED THE DRAINAGE PIPE. THE QUANTITY WAS ESTIMATED TO BE 10 BARRELS. CLEAN UP OF THE LAK WAS IMMEDIATELY STARTED. THE INCIDENTWAS REPORTED TO THE MICHIGAN DEPARTMENT OF NATURAL RESOURSES. AFTER ALL OF THE ABOVE GROUND GASOLINE HAD BEEN RECOVERED, A PUMP WAS SET UP AT THE END OF THE DRAINAGE PIPE TO PUMP ANY ADDITIONAL GASOLINE FLOW INTO WOLVERINE PIPE LINE CO'S DELIVERY STATION SUMP TANK. AS OF FEBRUARY 4, 1994, 52 BARRELS OF GASOLINE HAD BEEN RECOVERED MAKING THIS A D.O.T REPORTABLE INCIDENT. A TELEPHONIC REPORT WAS MADE TO PETTY OFFICER EASON AT THE NATIONAL RESPONSE CENTER, REPORT NO. 220199. PART C - TO THE MAINLINE PIPE.
2017-09-29 08:50 | YES | NO | 19940040 | 1993-12-15 | 26049 | INDIANA FARM BUREAU COOP ASSOC INC | NO | 1993-11-11 | 1805 | IN | TIPTON |  | NO |  | NO | MAP ATTACHED AT THE CORNERS OF C. RDS. 900 W & 550N R3E, T23N, SEC3 TIPTON COUNTY INDIANA |  | PUMPING STATION | VALVE |  | 1958 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2298.9719 | 4637.955 | OIL AND GASOLINE | 2 | 40 | 34 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TIMOTHY J. PALMER - MANAGER ENVIR. COMPLIANCE | 3172431523 | BOOSTER PUMP FAILED TO START, THE SUCTION CONTROL VALVE AND THE BLOW DOWN VALVE BOTH MALFUNCTIONED CAUSING THE RELEASE OF UNLEADED GASOLINE.
2017-09-29 08:50 | YES | NO | 19940041 | 1994-02-02 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1994-01-06 | 1235 | TX | WHARTON |  | NO |  | NO | NEAR DANEVANG STATION OFF OF COUNTY ROAD401; WEST OF TOWN OF DANEVANG; NEAR HIGHWAY 71. |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | L. P. G. | 2 | 20 | 0 | NO | NO | 12.75 | 0.2 | 46000 | OTHER |  | 1050 | 535 | YES | 8 | 1320 | 11 | 90 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW - ENVIRONMENTAL & SAFETY SUPERVISOR | 7138777370 | LEAK WAS FOUND BY COASTAL STATES CRUDE GATHERING MAINTENANCE CREW WHILE WORKING ON OUR HOUSTON 8" LINE NEARBY. VAPORS WERE OBSERVED COMING OUT OF CASING VENT ON NORTH SIDE OF COUNTY ROAD CROSSING. LINE WAS SHUT DOWN, STOPPLE FITTING INSTALLED, AND BLOWN-DOWN BEFORE REPLACING WITH 100' OF NEW PIPE.
2017-09-29 08:50 | YES | NO | 19940042 | 1994-02-06 | 10012 | KANEB PIPELINE CO | YES | 1994-01-13 | 811 | NE | YORK |  | NO |  | NO | NE1/4, SECTION 15, TOWNSHIP 12 NORTH, RANGE 2 WEST, YORK COUNTY, NEBRASKA |  | LINE PIPE | PIPE |  | 1965 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | OIL AND GASOLINE | 3 | 505 | 17 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1318 | 1315 | YES | 8 | 1674 | 4 | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.LEROY ANDERSON - MANAGER OF REGULATORY AFFAIRS | 3162621408 | LONGITUDINAL WELD SEAM FAILED, WHICH RESULTED IN AN APPROXIMATE THREE-FOOT LOTHE FAILURE WAS CAUSED BY HOOK CRACKS CONCENTRATED IN A SIX-INCH SECTION OF THE WELD SEAM. THE METALLURGICAL REPORT HAS BEEN SUBMITTED TO THE OFFICE OF PIPELINE SAFETY REGIONAL OFFICE IN KANSAS CITY, MISSOURI AND WASHINGTON, DC.
2017-09-29 08:50 | YES | NO | 19940043 | 1994-02-14 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | LOCATED IN A CHRISTMAS TREE FARM NORTH OF MAGIC MOUNTAIN PKWY. E. OF 1-5 S. OF SANTA CLARA RIVER W. OF THE CITY BOUNDARY SANTA CLARITA(SEC21,T4N,R16W)FCPL LINE1 |  | LINE PIPE | PIPE |  | 1925 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 74996.601 | 151298.4364 | CRUDE OIL | 1 | 35 | 5 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 638 | 10 | YES | 4 | 797 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | T SPILL SITE VACUUMED RECOVERABLE CRUDE OIL, REMOVED CONTAMINATED SOIL FOR ROAD BASE PROCESSING.
2017-09-29 08:50 | YES | NO | 19940044 | 1994-02-14 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | LOCATED NEAR THE CROSSING OF POSEY CREEK IN POSEY CANYON-ONE MILE E.OF I-5 SAND BUNKER, E. OF PYRAMID LAKE - W. OF OLD RIDGE ROUTE (SEC 36,T7N,R18W) FCPL LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 82496.261 | 166428.2801 | CRUDE OIL | 1 | 592 | 140 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 507 | 243 | YES | 4 | 634 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | ONE CALL |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | FAILURE OF GIRTH WELD DURING EARTHQUAKE, CONTAINED SPILL WITH PRIMARY AND SECONDARY EARTHEN DAMS. REPAIRED/REPLACED DAMAGED PIPELINE AT SPILL SITE. VACUUMED RECOVERABLE CRUDE OIL AND REMOVED CONTAMINATED SOIL FOR ROAD PROCESSING.
2017-09-29 08:50 | NO | NO | 19940045 | 1994-02-14 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | LOCATED IN THE VALENCIA GOLF COURSE W. OF MCBEAN PKWY N. OF VALENCIA BLVD S. OF MAGIC MOUNTAIN PKWY E. OF I-5 SANTA CLARITA (SEC 21,T4N,R16W) FCPL - LINE 1 |  | LINE PIPE | PIPE |  | 1925 | FAILED WELD | EARTHQUAKE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | CRUDE OIL | 1 | 5 | 1 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 638 | 10 | YES | 4 | 797 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | ONE CALL |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | FAILURE OF GIRTH WELD DURING EARTHQUAKE, REPAIRED/REPLACED DAMAGED PIPELINE AT SPILL SITE. VACUUMED RECOVERABLE CRUDE OIL AND REMOVED CONTAMINATED SOIL FOR ROAD BASE PROCESSING.
2017-09-29 08:50 | YES | NO | 19940046 | 1994-02-23 | 809 | ARCO PIPE LINE CO | YES | 1994-01-21 | 1300 | KS | MIAMI | OSAWATOMIE | NO |  | NO | SEC 10,T18S,R22E, MIAMI COUNTY, KANSAS ON THE SOUTH BANK OF MARAIS DES CYGNES RIVER, N. OF PARKER STREET, IN OSWATOMIE, KANSAS |  | LINE PIPE | GIRTH |  | 1929 | FAILED WELD | FROSTHEAVE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 2359000 | 1769169.8165 | 3569130.1156 | DIESEL FUEL | 3 | 3869 | 3535 | NO | NO | 8.63 | 0.5 | 35000 | WELDED |  | 700 | 350 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | FROSTHEAVE |  | Null | NO DATA |  | Null | Null | L.E. GRAVES - OPERATIONS ADVISOR PRODUCTS BUSINESS UNIT | 7139865368 | RELEASE WAS SUSPECTED AT 1300 HOURS ON 01/21/94 WHEN LINE LOST PRESSURE, BUTCOULD NOT BE CONFIRMED BY AERIAL PATROL INSPECTION OF LINE. AT THAT TIME THELINE WAS PRESSURED UP FROM BLOCK VALVE TO BLOCK VALVE STARTING AT NEODESHA, KANSAS. LINE WALKERS AND PILOT INSPECTED EACH SEGMENT BEFORE PRESSURE WAS ALLOWED THROUGH TO NEX BLOCK VALVE. THIS PROCESS CONTINUED UNTIL 01/23/94 WHEN LINE WALKERS FOUND DIESEL FUEL ON THE MARAIS DES CYGNES RIVER WHILE WALKING LINE BEFORE THIS SEGMENT WAS PRESSURED UP. PERMANENT REPAIRS WERE COMPLETED ONWEDNESDAY 02/02/94. APPROXIMAELY 700 FT OF .500 WALL PIPE WAS PULLED UNDER THE RIVER BY DIRECTIONAL DRILL. ONE ADDITIONAL BLOCK VALVE WAS INSTALLED ON EACH SIDE OF THE RIVER CROSSING. A CONTROLLED BURN WAS CONDUCTED ON FEBRUARY 11, 1994.
2017-09-29 08:50 | NO | NO | 19940047 | 1994-02-25 | 18273 | SHELL PIPELINE CORP | NO | 1994-01-31 | 900 | CA | KINGS | BAKERSFIELD | NO |  | NO | BAKERSFIELD 14-INCH PIPELINE TWO MILES SOUTHEAST FROM UTICA AND APPRIMATELY ONE -FOURTH MILE NORTHEAST FORM I-5 |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 33000 | 24748.8783 | 49928.484 | CRUDE OIL | 1 | 47 | 25 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 950 | 92 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. KORPAL - MANAGER REGULATORY COMPLIANCE | 7132410132
2017-09-29 08:50 | YES | NO | 19940048 | 1994-02-14 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | NEWHALL PUMP STATION, 26186 W. MCBEAN PKWY, VALENCIA CA. W. SIDE OF MCBEAN PKWY, & S. OF VALENCIA BLVD IN SANTA CLARITA FCPL - LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 12000000 | 8999592.1142 | 18155812.3725 | CRUDE OIL | 1 | 4207 | 1360 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 822 | 270 | YES | 4 | 1020 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | ONE CALL |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | FAILURE OF GIRTH WELD DURING EARTHQUAKE, OIL SPILT ONTO MCBEAN PARKWAY ENTERED STORM DRAIN AND SANTA CLARA RIVER (12 MILES). REPAIRED/REPLACED DAMAGED PIPELINE AT NEWHALL PUMP STATION. VACUUMED RECOVERABLE CRUDE OIL, REMOVED CONTAMINATED SOIL, STEAM CLEANED AND WATER WASHED AFFECTED AREAS.
2017-09-29 08:50 | YES | NO | 19940049 | 1994-01-06 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1993-12-06 | 720 | CA | SAN BERNARDINO |  | NO |  | NO | SW 1/4 OF SEC. 15, T2N, R12E,SBBM, SAN BERNARDINO CTY. (MILEPOST 166.1 - LINE 90). |  | LINE PIPE | PIPE |  | 1957 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 61305.9183 | 123678.7997 | CRUDE OIL | 1 | 75 | 35 | NO | NO | 16 | 0.25 | 52 | WELDED |  | 944 | 100 | YES | 8 | 1180 | 9 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | YES | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | CONTRACT BACKHOE OPERATOR DIGGING PARALLEL TO MAIN LINE HIT A 2" CONNECTION.LINE SHUT DOWN, PIPE REPLACED AND LINE PUT BACK IN SERVICE. PART D - CONTRACTOR PERSONNEL.
2017-09-29 08:50 | NO | NO | 19940050 | 1994-02-25 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1994-02-08 | 1500 | PA | DAUPHIN | REED TOWNSHIP | NO |  | NO |  |  | TANK FARM | OTHER | .5 INCH PIPING | 1973 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | GASOLINE | 3 | 15 | 7 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER - REGULATORY COMPLIANCE ADMINSTRATOR | 6108208300 | COLD WEATHER CAUSED FROSTHEAVE ON A 1/2" THERMAL RELIEF LINE ON A TANK MANIFOLD AND DAMAGED A THREADED JOINT. THE AFFECTED PIPING WAS PROMPTLY ISOLATED AND DRAINED. ALL NOTIFICATIONS WERE MADE IN A TIMELY MANNER. THE RELEASED PRODUCT WAS CONTAINED IN THE IMMEDIATE AREA. AFFECTED SOIL WAS REMOVED. CLEANUP IS PROCEEDING TO THE SATISFACTION OF THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL RESOURCES.
2017-09-29 08:50 | NO | NO | 19940060 | 1994-02-28 | 2552 | COLONIAL PIPELINE CO | YES | 1994-01-28 | 1544 | NJ | GLOUCESTER | WEST DEPTFORD TOWNSHIP | NO |  | NO | COLONIAL PIPELINE COMPANY'S WOODBURY JUNCTION MANTUA GROVE ROAD WOODBURY,NJ 08096 |  | TANK FARM | VALVE |  | 1964 | OTHER | FREEZING TEMP CAUSED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 6749.6941 | 13616.8593 | KEROSENE | 3 | 4 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR TECHNICAL & REGULATORY | 4048412402 | AT 1544 EST ON JANUARY 28, 1994, A STATION OPERATOR AT WOODBURY JUNCTION CHECKED TANK 1250 SHORTLY AFTER BEGINNING A KEROSINE DELIVERY INTO THE TANK AND FOUND A STREAM OF PRODUCT ESCAPING FROM A BRASS CHECK VALVE ON THE AUTOMATIC WATER DRAW (STINGER) SYSTEM OF THE TANK. THE OPERATOR IMMEDIATELY CLOSED THE BALL VALVE TO THE STINGER, SHUTTING OFF THE PRODUCT FLOW THROUGH THE STINGER LINE. A CONTRACTOR WAS CALLED TO THE SCENE AND RECOVERED APPROXIMATELY 3 BARRELS OF PRODUCT. CONTAMINATED SOIL WAS PLACED IN AN IMPERVIOUS ENVELOPE AND AWAITS DISPOSAL. AN INVESTIGATION FOUND THE LEAK WAS CAUSED BY A CRACK THAT DEVELOPED WHEN WATER TRAPPED IN THE VALVE FROZE DURING THE EXTREMELY LOW TEMPERATURES OF LATE JANUARY. NOTIFICATION OF THE INCIDENT WAS MADE TO THE NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION AND ENERGY (NJDEPE) AT 1622 EST ON JANUARY 28, 1994. ON JANUARY 31,1994, AT 0820 EST, AFTER IT WAS DETERMINED THAT CLEANUP AND REPAIR COSTS WOULD EXCEED $5000, NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER (REPORT NO 219966). PART D - CRACK IN CHECK VALVE.
2017-09-29 08:50 | YES | NO | 19940061 | 1994-02-18 | 808 | ARCO TERMINAL SERVICES CORP | NO | 1994-02-10 | 1900 | CA | LOS ANGELES |  | NO |  | NO | EAST HYNES FACILITY 5905 PARAMOUNT BLVD LONG BEACH,CALIFORNIA 90805 |  | TANK FARM | VALVE |  | 1977 | INCORRECT OPERATION BY OPERATOR PERSONNEL | OTHER | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1124.949 | 2269.4765 | GASOLINE | 2 | 15 | 14 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | NOT GIVEN | Null | NO DATA |  | Null | Null | EILEEN J. THRASHER - VICE PRESIDENT | 3104289300 | TRANSFER MANIFOLD DRAIN VALVE WAS INADVERTENTLY LEFT OPEN RESULTING IN THE SPILL.
2017-09-29 08:50 | YES | NO | 19940062 | 1994-02-25 | 15116 | PANOLA / RUSK GATHERERS | NO | 1994-01-29 | 425 | TX | PANOLA |  | NO |  | NO | RUPTURE OCCURED AT PIPELINE STATION 110 +51 |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 254000 | 190491.3664 | 384298.0286 | L. P. G. | 2 | 0 | 0 | YES | YES | 8 | 0.22 | 2133 | WELDED |  | 1280 | 1045 | YES | 8 | 1675 | 11 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | JOHN A. KROGUE - VICE PRESIDENT | 8178777106 | THE FAILURE OCCURRED AT STATION 110+51 ON PANOLA'S 8" "SANJAC PIPELINE". ON THURSDAY, JANUARY 27, 1994, UNION PACIFIC RESOURCES (UPRC) USED A CONTRACTOR TO EXCAVATE A 6" GAS GATHERING LINE OPERATED BY UPRC IN ORDER TO INSTALL A RISER AND VALVE. THE CONTRACTOR WAS TOLD ABOUT THE LOCATION OF THE PANOLA 8" LIQUID PIPELINE WHICH WAS ADJACENT TO THE PIPELINE BEING EXCAVATED. EVEN THOUGHTHE 8" LIQUID LINE MAY HAVE BEEN TEMPORARILY MARKED FOR EARLIER EXCAVATION IN THE SAME AREA, IT WAS NOT MARKED THAT DAY. IT WAS RAINING THAT DAY. THE HOEEXCAVATED NEAR AND ABOVE THE SANJAC LINE. HOWEVER, THE SANJAC LINE WAS NOT EXPOSED DURING THIS OPERATION. AN EXAMINATION OF THE SANJAC PIPELINE AFTER THERUPTURE FOUND THE LINE HAD SEVERE MECHANICAL DAMAGE THAT HAD GOUGED AND DENTED THE PIPE. ALTHOUGH, IT CAN NOT BE DETERMINED EXACTLY WHEN THE DAMAGE OCCURRED, IT IS FELT THAT THIS DAMAGE WAS THE RESULT OF THE HOE HITTING THE PIPELINE DURING THE EXCAVATION ON JANUARY 27, 1994. MECHANICAL DAMAGE WAS FOUND IN TWO OTHER AREAS NEAR THE RUPTURE POINT. THE CONTRACTOR HAS TOLD UPRC THAT THEHOE OPERATOR DID NOT EXPOSED, UPRC AND PANOLA DID NOT KNOW THAT ANY DAMAGE HAD OCCURRED. ON THURSDAY THE SANJAC PIPELINE WAS FLOWING LESS VOLUMES THAN NORMAL. THE FLOW WAS AVERAGING 170 BARRELS PER HOUR (BPH). STARTING ON FRIDAY, JANUARY 28, 1994, THE FLOW THROUGH THE PIPELINE BEGAN TO BE INCREASED TO START BRINGING IT BACK UP TO NORMAL FLOW. ABOUT 1:00 AM SATURDAY MORNING, JANUARY29, 1994 THE FLOW WAS RAISED TO 380 BPH. AT 4:25 AM ON THAT MORNING THE PIPELINE RUPTURED. IT IGNITED WITHIN MINUTES OF THE RUPTURE. THE LOCATION OF THE RUPTURE IS REMOTE AND THE SOURCE OF IGNITION SPARKS FROM ROCKS BEING THROWN AROUND. THE PRESSURE LOSS WAS IMMEDIATELY NOTICED BY THE SCADA SYSTEM. WITHIN 10 MINUTES THAT PIPELINE WAS SHUTDOWN. THE MANUAL VALVE AT THE EAST TEXAS PLANT, WHICH IS THE CLOSEST VALVE UPSTREAM OF THE RUPTURE WAS CLOSED AT APPROXIMATELY 4:54 AM. THE MANUAL VALVE ON THE PIPELINE IMMEDIATELY DOWNSTREAM OF THERUPTURE WAS CLOSED APPROXIMATELY 5:30 AM. THE EXPLOSION AND FIRE CAUSED SEVERAL GATHERING PIPELINES WHICH HAD ABOVEGROUND FACILITIES ADJACENT TO THE SANJAC LINE TO FAIL. THE POINTS OF FAILURE WERE THE INSULATING FLANGES WHERE THE INSULATING GASKETS MELTED. THE GAS AND LIQUID FROM THESE PIPELINES WERE ISOLATED AND THE CONTENTS OF THE PIPELINES WERE ALLOWED TO BURN OUT. THE FIRES WERE UNDER CONTROL BY 8:30 AM. DUE TO THE REMOTE LOCATION AND THE EARLY MORNING HOUR OF THE FAILURE, THERE WERE NO INJURIES.
2017-09-29 08:50 | YES | NO | 19940064 | 1994-03-16 | 13131 | CONOCO INC | YES | 1994-02-22 | 729 | MT | PARK |  | NO |  | NO | T1S,R12E,SECTION 9 PARK COUNTY,MONTANA |  | PUMPING STATION | OTHER | BEARING COOLING LINE ON | 1960 | OTHER | FATIQUE DUE TO VIBRATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 28000 | 20999.0483 | 42363.5622 | GASOLINE | 3 | 150 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY BEGGS - DIRECTOR REGULATORY COMPLIANCE | 3036494090 | AT 07:29, 02/22/1994, A BEARING COOLING LINE ON THE #1 PUMP UNIT AT THE SPRINGDALE STATION FAILED. PREMIUM NO-LEAD GASOLINE LEAKED OUT AND COVERED AN AREA INSIDE THE STATION YARD OF ABOUT 40' X 60' AND SPREAD OUT OF THE STATION YARD TO THE SOUTH AND WEST COVERING AN ADDITIONAL AREA OF 20' X 200'. STANDING PRODUCT WAS SOAKED UP WITH ABSORBENT PADS, REMAINDER EVAPORATED OR SOAKED INTOGROUND. SOIL REMEDIATION TO TAKE PLACE ON SITE.
2017-09-29 08:50 | YES | NO | 19940065 | 1994-03-16 | 12628 | MOBIL PIPELINE CO | YES | 1994-02-16 | 2245 | IL | WILL | WILMINGTON | NO |  | NO | 2140 S. WATER, WILMINGTON,IL 60481 |  | TANK FARM | TANK |  | 1948 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 41248.1305 | 83214.14 | CRUDE OIL | 1 | 200 | 195 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | T.P. MURPHY EHS & GA ADVISOR | 2146583869 | DISPATCHER LONNIE REED NOTIFIED BILL REYNOLDS AT 23:00 HRS, FEBRUARY 16, 1994 THAT A SMELL OF CRUDE OIL WAS NOTICED IN THE TOWN OF WILMINGTON. AT 23:10 OIL WAS FOUND FLOWING THRU THE ROOF DRAIN OF TANK 349. THE VALVE WAS CLOSED AND OIL MOVEMENTS WAS NOTIFIED OF THE SITUATION. TELEPHONIC NOTIFICATION MADE AT FIRST INDICATION OF CLEAN UP AND PRODUCT LOSS EXCEEDING $5000. NRC #22137.
2017-09-29 08:50 | YES | NO | 19940066 | 1994-02-08 | 18273 | SHELL PIPELINE CORP | YES | 1994-01-10 | 1420 | MT | FALLON | BAKER | NO |  | NO | BAKER STATION |  | PUMPING STATION | TANK |  | 1955 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 3200 | 2399.8912 | 4841.55 | CRUDE OIL | 1 | 200 | 200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. KORPAL - MANAGER REGULATORY COMPLIANCE | 7132410132 | THE CAUSE OF THE TANK OVERFLOW IS A FAILURE OF TWO INDEPENDENT TANK LEVEL ALARMS. WE CONTRIBUTE THE CAUSE OF THE TANK OVERFLOW TO THE MINUS 50 DEGREES FAHRENHEIT (-50F) WEATHER CONDITIONS DURING THE WEEK.
2017-09-29 08:50 | NO | NO | 19940067 | 1994-03-09 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1994-02-11 | 1000 | CA | RIVERSIDE |  | NO |  | NO | CORONA PUMP STATION 275 NORTH MAPLE STREET CORONA, CALIFORNIA 91720 FCPL - LINE 90 |  | PUMPING STATION | PUMP | INJECTION PUMP SEAL FAIL. | 1981 | OTHER | INJECTION PUMP SEAL FAIL. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 5249.7621 | 10590.8906 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | A PUMP SEAL FAILED ON THE INJECTION PUMP AND SPRAYED OIL ON A 30' X 60' AREAINSIDE CORONA PUMP STATION.
2017-09-29 08:50 | YES | NO | 19940068 | 1994-02-07 | 2330 | CHEVRON PIPELINE CO | YES | 1994-01-29 | 1330 | TX | SCURRY | SNYDER | NO |  | NO | APPROX. 15 MILES SOUTHWEST OF SNYDER |  | PUMPING STATION | PUMP |  | 1962 | OTHER | PACKING GLAND BOLTS BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 749.966 | 1512.9844 | CRUDE OIL | 1 | 260 | 258 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.J. DELANEY - SYSTEM TEAM LEADER | 7133637126 | THE TWO BOLTS HOLDING THE PACKING GLAND ON A POSITIVE DISPLACEMENT PUMP BROKE ALLOWING THE OIL TO ESCAPE FROM THE PACKING. ALL THE OIL WAS CONTAINED IN THE DIKED AREA AROUND THE PUMP. THE GROUND WAS FROZEN WHICH ALLOWED CLEAN UP CREWS TO RECOVER ALL BUT A VERY SMALL AMOUNT OF OIL.
2017-09-29 08:50 | NO | NO | 19940070 | 1994-03-17 | 12105 | MAPCO AMMONIA PIPELINE INC | YES | 1994-02-15 | 707 | NE | LANCASTER |  | NO |  | NO | TOWNSHIP 11 NORTH, RANGE 8 EAST, SECTION 1 OF LANCASTER COUNTY, NEBRASKA |  | NO DATA | OTHER | LOADING HOSE BLOW DOWN | 1968 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 68.9969 | 139.1946 | ANHYDROUS AMMONIA | 2 | 3 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH - MANAGER - OPERATIONS SUPPORT | 9185811800 | AFTER LOADING HIS TRUCK, A TRUCK DRIVER WAS DEPRESSURING THE TRUCK LOADINGHOSE COUPLING THROUGH A 1/2" VALVE TIED TO THE TRUCK'S BLOW DOWN VENT. THEMANUAL DELIVERY VALVE ON THE TERMINAL LOADING HOSE ADJACENT TO THE COUPLINGHAD NOT PROPERLY SEATED. A SMALL VOLUME OF AMMONIA WAS RELEASED THROUGH THETRUCK'S BLOW DOWN VENT BEFORE THE 1/2" BLOWDOWN VALVE COULD BE CLOSED. THEDELIVERY VALVE WAS TAKEN OUT OF SERVICE, REPAIRED AND RETURNED TO SERVICE.PART C - DEVICE/ PART D - PARTIALLY OPEN. SUPPLEMENTAL REPORT 9/13/94CORRECTS PART D FROM "OTHER" TO "MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT."REPORT FILED BY L.D. SMITH (918) 581-1800.
2017-09-29 08:50 | YES | NO | 19940071 | 1994-03-17 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1994-02-20 | 319 | CA | SAN DIEGO | CAMP PENDLETON | NO |  | YES | APPROX. 3/4 MILE SOUTH OF LAS PULGAS ROAD AND APPROX. 150 FEET EAST OF BASOLINE. ( 5.5 MILES DOWNSTREAM OF PENDLETON BOOSTER STATION). |  | LINE PIPE | PIPE |  | 1963 | OTHER | SEE PART K FOR 3/17/94 CH | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 149993.2019 | 302596.8729 | DIESEL FUEL | 3 | 2003 | 100 | NO | NO | 10 | 0.22 | 2120 | WELDED |  | 1440 | 1440 | YES | 24 | 1830 | 0 | 63 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT OPERATIONS & ENGINEERING | 2134867720 | APPROXIMATELY 0317 ON FEBRUARY 20, 1994, THE 10" SAN DIEGO PIPELINE RUPTURED;THE LINE WAS SHUT DOWN, AND DRAINED. THE PIPE WAS REPLACED AND THE LINE WASPUT BACK IN SERVICE AT 0800, FEBRUARY 21, 1994. THE CAUSE OF THE RUPTURE ISUNKNOWN AT THIS TIME, THE PIPE HAS BEEN SENT OUT FOR ANALYSIS. PART D - FORANALYSIS. IT IS NOT KNOWN AT THIS TIME WHAT CAUSED THE RUPTURE. SUPPLEMENTALREPORT 6/2/94: ANALYSIS OF THE 10" PIPELINE RUPTURE ON THE SAN DIEGO SYSTEMDOWNSTREAM OF PENDLETON BOOSTER WAS INCONCLUSIVE. THERE WAS NO EVIDENCE THATTHE FAILURE WAS CAUSED BY A LOCALIZED WALL THICKNESS THINNING IN THE WELDSEAM DUE TO UNDERCUT WHEN THE PIPELINE WAS MANUFACTURED.
2017-09-29 08:50 | NO | NO | 19940072 | 1994-03-18 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-02-16 | 1640 | NM | RIO ARRIBA |  | NO |  | NO | SECTION 14, RANGE 7 WEST, TOWNSHIP 23 NORTH, RIO ARRIBA COUNTY, NEW MEXICO |  | LINE PIPE | OTHER | NOT GIVEN | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2842 | 2131.4034 | 4299.9016 | NATURAL GAS LIQUID | 2 | 2 | 0 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1632 | 500 | YES | 24 | 2273 | 3 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | LARRY D. SMITH - MANAGER OPERATIONS SUPPORT | 9185811800 | THIRD PARTY PERSONNEL NOTIFIED MID-AMERICA PIPELINE COMPANY PERSONNEL OF AFROST SPOT ON THE PIPELINE RIGHT-OF-WAY. MID-AMERICA PIPELINE COMPANYPERSONNEL EXCAVATED THE PIPE AND DISCOVERED A SMALL LEAK. THE CAUSE OF THELEAK WAS ATTRIBUTED TO PRIOR MECHANICAL DAMAGE TO THE PIPE. THE LINE WASSLEEVED AND RE-COATED. MID-AMERICA PIPELINE COMPANY PERSONNEL HAD BEEN ATTHIS SITE THREE DAYS EARLIER AND HAD NOT NOTICED EVIDENCE OF A LEAK.SUPPLEMENTAL REPORT 9/15/94 INDICATES SUPPLEMENT TO PART D - CAUSE OFACCIDENT, WAS CHANGED FROM OTHER - THIRD PARTY DAMAGE TO OUTSIDE FORCE DAMAGE.
2017-09-29 08:50 | NO | NO | 19940073 | 1994-03-29 | 809 | ARCO PIPE LINE CO | YES | 1994-03-04 | 3 | OK | CARTER | ARDMORE | NO |  | NO | SE 1/4 SECTION 17 TOWNSHIP 4 SOUTH RANGE 2 EAST 4 MILES EAST OF I-35 ON STATE HIGHWAY 142. |  | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | DIESEL FUEL | 2 | 1 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 700 | 400 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.E. GRAVES - OPERATIONS ADVISOR | 7139865368
2017-09-29 08:50 | NO | NO | 19940074 | 1994-03-18 | 443 | AMOCO PIPELINE CO | YES | 1994-02-17 | 1830 | IL | ADAMS | QUINCY | NO |  | NO | QUINCY STATION, SEC7,T1S,R8W, ADAMS COUNTY, ILLINOIS. LOCATION OF STATION IS TWO MILES EAST OF MISSISSIPPI RIVER. |  | PUMPING STATION | PIPE |  | 1954 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | CRUDE OIL | 1 | 5 | 4 | NO | NO | 16 | 0.38 | 0 | WELDED |  | 1100 | 100 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES N. DICKERSON - DISTRICT MANAGER | 8154786104 | ON FEBRUARY 20, 1994, A LOCAL LANDOWNER NOTIFIED AMOCO PERSONNEL OF OIL IN HISDITCH. AMOCO PERSONNEL RECEIVED THE CALL AT 0858. AMOCO PERSONNEL RESPONDED TOTHE SUSPECTED LEAK IMMEDIATELY, ARRIVING ON-SCENE AND TALKING WITH THELANDOWNER AND STARTED CLEANUP EFFORTS BY 1000. THE OIL COLLECTED IN A FIELDDRAIN TILE AND RAN OFF AMOCO PROPERTY CAUSING A 300 FT. LONG STAIN IN A DITCH,BUT NO FREE STANDING OIL WAS OBSERVED. NRC WAS NOTIFIED AT 0940, INCIDENT#222508. ILLINOIS EMERGENCY ANY WATER AT THE TIME OF THE INCIDENT. BY FEBRUARY22, 1994, ROADWAY DITCH WAS ALL CLEANED UP EXCEPT FOR CULVERTS WHICH WERETREATED WITH OIL ABSORBENT PADS AND WILL BE POWER FLUSHED OUT BY AMOCO ONCETHE WEATHER WARMS ABOVE FREEZING.
2017-09-29 08:50 | NO | NO | 19940076 | 1994-03-25 | 12127 | MARATHON PIPE LINE CO | YES | 1994-02-24 | 955 | IL | BOND |  | NO |  | NO | 2 MILES EAST OF SORENTO, ILLINOIS SEC. 4;T. 6N;R. 4W |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 13499.3882 | 27233.7186 | DIESEL FUEL | 3 | 1 | 1 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1204 | 225 | YES | 8 | 1508 | 8 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM C. BEAUCHAMP - ENVIRONMENTAL & SAFETY COORD. | 4194213587
2017-09-29 08:50 | NO | NO | 19940077 | 1994-03-15 | 2339 | CHEVRON USA INC - HAWAII | NO | 1994-03-15 | 850 | HI | HONOLULU | HONOLULU | NO |  | NO | THE LEAK WAS LOCATED BY THE CAN FIELD, 200 YARDS FROM MP-7 VALVE BOX |  | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | FUEL OIL | 3 | 7 | 7 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1440 | 900 | YES | 8 | 1800 | 0 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.S. ROBISON - RELIABILITY SUPERINTENDENT | 8086822239 | LEAK OCCURRED DURING A ROUTINE SHIPMENT OF FUEL OIL. EXTERNAL CORROSION CAUSED A PIN HOLE LEAK IN THE PIPELINE AND FUEL OIL SURFACED TO THE GROUND. THE NATIONAL RESPONSE CENTER AND THE DEPARTMENT OF HEALTH WERE NOTIFIED.
2017-09-29 08:50 | YES | NO | 19940078 | 1994-04-05 | 13131 | CONOCO INC | YES | 1994-03-10 | 1323 | MO | PULASKI |  | NO |  | NO | LARRY SMITH FARM, 1.75 MILES WEST ON AA FROM THE INTERSECTION OF HIGHWAY 17 AND AA THEN 0.5 MILES SOUTH ON COUNTY ROAD U250 AND EAST THE SITE. |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 262488.1033 | 529544.5275 | L. P. G. | 2 | 9000 | 0 | YES | NO | 10 | 0.37 | 35000 | WELDED |  | 900 | 480 | YES | 4 | 1183 | 8 | 90 | NO DATA | Null | YES | OTHER | NOT GIVEN | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | VANCE WEBB - DIRECTOR REGULATORY COMPLIANCE | 4057674854 | ON MARCH 10, 1994 AT 13:23 HRS., CONOCO PIPE LINE (CPL) OIL MOVEMENTS GROUP LOCATED IN HOUSTON, TEXAS, RECEIVED A CALL FROM MR. JERRY SMITH REPORTING A POSSIBLE RELEASE. MR. SMITH REPORTED THAT A ROAD GRADER WORKING ON HIS PROPERTY HAD STRUCK CPL'S LINE AND THAT A "WHITE STREAM WAS GOING INTO THE AIR". OILMOVEMENTS IMMEDIATELY SHUT DOWN BOTH WOOD RIVER LINES AND BEGAN THEIR EMERGECY NOTIFICATION PROCEDURES. COMPANY PERSONNEL WERE DISPATCHED TO ISOLATE THE DAMAGED LINE SEGMENT. VALVES WERE CLOSED AT RICHLAND STATION, MILE POST 327, AND AT CROCKER, MILE POST 340. THE PUNCTURE WAS LOCATED A MILE POST 337.8. AFTER ISOLATING THE DAMAGED SEGMENT OF LINE, CPL WORKED CLOSELY WITH THE LOCAL EMERGECY RESPONDERS TO COORDINATE EMERGECY RESPONSE EFFORTS. THE EVACUATION OF 4 HOUSEHOLDS WERE NECESSARY TO MINIMIZE DANGER TO THE OCCUPANTS. DURING THEDAYLIGHT HOURS FOLLOWING THE RELEASE, THE PROPANE CLOUD WAS DISSIPATING RAPIDLY AND, THEREFORE, WAS BEING ALLOWED TO VENT. HOWEVER, AS EVENING APPROACHEDWEATHER CONDITIONS BEGAN TO CHANGE. IT WAS FEARED THAT THE PROPANE WOULD BEGIN POOLING AND POSSIBLY REACH AN ACCIDENTAL IGNITION SOURCE. FOR THIS REASON,IT WAS DECIDED TO INTENTIONALLY IGNITE THE VAPOR CLOUD ADJACENT TO THE DAMAGED PIPELINE. ALL NON-ESSENTIAL PERSONNEL WERE MOVED TO SHELTERING POSITIONS, WHILE CPL PERSONNEL, ALONG WITH THE PULASKI COUNTY SHERIFF MOVED INTO POSITION TO IGNITE THE VAPOR CLOUD. WHEN EVERYONE WAS SATISFIED THAT ALL POSSIBLE SAFETY PRECAUTIONS HAD BEEN TAKEN, FLARES WERE FIRED INTO THE CLOUD BY A CPL EMPLOYEE, IGNITING THE VAPOR CLOUD. STOPPLE EQUIPMENT WAS THEN MOVED IN AND INSTALLED TO REDUCE PRODUCT LOSS AND SHORTEN THE AMOUNT OF TIME REQUIRED TO FLARETHE EXISTING LINE FILL. WHEN LOCAL PERSONNEL WERE SATISFIED THAT THE LINE FILL HAD BEEN FLARED SUFFICIENTLY TO EFFECT REPLACEMENT OF THE DAMAGED SECTION SAFELY, WORK WAS BEGUN. THE DAMAGED SECTION OF LINE WAS REMOVED AND THE REPAIRED LINE WAS LOWERED TO A DEPTH OF 36 INCHES TO PREVENT FUTURE DAMAGED OF THIS TYPE. THE EXCAVATION REQUIRED THE USE OF ROCK BREAKING EQUIPMENT TO REACH THE 36 INCH DEPTH. THE SECOND LINE WAS ALSO LOWERED AS A PRECAUTION. UPON COMPLETION OF THESE REPAIRS, THE STOPPLE EQUIPMENT WAS ALSO REMOVED AND AFFECTED JOINT CUT OUT AND REPLACED. ROAD GRADER WAS BEING OPERATED BY STANLEY CHRISTMAN AN EMPLOYEE OF PULASKI COUNTY. HE WAS GRADING A PRIVATE DRIVEWAY AT THE REQUEST OF THE LANDOWNER, MR. JERRY SMITH WHEN THE INCIDENT OCCURRED.
2017-09-29 08:50 | NO | NO | 19940079 | 1994-04-05 | 2552 | COLONIAL PIPELINE CO | YES | 1994-03-04 | 900 | TN |  | DAVIDSON | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 29998.6404 | 60519.3746 | NOT GIVEN | 3 | 6 | 0 | NO | NO | 10.75 | 0.22 | 46000 | WELDED |  | 1440 | 150 | YES | 24 | 1800 | 0 | 73 | EXTERNAL | Null | NO | OTHER | NOT GIVEN | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR-TECHNICAL & REGULATORY | 4048412402 | ON MARCH 3, 1994, A CONTRACTOR DISCOVERED PRODUCT-CONTAMINATED SOIL WHILE INTHE PROCESS OF INSTALLING A FORCED SEWER MAIN ACROSS COLONIAL'S 10- INCH DELIVERY LINE THAT RUNS FROM EAST NASHVILLE DELIVERY TO LION OIL COMPANY. COLONIAL EXCAVATED THE SOIL SURROUNDING THE PIPELINE AND AT 0900 CST ON MARCH 4, 1994, FOUND A SMALL PINHOLE LEAK IN A CORROSION PIT IN THE LONGITUDINAL SEAM OFTHE PIPE. THIS LEAK WAS LOCATED AT THE 3 O'CLOCK POSITION AND 1-FOOT, 6-INCHES DOWNSTREAM OF AN INSULATOR NEAR THE FENCE OF LION OIL COMPANY. DUE TO CONFUSION OVER OWNERSHIP OF THIS 6 FEET OF PIPE DOWNSTREAM OF THIS INSULATOR, COLONIAL HAD INADVERTENTLY NOT MAINTAINED CATHODIC PROTECTION THIS SEGMENT. IT IS ESTIMATED THAT 6-BARRELS OF A MIXTURE OF VARIED PETROLEUM PRODUCTS SEEPED THROUGH THE SMALL PINHOLE. THIS PRODUCT HAS BEEN ABSORBED INTO THE SURROUNDINGSOIL. SINCE SEVERAL OTHER CORROSION PITS WERE DISCOVERED NEAR THIS LEAK, THEREPAIR INCLUDED THE INSTALLATION OF A SECTION OF APPROXIMATELY 10-FEET OF PREHYDROSTATICALLY TESTED PIPE, 2-90 DEGREE, 3R ELBOWS, AN 8" X 10" REDUCER ANDAN 8-INCH FLANGE. ALL THE TIE-IN WELDS WERE RADIOGRAPHED AND THE LINE WAS BACKFILLED WITH CLEAN SOIL AND RETURNED TO SERVICE. THE CONTAMINATED SOIL HAS BEEN PLACED IN A PLASTIC ENVELOPE AND WILL BE DISPOSED OF AT A LATER DATE.
2017-09-29 08:50 | NO | NO | 19940080 | 1994-04-04 | 15674 | PLANTATION PIPE LINE CO | YES | 1994-03-14 | 1435 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | BLOCK VALVE NO. MDA-12-1 (OUTGOING BLOCK VALVE) LOCATED AT PLANTATION'S TANK FARM IN BATON ROUGE, LOUISIANA. |  | LINE PIPE | VALVE |  | 1941 | OTHER | SEE REMARKS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 13900 | 10424.5275 | 21030.4827 | GASOLINE | 1 | 1 | 1 | NO | NO | 12 | 0.38 | 35000 | FLANGED |  | 1125 | 1120 | YES | 24 | 1437 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. COOK - VICE PRESIDENT- OPERATION | 4043645916 | ON THE AFTERNOON OF MARCH 14, 1994, A CONTRACT EMPLOYEE WORKING FOR PLANTATION DISCOVERED A SMALL AMOUNT OF GASOLINE AROUND PLANTATION'S 12-INCH OUTGOINGMDA BLOCK VALVE. THE BLOCK VALVE WAS EXCAVATED AND THE DOWNSTREAM FLANGE OF THE VALVE WAS FOUND TO BE LEAKING. THE FLANGE BOLTS WERE TIGHTENED TO STOP THE LEAK, THEN THE LINE WAS PRESSURED AND NO LEAK WAS OBSERVED. THE LINE WAS RETURNED TO SERVICE AND THE VALVE WAS VISUALLY MOINTORED. A VALVE BOX WILL BE INSTALLED AROUND THE VALVE TO ALLOW FOR FUTURE VISUAL INSPECTIONS.
2017-09-29 08:50 | NO | NO | 19940081 | 1994-04-01 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-03-14 | 1130 | CA | LOS ANGELES |  | NO |  | NO | LOCATED 200 FEET SOUTH OF NEWHALL PUMP STATION, MCBEAN PARKWAY FCPL - LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7499.6601 | 15129.8436 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 822 | 30 | YES | 4 | 1020 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | ONE CALL |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | WHILE PERFORMING GAS TST OF PIPELINE, CRUDE WAS PUSHED OUT OF UNDISCOVERED SEPARATION IN PIPELINE. PART D - NORTHRIDGE EARTHQUAKE, JANUARY 17, 1994.
2017-09-29 08:50 | NO | NO | 19940082 | 1994-03-29 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1994-02-27 | 1730 | TX | LOVING |  | NO |  | NO | 18 MILES NORTH OF MENTONE, TEXAS |  | NO DATA | BOLTED FITTING | GASKET | 1994 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4499.7961 | 9077.9062 | CARBON DIOXIDE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A FANT - SENIOR SAFETY ADMINISTRATOR | 7138537891 | ELPC CONTROL CENTER WAS NOTIFIED OF A LARGE CO2 VAPOR CLOUD AT THE EL MARMETER STATION AT 1730 HOURS FEBRUARY 27, 1994. ODESSA REGIONAL PERSONNEL WASNOTIFIED IMMEDIATELY AND DISPATCHED TO THE METER STATION. THE BLOCK VALVEUPSTREAM OF THE METER STATION WAS CLOSED AT 1928 HOURS. ( THIS LOCATION ISAPPROXIMATELY 2 HOURS FROM ODESSA.) DEPRESSURING TOOK 3.5 HOURS. THESUBSEQUENT INVESTIGATION REVEALED THAT THE INSULATING GASKET ON THE INLETVALVE FAILED, ALLOWING CO2 TO ESCAPE THE ATMOSPHERE. SUPPLEMENTAL REPORT3/28/94 INDICATES THAT THE ESTIMATED COST OF THE ACCIDENT WAS INADVERTENTLYOMITTED FROM THE ORIGINAL REPORT. ($6,000) IN ADDITION, PART G OF THEORIGINAL REPORT WAS REPORTED IN MILLION CUBIC FEET (MMCF) RELEASED INSTEAD OFBARRELS. THE REASON FOR THIS IS CARBON DIOXIDE IS MEASURED IN STANDARD CUBICFEET. THE CONVERSION TO BARRELS CANNOT BE ACCURATELY CALCULATED WITHOUTKNOWING THE EXACT PRESSURE AND TEMPERATURE OF THE CARBON DIOXIDE AT THE POINTOF RELEASE. WE HAVE CLARIFIED THAT THE MMCF WAS RELEASED (SPILLED), AND THEREWAS NOT RECOVERY.
2017-09-29 08:50 | YES | NO | 19940083 | 1994-03-30 | 808 | ARCO TERMINAL SERVICES CORP | NO | 1994-03-17 | 430 | CA | LOS ANGELES |  | NO |  | NO | BURNETT STREET VALVE BOX, WILLOW AND TERMINAL ISLAND FREEWAY, LONG BEACH ATSC-LINE E-40 |  | LINE PIPE | VALVE | GASKET FAILURE | 1993 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4499.7961 | 9077.9062 | GASOLINE | 2 | 12 | 12 | NO | NO | 12 | 0.38 | 42000 | WELDED |  | 720 | 400 | YES | 4 | 900 | 4 | 89 | NO DATA | Null | YES | NO DATA |  | OTHER | NOT GIVEN | Null | NO DATA |  | Null | Null | EILEEN J. THRASHER - BUSINESS UNIT MANAGER | 3104289300 | OPERATOR PUMPED AGAINST A CLOSED VALVE, GASKET BLEW OUT ON VALVE #11009 AT 400 PSIG.
2017-09-29 08:50 | YES | NO | 19940084 | 1994-03-28 | 2330 | CHEVRON PIPELINE CO | NO | 1994-01-06 | 1130 | CA | CONTRA COSTA | RICHMOND | NO |  | NO | GERTRUDE STREET DITCH & VARIOUS ADJACENTAREAS WERE IMPACTED. CASTRO COVE & WILDCAT CREEK. N.BANK OF THE GERTRUDE ST.DITCH AT A POINT ABOVE BAPL UNDER THE DITCH. |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NOT GIVEN | 2 | 371 | 371 | NO | NO | 10 | 0.22 | 46000 | WELDED |  | 1350 | 0 | YES | 4 | 1687 | 12 | 91 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DOUGLAS | 5106803217 | INITIAL RESPONSE ACTIVITIES.
2017-09-29 08:50 | YES | NO | 19940087 | 1994-03-01 | 2552 | COLONIAL PIPELINE CO | YES | 1994-02-08 | 1406 | LA | EAST FELICIANA | PORT HUDSON | NO |  | NO | COLONIAL PIPELINE COMPANY'S BATON ROUGE JUNCTION 1476 HIGHWAY 61 JACKSON, LA 70748 |  | PUMPING STATION | PUMP |  | 1976 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 374983.0048 | 756492.1822 | FUEL OIL | 3 | 430 | 420 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL - ADMINISTRATOR-TECHNICAL & REGULATORY | 4048412402 | ON FEBRUARY 8, 1994, AT 1406 CST, THE BATON ROUGE NO. 1 STATION CAN PUMP VESSEL RUPTURED DURING A LINE SWITCHING OPERATION AND SPILLED AN ESTIMATED 430 BARRELS OF NO.2 FUEL OIL INTO THE STATION YARD. THE IMMEDIATE RESPONSE ACTIONSOF THE STATION PERSONNEL RESULTED IN THE RECOVERY OF 90 - 95% OF THE PRODUCTWITHIN A FEW HOURS, AND PREVENTED THE SPILLED PRODUCT FROM REACHING THE STATION RETENTION POND OR ESCAPING THE FACILITY YARD. BECAUSE RECENT RAINS HAD SATURATED THE SOIL, RECOVERY OPERATIONS WERE GREATLY FACILITATED AND IT IS ESTIMATED THAT ONLY 10 BARRELS OF THE FUEL OIL SEEPED INTO THE SOIL. THE FOLLOWING AGENCIES WERE NOTIFIED OF THE INCIDENT: THE NATIONAL RESPONSE CENTER (REPORT NO. 220874) AT 1537 CST AND THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY AT 1545 CST. A COURTESY CALL WAS ALSO MADE TO THE SOUTHWEST REGION OF THE OFFICE OF PIPELINE SAFETY. THIS INCIDENT IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED AFTER FINAL DTERMINATIONS ARE KNOWN.
2017-09-29 08:50 | YES | YES | 19940088 | 1994-03-02 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1994-02-09 | 300 | CA | SAN BERNARDINO |  | NO |  | NO | YUCCA MESA ROAD, YUCCA VALLEY SECTION 28, T1N,R6E,M.P. 124 FCPL - LINE 90 |  | LINE PIPE | PIPE |  | 1957 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 60000 | 44997.9606 | 90779.0619 | CRUDE OIL | 1 | 150 | 80 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 628 | 400 | YES | 8 | 785 | 9 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | SAN BERNARDINO COUNTY ROAD GRADER OPERATOR HIT LINE. LINE REPAIRED/REPLACED.REMOVED CONTAMINATED SOIL. FCPL - LINE 90 PART D- LINE WAS STRUCK BY ROADGRADER OPERATOR DURING ROAD MAINTENANCE. SUPPLEMENTAL REPORT 4/19/94DOCUMENTED CHANGE IN CAUSE OF ACCIDENT FROM "OTHER" TO "OUTSIDE FORCEDAMAGE." REPORT SUBMITTED BY DANIEL REYNEVELD (310) 428-9217.
2017-09-29 08:50 | YES | NO | 19940089 | 1994-02-25 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1994-01-25 | 1530 | CA | SOLANO |  | NO |  | NO | PLMP 3.0, BETWEEN SOUTHERN PACIFIC RAILROAD AND WATERFRONT ROAD. LINE SECTION 25, SHT.5 |  | LINE PIPE | PIPE |  | 1967 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 374983.0048 | 756492.1822 | GASOLINE | 3 | 50 | 25 | NO | NO | 14 | 0.22 | 1630 | WELDED |  | 1170 | 820 | YES | 24 | 1430 | 1 | 67 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | J.M. ABBOUD - SENIOR VICE PRESIDENT OPERATIONS & ENG. | 2134867720 | ON JANUARY 25, 1994, SFPP PERSONNEL DETECTED A POSSIBLE LEAK ON THE CONCORD-SACRAMENTO 14" PIPELINE. UPON EXCAVATION, A PINHOLE LEAK WAS CONFIRMED. REPAIRS WERE COMPLETED ON JANUARY 27, 1994, AND THE LINE WAS RETURNED TO SERVICE FOLLOWING A SATISFACTORY PRESSURE TEST. CLEANUP WAS COMPLETED ON FEBRUARY 1, 1994, AND ENVIRONMENTAL REMEDIATION IS UNDER WAY.
2017-09-29 08:50 | NO | NO | 19940090 | 1994-02-18 | 26149 | ALYESKA PIPELINE SERVICE CO | NO | 1994-01-24 | 1030 | AK |  |  | NO |  | YES | PUMP STATION #10 SEC. 23 T17S - 10E FAIRBANKS MERIDIAN. |  | PUMPING STATION | VALVE |  | 1977 | OTHER | SEE REMARKS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN S. DAYTON - SENIOR VICE PRESIDENT | 9072658923 | TWO LABORERS WERE DISPATCHED LINEWIDE TO REMOVE INSULATION FROM THE SAME VALVE AT STATIONS 1 THROUGH 12. NINE STATIONS HAD BEEN SATISFACTORILY COMPLETED.WHILE PUMP STATION 10, THE PERSON COMPLETING THE WORK, COVERED BY A WRITTEN PROCEDURE, INITIATED ACTION OUTSIDE THE SCOPE OF WORK WHICH RESULTED IN AN EQUIPMENT FAILURE AND 50 GALLON CRUDE OIL LEAK. THE PROCEDURE DID NOT ALLOW FOREITHER LOOSENING OR TIGHTENING PIPING WHICH IS USED TO SERVICE ROLLER BEARINGS INSIDE THE VALVE, NOR WAS THE USE OF A PAIR OF CHANNEL LOCK PLIERS AUTHORIZED. FACTORS INVOLVED WHICH CONTRIBUTED TO THE FAILURE ARE: 1). THE PIPE WAS UNDER 185 POUNDS OF LIQUID PRESSURE. 2). CHANNEL LOCK PLIERS ARE CAPABLE OF PRODUCING A CONSIDERABLE AMOUNT OF TORQUE. 3). THE PERSON INVOLVED WAS PERFORMING WORK OUTSIDE THE SCOPE REQUIRED TO FOLLOW. 4). THE PERSON TURNING THE PIPE NIPPLE WAS UNSURE HE WAS LOOSENING OR TIGHTENING THE FITTING. 5). SOME THREADS WERE STRIPPED OUT INDICATING OVER TORQUE FROM TIGHTENING OR NOT ENOUGH BEARING SURFACE TO RETAIN THE PRESSURE. AT THIS TIME A DETERMINATION CANNOT BE MADE BECAUSE ALL PARTS OF THE PIPING SYSTEM HAVE NOT BEEN RECOVERED. THE GENERAL AREA AROUND THE SITE HAS BEEN CLEANED UP. CONTAMINATED SOIL HAS BEEN CLEANED UP. CONTAMINATED SOIL HAS BEEN REMOVED. APPROPRIATE STATE AND FEDERAL AUTHORITIES WERE NOTIFIED. ADDITIONAL INFORMATION IS INCLUDED TO FURTHER DESCRIBETHE EVENTS SURROUNDING THIS INCIDENT. IN ADDITION, THE USDOT HAS REQUESTED ADDITIONAL INFORMATION ON THIS INCIDENT. REFERENCE USDOT LETTER FOR SPECIFIC INFORMATION DATED JANUARY 31, 1994, ATTACHED, AND USDOT LETTER APPROVAL OF THEINITIAL RESPONSE DATE. INFORMATION REQUESTED WILL BE SUPPLIED TO THE USDOT/OPS WESTERN REGION BY MARCH 8, 1994. PART D - TIGHTENING OF LOOSE ZERK FITTINGRESULTED IN LEAK.
2017-09-29 08:50 | YES | NO | 19940091 | 1994-01-31 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1994-01-22 | 1100 | CA | SAN BERNARDINO |  | NO |  | YES | DANBY PUMP STATION 4 MILES SE OF DANBY MILLS, CA OFF ROUTE 66, 2/10 MILES WEST OF APM 197 FCPL - LINE 90 |  | PUMPING STATION | PUMP | PUMP 71-OUTBOARD SEAL FAL | 0 | OTHER | OUTBOARD PUMP SEAL FAILUR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 13499.3882 | 27233.7186 | CRUDE OIL | 1 | 50 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | PUMP 701 OUTBOARD SEAL FAILED CAUSING A SPILL OF APPRXIMATELY 50 BARRELS OF CRUDE OIL. LINE 90 WAS OPERATING AT THE TIME AND WAS SHUT DOWN AT 2:30PM. SPILL WAS CONTAINED WITHIN PUMP STATION AND CONTAMINATED SOIL WAS REMOVED TO A TEMPORARY STORAGE LOCATION UNTIL AN APPROVED SITE FOR RECYCLING IS SELECTED.
2017-09-29 08:50 | YES | NO | 19940092 | 1994-02-14 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-22 | 1230 | CA | LOS ANGELES |  | NO |  | NO | GRASSHOPPER CANYON, (SEC 3, T5N, R17W) FCPL - LINE 63 AT M.P. 42.1 |  | LINE PIPE | PIPE |  | 1950 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 487477.9062 | 983439.8368 | CRUDE OIL | 1 | 1600 | 440 | NO | NO | 14 | 0.25 | 42000 | NO DATA |  | 1029 | 987 | YES | 4 | 1300 | 3 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | SEE REMARKS | Null | ONE CALL |  | NO | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | PIPELINE RUPTURED DUE TO DENT AND GOUGE IN PIPE CAUSED BY AN UNKNOWN EXTERNAL FORCE. PIPE BROKE DURING STATIC TESTING PRIOR TO STARTUP FOLLOWING JANUARY 17, 1994 NORTHRIDGE EARTHQUAKE. PRESSURE DURING STATIC TEST EXCEEDED PRIOR HYDROTEST PRESSURE DUE TO VALVE POSITION MISCOMMUNICATION. PRESSURE AT TIME OF BURST WAS BELOW INTERNAL DESIGN PRESSURE RATING. PART D - MAY HAVE BEEN CAUSED BY ROAD GRADING. PART J- VALVE CLOSED DURING EARTHQUAKE EMERGENCY AND NOT CLEARLY REPORTED.
2017-09-29 08:50 | YES | NO | 19940093 | 1994-03-07 | 31077 | BP EXPLORATION (ALASKA) INC. | YES | 1994-02-16 | 600 | AK |  | NORTH SLOPE | NO |  | NO | BRITISH PETROLEUM EXPLORATION- MILNE POINT UNIT | 222009 | PUMPING STATION | VALVE |  | 1985 | OTHER | VALVE STEM O-RINGS FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 71 | 30 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JEFF D SCARBROUGH | 9076596322 | AT 0600 ON 2-16-94 THE STEM O-RINGS ON A 14" TK BALL VALVE FAILED CAUSING SEEPAGE ON TO THE FLOOR OF THE PIPELINE/PUMPING FACILITY. ABOUT 30 GALLONS OF DEAD CRUDE OIL ESCAPED BEFORE THE LEAK WAS DISCOVERED AT 0745 AND STOPPED AT 0820. NO DAMAGE TO PERSONAL, PROPERTY OR THE ENVIRONMENT OCCURED. THE CRUDE OIL WAS ALL CONTAINED INSIDE THE ABSORBENT AND A CLEANING SOLUTION. ALL ABSORBENT WAS DISPOSED OF PROPERLY. THE VALVE WAS REPLACED, FUNCTION TESTED AND PRESSURE TESTED BEFORE THE PIPELINE WAS PUT BACK IN SERVICE. THIS REPORT WAS DONE IN REFERENCE TO A TELEPHONIC DOT REPORT ON 2-16-99 #222009.
2017-09-29 08:50 | YES | NO | 19940094 | 1994-02-15 | 15490 | PHILLIPS PIPE LINE CO | YES | 1994-01-18 | 1015 | CO | CROWLEY |  | NO |  | NO | ORDWAY PUMP STATION - POWDER RIVER LINE SEC.28,T19S,R56W;11 MILES N.ON HWY.71 FROM ORDWAY,CO;THEN 2 MILES E.ON DIRT RD.(T);1 MILE N. ON DIRT RD.1 MILE E.ON DIRT |  | LINE PIPE | OTHER | STOPPLE FITTING | 1980 | OTHER | LOOSE SEGMENT BOLT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2249.898 | 4538.9531 | NATURAL GAS LIQUID | 2 | 11 | 0 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1380 | 920 | YES | 8 | 1825 | 10 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS - MANAGER OF ENGINEERING & TECHNICAL SVC | 9186616267 | WHILE ATTEMPTING TO REMOVE THE COMPLETION PLUG FROM A STOPPLE FITTING, A SEGMENT THRUST BOLT CAME LOOSE RELEASING NGL. REMOVAL OF THE STOPPLE INDICATOR ROD RESEATED THE COMPLETION PLUG CHECK VALVE AND ALLOWED THE LEAKING BOLT HOLETO BE PLUGGED.
2017-09-29 08:50 | YES | NO | 19940095 | 1994-04-08 | 15851 | PRIDE REFINING INC | YES | 1994-03-26 | 1300 | NM | EDDY | CARLSBAD | NO |  | YES | 9 MILES NORTH OF CARLSBAD, NEW MEXICO, 1/2 MILES EAST OFF COUNTY ROAD #206 |  | LINE PIPE | VALVE |  | 1992 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 889 | 70 | NO | NO | 4 | 0.25 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON - PIPELINE MANAGER | 9156748231 | HUMAN ERROR, VALVE LEFT OPEN TO SUMP. LEAK #23-1808
2017-09-29 08:50 | YES | NO | 19940096 | 1994-04-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-03-11 | 1138 | NM | LEA |  | NO |  | NO | SECTION 19, TOWNSHIP 17 SOUTH, RANGE 33 EAST, LEA COUNTY, NEW MEXICO |  | LINE PIPE | OTHER | NOT GIVEN | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 53500 | 40123.1815 | 80944.6635 | NATURAL GAS LIQUID | 2 | 545 | 0 | NO | NO | 6.63 | 0.16 | 42000 | WELDED |  | 1424 | 640 | YES | 24 | 1863 | 0 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | PIPELINE WARNING SIGNS | NO | NO | ROBERT T. CRONK - SENIOR VICE PRESIDENT | 9185811800 | THE PIPELINE WAS PUNCTURED BY A THIRD PARTY USING A POWER AUGER TO DIG HOLESFOR ANCHORS. A DUAL STOPPLE JOB WAS PERFORMED AND THE DAMAGED SECTION WASREPLACED WITH PRETESTED PIPE. ALL WELDS WERE X-RAYED. SUPPLEMENTAL REPORT9/15/94 INDICATED THAT THE CAUSE OF THE ACCIDENT WAS CHANGED FROM OTHER -THIRD PARTY DAMAGE TO OUTSIDE FORCE DAMAGE. SUPPLEMENTAL REPORT 9/21/94INDICATES PART H #3 SMYS(PSI) SHOULD HAVE BEEN 42000 INSTEAD OF 1978.
2017-09-29 08:50 | YES | NO | 19940097 | 1994-04-13 | 809 | ARCO PIPE LINE CO | YES | 1994-03-15 | 1107 | OK | OSAGE |  | NO |  | Null | HIGHWAY 75 TO RAMONA, OK. FOUR MILES WEST OF RAMONA, OK ON WOLCO ROAD. LEAK SITE IS ON NORTH SIDE OF WOLCO ROAD. |  | LINE PIPE | PIPE |  | 1929 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 74996.601 | 151298.4364 | GASOLINE | 3 | 1514 | 491 | NO | NO | 8 | 0.32 | 24000 | THREADED |  | 700 | 890 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.E. GRAVES - OPERATIONS ADVISOR, PRODUCTS BUSINESS UNIT | 7139865368 | FAILURE OF 3/8" TUBING FITTING ON PRESSURE CONTROLLER AT BOOSTER STATION. PRESSURE CONTROLLER ALLOWED DISCHARGE PRESSURE TO INCREASE ABOVE THE CONTROL SETPOINT.
2017-09-29 08:50 | YES | NO | 19940098 | 1994-04-06 | 4906 | EXXON PIPELINE CO | NO | 1994-03-04 | 1230 | TX | REFUGIO |  | NO |  | NO | APPROXIMATELY ONE MILE SOUTH OF THE TOWN OF REFUGIO, REFUGIO COUNTY, TEXAS, OFF (APPROX 1/4 MI EAST) OF U.S. HIGHWAY 77. |  | LINE PIPE | PIPE |  | 1961 | OTHER | OVERPRESSURED PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5999.7281 | 12103.8749 | NOT GIVEN | 1 | 50 | 45 | NO | NO | 12 | 0.38 | 25000 | WELDED |  | 847 | 0 | YES | 0 | 940 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | YES | GEORGE G. - MANAGER, ENVIRNMENTAL & REGULATORY COMPLIANCE | 7136565521 | MAINLINE VALVE ON THE EPC NEW QUINTANA-REFUGIO NO. 1 12-INCH CRUDE OIL PIPELINE WAS CLOSED AT EPC REFUGIO STATION FOR SCHEDULED WORK AT THE STATION. A FIELD LACT UNIT, FROM WHICH THE BREAKER HAD BEEN REMOVED AND WHICH UNIT HAD BEEN "TAGGED OUT" BY AN EPC EMPLOYEE, WAS INADVERTENTLY STARTED UP BY A THIRD PARTY PRODUCER. LINE PROTECTION AT EPC'S REFUGIO STATION WAS ISOLATED BECAUSE OF THE CLOSED VALVE. THE PIPELINE THEREFORE FAILED FROM OVERPRESSURING AS A RESULT OF PUMPING AGAINST THE CLOSED VALVE.
2017-09-29 08:50 | YES | NO | 19940099 | 1994-04-11 | 12628 | MOBIL PIPELINE CO | YES | 1994-03-13 | 1215 | TX | BOSQUE | MORGAN | NO |  | NO | HWY 174, EULOGY RD.N.E. OF MORGAN TX. |  | LINE PIPE | PIPE |  | 1957 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 230000 | 172492.1822 | 347986.4038 | CRUDE OIL | 1 | 2000 | 1590 | NO | NO | 16 | 0.25 | 46000 | OTHER |  | 930 | 180 | YES | 2 | 1136 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | GUN SHOT | Null | NO DATA |  | Null | Null | T.P. MURPHY | 2146583869 | AN INDIVIDUAL CALLED TO REPORT AN ODOR IN THE TOWN OF MAORGAN, TX. R. W. KOSECHATA RECEIVED THE CALL AND VERIFIED A LEAK AT M.P. .267. L.E. HAWTHORNE WASNOTIFIED AND THE GANG WAS DISPATCHED TO THE LEAK. OIL WAS ENTERING MESQUITE CREEK. BOOMS WERE DEPOLYED TO PREVENT OIL FROM GOING FURTHER DOWN STREAM. THELEAK WAS ISOLATED AND SECURED BY SHUTTING IN VALVES. LEAK AND CLEAN-UP WAS INITIATED AT THAT POINT.
2017-09-29 08:50 | YES | NO | 19940100 | 1994-04-15 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1994-03-14 | 840 | WI | RUSK |  | NO |  | NO | LAKEHEAD MILEPOST 90.5. APPROXIMATELY 1/4 MILE NORTH OF COUNTY RD. J ANED 1/4 MILE EAST OF FAIRVIEW RD. IN RUSK COUNTY, WI. |  | LINE PIPE | LONGITUDINAL WELD |  | 1968 | OTHER | SEE REMARKS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 86000 | 64497.0768 | 130116.6553 | CRUDE OIL | 1 | 5 | 1 | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 611 | 251 | YES | 24 | 764 | 11 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DENISE M. HAMSHER - SECRETARY & DIRECTOR CORPORATE SERVICE | 2187250103 | LAKEHEAD PATROL PILOT OBSERVED SMALL POOLS OF OIL WHILE PERFORMING ROUTINE RIGHT-OF-WAY INSPECTION. PILOT RADIOED LAKEHEAD SUPERIOR CONTROL CENTER AND INITIATED AN IMMEDIATE LIN SHUTDOWN AT 08:45 MST. MAINTENANCE CREWS EXECAVATED THE AREA, AND RECOVERED 1 BARREL OF THE ESTIMATED 5 BARRELS RELEASED. A PLIDCOSLEEVE WAS INSTALLED ON MARCH 14, 1994 AND THE LINE WAS RETURNED TO SERVICE ON MARCH 15, 1994.
2017-09-29 08:50 | NO | NO | 19940101 | 1994-04-11 | 5526 | FOUR CORNERS PIPELINE CO | NO | 1994-03-30 | 830 | CA | LOS ANGELES |  | NO |  | NO | ON SAN FERNANDO ROAD, 500 FT. SOUTH OF BALBOA BLVD. IN FRONT OF METROPOLITAN WATER DISTRICT BUILDING, CITY OF LOS ANGELES FCPL-LINE 1. |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8249.6261 | 16642.828 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 720 | 100 | YES | 4 | 900 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | LOCATED OIL STAIN ALONG RIGHT-OF-WAY , WHILE PERFORMING A LOW PRESSURE TRACER GAS TEST ON LINE.
2017-09-29 08:50 | NO | NO | 19940102 | 1994-04-11 | 5526 | FOUR CORNERS PIPELINE CO | NO | 1994-03-30 | 830 | CA | LOS ANGELES |  | NO |  | NO | ON RAILROAD RIGHT-OF-WAY, EAST OF SAN FERNANDO ROAD 1500 FEET NORTH OF BALBOA BLVD, CITY OF LOS ANGELES FCPL-LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | CRUDE OIL | 1 | 30 | 0 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 720 | 100 | YES | 4 | 900 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | LOCATED RUNNING OIL ALONG RIGHT-OF-WAY, WHILE PERFORMING A LOW PRESSURE TRACER GAS TEST ON LINE.
2017-09-29 08:50 | NO | NO | 19940103 | 1994-04-18 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-03-24 | 900 | CA | LOS ANGELES |  | NO |  | NO | STATION 215 +/-ON PINE STREET, CITY OF SANTA CLARITA FCPL-LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18749.1502 | 37824.6091 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 10 | 0.37 | 350000 | WELDED |  | 822 | 0 | YES | 4 | 1020 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD - VICE PRESIDENT | 3104289217 | LOCATED OIL STAIN ALONG RIGHT-OF-WAY, WHILE PERFORMING A LOW PRESSURE TRACERGAS TEST ON LINE.
2017-09-29 08:50 | YES | NO | 19940104 | 1994-04-20 | 300 | ALL AMERICAN PIPELINE CO | YES | 1994-03-22 | 815 | TX | CULBERSON |  | NO |  | NO | ("IMMEDIATE RESPONSE MAP#7) APPROXIMATELY 3 MILES WEST OF HIGHWAY 2185. |  | PUMPING STATION | OTHER | SEE REMARKS | 1990 | OTHER | SEE REMARKS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 57056 | 42790.0606 | 86324.8359 | CRUDE OIL | 1 | 850 | 685 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JORDAN JANAK | 7137504587 | AT 06:40 (CST ON MARCH 22, 1994 THE DISTRICT SUPERVISOR IN WINK, TEXAS WASINFORMED BY THE DISPATCHER IN THE ALL AMERICAN PIPELINE (AAPL CONTROL CENTERIN BAKERSFIELD, CA OF A PRESSURE TRANSMITTER PROBLEM AT AAPL"S UNMANNED BLACKRIVER STATION. THE SUPERVISOR IMMEDIATELY DISPATCHED A TECHNICIAN TO THESTATION. ON ARRIVAL AT THE STATION SITE AT 08:15 (CST) THE TECHNICIANDISCOVERED A LEAK ON A FITTING IN THE SENSING LINE OF THE STATION DISCHARGEPRESSURE TRANSMITTER. HE IMMEDIATELY NOTIFIED THE CONTROL CENTER AND THEPIPELINE WAS SHUT DOWN. THE TECHNICIAN ISOLATED AND STOPPED THE LEAK BYCLOSING THE INSTRUMENT ROOT VALVE THAT CONNECTS THE SENSING LINE TO THESTATION PIPING. BASED ON THE ANALYSIS OF THE OPERATIONAL DATA, THE RELEASEDOIL VOLUME AND THE CALCULATION OF THE LEAK RATE THROUGH A 3/8" O.D.INSTRUMENT FITTING IT IS ESTIMATED THE THE LEAK INITIALLY BEGAN BETWEEN 15:00TO 19:00 (CST) ON MARCH 21, 1994. THE FAILED FITTING IS COMPRISED OF A SHORTSECTION OF TUBING WHICH ATTACHES BETWEEN A HEXAGONAL PIPE FITTING AND ACOMPRESSION TUBING FITTING. THIS SHORT SECTION OF TUBING IS OCCASIONALLYEXPOSED TO VIBRATIONAL FORCES THAT CAUSED FATIGUE AND ULTIMATE FAILURE AT THEHEXAGONAL PIPE FITTING. THE STATION AREA WHERE THIS FAILURE OCCURRED ISSUSCEPTIBLE TO SMALL VIBRATIONAL STRESSES DURING STATION OPERATIONS. THEREPEATED EXPOSURE OF THIS FITTING TO THESE STRESSES, OVER AN EXTEDED TIMEPERIOD, WERE THE APPARENT CAUSE OF THIS FITTING FAILURE. ALL AMERICAN PIPELINEIS VISUALLY INSPECTING ALL OTHER LOCATIONS WITH RESPECT TO THESE PARTICULARFITTINGS. AAPL PROPOSES TO REPLACE THESE FITTINGS WITH A FITTING MORE SUITABLYDESIGNED FOR SERVICE IN APPLICATIONS WHERE VIBRATIONAL FORCES OF THIS NATUREMAY EXIST. EFFORTS ARE PRESENTLY UNDERWAY TO SELECT, PURCHASE, AND INSTALL THEAPPROPIATE FITTINGS. PART C - TYLOCK TUBING FITTING ON DISCHARGE PRESSURETRANSMITTER. PART D - COMPONENT FAILURE, A SMALL SECTION OF TUBING ON FITTINGCRACKED. SUPPLEMENTAL REPORT 6/24/94 INDICATEDS PART C, #1 IS A PRESSUREREDUCING STATION; PART C, #2 IS OTHER - TYLOCK TUBING FITTING ON DISCHARGEPRESSURE TRANSMITTER, AND PART D IS OTHER - COMPONENT FAILURE, A SMALL SECTIONOF TUBING ON FITTING CRACKED, AS PREVIOUSLY NOTED. ESTIMATED TOTAL PROPERTYDAMAGE ALSO CHANGED FROM $40,000 TO $57,056. REPORT FILED BY JORDAN JANAK(713) 750-4587.
2017-09-29 08:50 | YES | NO | 19940105 | 1994-04-20 | 30658 | KERN OIL & REFINING CO. | NO | 1994-04-01 | 800 | CA | KERN |  | NO |  | NO | NORTHEAST OF EDISON, CA AT THE HUNTER RESOURCES PORTALS NO. 1 LEASE. SECTION 3, T 29S, R 29E. |  | PUMPING STATION | OTHER | PRESSURE GAUGE | 1994 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7499.6601 | 15129.8436 | CRUDE OIL | 1 | 150 | 135 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | THOMAS L. EVELAND - VICE PRESIDENT | 8058450761 | THE PUMP STATION WAS PUMPING AT A DISCHARGE PRESSURE OF APPROXIMATELY 300 PSIG. THE PUMP WAS FOUND AT 8 A.M. APRIL 1 WITH THE PRESSURE GAUGE LYING A FEW FEET AWAY. OIL HAS SPRAYED UPWARD FROM THE GAUGE CONNECTION. MOST OF THE OIL WAS CONTAINED IN A DIKED TANK BASIN, BUT SOME SPRAYED PORTIONS OF THE VINEYARD. ATTEMPTS WERE MADE TO CLEAN THE VINES WITH A CITRUS BASED DEGREASER, BUT SOME DAMAGE IS ANTICIPATED. PART D- BELIEVED THAT AN UNATHORIZED PERSON UNSCREWED THE GAUGE.
2017-09-29 08:50 | YES | NO | 19940106 | 1994-04-28 | 12628 | MOBIL PIPELINE CO | NO | 1994-04-02 | 1630 | TX | LIBERTY | HUFFMAN | NO |  | NO | APPROX. 5 MILES E. OF HUFFMAN, TX. TO SALE BARN-TAKE 1ST RD JUST PAST SALE BARN, TURN S. AND GO APPROX. 1 MILE. JUST AFTER CROSSING RAILROAD TRACKS, THERE WILL |  | LINE PIPE | PIPE |  | 1924 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5880 | 4409.8001 | 8896.3481 | CRUDE OIL | 1 | 50 | 49 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 535 | 103 | YES | 8 | 669 | 10 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | 24 COLLECT CALL | NO | NO | J.E. LUDOVICO | 2146582028 | MR. ROY SEEBURG (RICE FARMER) WAS TERRACING HIS RICE FIELD AND HIT THE PIPE LINE CAUSING A GOUGE. DALLAS OPERATIONS CONTROLLER'S WERE NOTIFIED AND INTURNNOTIFIED FIELD PERSONAL OF THE INCIDENT AT 16:30. AT 20:00 MOBIL EMPLOYEES ARRIVED AT THE LEAK SITE, THE CURDE OIL WAS CONTAINED WITH TERRACES, VACUUM TRUCKS AND THE RESPONSE CREW WERE ON SITE FOR CLEAN_UP. THE GOUGE APPROX 3"X2" HAD A PATCH WELDED ON, THISWAS COMPLETED AT 21:30. ALL FREE OIL WAS PICKED UPAND THE AREA HAD BEEN CLEANED UP BY 22:30. PART B LOCATION- BE A DOUBLE GATE GOING INTO A RICE FIELD. GO THRU THE GATE AND TURN RIGHT. GO ABOUT 1/8 MILE, AND THE LEAK SITE IS TO THE LEFT 500-600 FT.
2017-09-29 08:50 | YES | NO | 19940107 | 1994-04-18 | 4906 | EXXON PIPELINE CO | YES | 1994-03-20 | 920 | LA | ST MARY |  | NO |  | NO | FROM MORGAN CITY, LA GO WEST ON HIGHWAY 90 UNTIL HIGHWAY 317 (CENTERVILLE/SALTPOINT EXIT). GO S. ON HWY 317 APPROX. 10 MILES TO THE EXXON PIPELINE CO. STATION. |  | TANK FARM | TANK |  | 1964 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 16499.2522 | 33285.656 | CRUDE OIL | 1 | 482 | 482 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.G. PERSYN - MANAGER | 7136565521 | CRUDE OIL BREAK OUT TANK OVERFLOWED WHEN IT WAS RECEIVING CRUDE OIL. THE CRUDE OIL WAS CONTAINED ON SITE WITHIN THE TANKS SECONDARY CONTAINMENT (FIREWALL) WHERE IT WAS RECOVERED. THE CAUSE IS CURRENTLY UNDER INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19940108 | 1994-05-02 | 10012 | KANEB PIPELINE CO | YES | 1994-04-01 | 920 | NE | PLATTE |  | NO |  | YES | SW 1/4, SECTION 36, TOWNSHIP 18 NORTH, RANGE 2 WEST |  | LINE PIPE | PIPE |  | 1965 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 56247.4507 | 113473.8273 | GASOLINE | 3 | 1666 | 465 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1054 | 1155 | YES | 8 | 1674 | 4 | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.LEROY ANDERSON - MANAGER OF REGULATORY AFFAIRS | 3162621408 | THE LONGITUDINAL WELD SEAM FAILED WHICH RESULTED IN AN APPROXIMATE 27 INCH LONG RUPTURE. METALLURGICAL TESTS PERFORMED SUBSEQUENT TO THE FAILURE INDICATETHE FAILURE WAS CAUSED BY HOOK CRACKS CONCENTRATED ALONG THE LONGITUDINAL WELD SEAM. THE METALLURGICAL REPORT HAS BEEN SUBMITTED TO THE OFFICE OF PIPELINE SAFETY REGIONAL OFFICE IN KANSAS CITY, MISSOURI.
2017-09-29 08:50 | YES | NO | 19940109 | 1994-04-29 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1994-04-01 | 740 | WI | DOUGLAS | SUPERIOR | NO |  | NO | LAKEHEAD'S SUPERIOR, WISCONSIN TERMINAL LOCATED WITHIN THE CITY OF SUPERIOR, WISCONSIN, 2800 E. 21ST STREET. |  | TANK FARM | WELDING FITTING |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18749.1502 | 37824.6091 | CRUDE OIL | 1 | 140 | 140 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR - DIRECTOR CORPORATE SERVICES | 2187250103 | FOLLOWING PUMP-OUT OF WATER ACCUMULATED IN OPERATOR'S FIELD BOOSTER PUMPHOUSE ON 03/31/94, AN ICE LAYER FORMED ON INSIDE CONCRETE WALLS. ON 04/01/94 ICE APPARENTLY BROKE LOOSE AND STRUCK A 1/2 INCH NIPPLE, BREAKING IT FROM THE BOOSTER PUMP PIPING. OIL FILLED THE BUILDING SUMP, AND APPROXIMATELY 40 BARRELS OVERFLOWED INTO THE NEARBY DITCH/FLUME SYSTEM AND WAS CONFINED TO COMPANY PROPERTY. THE PUMP AND LINE WERE NOT BEING USED AT THE TIME SO NO SHUTDOWN WAS NECESSARY, HOWEVER, BOOSTER PUMP VALVES WERE CLOSED TO ISOLATE THE SECTION. OILIN THE BUILDING SUMP WAS RECOVERED AND OIL IN THE DITCH WAS INTENTIONALLY FLUSED INTO THE FLUME BASIN AND RECOVERED WITH A SKIMMER. THE RELEASE WAS TELEPHONICALLY REPORTED TO THE WI DEPT. OF NATURAL RESOURCES.
2017-09-29 08:50 | YES | NO | 19940110 | 1994-05-23 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-04-18 | 729 | WI | LAFAYETTE |  | NO |  | NO | SECTION 23, RANGE 2 EAST, TOWNSHIP 1 NORTH LAFAYETTE COUNTY, WISCONSIN |  | NO DATA | VALVE |  | 1993 | OTHER | CRACK IN 6 INCH CHECK VAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 4124.8131 | 8321.414 | L. P. G. | 2 | 60 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH - MANAGER | 9185811800 | RECEIVED REPORT FROM A LANDOWNER OF DEAD VEGETATION AND A FROST SPOT ON THE GROUND. THE SITE WAS EXCAVATED AND A CRACK IN THE BODY OF A CHECK VALVE WAS DISCOVERD. THE CHECK VALVE WAS DETERMINED TO BE UNNECESSARY AT THIS LOCATION AND REPAIRS WERE COMPLETED USING LINE PIPE.
2017-09-29 08:50 | NO | NO | 19940111 | 1994-05-17 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1994-04-11 | 800 | MN | ITASCA | PHILBIN | NO |  | NO | LAKEHEAD MILEPOST 1019 APPROXIMATELY 1/9 MILE SOUTH OF U.S. HIGHWAY 2 AND EAST OF RICE LAKE IN BLACKBERRY TOWNSHIP, ITASCA COUNTY, MINNESOTA. |  | NO DATA | OTHER | 2 INCH PIPING ON THERMAL | 1994 | OTHER | MISALIGNED THREADS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | CRUDE OIL | 1 | 4 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR | 2187250103 | LAKEHEAD PERSONNEL INSTALLED 2" THERMAL RELIEF PIPING WITHIN A VERTICAL CULVENT AT AN UPSTREAM 48" LOOP END NEAR PHILBIN, MINNESOTA. FOLLOWING THE INSTALLATION, LAKEHEAD CREWS RETURNED TO INSPECT THE SITE ON APRIL 11, 1994 AND DISCOVERED A 2" UNION LEAKING, DUE TO MISALIGNED THREADING. AN ESTIMATED 4 BARRELS OF OIL WERE RELEASED BOTH WITHIN THE VERTICAL CULVERT AND A LIGHT SPRAY ONTO THE GROUND, OF WHICH 2 BARRELS WERE RECOVERED. THE 2" UNION WAS RETIGHTENED AND INSPECTED AS A PERMANENT REPAIR. UPON INITIAL ASSESSMENT, THE INCIDENT DID NOT APPEAR TO MEET SECTION 195.50, 195.52 REPORTING CRITERIA, HOWEVER, ITWAS REPORTED TO THE MINNESOTA STATE DUTY OFFICER AS A POLLUTION INCIDENT ON APRIL 14, 1994. AFTER FURTHER ASSESSMENT, DUE TO THE SOIL REMEDIATION OPTION CHOSEN, IT WAS DETERMINED THAT $5000 PROPERTY DAMAGE WOULD BE EXCEEDED AND A TELEPHONIC REPORT WAS MADE TO THE NATIONAL RESPONSE CENTER ON APRIL 29, 1994 (REPORT #237211).
2017-09-29 08:50 | NO | NO | 19940112 | 1994-05-17 | 2552 | COLONIAL PIPELINE CO | YES | 1994-04-11 | 1130 | MS | JEFFERSON | GOSS | NO |  | NO | COLONIAL PIPELINE COMPANY'S COLUMBIA STATION. |  | PUMPING STATION | OTHER | STRAINER | 1967 | OTHER | O-RING SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | OIL AND GASOLINE | 3 | 4 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.A. COX | 4048412296 | ON APRIL 11, 1994, A COMPANY EMPLOYEE ARRIVED AT COLONIAL PIPEINE COMPANY'S COLUMBIA PUMP STATION IN JEFFERSON DAVIS COUNTY, MS, AND IMMEDIATELY NOTED GASOLINE LEAKING FROM THE CLOSURE OF THE NO. 01 LINE VERTICAL , 36-INCH STRAINER. AT 1243, CDT, THE NATIONAL RESPONSE CENTER WAS NOTIFIED OF THE INCIDENT (REPORT NO..234295). THE MISSISSIPPI DEPARTMENT OF ENVIRONMENTAL QUALITY AND THE EPA REGION IV OFFICE IN ATLANTA, GA WERE ALSO NOTIFIED OF THE INCIDENT. APPROXIMATELY 4 BARRELS OF GASOLINE ARE ESTIMATED TO HAVE ESCAPED, ALL OF WHICH WAS CONTAINED WITHIN THE FACILITY. CLEAN-UP OF THE PRODUCT RECOVERED BETWEEN 3 AND 4 BARRELS OF PRODUCT. THE SMALL AMOUNT OF CONTAMINATED SOIL EXCAVATED HAS BEEN STOCKPILED AND AWAITS DISPOSAL. THE CAUSE OF THE LEAK WAS DETERMINED TO BE AN O-RING SEAL FAILURE ON THE CLOSURE OF THE STRAINER. A NEW O-RING WASINSTALLED, AND THE STATION WAS RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19940113 | 1994-05-17 | 2552 | COLONIAL PIPELINE CO | YES | 1994-04-20 | 355 | PA | DELAWARE | BETHEL TOWNSHIP | NO |  | NO | COLONIAL PIPELINE COMPANY'S BRANDYWINE PUMP STATION. |  | PUMPING STATION | VALVE |  | 1978 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 74996.601 | 151298.4364 | OIL AND GASOLINE | 3 | 7 | 6 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | ONTRACTORS WERE CALLED TO THE SITE TO BEGIN RECOVERY AND CLEAN-UP OPERATIONS.AT 1007 EDT THE NATIONAL RESPONSE CENTER WAS NOTIFIED OF THE INCIDENT (REPORT NO. 235758). AT 1010 EDT, THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL RESOURCES WAS NOTIFIED OF THE INCIDENT. EXCAVATION OF THE STATION YARD BEGAN ANDLATE IN THE EVENING OF APRIL 21, 1994, THE SOURCE OF THE LEAK WAS FOUND TO BEAT THE BLOW DOWN LINE ON THE BOTTOM OF THE STATION AUXILLARY DISCHARGE VALVE. LEAKAGE ONLY OCCURRED WHEN THE VALVE WAS UNDER PRESSURE AND PRODUCT WAS FLOWING THROUGH THE LINE SEGMENT. BECAUSE ACCESS TO THE BOTTOM OF THE VALVE IS LIMITED, THE ACTUAL CAUSE OF THE LEAK HAS YET TO BE DETERMINED. THE LINE SEGMENT HAS BEEN ISOLATED TO PREVENT FURTHER LEAKAGE UNTIL A PLAN CAN BE FORMULATED TO ALLOW ACCESS TO THE BOTTOM OF THE VALVE. AN ESTIMATED 7 BARRELS OF MIXEDPRODUCTS (GASOLINE, FUEL OIL, AND KEROSINE) ARE ESTIMATED TO HAVE ESCAPED FORM THE PIPELINE. APPROXIMATELY 6 BARRELS OF THE PRODUCT SPILLED HAVE BEEN RECOVERED; THE BALANCE SOAKED INTO THE SURROUNDING SOIL. THE CONTAMINATED SOIL HAS BEEN PLACED IN A PLASTIC ENVELOPE FOR DISPOSAL AT A LATER DATE. AN AMENDED7000-1 ACCIDENT REPORT WILL BE FILED WHEN VALVE CAN BE INSPECTED AND THE ACTUAL CAUSE OF THE LEAK IS DETERMINED. SUPPLEMENTAL REPORT 2/15/95 INDICATESTHAT AN INVESTIGATION REVEALED THAT INTERNAL CORROSION IN THIS SMALL BLOW DOWNLINE WAS THE CAUSE OF THIS LEAK.
2017-09-29 08:50 | NO | NO | 19940114 | 1994-05-17 | 2552 | COLONIAL PIPELINE CO | YES | 1994-04-17 | 749 | VA | CUMBERLAND |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S MITCHELL JUNCTION |  | TANK FARM | TANK |  | 1979 | OTHER | FAILED ROOF DRAIN VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | KEROSENE | 3 | 5 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | ON APRIL 17, 1994, AT 0749 EST, UPON COMPLETION OF A DELIVERY OF KEROSINE INTO TANK 950 AT MITCHELL JUNCTION, A COMPANY EMPLOYEE DISCOVERD A SMALL SPRAY OF KEROSINE ESCAPING FROM THE ROOF DRAIN VALVE. THIS VALVE WAS IN THE CLOSED POSITON DURING THE DELIVERY INTO THE TANK. A BLIND FLANGE WAS INSTALLED AT THE LEAKING VALVE AND THE FLOW OF PRODUCT WAS STOPPED. AN EMERGENCY RESPONSE CREW WAS DISPATCHED TO THE INCIDENT SITE AND BEGAN RECOVERY AND CLEAN-UP OPERATIONS. IT IS ESTIMATED THAT 5 BARRELS OF KEROSINE ESCAPED, ALL OF WHICH WAS CONTAINED WITHIN THE TANK DIKE. THREE BARRELS OF THE PRODUCT WERE RECOVERED; TWO BARRELS WERE ABSORBED INTO THE SOIL. THE CONTAIMINATED SOIL HAS BEEN EXCAVATED AND PLACED IN A PLASTIC ENVELOPE AND AWAITS DISPOSAL. ON MAY 5, 1994, AT 1500 EST, A DETERMINATION WAS MADE THAT REPAIR AND CLEAN-UP COSTS WOULD EXCEED $5000AND THE NATIONAL RESPONSE CENTER (REPORT NO. 238180) WAS NOTIFIED OF THE INCIDENT. IT HAS BEEN DETERMINED THAT SOMETIME BETWEEN FEBRUARY 10, 1994, THE LAST PREVIOUS TANK ACTIVITY AND APRIL 17TH, THE DATE OF THE INCIDENT, FREEZING TEMPERATURES DAMAGED THIS VALVE. REPAIRS HAVE BEEN MADE TO THE TANK DRAIN AND THE TANK HAS BEEN RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19940115 | 1994-04-25 | 12105 | MAPCO AMMONIA PIPELINE INC | YES | 1994-03-24 | 1243 | NE | WASHINGTON |  | NO |  | NO | SECTION 27, TS20N., R10 E. WASHINGTON COUNTY, NEBRASKA |  | NO DATA | VALVE |  | 1993 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1362 | 1021.4537 | 2060.6847 | ANHYDROUS AMMONIA | 2 | 43 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.T. CRONK - SENIOR VICE PRESIDENT | 9185811800 | A ONE-HALF INCH BODY RELEIF VALVE ON A GATE VALVE OPENED PREMATURELY, ALLOWIN WITHIN NORMAL OPERATING LIMITS. THE RELIEF VALVE DID NOT RE-SEAT, HOWEVER, T REPLACED AND IS BEING EXAMINED FOR THE CAUSE OF FAILURE.
2017-09-29 08:50 | YES | NO | 19940116 | 1994-05-16 | 19226 | TEXACO PIPELINE INC | YES | 1994-05-02 | 700 | TX | WICHITA | WICHITA FALLS | NO |  | NO | 2110 HARDING STREET, WICHITA FALLS, TX |  | TANK FARM | OTHER | DENSITOMETER PUMP COUPLIN | 1991 | OTHER | FAILED DENSITOMETER PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1499.932 | 3025.9687 | CRUDE OIL | 1 | 90 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID R. SEATON | 8177120761 | THE COUPLING BETWEEN THE PUMP AND MOTOR ON THE DENSITOMETER FAILED, ALLOWINGOIL TO BE RELEASED ON COMPANY OWNED PROPERTY.
2017-09-29 08:50 | YES | NO | 19940117 | 1994-05-17 | 15490 | PHILLIPS PIPE LINE CO | YES | 1994-04-23 | 2310 | TX | FAYETTE |  | NO |  | NO | BENEDUM-SWEENY LINE, MP 324-4+03 LAGRANGE PUMP STATION, 1 MILE NORTH OF LAGRANGE ON U.S. 77 AND 4.5 MILES EAST ON FM 2145. |  | PUMPING STATION | SCRAPER TRAP |  | 1991 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 74.9966 | 151.2984 | NATURAL GAS LIQUID | 2 | 10 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS | 9186616267 | A 1/8" VALVE ON THE LAUCHING TRAP CLOSURE WAS OPENED IN CONJUNCTION WITH MAINTENANCE WORK AND WAS NOT CLOSED UPON COMPLETION OF THE WORK. NGL ESCAPED FROM THE OPEN VALVE. THE VALVE WAS CLOSED TO STOP THE RELEASE.
2017-09-29 08:50 | YES | NO | 19940118 | 1994-05-17 | 443 | AMOCO PIPELINE CO | YES | 1994-02-27 | 1105 | WY | FREMONT |  | NO |  | NO | SECTION 22, TOWNSHIP 3 NORTH, RANGE 1 WEST |  | PUMPING STATION | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 374.983 | 756.4922 | CRUDE OIL | 1 | 85 | 80 | NO | NO | 8 | 0.31 | 35000 | WELDED |  | 20 | 15 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | COAL TAR/FELT | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. PETERSON | 3038305067 | THE SPILL OCCURRED AT AMOCO PIPELINES PUMPING FACILITY, PILOT BUTTE STATION OF FREMONT COUNTY, WYOMING, SECTION 22/TOWNSHIP 3 NORTH/RANGE 1 WEST. THE SPILL WAS CONTAINED ON AMOCO PROPERTY. AN ESTAMATED 85 BARRELS WAS SPILLED AND 80 BARRELS RECOVERED. THE LEAK WAS CAUSED BY EXTERNAL CORROSIFON ON AN 8" TANKFILL LINE. THE LINE WAS SHUTDOWN/ISOLATED AND REPAIRED WITH 4X6 INCH PATCH THAT WAS WELDED, RE-COATED. THE LINE WAS THEN PUT BACK INTO SERVICE. APL PLANSTO REPAIR/REPLACE THE FILL LINE WITH NEW PIPE/NEW COATING IN THE SPRING OF 1994.
2017-09-29 08:50 | NO | NO | 19940119 | 1994-05-31 | 12105 | MAPCO AMMONIA PIPELINE INC | YES | 1994-04-30 | 1830 | IA | WOODBURY |  | NO |  | NO | SECTION 6 TOWNSHIP 86-N, RANGE 42-W WOODBURY COUNTY, IOWA |  | LINE PIPE | PIPE |  | 1968 | OTHER | PIN HOLE LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5076 | 3806.8275 | 7679.9086 | ANHYDROUS AMMONIA | 2 | 4 | 0 | NO | NO | 6.63 | 0.16 | 46000 | WELDED |  | 1555 | 600 | YES | 24 | 1980 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH | 9185811800 | OXIMATELY (7) FEET IN DIAMETER. AN INVESTIGATION REVEALED A PINHOLE LEAK IN THE PIPE. THE LEAK WAS REPAIRED WITH A FULL ENCIRCLEMENT SPLIT SLEEVE WELDED IN PLACE. THIS SECTION OF PIPE WILL BE CUT OUT AND METALLURGICALLY EXAMINED.
2017-09-29 08:50 | NO | NO | 19940122 | 1994-05-25 | 12127 | MARATHON PIPE LINE CO | YES | 1994-05-04 | 830 | IL | BOND |  | NO |  | NO | 4 MILES SOUTH OF DONALDSON, IL SEC. 12, T6N, R4W INFORMATION SUPPLIED RELATES TO RECEIPT OF NOTICE OF ACCIDENT. |  | LINE PIPE | OTHER | FAILURE OF WELD | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 22269 | 16700.9931 | 33692.6488 | FUEL OIL | 3 | 1 | 0 | NO | NO | 10 | 0.31 | 0 | WELDED |  | 1204 | 0 | YES | 8 | 1508 | 8 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 8:30 A.M. CST ON MAY 4, 1994, MARATHON PIPE LINE COMPANY'S (MPLC) PERSONNEL AT PATOKA STATION WERE NOTIFIED THAT A LAND OWNER HAD DETECTED A POSSIBLE PIPELINE RELEASE IN BOND COUNTY, ILLINOIS. MPLC PERSONNEL WERE DISPATCHED TO THE LOCATION AND AT 09:30 A.M. CST CONFIRMED A RELEASE FROM THE #1-10" PRODUCTS PIPELINE. THE RELEASE WAS LOCATED IN A PASTURE AND AFFECTED AN AREA OF 20 FEET BY 100 FEET. SOME SMALL DARK, OILY PATCHES WERE DISCOVERED IN A NO NAME DITCH WITH WATER. THIS NO NAME DITCH IS A TRIBUTARY TO A SECOND NO NAME DITCHWHICH IS A TRIBUTARY TO SHOAL CREEK. THERE WAS NO EVIDENCE OF ANY PRODUCT REACHING THE SECOND NO NAME DITCH. THE EXACT DATE AND TIME OF THE FAILURE IS NOT KNOWN; THEREFORE THE PRESSURE AT THE LOCATION AT THE TIME OF THE FAILURE ISUNKNOWN. AT THE TIME OF NOTIFICATION THE LINE WAS IN A NORMAL SHUT DOWN MODEDUE TO SCHEDULING CONSTRAINTS WITH AN ESTIMATED PRESSURE OF 204 PSIG AT THE RELEASE LOCATION. PRIOR TO THIS SHUT DOWN THE LINE WAS IN OPERATION AT A PRESSURE OF 990 PSIG AT THIS LOCATION BASED ON SCADA INFORMATION AND ELEVATION CONSIDERATIONS. THE SOURCE OF THE RELEASE WAS A CRACKED WELD ON A PREVIOUS REPAIR, PERFORMED IN 1965, OF AN EXTERNAL CORROSION ANOMALY. ON MAY 6, 1994 HE PREVIOUSLY REPAIRED SECTION WAS CUT OUT AND REPLACED WITH 80 FEET OF NEW 10" 0.279" WALL X42 HYDROSTATICALLY PRE-TESTED PIPE.
2017-09-29 08:50 | NO | NO | 19940123 | 1994-05-25 | 12127 | MARATHON PIPE LINE CO | YES | 1994-05-05 | 1230 | IL | EFFINGHAM |  | NO |  | NO | 1-1/4 MILE WEST OF FUNKHOUSER, IL SEC.4, T7N, R5E |  | LINE PIPE | OTHER | PINHOLE IN WELD | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 10865 | 8148.3807 | 16438.5751 | FUEL OIL | 3 | 0 | 0 | NO | NO | 10 | 0.31 | 0 | WELDED |  | 1189 | 0 | YES | 8 | 1509 | 8 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 12:30 P.M. CST ON MAY 5, 1994, A PRIVATE CITIZEN NOTIFIED MARATHON PIPE LINE COMPANY'S (MPLC) PERSONNEL AT PATOKA STATION OF A POSSIBLE RELEASE IN EFFINGHAM COUNTY, ILLINOIS. MPLC PERSONNEL LOCATED AND AT 01:00 P.M. CST CONFIRMED THE RELEASE TO BE FROM THE #1-10" PRODUCTS PIPELINE. THE RELEASE WAS LOCATED NEXT TO A WOODED AREA AND IMPACTED AN AREA OF 2 FEET BY 4 FEET. NO WAER WAS IMPACTED. THE EXACT DATE AND TIME OF THE FAILURE IS NOT KNOWN; THEREFORE THE PRESSURE AT THE LOCATION AT THE TIME OF THE FAILURE IS UNKNOWN. AT THE TIMEOF NOTIFICATION THE LINE WAS IN A NORMAL SHUT DOWN MODE DUE TO SCHEDULING CONSTRAINTS WITH AN ESTIMATED PRESSURE OF 35 PSIG AT THE RELEASE LOCATION. PRIOR TO THIS SHUT DOWN THE LINE WAS IN OPERATION AT A PRESSURE OF 1000 PSIG AT THIS LOCATION BASED ON SCADA INFORMATION AND ELEVATION CONSIDERATIONS. THE CAUSE OF THE RELEASE WAS ATTRIBUTED TO A PINHOLE LEAK IN A WELD ON A PREVIOUS REPAIR PERORMED IN 1965, OF AN EXTERNAL CORROSION ANOMALY. ON MAY 6, 1994, THE PREVIOUSLY REPAIRED SECTION WAS CUT OUT AND REPLACED WITH 19 FEET OF NEW 10",0.365 WALL X42 HYDROSTIATICALLY PRE-TESTED PIPE.
2017-09-29 08:50 | NO | NO | 19940124 | 1994-05-25 | 12127 | MARATHON PIPE LINE CO | YES | 1994-04-25 | 1933 | IL | EFFINGHAM |  | NO |  | NO | 4 MILES EAST OF ALTAMONT, IL SEC.6, T7N, R5E |  | LINE PIPE | OTHER | FAILURE AT WELD | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 9476 | 7106.6779 | 14337.0398 | FUEL OIL | 3 | 2 | 2 | NO | NO | 10 | 0.31 | 0 | WELDED |  | 1189 | 0 | YES | 8 | 1509 | 8 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 07:33 P.M. CST ON APRIL 25, 1994, A TENANT FARMER NOTIFIED MARATHON PIPE LINE COMPANY'S (MPLC) FINDLAY OPERATIONS CENTER VIA THE TOLL-FREE 800 NUMBER OF A POSSIBLE RELEASE IN EFFINGHAM COUNTY ILLINOIS. OPERATION CENTER PERSONNEL IDENTIFIED THE CORRESPONDING LINE SECTION AND NOTIFIED THE AREA OPERATIONS FOREMAN. MPLC EMPLOYEES LOCATED AND AT 08:00 P.M. CST CONFIRMED THE RELEASE TO BE FROM THE #1-10" PRODUCTS PIPELINE. THE RELEASE WAS LOCATED IN A GRASSY AREA AT THE EDGE OF A PLOWED FIELD AND IMPACTED AN AREA OF 1 FOOT WIDE BY 300 FEET LONG. THE FREE PRODUCT WAS RECOVERED WITH VAC-TRUCKS. NO WATER WAS IMPACTED BY THE PRODUCT. THE EXACT DATE AND TIME OF THE FAILURE IS NOT KNOWN; THEREFORE THE PRESSURE AT THE LOCATION AT THE TIME OF THE FAILURE IS UNKNOWN. THELINE HAD BEEN PLACED INTO A NORMAL SHUT DOWN MODE AT 3:15 P.M. CST ON APRIL 25, 1994, DUE TO SCHEDULING CONSTRAINTS. PRIOR TO THIS SHUT DOWN THE LINE WASIN OPERATION AT A PRESSURE OF 1020 PSIG AT THIS LOCATION BASED ON SCADA INFORMATION AND ELEVATION CONSIDERATIONS. AT THE TIME OF NOTIFICATION THE LINE WAS IN NORMAL SHUT DOWN WITH AN ESTIMATED PRESSURE OF 210 PSIG AT THE RELEASE LOCATION. THE SOURCE OF THE RELEASE WAS A CRACKED LONGITUDINAL WELD ON A REPAIR, PERFORMED IN 1962, OF AN EXTERNAL CORROSION ANOMALY. A CLAMP WAS INSTALLEDTO TEMPORARILY REPAIR THE CRACKED WELD ON 04/25/1994, AND ON 04/27/1994, THECRACKED WELD WAS CUT OUT AND REPLACED WITH 116 INCHES OF 0.365 WALL X42 HYDROSTATICALLY PRE-TESTED PIPE. PART C- FAIURE OF WELD AT PREVIOUS REPAIR MADE IN1962.
2017-09-29 08:50 | NO | NO | 19940125 | 1994-05-25 | 12127 | MARATHON PIPE LINE CO | YES | 1994-04-30 | 1030 | IL | LAWRENCE |  | NO |  | YES | 1 MILE NORTH OF BRIDGEPORT, IL. SEC. 32, T4N, R12W |  | LINE PIPE | PIPE |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6219 | 4664.0386 | 9409.2498 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 550 | 340 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 10:30 A.M. CST ON APRIL 30, 1994, MARATHON PIPE LINE COMPANY'S (MPLC) BRIDGEPORT STATION WAS NOTIFIED BY A MARATHON OIL COMPANY EMPLOYEE OF A POSSIBLEPIPELINE RELEASE NEAR BRIDGEPORT, ILLINOIS. MPLC EMPLOYEES LOCATED AND CONFIRMED THE RELEASE TO BE FROM THE TRI-STATE GATHERING SYSTEM TRUNK LINE AT 10:35 A.M. CST. THE RELEASE WAS LOCATED IN A CLEARED RIGHT-OF-WAY NEAR A SMALL DRAINAGE DITCH. IT WAS ESTIMATED THAT 1 GALLON OF CRUDE OIL WAS RELEASED WHICH IMPACTED AN AREA OF 6 FOOT BY 6 FOOT SQUARE. THE DRAINAGE DITCH CONTAINED SOMESTANDING POCKETS OF WATER FROM RECENT RAIN RUN-OFF WHICH HAD A RAINBOW SHEEN.THE CAUSE OF THE RELEASE WAS DETERMINED TO BE EXTERNAL GALVANIC CORROSION. THIS LINE IS PROTECTED BY CATHODIC PROTECTION BUT IS NOT COATED. ON MAY 6, 1994, 63 FEET OF PIPE WAS REMOVED AND REPLACED WITH 63 FEET OF HYDROSTATICALLY PRE-TESTED 10", 0.365 WALL X42 PIPE AS A PERMANENT REPAIR.
2017-09-29 08:50 | YES | NO | 19940126 | 1994-05-17 | 10313 | KOCH PIPELINE INC | NO | 1994-04-29 | 1100 | OK | PAYNE |  | NO |  | NO | APPROX 8 MILES SE OF STILLWATER OKLAHOMA NW SEC 9 T18N R4E PAYNE COUNTY OKLAHOMA |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2999.864 | 6051.9375 | GASOLINE | 2 | 5 | 1 | NO | NO | 6 | 0.22 | 46000 | WELDED |  | 1440 | 675 | YES | 24 | 1943 | 0 | 72 | EXTERNAL | Null | YES | OTHER | LOCALIZED CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES H. ELMORE | 4053952377 | PRESSURE LOSS DETECTED ON LINE BY SCADA SYSTEM. PERSONNEL SENT OUT TO INVESTIGATE AND DISCOVERED LEAK. EXCAVATED SITE AND FOUND EXTERNAL LOCALIZED CORROSION HAD CAUSED PIN-HOLE LEAK. RAPAIRED LEAK AND RESUMED NORMAL OPERATIONS.
2017-09-29 08:50 | YES | NO | 19940127 | 1994-05-23 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1994-04-22 | 900 | CA | LOS ANGELES | NORWALK | NO |  | YES | APPROX. 25' EAST OF DEFENSE FUEL FIE ROAD GATE. |  | LINE PIPE | VALVE | HAND OPERATED BLOCK VALVE | 1985 | OTHER | BLK VALVE GASKET SWEATLEA | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 187491.5024 | 378246.0911 | NOT GIVEN | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | EVIDENCE OF PRODUCT WAS FOUND IN A NEWLY INSTALLED MONITORING WELL LOCATED NEAR A BLOCK VALVE AT NORWALK. MAINTENANCE CREW DUG OUT THE BLOCK VALVE AT NORWALK AND DISCOVERD THE BONNET GASKET ON THE FLANGE WAS "SWEATING". THEY REPLACED "O" RING AND GASKET IN THE BONNET. AMOUNT OF PRODUCT RELEASED IS UNDETERMINED. SITE WILL BE UNDER ENVIRONMENTAL REMEDIATION.
2017-09-29 08:50 | YES | NO | 19940128 | 1994-05-23 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1994-04-17 | 1400 | MN | CLEARWATER |  | NO |  | NO | LAKEHEAD MILEPOST 920.5 APPROXIMATELY 1/2 MILE WEST OF COUNTY ROAD 3 AND 1/2 MILE NORTH OF COUNTY ROAD 86 IN CLEARWATER COUNTY, MN. |  | LINE PIPE | LONGITUDINAL WELD |  | 1967 | OTHER | 1 INCH DEFECT ON L. WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 187491.5024 | 378246.0911 | CRUDE OIL | 1 | 30 | 22 | NO | NO | 34 | 0.31 | 52000 | WELDED |  | 687 | 40 | YES | 8 | 863 | 10 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PAUL W. NORGREN | 2187250150 | ON APRIL 17, 1994, 13:55 MST, LAKEHEAD CONTROL CENTER PERSONNEL RECEIVED A CALL FROM A LANDOWNER REPORTING OIL ON THE GROUND IN A GRASSY PASTURE NEAR LEONARD MINNESOTA. LAKEHEAD'S LINE 2 AND 3 WERE IDLE AT THE TIME, DUE TO AN UPSTREAM DELIVERY. LINE 1 ALSO IN THE SAME RIGHT-OF -WAY, WAS SHUTDOWN AT 14:00 MST. COMPANY PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE AREA AND WERE ON-SITE AT 14:35 MST. THE LEAK WAS CONFIRMED ON LAKEHEAD'S LINE 3 WITH APPROXIMATELY 30 BARRELS RELEASED, OF WHICH 22 BARRELS WERE RECOVERED. EXCAVATION REVEALED A 1 INCH LONG DEFECT IN THE LONGITUDINAL SEAM. THE LEAK WAS REPAIRED WITH APLIDCO SLEEVE AND THE LINE RETURNED TO SERVICE ON APRIL 18, 02:25 (MST). LAKEHEAD PLANS TO CUT-OUT AND REPLACE THE JOINT AND ACCORDINGLY, THE TOTAL PROPERTY DAMAGE FIGURE REFLECTS THIS DECISION. THE NATIONAL RESPONSE CENTER AND THE MINNESOTA STATE DUTY OFFICER WERE NOTIFIED OF THE INCIDENT ON APRIL 17, 1994. ADDITIONALLY, INCIDENT INFORMATION UPDATES WERE PROVIDED TO MR. ROLAND MILLER, OFFICE OF PIPELINE SAFTEY - CENTRAL REGION ON APRIL 18 AND 19, 1994. PART D - 1 INCH DEFECT IN LONGITUDINAL WELD.
2017-09-29 08:50 | NO | NO | 19940129 | 1994-05-23 | 809 | ARCO PIPE LINE CO | YES | 1994-05-09 | 2024 | TX | HARRIS |  | NO |  | NO | 11316-1/2 GLORIA ST., HOUSTON, TX 77013 |  | PUMPING STATION | OTHER | CORROSION COUPON HOLDER | 1993 | OTHER | O-RING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | GASOLINE | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.E. GRAVES | 7139865368 | A CLOSURE CAP O-RING ON A CORROSION COUPON HOLDER FAILED.
2017-09-29 08:50 | NO | NO | 19940130 | 1994-04-18 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1994-03-16 | 800 | MI | ST CLAIR | MARYSVILLE | NO |  | NO | LAKEHEAD MILEPOST 1730.9 APPROX. 1/8 MILE N. OF SMITH'S CREEK RD. AND 3/8 MILE E. OF WADHAMS RD IN ST. CLAIR COUNTY, MICHIGAN. |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 21000 | 15749.2862 | 31772.6717 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 30 | 0.28 | 52000 | WELDED |  | 633 | 181 | YES | 4 | 824 | 10 | 66 | NO DATA | Null | Null | NO DATA |  | OTHER | SEE REMARKS | Null | NO DATA |  | Null | Null | JON E. STAUDOHAR - SECRETARY & DIRECTOR CORPORATE SERVICE | 2187250103 | LAKEHEAD PATROL PILOT OBSERVED SMALL PUDDLE OF OIL WHILE PERFORMING ROUTINE RIGHT-OF-WAY INSPECTION. PILOT RADIOED LAKEHEAD SUPERIOR CONTROL CENTER AND INITIATED AN IMMEDIATE LINE SHUTDOWN 08:02 MST. MAINTENANCE CREWS WERE IMMEDIATELY DISPATCHED TO THE AREA. THE MINIMAL FREE OIL WAS RECOVERED AND THE LINE WAS EXCAVATED, UNCOVERING A 14" LONG X 2-1/8" DEEP DENT AT THE 12: POSITION ON THE PIPE. THE DENT APPEARED TO BE ATTRIBUTABLE TO ORIGINAL CONSTRUCTION. A 3" HAIRLINE CRACK AT THE OUTER EDGE HAD DEVELOPED WITHIN THE DENT. THE LEAK WAS REPAIRED WITH A PLIDCO SLEEVE AND THE LINE WAS RETURNED TO SERVICE THE EVENING OF MARCH 16, 1994. BOTH THE NATIONAL RESPONSE CENTER (REPORT #230430) AND MICHIGAN DEPARTMENT OF NATURAL RESOURCES WERE TELEPHONICALLY NOTIFIED OF THEINCIDENT ON MARCH 16, 1994. PART J - HAIRLINE CRACK DEVELOPED IN A 14" LONG BY 2-1/8" DEEP DENT THAT APPEARED ATTRIBUTABLE TO ORIGINAL CONSTRUCTION.
2017-09-29 08:50 | YES | NO | 19940131 | 1994-06-14 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1994-05-12 | 922 | CA | SOLANO | FAIRFIELD | NO |  | NO | 3/10 MILE WEST OF PEABODY ROAD, 30 FEET NORTHWEST OF SOUTHERN PACIFIC RAILROAD |  | LINE PIPE | PIPE |  | 1967 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 306000 | 229489.5989 | 462973.2155 | NOT GIVEN | 3 | 4 | 4 | NO | NO | 14 | 0.22 | 1630 | WELDED |  | 1170 | 0 | YES | 24 | 1464 | 12 | 67 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | ON MAY 12, 1994, RECEIVED CALL ADVISING US OF A POTENTIAL LEAK ON RAILROAD RIGHT OF WAY APPROXIMATELY 1/3 MILE WEST OF PEABODY ROAD IN FAIRFIELD, CALIFORNIA. SFPP PERSONNEL AND CONTRACTOR WERE MOBILIZED TO SITE TO UNCOVER AND EVALUATE THE PIPELINE. AFTER IDENTIFYING THE SURFACE STAIN, PIPELINE WAS EXPOSED FOR EVALUATION AND LEAK WAS DETECTED IN THE WELDED SEAM OF THE PIPELINE. THE SECTION WAS REMOVED AND REPLACED WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 19940132 | 1994-06-07 | 18718 | SUN PIPELINE CO | YES | 1994-05-08 | 2140 | PA | INDIANA |  | NO |  | NO | APPROX 2.5 MI N OF THE TOWN OF ROBINSON, INDIANA COUNTY, PA. FROM THE INTERSECTION OF RTES 22 & 259, PROCEED S ON RTE 259 FOR APPROX 1 MI; INCIDENT WAS APPROX |  | LINE PIPE | PIPE |  | 1935 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 487477.9062 | 983439.8368 | GASOLINE | 1 | 537 | 112 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1200 | 355 | NO | 0 | 0 | 7 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KEVIN D. FULMER | 2159773350 | CONTROL ROOM RECEIVED A CALL AT 2140 HOURS ON 05/08/94 FROM THE INDIANA COUNTY HAZMAT TEAM OF A GASOLINE LEAK IN WEST WHEATFIELD TOWNSHIP, INDIANA COUNTY, PA. WITHIN FOUR HOURS OF THIS NOTIFICATION, SPL, CONTRACTORS & LOCAL RESPONDERS HAD CONTAINED THE LEAK. THE US ENVIRONMENTAL PROTECTION AGENCY AND THE PENNSYLVANIA DER, WHO HAD OVERSIGHT RESPONSIBILITY FOR THE CLEANUP OF THIS INCIDENT, LAUDED OUR EMERGENCY RESPONSE AND SUBSEQUENT REMEDIATION EFFORTS. THE PIPELINE WAS NOT OPERATING AT THE TIME OF THE LEAK, BUT WAS "LAID-DOWN" UNDERPRESSURE (372 PSI AT DELMONT TERMINAL) WITH PREMIUM GASOLINE. LINE WAS INACTIVE DUE TO A PLANNED "SHUT-DOWN" PART B- APPROXIMATELY 2.5 MILES NORTH OF THETOWN OF ROBINSON, INDIANA COUNTY, PA. FROM THE INTERSECTION OF ROUTES 22 AND259, PROCEED SOUTH ON ROUTE 259 FOR APPROXIMATELY ONE MILE; INCIDENT WAS APPROXIMATELY 3000 FEET WEST OF THIS LOCATION. PART D- TO BE DETERMINED FROM LABANALYSIS OF PIPE; INFORMATION TO BE SUBMITTED IN A SUPPLEMENTAL REPORT.
2017-09-29 08:50 | NO | NO | 19940134 | 1994-06-07 | 12127 | MARATHON PIPE LINE CO | YES | 1994-03-26 | 730 | IL | CLAY |  | NO |  | NO | MARATHON PIPE LINE COMPANY'S BIBLE GROVE STATION LOCATED IN THE NE 1/4 OF THE NW 1/4 OF SEC.4, TOWNSHIP 5N, RANGE 7E, CLAY COUNTY, IL |  | PUMPING STATION | PUMP |  | 1960 | OTHER | PACKING GLAND FAILURE ON | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6063 | 4547.0439 | 9173.2242 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSPEH A. FISHER | 4194213201 | AT APPROXIMATELY 0730 CENTRAL STANDARD TIME ON MARCH 26,1994, THE PACKING GLAND FAILED ON AN INJECTION PUMP ON A 4" CRUDE LINE CONNECTED TO MARATHON PIPELINE COMPANY'S (MPLC'S) #2-20" CRUDE LINE. APPROXIMATELY 3 BBL. OF CRUDE OILWAS RELEASED FROM THE PACKING GLAND, SPREAD OVER AN AREA OF APPROXIMATELY 1250 SQUARE FEET OF GRAVEL AND DRY DITCH IN THE VICINITY OF THE PUMP. WHEN THE RELEASE WAS DISCOVERED, THE PUMP WAS IMMEDIATELY SHUT DOWN; IT WAS THEN ISOLATED FROM THE SYSTEM, REPAIRED, AND RETURNED TO SERVICE. MOST OF THE FREE CRUDE OIL WAS RECOVERED BY VACUUM TRUCK AND RETURNED TO THE PIPE LINE SYSTEM. THEREMAINDER WAS RECOVERED BY SORBENT BOOMS AND PADS, AND SURFACE SCRAPING OF THE AFFECTED AREA. THE ILLINOIS EMERGENCY MANAGEMENT AGENCY WAS NOTIFIED OF THE RELEASE ON THE DAY OF OCCURRENCE. THE NATIONAL RESPONSE CENTER WAS NOTIFIEDON MAY 19, 1994 WHEN IT WAS DETERMINED THAT THE CLEANUP CONTRACTORS' INVOICES HAD EXCEEDED $5,000.00. PART D- PACKING LAND FAILURE ON PUMP.
2017-09-29 08:50 | NO | NO | 19940135 | 1994-06-14 | 15786 | PORTLAND PIPELINE CORP | YES | 1994-05-24 | 1235 | VT | ESSEX | VICTORY | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1965 | OTHER | CRACK ON DENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 24 | 0.28 | 52000 | WELDED |  | 747 | 700 | YES | 24 | 934 | 0 | 65 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. WINK | 2077670449 | APPROXIMATELY ONE BARREL OF OIL LEAKED FROM THE 24-INCH PIPELINE BECAUSE OF A SMALL CRACK CAUSED BY THE PIPELINE RESTING ON A LARGE BOULDER. THE CRACK OCCURRED IN AN AREA WHERE SUBSTANDARD BACKFILL EXISTED. THE MOVEMENT OF THE BOULDER, DUE TO THE FROST HEAVES, MOVED THE BOULDER TO A POINT WHERE THE PIPELINE WAS DENTED BY THE BOULDER. THE LEAK WAS STOPPED BY TEMPORARILY INSTALLING AMECHANICAL CLAMP AROUND THE PIPELINE. WORK CREWS ARE CURRENTLY REMOVING UNSATISFACTORY MATERIAL FROM THE IMMEDIATE AREA AND REPLACING WITH COMPACTED SANDFILLS. PERMANENT REPAIR OF THE DEFECT IS BEING PLANNED FOR THE SUMMER, 1994.REPAIR WILL BE A MAIN LINE CUT-OUT OF THE DEFECT. PART D - CRACK IN A DENT CAUSED BY PIPELINE RESTING ON A LARGE BOULDER.
2017-09-29 08:50 | YES | NO | 19940137 | 1994-06-13 | 22610 | WILLIAMS PIPELINE CO | YES | 1994-05-18 | 300 | KS | WYANDOTTE | KANSAS CITY | NO |  | NO | LOCATED AT 45TH STREET APPROXIMATELY 400'NORTH OF GEORGIA AVE. IN THE NE QUARTER OF SEC 36, TOWNSHIP 10S, RANGE 24E IN WYANDOTTE COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 74996.601 | 151298.4364 | GASOLINE | 3 | 33 | 26 | NO | NO | 8 | 0.2 | 35000 | WELDED |  | 1150 | 260 | YES | 8 | 1532 | 0 | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883850 | ON MAY 17, 1994 AT APPROX. 0847 HOURS, VICKI BEACH, WILLIAMS PIPE LINE (WPL)REGIONAL ADMINISTRATIVE COORDINATOR, RECEIVED A CALL FROM THE KANSAS CITY WATER AND SEWER DEPARTMENT ABOUT THE APPARENT PRESENCE OF GASOLINE IN THEIR SEWER SYSTEM. AT 0850 HURSK WPL'S AREA MAINTENANCE SUPERVISOR WAS DISPATCHED TO THE SITE AND CONFIRMED THE PRESENCE OF GASOLINE AT 0901 HOURS. WPL"S OPERATIONS CONTROL WAS IMMEDIATELY NOTIFIED OF THE SITUATION AND ALL ACTIVE LINES IN THE CORRIDOR WERE SHUT DOWN. AT APPROX. 0930 HOURS, WPL EMERGENCY RESPONDERS HAD A BACKHOE AND EMERGENCY RESPONSE EQUIPMENT IN PLACE, AND BY 1130 HOURS THE MAINLINE VALVES WERE CLOSED TO ISOLATE THE LEAK SITE. AT APPROX. 0300 HOURS, MAY 18, 1994, A PINHOLE SIZE LEAK, CAUSED BY EXTERNAL CORROSION, WAS DISCOVERED. THE WPL AREA MAINTENANCE CREW PLACED A TEMPORARY PATCH ON THE PIPELINE AT APPROX. 0400 HOURS AND BY 1500 HOURS THE WPL CREW HAD INSTALLED TWO (2) PATCHES AND FULL SLEEVE ON THE PIPELINE TO PERMANENTLY REPAIR THE CORRODED AREA. AN ANALYSIS OF THE LEAK OCCURENCE INDICATED THAT APPROX. 33 BARRELS OF GASOLINE HAD LEAKED FROM THE PIPELINE OF WHICH 26 BARRELS WERE RECOVERED THROUGH CONTAMINATED SOIL EXCAVATION. THE CLEANUP EFFORT WAS COORDINATED WITH THE KANSAS CITY FIRE DEPARTMENT, KANSAS OFFICE OF EMERGENCY MANAGEMENT, FEDERAL DOT,THE KANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT AND THE EPA.
2017-09-29 08:50 | NO | NO | 19940138 | 1994-06-22 | 12127 | MARATHON PIPE LINE CO | YES | 1994-05-23 | 1145 | IL | EFFINGHAM |  | NO |  | NO | 1 MILE WEST OF MONTROSE, IL SEC 10, T8N,R7E |  | LINE PIPE | OTHER | WELD FAILURE | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 19593 | 14694.084 | 29643.9027 | TRANSMIX (PART. REFINED PETRO) | 3 | 1 | 0 | NO | NO | 10 | 0.31 | 0 | WELDED |  | 1189 | 0 | YES | 8 | 1509 | 8 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | PART D- FAILURE IN A WELD OF PREVIOUS REPAIR MADE IN 1962. PART K- AT APPROXIMATELY 11:45 A.M. CST MARATHON PIPE LINE COMPANY (MPLC) PERSONNEL AT THE PATOKA STATION WEE NOTIFIED BY THE AERIAL PATROL OF A POSSIBLE RELEASE IN THE AREA OF ROW 710. THE PILOT NOTICED A "WET SPOT" IN A CULTIVATED FIELD. LOCAL MPLC PERSONNEL WERE DISPATCHED AND ARRIVED IN THE AREA OF THE SUSPECTED RELEASEAT 12:45 P.M. CST.AT 01:15 P.M. CST A RELEASE FROM THE #1-10" PRODUCTS PIPELINE WAS CONFIRMED IN A CULTIVATED FIELD COVERING AN AREA OF APPROXIMATELY 10 FEET BY 2 FEET. NO FREE PRODUCT WAS PRESENT AND NO WATER WAS IMPACTED BY THE RELESE. THE EXACT TIME OF THE FAILURE IS NOT KNOWN THEREFORE THE PRESSURE AT THE LOCATION AT THE TIME OF THE FAILURE IS UNABLE TO BE DETERMINED. THE LINE WAS PLACED INTO A NORMAL SHUT DOWN MODE AT 08:22 A.M. CST DUE TO SCHEDULING CONSTRAINTS. PRIOR TO THE SHUT DOWN THE LINE WAS IN NORMAL OPERATION AT A PRESSURE 503 PSIG AT THIS LOCATION BASED ON SCADA INFORMATION AND ELEVATION CONSIDERATIONS. AT THE TIME OF DISCOVERY THE PRESSURE AT THE LOCATION OF THE RELEASE WAS ESTIMATED AT 236 PSIG. THE SOURCE OF THE RELEASE WAS A FAILURE IN A WELD TO A PREVIOUS INSTALLED HALF SOLE REPAIR MADE IN 1962. A CLAMP WAS INSTALLED TO TEMPORARILY SEAL THE FAILURE ON MAY 23, 1994 TO ALLOW MOVEMENT OF FUEL OIL INTO THE REPAIR AREA. ON MAY 26, 1994, 117 FEET OF PIPE WAS CUT OUT AND REPLACED WITH TESTED 10" 0.365 WALL X42 PIPE AS A PERMANENT REPAIR.
2017-09-29 08:50 | YES | NO | 19940139 | 1994-06-21 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1994-05-22 | 600 | OK | OKLAHOMA |  | NO |  | NO | KOCH GATHERING - OKLAHOMA CITY STATION; NE 10TH ST AND SOONER ROAD OKLAHOMA CITY, OK |  | TANK FARM | TANK |  | 0 | OTHER | MISCALCULATED VOLUMES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4200 | 3149.8572 | 6354.5343 | CRUDE OIL | 1 | 900 | 899 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CODY PRESGROVE | 4058784125 | INTERFACE BETWEEN OIL AND WATER WAS NOT CAUGHT IN TIME WHILE DEWATERING A HYDROSTATIC TEST. THE OIL WAS CONTAINED IN THE TANK DIKE. APPROXIMATELY 900 BARRELS WAS RELEASED WITH APPROXIMATELY 899 BARRELS RECOVERED. NATIONAL RESPONSECONFIRMAION NUMBER 240470. PART D - DURING DEWATERING PROCESS, VOLUMES WERE MISCALCULATED.
2017-09-29 08:50 | YES | NO | 19940141 | 1994-06-17 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-05-17 | 820 | UT | SAN JUAN |  | NO |  | NO | SW QUARTER OF SECTION 22, TOWNSHIP 30 S., RANGE E. SAN JUAN COUNTY, UTAH, SLB & M SURVEY |  | PUMPING STATION | OTHER | RELIEF VALVE | 1993 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1487 | 1115.1995 | 2249.8077 | NATURAL GAS LIQUID | 3 | 86 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH | 9185811800 | CONTROL EQUIPMENT FAILURE RESULTED IN THE CLOSURE OF THE METER RUN CONTROL VALVE. THE RESULTING PRESSURE SURGE ACTIVATED THE METER SKID THERMAL RELIEF VALVE WHICH SUBSEQUENTLY FAILED TO RESEAT. THE CONTROL EQUIPMENT AND RELIEF VAVE WERE REPLACED.
2017-09-29 08:50 | YES | NO | 19940142 | 1994-06-16 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO., LP | YES | 1994-05-28 | 1212 | TX | PANOLA | CARTHAGE | NO |  | NO | SOUTH SIDE OF U.S. HIGHWAY 79, 3.4 MILES EAST OF INTERSECTION WITH CARTHAGE LOOP 455 |  | PUMPING STATION | OTHER | TEMPORARY BLIND FLANGE | 1994 | OTHER | NOT GIVEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 5249.7621 | 10590.8906 | DIESEL FUEL | 3 | 252 | 250 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM L. THACKER | 7137593500 | IMPROPER ALIGNMENT OF THE UPPER AND LOWER SECTIONS OF A PUMP CASE RESULTED IN THE RELEASE OF HIGH SULPHUR DIESEL FUEL. UPON DISCOVERY, TEPPCO'S PIPELINE CONTROL PERSONNEL TOOK IMMEDIATE STEPS TO RELIEVE THE PRESSURE FROM THE PUMP.APPROXIMATELY 252 BARRELS OF PRODUCT MIGRATED TO THE TERMINAL SKIMMER/CONTAINMENT POND. 250 BBLS WERE RECOVERED. APPROXIMATELY 2 BBLS WERE LOST TO ABSORPTION. THIS AREA IS CURRENTLY BEING REMEDIATED IN-SITE.
2017-09-29 08:50 | YES | NO | 19940143 | 1994-05-10 | 12470 | MID - VALLEY PIPELINE CO | YES | 1994-04-12 | 1732 | LA | UNION |  | NO |  | NO | 2 1/2 MILES W. OF SPEARSVILLE, 3/4 MILES E. OF LILLIE AND 3/4 MILES N. OF STATE ROUTE 15. LOCATION IS IN THE SW 1/4,NW 1/4,SE 1/4 OF SECTION 35,T 23N. |  | LINE PIPE | GIRTH |  | 1949 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 56247.4507 | 113473.8273 | CRUDE OIL | 1 | 35 | 32 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 840 | 514 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.W. TORBET | 9037570207 | AT 1732 CST ON 04/12/1994, MID-VALLEY PIPELINE CO. CONTROL ROOM SUPERVISOR, MR. BRADLEY MCCORD, RECEIVED A TELEPHONE CALL FROM A MRS. VERNA SINGLETON REPORTING A "BAD SMELL OF OIL IN THE AREA." MR. MCCORD NOTIFIED M.R. DEAHL, AREASUPERINTENDENT, AT 1735 CST. THE LINE SECTION WAS SHUT DOWN AT 1739 CST AND A CREW WAS DISPATCHED TO THE AREA TO INVESTIGAT. AT 1925 CST, OIL WAS DISCOVERED ON THE RIGHT OF WAY NEAR MP 134, AND CONTAINMENT WAS IMMEDIATELY STARTED.AFTER EXCAVATION WAS COMPLETED AT THE SITE, A 1/8" CRACK WAS DISCOVERED IN THE GIRTH WELD, 3/4" FROM THE PIPE SEAM. THE CRACK WAS AT THE 8:00 POSITION ONTHE PIPE LOOKING DOWNSTREAM. APPROXIMATELY 35BBLS. OF OIL WERE RELEASED DURING THE LEAK. THE OIL WAS SPREAD OVER AN AREA OF APPROXIMATELY 1 MILE WITH THEMAJORITY BEING CONTAINED IN AND AROUND STEEP BANK CREEK. A TOTAL OF 32 BBLS. WERE RECOVERED. IT SHOULD BE NOTED THAT THE GROUND AT THE AROUND THE LEAK SITE WAS FOUND IN AN UNDISTURBED CONTISION.
2017-09-29 08:50 | YES | NO | 19940144 | 1994-05-03 | 2552 | COLONIAL PIPELINE CO | YES | 1994-03-30 | 1553 | SC |  | SPARTANBURG | NO |  | NO | 40" ( LN.1) & 36" (LN.2) COLONIAL PIPELINES. LEAK SITE LINE 32 STATION 3601+32 |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 187491.5024 | 378246.0911 | FUEL OIL | 3 | 76 | 36 | NO | NO | 36 | 0.31 | 52000 | WELDED |  | 901 | 210 | YES | 24 | 762 |  | 63 | EXTERNAL | Null | YES | OTHER | NOT GIVEN | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | ON THE AFTERNOON OF MARCH 30, 1994, THE CITY GAS COMPANY OF UNION, SC, NOTIFIED THE ATLANTA CONTROL CENTER THAT A DIESEL FUEL ODOR AND A SMALL AMOUNT OF OIL WERE NOTICED ON THE COLONIAL RIGHT-OF-WAY NEAR THE NATURAL GAS COMPANY'SMETERING STATION ON DOGWOOD CLUB ROAD. LOCAL COLONIAL PERSONNEL WERE DISPATCHED TO THE SITE WHERE AT 1533, EST ON MARCH 30, 1994, A LEAK WAS CONFIRMED ONCOLONIAL'S LINE 02, A 36-INCH DIAMETER PIPELINE WHICH RUNS FROM HOUSTON, TX TO GREENSBORO, NC. AT 1626, EST, A TELEPHONIC NOTICE OF THE INCIDENT WAS GIVEN TO THE NATIONAL RESPONSE CENTER (REPORT NO. 232543). THE SOUTHERN REGION OFTHE OFFICE OF PIPELINE SAFETY AND SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL WERE ALSO INFORMED OF THE INCIDENT. EXCAVATION OF THE PIPELINE REVEALED THE SOURCE OF THE LEAK TO BE A SMALL 3-INCH LONGITUDINAL CRACKTHAT HAD DEVELOPED IN A CORROSION PIT. A 4-FOOT, FULL-ENCIRCLEMENT SLEEVE WAS INSTALLED OVER THE CORRODED AREAS. ALL CONTAMINATED SOIL HAS BEEN PLACED I A PLASTIC ENVELOPE FOR DISPOSAL AT A LATER DATE. AN ESTIMATED 76 BARRELS OF AMIXTURE OF FUEL OIL AND KEROSINE SEEPED INTO SURROUNDING SOIL AND A NEARBY CASING. THIRY-SIX BARRELS OF THE AMOUNT SPILLED WERE RECOVERED; THE BALANCE WAS ABSORBED INTO THE SURROUNDING SOIL. CLEAN-UP ACTIVITIES ARE CONTINUING.
2017-09-29 08:50 | YES | NO | 19940145 | 1994-05-09 | 15490 | PHILLIPS PIPE LINE CO | YES | 1994-04-09 | 1910 | TX | COCHRAN |  | NO |  | NO | GAINES-BORGER, LINE 80, MP 117-13+47. LIPSCOMB CO. SCH LAND SURVEY, BLOCK A-81, SEC.92 5 MILES W. OF STATE RD 1780, THEN 1/4 MILES N. OF STATE RD 1585. |  | LINE PIPE | PIPE |  | 1942 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 48747.7906 | 98343.9837 | NATURAL GAS LIQUID | 2 | 4767 | 0 | NO | NO | 8.63 | 0.19 | 40000 | WELDED |  | 1150 | 795 | YES | 24 | 1514 | 4 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS - MANAGER OF ENGINEERING & TECHNICAL SVC | 9186616267 | AT 1910 HOURS ON SATURDAY, APRIL 9, 1994, A THIRD PARTY NOTIFIED PHILLIPS PIPE LINE OF A POSSIBLE LEAK ON LINE 80. THE LINE WAS SHUT DOWN AND THE SECTIONCONTAINING THE REPORTED LEAK WAS ISOLATED BY BLOCK VALVES. THE LEAK OCCURRED1/4 MILE NORTH OF STATE ROAD 1585 AND FORCED STATE ROAD 1585 TO BE CLOSED UNTIL THE LEAK COULD BE STOPPED. THERE WERE NO INJURIES OR DAMAGES OTHER THAN TO THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19940146 | 1994-05-09 | 15490 | PHILLIPS PIPE LINE CO | YES | 1994-04-16 | 745 | KS | COFFEY |  | NO |  | NO | BORGER-E. CHICAGO "BLUE" LINE - MP 360-00+00. SEC 11, T21S,R14E. 2 MILES N. OF BURLINGTON, KS AND THEN 5 MILES WEST. |  | LINE PIPE | GIRTH |  | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 224.9898 | 453.8953 | L. P. G. | 2 | 1 | 0 | YES | NO | 12.75 | 0.25 | 45000 | WELDED |  | 990 | 178 | YES | 24 | 1470 | 4 | 80 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS - MANAGER OF ENGINEERING & TECHNICAL SVC | 9186616267 | LANDOWNER REPORTED SMALL SURFACE FIRE FOLLOWING SPRING PASTURE BURN. PINHOLEIN GIRTH WELD WAS REPAIRED WITH REPAIR SLEEVE.
2017-09-29 08:50 | YES | NO | 19940147 | 1994-05-06 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1994-04-09 | 108 | MT | DAWSON |  | NO |  | NO | SEVEN MILES S. OF MONTANA HIGHWAY 200 ON MONTANA HIGHWAY 254 THEN 2 MILES E. NE SEC 10 TWN 21N RNG 53E |  | PUMPING STATION | SCRAPER TRAP | RELIEF | 1993 | OUTSIDE FORCE DAMAGE | FROSTHEAVE | NATURAL FORCE DAMAGE | TEMPERATURE | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 3374.847 | 6808.4296 | CRUDE OIL | 1 | 1100 | 958 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | FROSTHEAVE |  | Null | NO DATA |  | Null | Null | RICHARD PETER | 3072662167 | AT 1:08, A POSSIBLE LINE FAILURE WAS FOUND BY SIDNEY SCADA OPERATOR. THE PIPELINE WAS SHUT DOWN IMMEDIATELY, VALVES CLOSED AND STATION OPERATORS FOR BAKER, GLENDIVE AND RICHEY WERE CALLED OUT TO INVESTIGATE. AT 2:10 AM RICHEY STATION OPERATOR FOUND 1" PIPING BROKE FROM SCRAPER TRAP RELIEF. NO SIGNS OF CORROSION OR VANDALISM CAN BE FOUND. THE MOST LOGICAL EXPLANATION IS HEAVING DUE TO FROST COMING OUT OF THE GROUND. THE NIPPLE BROKE OFF FLUSH WITH THE THREAD-O-LET ALLOWING SWEET CRUDE TO ESCAPE STRAIGHT INTO THE AIR UNTIL 800 PSI WASRELIEVED. APPROXIMATELY 1100 BBLS OF CRUDE LEAKED ONTO OUR PROPERTY AND ADJACENT LANDOWNERS PASTURE. OUR STATION DIKES CONTAINED THE MAJORITY OF THE SPILL AND AS OF 10 AM ON 04/11/1994, WE HAVE RECOVERED 958 MEASURED BARRELS. THE REMAINING IS MIXED WITH MUD AND WATER AND IS BEING TAKEN TO DISPOSAL. THE LANDOWNERS PASTURE WAS MISTED WITH A VERY LIGHT OIL COVERING AND WAS BURNT 04/09/94 IN A COANTROLLED SITUATION WITH STATE APPROVAL.
2017-09-29 08:50 | YES | NO | 19940148 | 1994-05-13 | 12627 | MOBIL OIL CORP | NO | 1994-04-21 | 1000 | CA | LOS ANGELES |  | NO |  | NO | NORTHWEST CORNER OF TELEGRAPH RD AND GARFIELD AVE, COMMERCE, CA. CNTY OF L.A., SEE ATTACHED THOMAS BROTHER GUIDE. |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 52497.6207 | 105908.9055 | GASOLINE | 2 | 60 | 20 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 592 | 350 | YES | 4 | 843 | 1 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | T.W. SALLES | 3104937224 | GS WERE FORWARDED TO BOTH THE COUNTY AND THE CONTRACTOR RESPECTIVELY PRIOR TO THE REMOVAL OF THE EMBANKMENT. WHILE THE CONTRACTOR WAS TRYING TO FINISH THE GRADE WITH A LARGE GRADING EXCAVATOR THE BLADE PUNCTURED A 2" DIAMETER HOLEIN THE TOP OF MOBIL'S 8" PIPELINE. THE PIPELINE WAS IMMEDIATELY SHUTDOWN ANDISOLATED AND CORRECTIVE MEASURES WERE IMPLEMENTED AT THIS TIME TO DIMINISH ANY ADDITIONAL PROBLEMS.
2017-09-29 08:50 | NO | NO | 19940149 | 1994-05-12 | 561 | ARCO OIL & GAS CO - DIV OF ATLANTIC RICHFIELD | NO | 1994-04-15 | 830 | OK | GARFIELD |  | NO |  | NO | 6 MILES EAST OF ENID OKLAHOMA SEVENTY FIVE (75 YARDS WEST OF UN-PAVED COUNTY ROAD IN GRASS PASTURE. |  | LINE PIPE | PIPE |  | 1982 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 16600 | 12449.4358 | 25115.5404 | CARBON DIOXIDE | 3 | 0 | 0 | NO | NO | 8 | 0.25 | 3014 | WELDED |  | 2150 | 1550 | YES | 54 | 2863 | 5 | 82 | EXTERNAL | Null | YES | OTHER | SEE REMARKS | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY S. ENICOTT - SR. PRODUCTION SUPERVISOR | 4054442751 | R HERE AT VELMA AND NOTIFIED US OF A POTENTIAL CO2 LEAK. WE CONTACTED THE FARMLAND CO2 PLANT AND THEY INVESTIGATED THE LEAK SITE IMMEDIATELY AND DETERMINED THAT WE HAD A LEAK. THE PLANT WAS SHUT-DOWN AND THE MLV #2 30 MILES SOUTH WAS CLOSED AND THAT SECTION OF LINE WAS DE-PRESSURED IMMEDIATELY. PEOPLE IN THE AREA OF THE LEAK WERE NOTIFIED BY ARCO PERSONNEL OF THE LEAK. NO OTHER ACTION WAS NEEDED FOR THIS LEAK. IT WAS IN A RURAL AREA LEAK WAS TESTED AND REPLACED. PART I - GALVANIC CORROSION/DISMILAR ELECTROLYTES.
2017-09-29 08:50 | YES | NO | 19940150 | 1994-05-09 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-04-07 | 755 | OK | BEAVER |  | NO |  | NO | TOWNHSIP 5 NORTH RANGE 25 EAST, SECTION 18, BEAVER COUNTY, OKLAHOMA |  | PUMPING STATION | PUMP |  | 1963 | OTHER | MALFUNCTION PUMP SLEEVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NOT GIVEN | 2 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.T. CRONK - SENIOR VICE PRESIDENT | 9185811800 | WITHIN TWO MINUTES OF RELEASE. NO DAMAGE WAS ATTRIBUTED TO THE FIRE, WHICH REMAINED LOCALIZED IN THE SEAL SLEEVE AREA. THIS EVENT WAS NOT TELEPHONICALLY REPORTED DUE TO A MISINTERPRETATION OF THE TELEPHONE REPORTING REQUIREMENTS AND THE SHORT DURATION AND LACK OF DAMAGE ASSOCIATED WITH THE EVENT. A REVIEW OF AND TRAINING ON REPORTING PROCEDURES HAS BEEN COMPLETED WITH THE APPROPIATE PERSONNEL.
2017-09-29 08:50 | YES | NO | 19940151 | 1994-05-31 | 15498 | PHILLIPS GAS PIPELINE CO | YES | 1994-05-02 | 1400 | CO | BACA |  | NO |  | NO | BORGER-DENVER LINE-CAMPO STATION-MP 127-5+00 APPROXIMATELY 9 MILES SOUTHWEST OF CAMPO, CO. |  | PUMPING STATION | VALVE |  | 1963 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1770 | 1327.4398 | 2677.9823 | L. P. G. | 2 | 23 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS | 9186616267 | ON MAY 2, 1994, A PROPERTY OWNER CALLED THE BARTLESVILLE CONTROL CENTER TO REPORT HEARING A LOUD NOISE AND SEEING A WHITE GAS CLOUD AT OUR CAMPO STATION.THE CONTROL CENTER SHUT DOWN THE LINE WHICH HALTED THE RELEASE. THE BACA COUNTY SHERIFF DEPT. AND PPL MAINTEANCE CREW RESPONDED TO THE STATION. THE CAUSEOF THE LEAK WAS A MALFUNCTIONING THERMAL RELIEF VALVE, WHICH WAS REPAIRED.
2017-09-29 08:50 | NO | NO | 19940152 | 1994-07-26 | 22610 | WILLIAMS PIPELINE CO | YES | 1994-06-21 | 1600 | OK | HASKELL |  | NO |  | NO | SOUTHWEST QUARTER OF SECTION 36; TOWNSHIP 9N; RANGE 22E; IN HASKELL COUNTY, OKLAHOMA |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | GASOLINE | 3 | 40 | 8 | NO | NO | 12.75 | 0.25 | 46000 | WELDED |  | 1200 | 225 | YES | 0 | 0 | 0 | 54 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883850 | ON TUESDAY, JUNE 21, 1994, AT 2;05 PM, THE PATROL PILOT NOTIFIED THE SOUTHERN REGION OFFICE OF DEAD VEGETATION ALONG THE PIPELINE RIGHT-OF-WAY NEAR MILE POST 184 ON THE DUNCAN TO FT. SMITH LINE. IMMEDIATELY, THE TULSA DISPACTHER WAS NOTIFIED TO SHUT THE LINE DOWN AND A MEMBER OF THE MAINTENANCE CREW WAS SENT TO THE SITE FOR VERIFICATION. AT 4:00 PM, JUNE 21, 1993, THE LEAK WAS CONFIRMED. AT APPROXIMATELY 5:00 PM, THE LEAK WAS ISOLATED BY CLOSING THE BLOCK VALVES ON EITHER SIDE OF THE LEAK WHILE EQUIPMENT WAS BEING MOBILIZED TO THE SITE FOR REPAIR. AT APPROXIMATELY 6;30 PM, THE BACKHOE AND ADDITIONAL PERSONNEL ARRIVED AT SITE. AT APPROXIMATELY 7:00 PM, THE LEAK WAS EXPOSED AND IT WAS DETERMINED THAT THERE WAS A PIN-HOLE SIZE LEAK CAUSED BY EXTERNAL CORROSION. THE LEAK WAS IMMEDIATELY STOPPED USING TEMPORARY CLAMPS AND THE SITE WAS EXCAVATED FURTHER TO MAKE SAFE FOR WELDING. AT 8:00 AM ON WEDNESDAY, JUNE 22, 1994, THE PERMANENT PATCH WAS WELDED ON THE LINE AND THE LINE WAS PUT BACK IN SERVICE. ON JUNE 23, 1994, FULL SCALE REMEDIATION WAS COMPLETED BY JULY 15, 1994 EXCEPT FOR THE DISCING OF THE SOILS, WHICH IS AN ONGOING PROCESS.
2017-09-29 08:50 | NO | NO | 19940153 | 1994-07-19 | 26148 | WITCO CHEMICAL CORP | YES | 1994-07-14 | 0 | CA | KERN | BAKERSFIELD | NO |  | NO | 2523 NORTH CHESTER AVE. WEST SIDE OF ROAD LEFT FROM THE CRUB. CROSS STREET CHINA GRADE LOOP. |  | LINE PIPE | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 6 | 0.25 | 340 | WELDED |  | 340 | 60 | YES | 4 | 450 | 11 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHARLES LANKFORD | 8053937110 | 1). 6:30 P.M. LEAK REPORTED TO DAN MARTIN BY DAVE KAUS KCFD STATION #63. 2).6:35 P.M. DAN CONTACTED TOM BOYD, BUD WYANT, MERLE MENGHINI, AND CHARLES LANKFORD (CHARLES NOT IN). 3). 7:00 P.M. FIRE DEPARTMENT EVACUTATED BROOKS RANCHAND CLOSED THEM DOWN. 4). 7:00 P.M. BOYD CALLED FITZ TO SHUT DOWN THE PIPELINE AND KEN SMALL CONSTRUCTION FOR REPAIR AND CLEAN UP. 5). 8:30 A.M. DAN CALLED LANKFORD AND REPORTED THE LEAK. 6). 9:00 P.M. LANKFORD CALLED - PG&E - WARNER CABLE PACIFIC TELEPHONE - NORTH OF THE RIVER WATER - SO. CALIF. GAS TO MOBILE ANY UNDERGROUND LINES THEY HAVE IN THE AREA. ALL RESPONDED EXCEPT FOR THE PHONE COMPANY. 7). 1:00 A.M. LEAK WAS UNCOVERED AND CLAMPED WELDER WILL INSTALL A FULL SLEEVE 36" LONG FINISHED AT 4:30/A.M. 8). WILL START CLEAN UP FRIDAY 7/15/1994.
2017-09-29 08:50 | YES | NO | 19940154 | 1994-06-28 | 26303 | UNOCAL PIPELINE CO - EASTERN REGION | NO | 1994-06-21 | 900 | IL | PIATT |  | NO |  | NO | 1 MILE WEST OF THE TOWN OF LODGE, IL LOCATED IN SEC. 13 T19N R5E PIATT COUNTY, IL |  | PUMPING STATION | PUMP | 5/8" SEAL COOLING RUPTURE | 1974 | OTHER | TUBING WORN THIN RUPTURED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | CRUDE OIL | 1 | 90 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID T. HOCKING | 7084799260 | AT CHICAP'S MONTICELLO PUMP STATION A 5/8" STEEL TUBING LINE, USED FOR PUMP SEAL COOLING, RUPTURD ON UNIT #4 SPRAYING CRUDE OIL ONTO GROUND.
2017-09-29 08:50 | YES | YES | 19940155 | 1994-06-06 | 26303 | UNOCAL PIPELINE CO - EASTERN REGION | NO | 1994-06-23 | 700 | CA | SAN LUIS OBISPO |  | NO |  | NO | SANTA MARGARITA PUMP STATION ONE MILE NORTH OF SANTA MARGARITA, CALIFORNIA ON EL CAMINO REAL. |  | TANK FARM | TANK |  | 1967 | OTHER | UNKNOWN SOURCE IGNITION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 0 | 2 | 2000000 | 1499932.019 | 3025968.7288 | NOT GIVEN | 1 | 0 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RONALD L. JAMES | 8055477227 | TANK 55400 AT SANTA MARGARITA PUMP STATION HAD BEEN EMPTIED OF PRESSURE DISTILLATE BY DECANTING. THE REMAINING OIL AND WATER HAD BEEN PUMPED OFF THE ROOFWAS SETTING ON HIGH LEGS WITH ONLY BOTTOM SLUDGE REMAINING IN THE TANK. GAS FREEING HAD BEGUN THE PREVIOUS DAY. AT 0700 WORKERS WERE SETTING UP TO CONTINUE GAS FREEING THE TANK WHEN THERE WAS AN EXPLOSION AND FIRE. FIRE WAS OUT AT1130. THE 55,000 BARREL TANK WAS COMPLETELY DESTROYED. CAUSE OF IGNITION IS NOT KNOWN AT THIS TIME.
2017-09-29 08:50 | YES | NO | 19940156 | 1994-07-12 | 18273 | SHELL PIPELINE CORP | YES | 1994-06-10 | 730 | TX | CULBERSON |  | NO |  | NO | BLACK RIVER PUMP STATION |  | PUMPING STATION | PUMP |  | 1958 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 73000 | 54747.5187 | 110447.8586 | FUEL OIL | 1 | 1890 | 0 | NO | NO | 6 | 0.25 | 46000 | WELDED |  | 2150 | 1900 | YES | 36 | 2200 | 0 | 58 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132 | PUMP EQUALIZATION LINE ON PUMP LOCATED AT BLACK RIVER PUMP STATION FAILED AND CAUSED RELEASE.
2017-09-29 08:50 | NO | NO | 19940157 | 1994-06-20 | 18273 | SHELL PIPELINE CORP | YES | 1994-05-16 | 1200 | TX | CRANE | MONAHANS | NO |  | NO | NE 1/4, SW 1/4, SECTION 4, BLOCK 27, 20 MILES SOUTHEAST OF MONAHANS HENDRICK-MACAMEY 10-INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1936 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4499.7961 | 9077.9062 | CRUDE OIL | 1 | 10 | 0 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 1000 | 105 | YES | 8 | 1250 | 0 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | YES | NO | J.M. KORPAL | 7132410132
2017-09-29 08:50 | YES | NO | 19940158 | 1994-06-29 | 14295 | OLYMPIC PIPE LINE CO | YES | 1994-06-20 | 648 | WA | PIERCE | SPANAWAY | NO |  | NO | 4420 -18TH ST. EAST R-3E, T-19N, 3 MILES EAST OF HIGHWAY 7 AT 180TH ST. E. SPANAWAY, WASHINGTON. |  | PUMPING STATION | OTHER | 3/4"THREADED FITTING | 1993 | OTHER | FAILURE IN FITTING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4025 | 3018.6132 | 6089.7621 | DIESEL FUEL | 3 | 115 | 12 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM A. MULKEY | 2062357745 | 06:47 500/2500 HP UNITS ON-LINE - DIESEL FUEL IN TRANSIT.PRESS. SUC - 370 DISC - 1260 - CONTROL CENTER RECORDS CON - CON 1518 06:48 DEVIATION IN PRESSURE. LOSS OF SOME CONTROL AND SUCTION PRESSURE. 06:49 CONTROL CENTER RECEIVED LOW SUCTION ALARM. 06:51 CONTROLLER S/D 1500 HP UNIT - SUCTION CONTINUES TO SLOWLY DROP. 06:54 CONTROLLER S/D 2500 HP UNIT & BEGINS S/D OF ENTIRE PIPELINE. 06:58 STATION PRESSURE AT SPANAWAY IS FLAT - NOTIFICATION BEGINS 07:07 BLOCK VALVES REMOTELY CLOSED ON BOTH SIDES OF PUMP STATION 07:25 LEAK CONFIRMED BY ON-SITE PERSONNEL. 3/4" THREADED TEMPERATURE PROBE THERMAL WELL FAILURE. THE CAUSE OF FAILURE COULD NOT BE IMMEDIATELY DETERMINED. THERMAL WELL TO BE SUBMITTED FOR LABORATORY ANALYSIS. ESTIMATED LOSS TO BE 115 BBLS. LOW SULFUR DIESEL TACOMA PUMP STATION SPANAWAY, WA 06/20/1994.
2017-09-29 08:50 | YES | NO | 19940159 | 1994-06-26 | 15674 | PLANTATION PIPE LINE CO | YES | 1994-07-02 | 800 | GA | DOUGLAS | LITHIA SPRINGS | NO |  | NO | ACCIDENT OCCURRED AT PLANTATION'S AUSTELL TANK FARM. THE ACCIDENT INVOLVED THE MAF SUMP SYSTEM AS WELL AS THE STATION'S WATER COLLECTION AND CONTAINMENT SYSTEMS |  | TANK FARM | OTHER | FILTER VESSEL & SUMP TANK | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL | MALFUCTION OF RELIEF EQUP | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2249.898 | 4538.9531 | JET FUEL | 3 | 86 | 86 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK | 4043645916 | ON JULY 2, 1994, AT APPROXIMATELY 8:00 A.M., PLANTATION'S AUSTELL TANK FARM UTILITY OPERATOR REPORTED TO WORK AND DISCOVERED JET-A TURBINE FUEL ON THE FACILITY'S CATCHMENT POND. APPARENTLY, A SIMULTANEOUS FAILURE OF THE STATION'S FILTER VESSEL DEWATERING VALVES AND WATER COLLECTION SYSTEM BOOSTER MOTOR ON JULY 1 RESULTED IN PRODUCT OVERFILLING A STATION SUMP TANK AND ENTERING THE WATER COLLECTION SYSTEM. AT 8:05 A.M. ON JULY 2, THE UTILITY OPERATOR HAD THE AFFECTED PIPELINE SYSTEM SHUT DOWN. THE PRODUCT WAS CONTAINED ENTIRELY WITHINTHE FACILITY IN HARD PIPED SYSTEMS, CONCRETE FLUMES AND THE CATCHMENT POND. ALL TRACES OF PRODUCT WERE SKIMMED FROM THE POND ON JULY 2. THE SUSPECT DEWATERING VALVES WILL BE REMOVED FROM OPERATION.
2017-09-29 08:50 | YES | NO | 19940160 | 1994-07-21 | 15851 | PRIDE REFINING INC | NO | 1994-06-10 | 830 | TX | JONES |  | NO |  | NO | APPROXIMATELY 9 MILES NORTH OF ABILENE, TEXAS OFF HWY 277 |  | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1250 | 937.4575 | 1891.2305 | OIL AND GASOLINE | 1 | 70 | 60 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 580 | 470 | YES | 8 | 755 | 11 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON | 9156748231 | AT APPROXIMATELY 8:30 AM ON JUNE 10, 1994 OUR COMPANY AIR PATROL PILOT SPOTTED THE LEAK . HE RADIOED OUR FIELD OFFICE, AND PERSONNEL WERE DISPATCHED TO BEGIN CLEAN UP AND SHUT DOWN OF PIPELINE OPERATIONS. LEAK WAS CLAMPED. EM-TECHENVIRONMENTAL SERVICES WERE CONTACTED TO BEGIN SAMPLING AND REMOVAL OF SOIL FOR CLEAN UP. PERMANENT REPAIRS WILL BE MADE BY LINE REPLACEMENT ON JUNE 27, 1994.
2017-09-29 08:50 | YES | NO | 19940161 | 1994-06-23 | 15674 | PLANTATION PIPE LINE CO | YES | 1994-05-23 | 2336 | GA | DOUGLAS | LITHIA SPRINGS | NO |  | NO | ACCIDENT OCCURED AT PLANTATION'S AUSTELL TANK FARM. THE ACCIDENT INVOLVED THE B3 BOOSTER PUMP NEAR THE WARNER-LEWIS FILTER VESSELS. |  | TANK FARM | PUMP |  | 1969 | OTHER | PUMP/MOTOR MALFUNCTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | JET FUEL | 3 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK | 4043645916 | ON MONDAY, MAY 23 AT APPROXIMATELY 11:36 P.M. , PLANTATION'S BOOSTER PUMP UNIT B3 ON THE 12" MAF PIPELINE AT AUSTELL TANK FARM FAILED RESULTING IN A FIRE. IT APPEARS THAT BOLTS HOLDING DOWN THE PUMP MOTOR VIBRATED LOOSE CAUSING THE MOTOR TO SHIFT. THE PUMP SEAL FAILED ALLOWING PRODUCT TO ESCAPE. THE HEAT GENERATED BY THE GRINDING OF THE PUMP SLEEVE COUPLING IGNITED THE FUEL. PLANTATION WAS NOTIFIED OF THE INCIDENT AT 11:47 P.M. PLANTATION SHUT DOWN THE 12" PIPELINE AND CLOSED ALL TANK VALVES TO STOP FUEL FLOW AT 11:48 P.M. THE FIRE WAS EXTINGUISHED BY THE DOUGLAS COUNTY FIRE DEPARTMENT BY 12:05 A.M. ALL VISIBLE TRACES OF PRODUCT WERE CLEANED UP AND DISPOSED OF. THE BOOSTER PUMP AND MOTOR WERE REPLACED.
2017-09-29 08:50 | NO | NO | 19940162 | 1994-07-12 | 12628 | MOBIL PIPELINE CO | YES | 1994-06-13 | 800 | NY | CAYUGA | THROOP | NO |  | NO | FROM RT. 31 IN PORT BYRON, NY THE LOCATION IS 1.5 MILES SO. OF KING RD., .25 MILES W. ON HENVEY RD .25 MILES SO. ON ARMSTRONG, AND 700 FEET WEST OF ARMSTRONG RD |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 8999.5921 | 18155.8124 | GASOLINE | 1 | 3 | 3 | NO | NO | 6.38 | 0.25 | 35000 | WELDED |  | 1440 | 300 | YES | 8 | 1835 | 8 | 81 | NO DATA | Null | YES | OTHER | NOT GIVEN | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES |  | 7162738107 | AT APPROXIMATELY 0700, OPERATOR AND ITS CONTRACT CREW BEGAN AN EXPLORATORY EXCAVATION TO EXPOSE AN ANOMALLY INDICATION AS INDICATED BY A SMART PIG LOG. BACKHOE OPERATOR WAS EXCAVATING ON THE SOUTH SIDE OF PIPELINE. AT APPROXIMATELY 0800, THE BACKHOE OPERATOR HIT A 3/4" NIPPLE AND VALVE THAT WAS 9" LONG AND PERPENDICULAR TO THE PIPE, CRACKING THE NIPPLE, CAUSING THE SPILL. PRODUCT SPRAYED INTO THE EXCAVATED DITCH AND WAS CONTAINE. SECONDARY CONTAINMENT DITCHES WWERE EXCAVATED SOUTH OF THE PRIMARY DITCH AS A PRECAUTION. PIPELINE WAS PROPERLY REPAIRED AND PUT BACK INTO SERVICE. CONTAIMINATED SOIL WAS REMOVED AND HAULED TO AN APPROVED DISPOSAL SITE.
2017-09-29 08:50 | YES | NO | 19940163 | 1994-07-13 | 12625 | MOBIL OIL EXPLORATION & PRODUCTION SE INC | NO | 1994-06-22 | 1445 | TX | MIDLAND |  | NO |  | NO | SEE SKETCH ATTACHED |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4499.7961 | 9077.9062 | L. P. G. | 2 | 205 | 0 | NO | NO | 4.5 | 0.24 | 24000 | WELDED |  | 500 | 450 | YES | 8 | 1200 | 5 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | NOTIFICATION OF OFFICIALS | NO | NO | GERALD E. WILKINSON | 9156882024 | AT 2:45 PM ON JUNE 22, 1994, CENTURY SERVICE COMPANY WAS DRILLING A HOLE FORTHE INSTALLATION OF A GUY ANCHOR FOR A UTILITY POLE AND DRILLED INTO THE SIDE OF OUR PIPELINE CAUSING A LEAK AND RUPTURE OF OUR PIPELINE SYSTEM. CENTURY SERVICE COMPANY WAS WORKING AS A CONTRACTOR FOR TEXAS UTILITITES ELECTRIC COMPANY. AFTER THE RUPTURE THE PIPELINE WAS IMMEDIATELY SHUT-IN AND THE PRESSUREWAS BLED OFF. THE PIPELINE WAS REPAIRED AND PLACED BACK IN SERVICE WITHIN 24HOURS OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19940164 | 1994-07-12 | 9175 | JAYHAWK PIPELINE CORP | YES | 1993-11-24 | 700 | KS | MEADE |  | NO |  | NO | NW/4 SECTION 34-T33S-R30W, MEADE COUNTY, KANSAS 8 MILES SOUTH OF PLAINS, KANSAS AND 1/2 MILE EAST. |  | PUMPING STATION | WELDING FITTING |  | 1992 | OTHER | NIPPLE ON VOL.BOT. BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2400 | 1839.1775 | 3710.364 | CRUDE OIL | 1 | 160 | 150 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162651700 | 1" INCH NIPPLE ON VOLUME BOTTLE NEST TO PUMP AT JAYHAWK'S MEADE STATION, MEADE COUNTY, KANSAS BROKE DURING THE NIGHT. THE AREA GAUGER ARRIVED AT 0700 AND SAW OIL SPILLING FROM THE NIPPLE. THE GAUGER IMMEDIATELY SHUT DOWN PUMP ANDCLOSED ALL VALVES TO STOP THE FLOW OF OIL. AN ESTIMATED 160 BARRELS OF CRUDEOIL WAS SPILLED AND 150 BARRELS RECOVERED. THE OILY DIRT WAS REMOVED AND NEWTOP SOIL REPLACED. INSTALLED NEW FITTING WITH BRACE FOR VOLUME BOTTLE.
2017-09-29 08:50 | NO | NO | 19940166 | 1994-07-05 | 9175 | JAYHAWK PIPELINE CORP | YES | 1993-10-28 | 1630 | KS | SEDGWICK |  | NO |  | NO | 6358 NORTH MERIDIAN OR 3 1/4 MILES SOUTH OF VALLEY CENTER, KANSAS. |  | PUMPING STATION | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3831.6199 | 7729.925 | OIL AND GASOLINE | 1 | 45 | 0 | NO | NO | 10 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | NOT GIVEN | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162651700 | LEAK WAS IN TANK SECTION LINE AT JAYHAWK'S VALLEY CENTER STATION NO.4, SEDGWICK COUNTY, KANSAS. THE STATION OPERATOR SHUT DOWN PUMP AND CLOSED ALL VALVESAND NOTIFIED THE DISTRICT SUPERVISOR AND OIL MOVEMENTS SCHEDULER. CREW WELDED HALF SOLE ON PIPE.
2017-09-29 08:50 | YES | NO | 19940167 | 1994-07-05 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-02-01 | 1012 | IA | JOHNSON |  | NO |  | NO | SECTION 27, TOWNSHIP 79N, RANGE 5W, JOHNSON COUNTY, IOWA |  | PUMPING STATION | VALVE |  | 1990 | OTHER | MECHANICAL FAILURE VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1644165 | 1233067.864 | 2487595.9375 | L. P. G. | 2 | 6720 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.D. SMITH | 9185811800 | PRELIMINARY INDICATIONS ARE THAT A 1" BALL VALVE ON STATION BLOWDOWN SYSTEM FAILED. FAILED PIPE AND VALVE PARTS ARE BEING ANALYZED BY A METALLURGIST TO DETERMINE CAUSE OF FAILURE. SUPPLEMENTAL INFORMATION: THE ANALYSIS INDICATED THAT MECHANICAL FAILURE OF THE 1" BALL VALVE WAS THE PROBABLE CAUSE OF THE RELEASE AND SUBSEQUENT FIRE. HOWEVER, THE CAUSE OF THE VALVE'S FAILURE COULD NOTBE DETERMINED.
2017-09-29 08:50 | NO | NO | 19940168 | 1994-06-24 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-05-21 | 1020 | IA | MONONA |  | NO |  | NO | SECTION 15, TOWNSHIP 84 NORTH, RANGE 46 WEST, MONONA COUNTY, IOWA. |  | LINE PIPE | PIPE |  | 1974 | OTHER | PINHOLE LEAK IN WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3700 | 2774.8742 | 5598.0421 | ANHYDROUS AMMONIA | 2 | 2 | 0 | NO | NO | 4.5 | 0.14 | 2193 | WELDED |  | 1160 | 800 | YES | 24 | 2148 | 0 | 74 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH | 9185811800 | PINHOLE IN A WELD WAS DISCOVERED. A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED.THE REPAIRED SECTION WAS COATED AND BACKFILLED.
2017-09-29 08:50 | YES | NO | 19940169 | 1994-07-05 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-03-24 | 1243 | NE | WASHINGTON |  | NO |  | NO | SECTION 27, TS20 N, R10E, WASHINGTON COUNTY, NEBRASKA. |  | NO DATA | VALVE |  | 1993 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1362 | 1021.4537 | 2060.6847 | ANHYDROUS AMMONIA | 2 | 43 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.D. SMITH | 9185811800 | A ONE-HALF INCH BODY RELIEF VALVE ON A GATE VALVE OPENED PREMATURELY, ALLOWING PRODUCT TO BE RELEASED. PRESSURE CHARTS INDICATED THAT LINE CONDITIONS WERE WITHIN NORMAL OPERATING LIMITS. THE RELIEF VAVLE DID NOT RE-SEAT, HOWEVER, THE RELEASE WAS CONTAINED WHEN THE GATE VALVE WAS CLOSED. THE RELIEF VALVE WAS REPLACED AND IS BEING EXAMINED FOR THE CAUSE OF FAILURE. SUPPLEMENTAL INFORMATION: AFTER EXAMINATION BY A RELIEF VALVE REPAIR FACILITY, THE CAUSE FOR THE VALVE OPENING PREMATURELY WAS NOT DETERMINED. THE REPORT DID INDICATE THAT A FOREIGN SUBSTANCE WAS FOUND BETWEEN THE SEATING SURFACES OF THE VALVE, CAUSING THE VALVE NOT TO RE-SEAT.
2017-09-29 08:50 | NO | NO | 19940170 | 1994-07-05 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-05-28 | 942 | IA | MONONA |  | NO |  | NO | SECTION 7 TOWNSHIP 85 NORTH, RANGE 46 WEST, MONONA COUNTY, IOWA |  | LINE PIPE | PIPE |  | 1974 | OTHER | PINHOLE LEAK IN WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1700 | 1274.9422 | 2572.0734 | ANHYDROUS AMMONIA | 2 | 4 | 0 | NO | NO | 4.5 | 0.14 | 35000 | WELDED |  | 1579 | 761 | YES | 24 | 2148 | 0 | 74 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.D. SMITH | 9182271800 | LANDOWNER REPORTED AN AMMONIA ODOR AND DEAD VEGETATION. UPON INVESTIGATION, A PINHOLE LEAK WAS DISCOVERED. A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED.
2017-09-29 08:50 | NO | NO | 19940171 | 1994-07-19 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-04-30 | 1830 | IA | WOODBURY |  | NO |  | NO | SECTION 6, TOWNSHIP 86-N, RANGE 42-W, WOODBURY COUNTY, IOWA |  | LINE PIPE | PIPE |  | 1968 | OTHER | PINHOLE LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5075 | 3806.0775 | 7678.3956 | ANHYDROUS AMMONIA | 2 | 4 | 0 | NO | NO | 6.63 | 0.16 | 46000 | WELDED |  | 1555 | 600 | YES | 24 | 1980 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH | 9185811800 | A LANDOWNER REPORTED AN AMMONIA ODOR AND DEAD VEGETATION OVER AN AREA OF APPROXIMATELY (7) FEET IN DIAMETER. AN INVESTIGATION REVEALED A PINHOLE LEAK INTHE PIPE. THE LEAK WAS REPAIRED WITH A FULL ENCIRCLEMENT SPLIT SLEEVE WELDED INPLACE. THIS SECTION OF PIPE WILL BE CUT OUT AND METALLURGICALLY EXAMINED. SUPPLEMENTAL REPORT: THE CONCLUSION OF THE ANALYSIS DETERMINED THE CAUSE OF THELEAK WAS LACK OF FUSION IN THE GIRTH WELD AT THE TIME OF INSTALLATION AND SUBSEQUENT EROSION OF THE SLAG.
2017-09-29 08:50 | YES | NO | 19940172 | 1994-06-27 | 4906 | EXXON PIPELINE CO | YES | 1994-05-29 | 1255 | LA | EAST BATON ROUGE |  | NO |  | NO | FROM THE INTERSECTION OF HWY 64 &67 GO NORTH ON HWY 67 APPROX. 1 MILE TO REDWOOD CREEK BRIDGE. LEAK SITE IS APPROX. 50 YDS IN AN EASTERLY DIRECTION. |  | LINE PIPE | PIPE |  | 1948 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 425000 | 318735.554 | 643018.3549 | CRUDE OIL | 1 | 5 | 5 | NO | NO | 16 | 0.31 | 42000 | WELDED |  | 1400 | 15 | YES | 8 | 850 | 0 | 68 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | YES | G.G. PERSYN | 7136565521 | EXXON PIPELINE COMPANY (EPC) RECEIVED A REPORT FROM A THIRD PARTY AT APPROX.12:55 OF OIL ON A CREEK NEAR EPC"S PIPELINE RIGHT OF WAY. THE VALVES WERE CLOSED ON THE THE PIPELINE AT APPROX. 13:15. THE PIPELINE WAS NOT IN OPERATION AT THE TIME THE LEAK WAS DISCOVERED. EMPLOYEES AND CONTRACTORS WERE DISPATCHEDTO THE LOCATION TO INVESTIGATE AND RESPOND AS APPROPRIATE. THE RELEASE WAS VERIFIED AT APPROX. 15:00. THE CRUDE OIL WAS CONTAINED AND RECOVERED. REPAIRS INCLUDED DIRECTIONALLY DRILLING UNDER THE CREEK TO REPLACE THE PIPELINE SEGMENT THAT LEAKED. THIS PIPELINE SEGMENT WAS DISPLACED & ABANDONED.
2017-09-29 08:50 | YES | NO | 19940173 | 1994-07-13 | 3466 | DOME PIPELINE CORP | YES | 1994-06-26 | 337 | MI | MONROE |  | NO |  | NO | SYSTEM MP 1797 (SECTION 1, T5S, R9E) |  | PUMPING STATION | VALVE |  | 0 | OTHER | LEAKING 1" NEEDLE VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1124.949 | 2269.4765 | L. P. G. | 2 | 20 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W. N. HALL | 3193547722 | FAILURE OF BLOWDOWN VALVE ON THE DOME/COCHIN PIPELINE RESULTED IN LEAK OF HYDROCARBON (ETHYLENE) INTO THE FLARE SYSTEM. LEAKING HYDROCARBONS IGNITED AT FLARE STACK (CAUSE OF IGNITION UKNOWN). NEIGHBOR OBSERVED FIRE AT FLARE STACK AND CALLED ASHLAND FIRE DEPARTMENT WHO THEN NOTIFIED BUCKEYE PIPELINE (CONTRACT OPERATOR FOR DOM PIPELINE). BUCKEYE NOTIFIED SARNIA CONTROL CENTER (EASTERN DELIVERY SYSTEM) WHO THEN CALLED COCHIN CONTROL CENTER (DOME PIPELINE SYSTEM ). BOTH PIPELINES TRAVERSE THE FLAT ROCK METER STATION. NEITHER PIPELINE WAS FLOWING AT THE TIME OF THE ACCIDENT. PRODUCT IN THE EDS WAS PROPANE AT 490PSIG, AND PRODUCT IN THE DOME/COCHIN PIPELINE WAS ETHYLENE AT 950 PSIG. EMERGENCY RESPONSE PLANS WERE INITIATED AND BOTHE PIPELINES WERE BLOCKED IN ISOLATING FLAT ROCK METER STATION. IN ADDITION THE METER WAS THEN BLOCKED IN AND BLOWN DOWN TO THE FLARE SYSTEM. THE METER STATION WAS BLOWN DOWN TO FACILITATETHE REPAIR OF THE DEFECTIVE BLOWDOWN VALVE. DEFECTIVE ONE-INCH BLOWDOWN VALVE REPLACED METER STATION WAS PURGED WITH NITROGEN, AND THE PIPELINE WAS RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19940174 | 1994-07-06 | 13131 | CONOCO INC | YES | 1994-06-15 | 2130 | MT | JUDITH BASIN |  | NO |  | NO | T13N, R14E, SW NW SECTION 3, MILE POST 201 |  | LINE PIPE | PIPE |  | 1961 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 149993.2019 | 302596.8729 | CRUDE OIL | 1 | 2870 | 1070 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1632 | 1425 | YES | 8 | 2031 | 0 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W. BEGGS | 3036494090 | AT APPROXIMATELY 21:30, ON JUNE 15 1994, A ERW SEAM FAILURE WAS EXPERIENCED ON THE 8-INCH CONOCO PIPE LINE IN JUDITH BASIN COUNTY IN CENTRAL MONTANA. THIS FAILURE RELEASED APPROXIMAELY 2870 BARRELS OF CANADIAN - LIGHT CRUDE OIL OFWHICH 1070 BARRELS WAS RECOVERED AND THE REMAINDER WAS BURNED OFF AFTER RECEIVING A BURN PERMIT FROM THE STATE OF MONTANA. THE CRUDE ENTERED AN ADJACENT COULEE AND FLOWED APPROXIMATELY 1 MILE. THE CAUSE OF THE ERW SEAM FAILURE IN UNKNOWN AT THIS TIME, HOWEVER, A METALLURGICAL ANALYSIS WILL BE PERFORMED ON THE PIPE TO DETERMINE THE CAUSE.
2017-09-29 08:50 | NO | NO | 19940175 | 1994-07-05 | 2552 | COLONIAL PIPELINE CO | YES | 1994-06-08 | 1500 | NC | GUILFORD |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S GREENSBORO JUNCTION 411 GALLIMORE DAIRY ROAD GREENSBORO, NC 27409 |  | TANK FARM | OTHER | YARD DRAIN | 1978 | OTHER | IMPROPER DRAIN PIPING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | TRANSMIX (PART. REFINED PETRO) | 3 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | ON 05/23/94, WORK BEGAN ON A PROJECT TO IMPROVE STORM WATER DRAINAGE AND THEREPLACEMENT OF THE OIL/WATER SEPARATOR AT GREENSBORO JUNCTION. DURING EXCAVATIONS OF THE PERFORATED DRAIN LINES THAT LEAK FROM THE WAS DOWN CONCRETE SLABAT THE INCOMING SCRAPER TRAPS TO THE OIL/WATER SEPARATOR, SOME PRODUCT RESIDUES IN THE DRAIN LINES AND CONTAMINATED SOIL AND GRAVEL SURROUNDING THESE DRAIN LINES WERE DISCOVERED. WHILE NO FREE PRODUCT WAS EVIDENT IN THE SURROUNDING SOIL, THE FLUSHING OF THESE DRAIN LINES RESULTED IN THE RECOVERY OF LESS THAN ONE BARREL OF A MIXTURE OF PETROLEUM PRODUCTS. THE DRAIN LINES HAVE BEEN EXCAVATED AND THE CONTAMINATED SOIL HAS BEEN PLACED IN A PLASTIC ENVELOPE FOR DISPOSAL AT A LATER DATE. AN INVESTIGATION INTO THE CAUSE OF THE LEAK REVEALED THAT THE DRAIN LINES WERE DESIGNED AND INSTALLED WITH LESS THAN ADEQUATE FALL BETWEEN THE WASH DOWN SLAB AND THE OIL/WATER SEPARATOR. AS A RESULT, PRODUCT THAT COLLECTED ON THE CONCRETE PAD DURING SCRAPER REMOVAL FLOWED INTO THESE DRAIN LINES WHERE IT SETTLED IN LOW AREAS. RAINFALL, THEN FLUSHED THE PRODUCT FROM THESE DRAIN LINES INTO THE SURROUNDING SOIL. ON 06/08/94, IT BECAME EVIDENT THAT ENVIRONMENTAL DAMAGES WOULD EXCEED $5,000 AND NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER AT 1630 EST (REPORT NO. 243013). NOTIFICATION TO THE NORTH CAROLINA DIVISION OF ENVIRONMENTAL MANAGEMENT WAS NOT REQUIRED SINCE WE DO NOT BELIEVE GROUNDWATER WAS THREATEENED. HOWEVER, A TELEPHONE CALL WAS MADE TO THE AGENCY AS A COURTESY. THE GREENSBORO AREA ENVIRONMENTAL TECHNICIAN WILL TEST PIT THE AFFECTED AREA TO DETERMINE THE EXTENT OF CONTAMINATION AND AN ESTIMATE OF THE SPILL VOLUME. A SUPPLEMENTAL REPORT WILL BE FILED UPON COMPLETION OF THE INVESTIGATION
2017-09-29 08:50 | YES | NO | 19940176 | 1994-06-30 | 2271 | CHASE TRANSPORTATION CO | YES | 1994-06-02 | 410 | KS | SEDGWICK |  | NO |  | NO | S.W. OF INTERSECTION OF WEBB ROAD AND 69TH ST. N. SEDGWICK CNTY, KS NE NE 1/4 SEC. 8 T. 26S R, 2E, SEDGWICK COUNTY, KS |  | LINE PIPE | PIPE |  | 1972 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 374983.0048 | 756492.1822 | GASOLINE | 1 | 1100 | 640 | NO | NO | 10 | 0.19 | 0 | WELDED |  | 1600 | 1375 | YES | 24 | 2017 | 4 | 73 | EXTERNAL | Null | YES | OTHER | GROOVING | NO DATA |  | Null | NO DATA |  | Null | Null | CHUCK JOHNSON_063094 | 3168327484 | AT APPROXIMATELY 0200 ON JUNE 2, 1994, THE CHASE EL DORADO MAINLINE PUMP STATION WENT DOWN ON LOW SUCTION PRESSURE. THE EL DORADO BOOSTER STATION WENT DOWN ON HIGH DISCARGE PRESSURE, SHUTTING DOWN THE PIPELINE. THESE EVENTS ALERTED CONTROL CENTER PERSONNEL IN WICHITA, KANSAS TO A PROBLEM OF UNKNOWN ORIGIN AND TYPE. CONTROL CENTER PERSONNEL IMMEDIATELY COMMUNICATED WITH CHASE PERSONNEL IN EL DORADO, IN AN EFFORT TO LOCATE THE PROBLEM. WHEN IT WAS DETERMINED THAT THE PROBLEM WAS NOT LOCATED AT EITHER THE PUMP STATION OR THE BOOSTER STATION. CHASE PERSONNEL BEGAN CHECKING THE PIPELINE. IT WAS DETERMINED THAT THE PROBLEM WAS NOT LOCATED BETWEEN THE MAIN LINE PUMP STATION AND THE BOOSTER STATION. CHASE PERSONNEL THEN BEGAN CHECKING THE PIPELINE DOWNSTREAM OF THE BOOSTER STATION. WHILE CHASE PERSONNEL WERE IN THE PROCESS OF CHECKING THE PIPELINE DOWNSTREAM OF THE BOOSTER STATION, CONTROL CENTER PERSONNEL IN WICHITA RECEIVED A TELEPHONE CALL FROM THE SEDGWICK COUNTY 911 OPERATOR, NOTIFYING CONTROL CENTER PERSONNEL OF DISCHARGED PRODUCT AT THE JUNCTION OF 69TH STREET NORTH AND WEBB ROAD IN RURAL SEDGWICK COUNTY. THIS TELEPHONE CALL WAS RECEIVEDAT APPROXIMATELY 03:15 ON JUNE 2, 1994. CHASE CONFIRMED THAT THERE WAS A LEAK AT 04:10 AND EMERGENCY CREWS WERE IMMEDIATELY DISPATCHED TO THE LOCATION OFTHE LEAK AND BEGAN CONTAINMENT EFFORTS. THE PIPE WAS EXCAVATED, REMOVED AND SENT TO METALLURGICAL CONSULTANTS IN HOUSTON, TEXAS, FOR ANALYSIS. ANALYSIS OF THE PIPE SHOWED THAT THE LEAK WAS CAUSED BY AN INACTIVE CELL OF EXTERNAL CORROSION. PRESSURE ON THE PIPELINE HAS BEEN REDUCED TO 1180 PSIG. CHASE PERSONNEL ARE IN THE PROCESS OF ARRANGING FOR AN INTERNAL INSPECTION OF THE PIPELINE
2017-09-29 08:50 | YES | NO | 19940177 | 1994-06-30 | 2271 | CHASE TRANSPORTATION CO | YES | 1994-06-02 | 1636 | KS | SEDGWICK |  | NO |  | NO | S.W. OF INTERSECTION OF 69TH STREET NORTH AND WEBB RD, SEDGWICK CNTY, KS NENE 1/4 SC. 8 T 26S R 2E RSEDGWICK CNTY, KS. |  | LINE PIPE | BOLTED FITTING |  | 1994 | OTHER | PRESSURE FROM PIPELINE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1499.932 | 3025.9687 | JET FUEL | 3 | 640 | 600 | NO | NO | 10 | 0.19 | 0 | OTHER |  | 1600 | 780 | YES | 24 | 2017 | 4 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHUCK JOHNSON | 3168327484 | SUBSEQUENT TO THE JUNE 2, 1994, LEAK ON THE CHASE PIPELINE, THE AFFECTED PORTION OF PIPE WAS REMOVED AND REPLACED WITH A NEW SECTION OF PIPE WITH TEMPORARY, WELD PLUS ENDS. THE PIPELINE WAS PLACED BACK INTO OPERATION WITH CHASE PERSONNEL PRESENT AT THE SITE. ONE OF THE WELD PLUS ENDS ON THE NEW PIPE FAILED WITH THE SURGE PRESSURE AS THE PIPELINE WAS PLACED BACK INTO OPERATION, CAUSING THE DISCHARGE OF JET FUEL. THE PIPELINE WAS IMMEDIATELY SHUT DOWN THE BLOCK VALVES CLOSED ON THE PIPELINE, PREVENTING DRAIN DOWN. EMERGENCY CREWS PRESENT AT THE SITE DURING THE LEAK RECOVERED THE DISCHARGED PRODUCT FROM THE EXCAVATION. THE PIPELINE REMAINED DOWN UNTIL THE WELD PLUS WERE PERMANENTLY WELDED.
2017-09-29 08:50 | YES | NO | 19940178 | 1994-06-20 | 25145 | B H P PETROLEUM (AMERICAS) INC | NO | 1994-06-05 | 1700 | HI | HONOLULU |  | NO |  | NO |  |  | NO DATA | VALVE | PIG TRAP BLOCK VALVE | 1981 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | GASOLINE | 3 | 100 | 90 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROGER GOENNER | 8085473480 | AT APPROXIMATELY 5:00 PM ON SUNDAY, 5TH JUNE AN ESTIMATED 4,000 U.S. GALLONSOF GASOLINE SPILLED FROM THE BHPPA (H) PIPELINE WITHIN THE CONFINES OF THESAND ISLAND TERMINAL, HONOLULU HARBOR. THE RELEASE OCCURRED DURING OPERATIONSTO REMOVE POLYURETHANE "PIGS" FROM THE PIPELINE. NO INJURIES WERE SUSTAINED.NO FIRE ENSUED AND MOST (ABOUT 80 TO 90%) OF THE SPILLED PRODUCT WASCONTAINED BY A CONCRETE PAD AND CURBING SURROUNDING THE PIG RECEIVING STATION.PROMPT CLEAN-UP ACTIONS WERE TAKEN. ALL APPLICABLE AUTHORITIES HAVE BEENNOTIFIED AND INVESTIGATIONS BY BHPPA (H) INTO THIS INCIDENT ARE CONTINUING.GASOLINE HAD BEEN USED TO DISPLACE DIESEL FROM THE LIQUIDS PIPELINE INPREPARATION FOR A TRANSFER OF GASOLINE FROM THE REFINERY TO THE PIER 29TERMINAL AT HONOLULU HARBOR. THE PIPELINE TRANSFER PUMPS AT THE REFINERY WERESHUT OFF, THE PIPELINE WAS BLOCKED IN UNDER PRESSURE BY TWO MOTOR-OPERATEDVALVES AT THE SAND ISLAND TERMINAL. ONE OPERATOR WAS ON DUTY AT THE SANDISLAND TERMINAL AND A SECOND OPERATOR ON DUTY AT THE PIER 29 TERMINAL(APPROXIMATELY 3 MILES AWAY BY ROAD). THE OPERATOR AT THE SAND ISLANDTERMINAL PREPARED TO OPEN THE PIG RECEIVER STATION TO RECOVER THE POLYURETHANEPIPELINE "PIGS" WHICH HAD BEEN USED TO SEPARATE THE GASOLINE FROM THE DIESELDURING THE PIPELINE DISPLACEMENT OPERATION. THE MOV AT THE UPSTREAM END OFTHE PIG RECEIVER WAS CLOSED. THE OPERATOR DEPRESSURED THE RECEIVER, REMOVEDTHE END COVER AND PROCEEDED TO EXTRACT THE "PIGS". WHILE THIS WAS BEING DONE,THE MOTOR-OPERATED VALVE STARTED TO OPEN, RELEASING GASOLINE UNDER PRESSURE.ATTEMPTS BY THE OPERATOR TO RECLOSE THE VALVE WERE UNSUCCESSFUL AND IT WASWAS EVENTUALLY CLOSED BY REMOTE CONTROL FROM THE REFINERY PUMPHOUSE.SUPPLEMENTAL REPORT JUNE 9, 1994 INDICATES THAT BHP INADVERTENTLY REPORTED 10BARRELS RECOVERED IN THE ORIGINAL REPORT. IT SHOULD HAVE READ 90 BARRELSRECOVERED. THIS CHANGE WAS MADE 1/17/95.
2017-09-29 08:50 | NO | NO | 19940179 | 1994-07-06 | 809 | ARCO PIPE LINE CO | YES | 1994-06-17 | 2115 | OK | OSAGE |  | NO |  | NO | FROM HOMINY, OKLAHOMA - 10 MILES EAST ON HIGHWAY 20, NORTH 1/2 MILE ON PRIVATE ROAD. |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | DIESEL FUEL | 3 | 25 | 20 | NO | NO | 8 | 0.32 | 24000 | THREADED |  | 650 | 640 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY E. GRAVES | 7139865368 | LEAK WAS CAUSED BY EXTERNAL CORROSION.
2017-09-29 08:50 | NO | NO | 19940181 | 1994-07-18 | 443 | AMOCO PIPELINE CO | YES | 1994-06-24 | 941 | IN | ST JOSEPH |  | NO |  | NO | AMOCO OIL COMPANY 12694 ADAMS ROAD GRANGER, IN 46530 |  | TANK FARM | OTHER | SUN PRESSURE REL. VALVE | 1991 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 26248.8103 | 52954.4528 | GASOLINE | 1 | 42 | 30 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD W. WHITE | 7089906105 | ON JUNE 24, 1994, THE TULSA CONTROL CENTER (TCC) RECEIVED A COMMUNICATION OUTAGE AT 0658 CAUSED BY A POWER FAILURE. THE TERMINAL DELIVERY HEADGATE ALSO WENT IN TRANSIT FROM OPEN TO CLOSE BUT STUCK IN A PARTIALLY OPEN POSITION. AN AMOCO TECHNICIAN WAS CALLED AND ARRIVED AT 0900. TCC AND TECHNICIAN WORKED TOCORRECT THE STUCK HEADGATE. AT APPROXIMATELY 0933, A SUN PRESSURE RELIEF VALVE ACTIVATED, FILLING AN ELEVEN BARREL SUMP AT APPROXIMATELY 250 BPH. THE STATION SHUT DOWN ON A HAZARDOUS FAULT AT 0941. THE SUMP OVERFLOW WAS SEEN BY THE TECHNICIAN WHEN THE HAZARDOUS FAULT SOUNDED. THE TECHNICIAN RECEIVED HELP FROM ANOTHER AMOCO EMPLOYEE AND QUICKLY CLOSED THE MANUAL GATE VALVE AT 0953.THE TWO AMOCO EMPLOYEES IMMEDIATELY STARTED CONTAINMENT PROCEDURES AND NOTIFIED THE TERMINAL MANAGER. THE TERMINAL MANAGER THEN PROCEEDED WITH NOTIFICATION PROCEDURES. NRC WAS NOTIFIED AT 1135 AND ASSIGNED INCIDENT NUMBER 245897.INDIANA DEPT OF ENVIRONMENTAL MANAGEMENT WAS NOTIFIED AT 1145 AND ASSIGNED INCIDENT NUMBER 9406215. BY 1400 ALL FREE PRODUCT WAS CLEANED UP AND GROUND REMEDIATION STARTED. ALL CONTAMINATED SOIL WAS REMOVED BY JUNE 26, 1994.
2017-09-29 08:50 | YES | NO | 19940182 | 1994-08-08 | 18214 | SHAMROCK PIPE LINE CORP | NO | 1994-06-24 | 1315 | TX | RANDALL |  | NO |  | NO | SECTION 113, BLOCK 6, I^GN SURVEY, RANDALL COUNTY, TEXAS APPROX. 2 MILES SE OF THE CITY OF CANYON, TEXAS AT INTERSECTION OF HIX AND PONDASETTA LANE. |  | PUMPING STATION | PIPE |  | 1984 | OTHER | THERMAL PRESSURE PIPING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 35248.4024 | 71110.2651 | GASOLINE | 3 | 654 | 4 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1440 | 0 | YES | 8 | 1950 | 10 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA | COMPANY PROGRAM | Null | Null | GERALD CHILDERS | 8063783583 | AT APPROXIMATELY 1315 HOURS ON JUNE 24, 1994, A PUMP DISCHARGE LEAD RUPTUREDAT OUR PALO DURO PUMP STATION LOCATED IN RANDALL COUNTY 2 MILES SOUTHEAST OFCANYON, TEXAS. UPON INVESTIGATION IT WAS DISCOVERED THE PIPE HAD RUPTURED DUE TO THERMAL PRESSURE IN THE STATION PIPING. THE STATION HAS BEEN OUT OF SERVICE SINCE SEPTEMBER 1988. THE ACCIDENT ALLOWED 654 BARRELS OF GASOLINE AND DIESEL TO ESCAPE. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING TWO 45 DEGREE FITTINGS AND 2 FEET OF LINE WITH PRE-TESTED PIPE AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19940183 | 1994-08-26 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-07-27 | 138 | KS | SALINE |  | NO |  | NO | RANGE 2 W. TOWNSHIP 15 SOUTH, SECTION 34, SALINE COUNTY, KANSAS 3.5 MILES N./E. OF ASSARIA, KANSAS. |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 34474 | 25854.3282 | 52158.623 | GASOLINE | 3 | 1342 | 80 | NO | NO | 8.63 | 0.16 | 52000 | WELDED |  | 1350 | 1200 | YES | 24 | 1802 | 0 | 69 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH | 9185811800 | CENTRAL DISPATCH RECEIVED A RATE OF CHANGE ALARM SHOWING AN INCREASE IN FLOWAND A DECREASE IN PRESSURE. EMERGENCY PROCEDURES WERE IMPLEMENTED AND THE LINE WAS BLOCKED IN. THE LEAK WAS LOCATED AND THE CAUSE DETERMINED TO BE EXTERNAL CORROSION. THE DAMAGED SECTION WAS REPLACED AND THE LINE RETURNED TO SERVIC
2017-09-29 08:50 | NO | NO | 19940184 | 1994-08-26 | 15490 | PHILLIPS PIPE LINE CO | YES | 1994-07-26 | 1330 | MO | PETTIS |  | NO |  | NO | BORGER-E. CHICAGO "BLUE" LINE - MP 500 51+60 SEC. 6, T44N, R22W |  | LINE PIPE | PIPE |  | 1942 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 13499.3882 | 27233.7186 | L. P. G. | 2 | 1 | 0 | NO | NO | 8.63 | 0.19 | 40000 | WELDED |  | 1180 | 500 | YES | 8 | 1615 | 8 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D. R. DUBOIS | 9186616267 | MAINTENANCE CREW PERSONNEL HEARD A FAINT BURPING NOISE FROM CASING VENT PIPE. DETECTED HYDROCARBON VAPORS WITH LEL METER. BLOCKED IN LINE, STOPPLED, AND REPLACED WITH NEW PIPE. AFTER REMOVAL, ANALYSIS OF THE PIPE INDICATED AN EXTREMELY SMALL MANUFACTURING DEFECT THAT WAS NOT DETECTABLE DURING HYDROTESTING.PROPERTY DAMAGED EXCEEDED $5,000 BECAUSE THE LINE CONTAINED HVL AND IN-LINE REPAIRS WERE NOT PRACTICAL.
2017-09-29 08:50 | YES | NO | 19940185 | 1994-08-25 | 22610 | WILLIAMS PIPELINE CO | YES | 1994-07-23 | 1045 | KS | MONTGOMERY |  | NO |  | NO | SOUTHWEST CORNER OF THE SOUTHWEST QUARTER OF SECTION 32, TOWNSHIP 34S, RANGE 15 EAST IN MONTGOMERY COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1933 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 48747.7906 | 98343.9837 | GASOLINE | 3 | 340 | 20 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 600 | 450 | YES | 8 | 790 | 0 | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883850 | AT 1400 HOURS ON JULY 22, 1994, TULSA DISPATCHING NOTICED A LOSS IN THROUGHPUT AND IMMEDIATELY SHUT THE LINE DOWN AND PRESSURED THE SYSTEM UP FOR A STATIC PRESSURE CHECK. AT 1605 HOURS, THE AREA MAINTENANCE CREW WAS NOTIFIED THAT PRESSURE WAS CONTINUING TO DROP ON THE PIPELINE AND REQUESTED THE VALVE AT CANEY JUNCTION BE CLOSED FOR FUTHER LEAK ISOLATION, WHICH WAS COMPLETED AT 1900HOURS. AT THIS TIME THE RIGHT-OF-WAY WAS DRIVEN TO INSPECT FOR LEAKS AT ROADCROSSINGS. AT 1930 HOURS, EXCAVATION CONTRACTORS WERE CALLED TO ARRIVE AT THE SITE THE MORNING OF JULY 23. AT 0800 HOURS ON JULY23, THE MAINTENANCE CREW BEGAN WALKING THE LINE AND THE PILOT PATROL WAS DISPATCHED TO FLY OVER THE LINE TO LOOK FOR THE LEAK. AT 1000 HOURS, THE PILOT PATROL DISCOVERED THE LEAK NEAR MILE POST ELEVEN (11). BY 1045 HOURS, THE MAINTENANCE CREW AND EXCAVATION 1145 HOURS, A TEMPORARY PATCH WAS CLAMPED TO THE LINE STOPPING THE LEAK. BECAUSE OF HIGH "LEL" LEVELS IN THE REPAIR AREA, THE WELDING OF THE PERMANENT PATCH COULD NOT BE COMPLETED UNTIL 1930 HOURS, AT WHICH TIME THE LINE WAS PLACED BACK IN SERVICE. CLEANUP OF THE LEAK AREA BEGAN ON JULY 23, 1994, BY DIGGING TRENCHES TO DETERMINE THE EXTENT OF THE CONTAMINATED AREA. THE DITCHES WERE THEN IGNITED TO REMEDIATE THE FREE PRODUCT PRESENT. ADDITIONAL DITCHES WEREEXCAVATED ON JULY 24, WHICH WERE ALSO IGNITED. THE CONTAMINATED SOILS WERE THEN LAND FARMED AND ARE EXPECTED TO BE PLACED BACK IN THE EXCAVATED AREA DURING THE LATTER PART OF 1994.
2017-09-29 08:50 | YES | NO | 19940186 | 1994-08-24 | 22610 | WILLIAMS PIPELINE CO | YES | 1994-07-18 | 530 | IL | MENARD |  | NO |  | NO | NE CORNER OF NW 1/4 OF SECTION 19, TOWNSHIP 18 NORTH, RANGE 6 WEST IN MENARD COUNTY, ILLINOIS. |  | LINE PIPE | TANK |  | 1936 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 41248.1305 | 83214.14 | GASOLINE | 3 | 200 | 72 | NO | NO | 12.75 | 0.3 | 35000 | WELDED |  | 750 | 567 | YES | 8 | 1043 | 0 | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883850 | AT 2115 HOURS ON JULY 17, 1994, WILLIAMS PIPE LINE COMPANY (WPL) WAS NOTIFIED OF A SUSPECTED LEAK NEAR MP 545. AT THAT TIME, THE LINE WAS SHUT DOWN AND PRESSURED UP FOR STATIC PRESSURE LOSS MONITORING; THE OPERATOR AT MENARD TERMINAL WAS INSTRUCTED TO CLOSE THE VALVE AT MP 544; AND THE AREA MAINTENANCE CREW WAS DISPATCHED TO THE SCENE. THE AREA MAINTENANCE CREW ARRIVED AT THE SITE AT 0145 HOURS ON JULY 18, 1994 AND DISCOVERED PRODUCT ESCAPING FROM DRAIN TILE AT APPROXIMATELY 0200 HOURS AT WHICH TIME AN EXCAVATING CONTRACTOR WAS CONTACTED AND CONTAINMENT AND ABSORBENT BOOMS WERE PLACED IN THE DRAINAGE DITCH. THE EXCAVATING CONTRACTOR ARRIVED AT THE SITE AT 0330 HOURS AND BY 0530 HOURSTHE LEAK AREA WAS DISCOVERED AND EXCAVATION OF THE PIPELINE COMMENCED. THE EXCAVATION, HAMPERED BY HIGH "LEL" LEVELS IN THE AREA, CONTINUED UNTIL 1500 HOURS WHEN THE LEAK WAS DISCOVERED. THE LEAK WAS FOUND TO BE A RESULT OF A PIN HOLE IN A GIRTH WELD. AT 1600 HOURS, THE LEAK STOPPED BY "CLAMPING OFF" THE LEAK WITH A FULL ENCIRCLEMENT SLEEVE AND RUBBER STOPPER. AT 1930 HOURS, THE REPAIR OPERATION WAS HALTED AGAIN DUE TO HIGH "LEL" LEVELS WERE SAFE FOR WELDING. ON THE MORNING OF JULY 19, 1994, THE MAINTENANCE CREW RETURNED TO THE LEAKSITE AND COMPLETED THE WELDING OF THE FULL ENCIRCLEMENT SLEEVE AND PUT THE LINE BACK IN SERVICE AT 1300 HOURS. REMEDIATION ACTIVITIES BEGAN BY AUTHORIZING BORINGS TO BE MADE TO DEFINE THE EXTENT OF THE CONTAMINATION AND TO MONITORTHE QUALITY OF THE GROUNDWATER. FURTHER REMEDIATION WAS HALTED AWAITING THE APPROVAL OF THE LANDOWNER REGARDING OUR PROPOSED REMEDIATION PLAN BASED UPON THE BORING ANALYSIS.
2017-09-29 08:50 | YES | NO | 19940187 | 1994-08-23 | 1036 | BADGER PIPELINE CO | YES | 1994-07-27 | 800 | IL | DUPAGE | OAK BROOK | NO |  | NO | ON THE WEST SIDE OF ILLINOIS HIGHWAY 83 JUST NORTH AT 22ND STREET |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 74996.601 | 151298.4364 | OIL AND GASOLINE | 1 | 3100 | 47 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 1000 | 0 | YES | 8 | 1250 | 0 | 54 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAY ANDERSON | 7084390270 | ON JULY 27 AT AROUND 08:00 BADGER PIPELINE EMPLOYEES DISCOVERED A LEAK ON OUR 12" PETROLEUM PRODUCT PIPELINE. BADGER PIPE LINE HAD RECEIVED REPORTS OF GASOLINE ODORS FROM AN ADJACENT BUILDING OWNER AND WAS DOING INVESTIGATIVE DIGGING. THE LEAK WAS FROM A 2 INCH CREASE ON THE UNDERSIDE OF THE PIPE. THE CAUSE OF THE LEAK APPEARS TO BE FROM OUTSIDE PARTY DAMAGE INCURRED DURING THE CONSTRUCTION OF AN ADJACENT BUILDING WAS FOUND TO BE POURED DIRECTLY UNDER THE LINE AND THE LINE WAS RESTING ON THE CONCRETE. IT APPEARS THAT THE PIPE WAS DENTED BY THE IMPACT OF A POWERED DIGGING MACHINE DURING THE INSTALLATION OF THE TIE BACKS. THE CONCRETE WAS THEN POURED AGAINST THE LINE. THIS WORK WAS DONE WITHOUT OUR KNOWLEDGE OR PERMISSION. OVER TIME THE DENT WEAKENED AND THE LINE BEGAN TO LEAK. THE LINE WAS REPAIRED BY INSTALLING A SLEEVE AND RETURNED TO SERVICE. ONCE THE LINE HAD BEEN FURTHER EXPOSED AND SEARCHED FOR DAMAGE WEWILL CUT OUT AND REPLACE THE DAMAGED SECTION. THE LINE IS ADJACENT TO A TEN STORY OFFICE BUILDING WITH AN UNDERGROUND PARKING GARAGE. THE LEAKING PRODUCTAPPEARS TO HAVE FOLLOWED THE FOUNDATION OF THE BUILDING DOWN AND WAS CONTAINED BY PERCHED GROUND WATER AT A DEPTH OF ABOUT 30 FEET. FOR THIS REASON THEREWAS NO PRODUCT ON THE SURFACE OF THE GROUND. INITIAL SOIL INVESTIGATIONS SHOW THAT THE PRODUCT IS CONTAINED IN AN AREA OF PERCHED GROUND WATER AT A DEPTHOF ABOUT 30 FEET. THE AREA OF CONTAMINATION IS APPROXIMATELY 100,000 SQUARE FEET. BECAUSE THE SPILL WAS FROM A SUBSURFACE WEEP IN THE PIPE ACCURATE LOSSES CANNOT BE CALCULATED AT THIS TIME. HOWEVER IT IS ESTIMATED TO BE BETWEEN 60,000 AND 130,000 GALLONS. WE HAVE STARTED RECOVERY AND AT THIS TIME HAVE RECOVERED APPROXIMATELY 47 BARRELS.
2017-09-29 08:50 | YES | NO | 19940188 | 1994-08-22 | 13131 | CONOCO INC | YES | 1994-07-21 | 1404 | OK | OTTAWA | WYANDOTTE | NO |  | NO | SEC. 28, T27N, R24E, OTTAWA COUNTY, OKLAHOMA RUPTURE OCCURRED 204 N. OF THE INTERSECTION OF BROADWAY & POPULAR |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 374983.0048 | 756492.1822 | L. P. G. | 2 | 1968 | 0 | YES | YES | 10 | 0.37 | 35000 | WELDED |  | 845 | 762 | YES | 4 | 1076 | 8 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | VANCE WEBB | 4057674845 | ON JULY 21, 1994 CONOCO PIPE LINE'S (CPL) MOUNT VERNON FACILITY RECEIVED A CALL FROM KEN STURDVANT WITH A-1 TELEPHONES, ADVISING OF A RUPTURE AND FIRE INTHE WYANDOTTE AREA. THE CALLER INDICATED THAT IT WAS DEFINITELY CPL'S LINE. MOUNT VERNON PERSONNEL IMMEDIATELY NOTIFIED CPL'S OIL MOVEMENTS GROUP IN HOUSTON TO SHUT DOWN THE WOOD RIVER SYSTEM (BOTH LINES #1 AND #2) AND ISOLATE THEWYANDOTTE SECTIONS OF THE LINE WITH THE NEAREST REMOTELY OPERATED VALVES. WHILE THE NOTIFICATIONS WERE TAKING PLACE EMERGENCY RESPONSE CREWS WERE DISPATCHED TO THE LOCATION TO CLOSE THE MANUALLY OPERATED VALVES LOCATED ON EITHER SIDE OF THE RUPTURE SITE. THIS WAS DONE TO FURTHER ISOLATE THE DAMAGED SEGMENTOF LINE. UPON ARRIVAL AT THE SITE OF THE RUPTURE AND FIRE COMPANY PERSONNEL COORDINATED WITH LOCAL EMERGENCY RESPONSE OFFICIALS TO ISOLATE THE AREAAND DISCUSS AVAILABLE OPTIONS FOR ADDRESSING THE SITUATION. AFTER ASSESSING THE SITUATION, THE RUPTURE WAS DETERMINED TO BE ON THE #1 WOOD RIVER 10" LINE. BASEDON THIS ASSESSMENT, RESTRICTED OPERATIONS OF THE #2 LINE WERE RESUMED AT 04:50 HRS ON 7-22-94. OPERATING PRESSURES WERE HELD TO 50% OF THE OPERATING PRESSURE AT THE TIME OF THE RUPTURE ON THE #1 LINE. AFTER FURTHER DISCUSSING THE SITUATION, IT WAS DECIDED THAT THE SAFEST OPTION WOULD BE TO ALLOW THE REMAINING PROPANE IN THE #1 LINE TO BURN ITSELF OUT. TO SPEED THIS PROCESS, PROPANEWAS LOADED OUT OF THE #1 LINE AND INTO TRUCKS VIA A TOR FITTING AT THE UPSTREAM BLOCK VALVE SITE. APPROXIMATELY 300 BBLS. WERE LOADED BEFORE THE PRODUCT BEGAN GOING TO VAPOR, DUE TO DECREASING PRESSURE IN THE LINE. AS AN ADDITIONAL MEASURE TO REDUCE THE VOLUME OF PROPANE IN THE LINE, A PROCESS OF MONITOREDVENTING WAS THEN BEGUN AT BOTH THE UPSTREAM AND DOWNSTREAM BLOCK VALVES. THIS PROCESS WAS ACCOMPLISHED VIA 2" STACKS FABRICATED ON SITE. AT 10:14 H RS ON7-24-94, THE REMAINING PROPANE IN THE LINE WAS CONSUMED AND THE FLAME EXTINGUISHED ITSELF. AFTER ALLOWING THE AREA TO COOL, AND INSURING THAT THE AREA WAS SAFE TO BEGIN REPAIRS, THE RUPTURED LINE WAS EXCAVATED AND APPROXIMATELY 83FEET OF PIPE WAS REPLACED. UPON COMPLETING THESE REPAIRS AND RESUMING NORMALOPERATION OF THE #1 LINE, THE #2 LINE WAS EXCAVATED AND EXAMINED FOR DAMAGE.NO DAMAGE WAS OBSERVED BY CPL PERSONNEL, OR RALPH HANLIN, (DOT ONSITE INVESTIGATOR CENTRAL REGION). MR. HANLIN APPROVED RETURNING THE #2 LINE TO NORMAL OPERATING PRESSURE AT THE TIME (APPROX. 21:30 HRS ON 7-24-94).
2017-09-29 08:50 | YES | NO | 19940189 | 1994-08-22 | 13131 | CONOCO INC | YES | 1994-08-14 | 1100 | WY | PLATTE |  | NO |  | NO | GUERNSEY, WY S17, T26N, R65W RELEASE WAS CONTAINED IN A TANK DIKE AT CONOC'S GUERNSEY CRUDE STATION. |  | TANK FARM | PIPE |  | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 350 | 340 | NO | NO | 8 | 0.25 | 25000 | WELDED |  | 20 | 15 | YES | 4 | 150 | 0 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHNNA S. VAN KEAREN | 3036494127 | DISPOSAL FO CRUDE CONTAMINATED SOIL (108 YDS) : $1000.00.
2017-09-29 08:50 | YES | YES | 19940190 | 1994-08-19 | 19226 | TEXACO PIPELINE INC | YES | 1994-07-15 | 1500 | KS | WYANDOTTE |  | NO |  | NO | NE 1/4, SECTION 3, TOWNSHIP 11S, RANGE 24E WYANDOTTE COUNTY, KANSAS |  | LINE PIPE | OTHER | TEMPORARY HOSE | 1994 | OTHER | HOSE TO PIPELINE FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES H. PYEATTE | 9185853344 | DURING PROCESS OF VENTING AIR OUT OF THE PIPELINE SYSTEM UTILIZING A 3" HOSETEMPORARY ATTACHED TO A 2" VENT VALVE AND THE PIPELINE, THE 3" HOSE FAILED. THE HOSE FAILURE ALLOWED THE AIR, POSSIBLY WET WITH A TRACE OF GASOLINE, TO BE RELEASED INTO THE ATMOSPHERE. DURATION OF RELEASE APPROXIMATELY 30 SECONDS.ACCIDENT DID NOT RESULT IN ANY LIQUIDS TO BE RELEASED ONTO THE ADJACENT SOIL. ANY PRODUCT, IF RELEASED, WAS IN VAPOR FORM AND DISSIPATED INTO THE AIR.
2017-09-29 08:50 | YES | NO | 19940191 | 1994-08-19 | 18273 | SHELL PIPELINE CORP | NO | 1994-07-14 | 1330 | CA | KERN |  | NO |  | NO | BAKERSFIELD 14-INCH CRUDE PIPELINE |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 41248.1305 | 83214.14 | CRUDE OIL | 1 | 137 | 50 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 400 | YES | 24 | 1600 | 0 | 67 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132
2017-09-29 08:50 | YES | NO | 19940192 | 1994-08-19 | 18273 | SHELL PIPELINE CORP | YES | 1994-07-14 | 1915 | LA | LAFOURCHE |  | NO |  | NO | CLOVELLY-NORCO 24-INCH PIPELINE |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 299986.4038 | 605193.7458 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 24 | 0.31 | 60000 | WELDED |  | 720 | 329 | YES | 24 | 1404 | 0 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR | DAMAGE BY OTHERS | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132 | UNABLE TO DETERMINE WHETHER DAMAGE OCCURRED DU RING CONSTRUCTION OF THE PIPELINE OR DURING CONSTRUCTION OF OTHER PIPELINES IN THE AREA. DAMAGE WAS NOT NEW - INITIAL DAMAGE MAY HAVE OCCURRED 14 YEARS AGO.
2017-09-29 08:50 | YES | NO | 19940193 | 1994-08-11 | 13131 | CONOCO INC | YES | 1994-04-15 | 2015 | MT | MISSOULA |  | NO |  | NO | SEC 8, T13W, R19W |  | PUMPING STATION | OTHER | NOT GIVEN | 1953 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 44997.9606 | 90779.0619 | GASOLINE | 3 | 75 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W. BEGGS | 3036494090 | FAILURE OF O-RING GASKET ON SCRAPER TRAP CLOSURE, RESULTING IN LOSS OF 75 BARRELS OF REGULAR LEADED GASOLINE.
2017-09-29 08:50 | YES | NO | 19940194 | 1994-08-18 | 3369 | DIAMOND SHAMROCK CORP | YES | 1994-07-16 | 1300 | TX | PARKER |  | NO |  | NO | S.COBB SURVEY, ABSTRACT 221, PARKER COUNTY, TX. APPROX. 2 MILES W. OF WHEATLAND, TX ON HWY 377, N. 2 MILES ON KELLY RD TO JAKES TRAIL AND 3/4 MILES EAST. |  | LINE PIPE | PIPE |  | 1990 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 4049.8165 | 8170.1156 | NATURAL GAS LIQUID | 2 | 301 | 0 | NO | NO | 8 | 0.2 | 52000 | WELDED |  | 1760 | 750 | YES | 24 | 2436 | 1 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GERALD CHILDERS | 8063783583 | AT APPROXIMATELY 1300 HOURS ON JULY 16, 1994, A CONTRACTOR DRILLING HOLES FOR ELECTRIC POWER POLES DRILLED INTO AND PUNCTURED OUR 8" TRANS TEXAS PRODUCTSPIPELINE LOCATED IN PARKER COUNTY APPROXXIMATELY 2 MILES WEST OF WHEATLAND, TEXAS. THE ACCIDENT ALLOWED 301 BARRELS OF BUTANE TO ESCAPE. THE PRODUCT DID NOT IGNITE AND NO INJURIES WERE SUSTAINED. THE PIPELINE WAS REPAIRED WITHOUT INCIDENT BY REPLACING 40 FEET OF LINE WITH PRE-TESTED PIPE AND RETURNED TO SER
2017-09-29 08:50 | YES | NO | 19940195 | 1994-08-18 | 12628 | MOBIL PIPELINE CO | NO | 1994-07-13 | 2310 | TX | MIDLAND | MIDLAND | NO |  | NO | 1/2 MILE SOUTH OF U.S 80 1/2 MILE EAST ON INDUSTRIAL AVE. IN THE MOBIL TANK FARM TANK NO. 2726. |  | TANK FARM | TANK |  | 1957 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 149993.2019 | 302596.8729 | NOT GIVEN | 1 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | OTHER | NOT GIVEN | Null | Null | T.P. MURPHY | 2146583869 | AT APPROX. 11:00 TO 11:10 P.M. DURING A SEVERE LIGHTNING AND RAIN STORM, TANK NO.2726 WAS STRUCK BY LIGHTNING. AT 11:10 P.M. WHILE ROUTINELY CHECKING ROOF DRAINS ON THE TANKS GARY MOSLEY NOTICED THE GLOW OF FIRE ON TOP OF TANK 2726. GARY RADIOED BACK TO JANET SMITH IN THE CONTROL ROOM TO CALL TERRY LOUGH FOR ASSISTANCE. JANET CALLED TERRY AT 11:26 P.M. TERRY NOTIFIED JOHN TURNER. AT THIS TIME GARY WENT UP THE TANK WITH AN ANSUL 30# EXTINGUISHER IN AN ATTEMPT TO CONTROL THE FIRE. WHEN TERRY LOUGH ARRIVED AT APPROX. 11:50 P.M., HE JOINED GARY WITH HIS FIRE EXTINGUISHER. THE MIDLAND FIRE DEPT. ARRIVED ON THE SCENE AT APPORX. 12:A.M. WITH A SMALL PUMPER TRUCK/ A LARGER WATER TANK TRUCK WAS ALSO ORDERED AT THIS TIME TO SUPPLEMENT WATER SUPPLY. MIDLAND FIRE DEPT. HAD ONLY ONE PALE OF FOAM AVAILABALE FOR USE. TERRY LOUGH AND TOMMY SIX IMMEDIATEALY STARTED CALLING SUPPLY HOUSES FOR FOAM. AT 1:40 A.M. EDCO ARRIVED WITHSEVERAL PALES OF FOAM.. AT 2:11 A.M. THE TANK FIRE WAS EXTINGUISHED AND WATER SPRAYED AROUND TANK TO COOL DOWN THE METAL. NO ONE WAS INJURED AND THE TANKWAS PUMPED DOWN ITS LOW LEVEL LIMIT BY 8:45 A.M.
2017-09-29 08:50 | YES | NO | 19940196 | 1994-08-15 | 879 | CHEMOIL REFINING | NO | 1994-05-27 | 105 | CA | LONG BEACH |  | NO |  | NO | PIPELINE BREAK OCCURRED WITHIN THE CONFINES OF PROPERTY, LOCATED AT 2702 CALIFORNA AVE. LONG BEACH CA AND CONTAINED WITHIN A 2 ACRE TOPOGRAPHIC DEPRESION OF |  | LINE PIPE | PIPE | LONGITUDIAL WELD | 1923 | FAILED WELD | INCORRECT OPERATION | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 240000 | 179991.8423 | 363116.2475 | NOT GIVEN | 1 | 3150 | 3100 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 250 | 600 | YES | 4 | 400 | 11 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MILO SOTO | 3104248515 | ON MAY 27, 1994, THE CHEMOIL CARSON TANK FARM OPERATOR ON DUTY AT THE TIIME BEGAN TO SHIP A PRODUCT FROM THE TANK FARM TO GATX TERMINAL. THE COMPANY-ESTABLISHED PROCEDURE WAS TO CLOSE THE VALVE TO ISOLATE THE NO. 1 LINE TO AVOID SUBJECTING THE NO. 1 LINE TO THE HIGH PRESSURE THAT WOULD RESULT FROM THE SHIPMENT. THE OPERATOR FAILED TO CLOSE THE VALVE DESPITE THE COMPANY PROCEDURE. WHEN THE OPERATOR BEGAN SHIPPING AT THE PRESSURE OF 240 POUNDS PER SQUARE INCH("PSI") EXERTED BY THE FIRST PUMP, HE FAILED TO NOTE THAT THE PRESSURE CHARTFOR NO. 1 LINE SHOWED 240 PSI, WHICH MEANT THAT NO. 1 LINE WAS UNDER PRESSURE. AFTER THE OPERATOR STARTED THE SECOND PUMP, THE DISCHARGE PRESSURE INCREASED TO 600 PSI, (WHICH IS THE NORMAL PRESSURE WHEN SHIPPING TO GATX.) A SHORT LENGTH OF A WELD ON NO. 1 LINE FAILED AFTER THE PUMPS SUBJECTED THE LINE TO THE PRESSURE OF 600 PSI FOR 5 TO 10 MINUTES. THE WELD FAILURE CAUSED THE PRODUCT SPILLING OUT ON THE STREET ON THE NORTH SIDE OF SUNNYSIDE CEMETERY, EAST OF CALIFORNIA AND WEST OF ORANGE AVENUE(S). PART B. SPECIFIC LOCATION - LAND COMMONLY KNOWN AS THE CALIFORNIA BOWL LOCATED EAST OF CALIFORNIA AVE. BOUNDEDTO THE NORTH BY SPRING ST. AND THE SOUTH BY THE NORTH SIDE OF SUNNYSIDE CEMETERY PROPERTY.
2017-09-29 08:50 | NO | NO | 19940197 | 1994-08-08 | 15681 | PLATTE PIPE LINE CO | YES | 1994-07-14 | 2030 | WY | PLATTE | GUERNSEY | NO |  | NO | SECTION 17, T26N, R65W, PLATTE COUNTY, GUERNSEY STATION 198 TANK FARM ROAD GUERNSEY, WY 82214. |  | PUMPING STATION | OTHER | SUMP | 1955 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CONDENSATE | 3 | 20 | 18 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | DAVID HISCOTT | 3072617221 | HEAVY RAINFALL (APPROX. 1.5" IN 20 MINUTES) CAUSED SUMP TO OVERFLOW. SUMP HAD BEEN PUMPED DOWN BY PREVIOUS DAY SHIFT. THE MAJORITY OF SPILL WAS RETAINED WITHIN THE STATION BY RETAINING WALLS. ADDITIONAL RAIN DURING CLEAN UP CAUSEDMATERIAL TO MIGRATE TO A FIELD ACROSS THE STATION. CLEAN UP WAS WITH SORBENTPADS. 18 BBLS ESTIMATE WERE RECOVERED. 2 BBLS LOST TO SOIL IN STATION/RETAINING WALLS.
2017-09-29 08:50 | NO | NO | 19940198 | 1994-08-10 | 15156 | SINCLAIR PIPELINE CO | NO | 1994-07-26 | 1055 | WY | NATRONA |  | NO |  | NO | NE/4 SEC 22, T. 30., R. 85 W. NATRONA COUNTY, WYOMING |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4499.7961 | 9077.9062 | CRUDE OIL | 1 | 10 | 0 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 800 | 330 | YES | 24 | 1000 | 0 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R.D. DANIELSON | 3073283578 | THE SPILL WAS DETECTED BY PIPELINE PERSONNEL THAT WERE MARKING THE PIPELINE RIGHT OF WAY. THE PIPELINE WAS SHUT DOWN, ISOLATED, AND EXCAVATED. THE LINE HAD BEEN DAMAGED BY EQUIPMENT WORKING IN THE VICINITY OF THE PIPELINE PROBABLEY YEARS AGO. THE EQUIPMENT STRIKING THE PIPE CAUSED A FLAT AREA IN THE PIPE AND CAUSED STRESS ON THE PIPE THAT PRODUCED THIS DISCHARGE. WE DO NOT BELIEVE THE PIPE BEGAN LEAKING WHEN THE PIPE WAS DAMAGED BUT STARTED LEAKING RECENTLY. SINCLAIR PERSONNEL REPLACED THE DAMAGED SECTION OF PIPE WITH NEW PIPE AND CLEANED UP THE SPILL SITE.
2017-09-29 08:50 | NO | NO | 19940199 | 1994-08-10 | 15156 | SINCLAIR PIPELINE CO | NO | 1994-07-13 | 1030 | WY | NATRONA | MILLS | NO |  | NO | 6250 ZERO ROAD MILLS, WYOMING 82644 |  | PUMPING STATION | OTHER | METER CASE | 1994 | OTHER | O RING FAILURE METER CASE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2999.864 | 6051.9375 | CRUDE OIL | 1 | 8 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.D. DANIELSON | 3073283578 | AT 10:30 A.M. ON JULY 13, 1994, AN O-RING ON A METER CASE FAILED AND STARTEDRELEASING CRUDE OIL ONTO THE SURROUNDING AREA. A SINCLAIR EMPLOYEE WAS ON SITE AT THE TIME THE O-RING MALFUNCTIONED AND WAS ABLE TO SHUT DOWN AND ISOLATETHE METER WITHIN THREE MINUTES. APPROXIMATELY 6-8 BBLS. OF CRUDE OIL WAS SPILLED.
2017-09-29 08:50 | YES | NO | 19940200 | 1994-08-04 | 9175 | JAYHAWK PIPELINE CORP | YES | 1994-03-24 | 700 | KS | HASKELL |  | NO |  | NO | SW/4 SECTION 23-T30S-R32W, HASKELL COUNTY, KANSAS 4 MILES SOUTH AND 2 EAST OF SUBLETTE, KANSAS |  | PUMPING STATION | PUMP |  | 1993 | OTHER | PUMP ROD BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4250 | 3187.3555 | 6430.1835 | CRUDE OIL | 1 | 900 | 860 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162651700 | THE AREA GAUGER ARRIVED AT 0700 AND OIL WAS SPILLING FROM THE PUMP AT JAYHAWK'S SUBLETTE STATION, HASKELL COUNTY, KANSAS. THE GAUGER SHUT PUMP DOWN AND CLOSED ALL VALVES. THE PROBLEM WAS TRACED TO ROD AND GLAND NUT BROKE ON PUMP LETTING THE OIL SPILL. THE TOTAL QUANTITY OF CRUDE OIL SPILLED WAS CONTAINED ON COMPANY PROPERTY INSIDE A DIKE AREA. AN ESTIMATED 900 BARRELS WAS OUT WITH 860 BARRELS BEING RECOVERED. THE OILY DIRT WAS REMOVED AND NEW TOP SOIL REPLACED. NEW PUMP ROD AND GLAND NUT WAS INSTALLED IN PUMP.
2017-09-29 08:50 | YES | NO | 19940203 | 1994-08-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-07-03 | 2337 | KS | KIOWA |  | NO |  | NO | SECTION 3, TOWNSHIP 29 SOUTH, RANGE 16 WEST OF KIOWA COUNTY, KANSAS |  | NO DATA | PUMP |  | 1960 | OTHER | SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2751 | 2063.1565 | 4162.22 | L. P. G. | 2 | 12 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.T. CRONK | 9185811800 | AT 22:49 CENTRAL DISPATCH RECEIVED A SEAL FAILURE INDICATION WHICH HAD AUTOMATICALLY SHUTDOWN THE MAINLINE UNIT. A TECHNICIAN ARRIVED AT 00:15 TO INVESTIGATE AND OBSERVED A LARGE VAPOR CLOUD OVER THE STATION. AT 23:37 CENTRAL DISPATCH RECEIVED THIRD PARTY NOTIFICATION BY PHONE OF A PRODUCT RELEASE AT THE PUMP STATION. LOCAL SHERIFF AND FIRE DEPARTMENT OFFICIALS WERE NOTIFIED OF THEINCIDENT. EMERGENCY RESPONDERS ARRIVED ON SITE, BLOCKED ROADS AND SECURED THE AREA. AT 02:20 WIND DISSIPATED VAPORS AWAY FROM THE SUCTION AND DISCHARGE VALVES. THE TECHNICIAN VERIFIED CAUSE OF THE RELEASE AS A SEAL FAILURE, REPLACED THE DEFECTIVE SEAL AND THE UNIT WAS RETURNED TO SERVICE. THE CHECK VALVE DID NOT COMPLETELY CLOSE DUE TO AN OBSTRUCTION IN THE CLAPPER, AND THE SUCTIONVALVE DID NOT CLOSE COMPLETELY DUE TO BEING SLIGHTLY OUT OF ADJUSTMENT. AFTER THE SEAL WAS REPAIRED, THE SUCTION VALVE AND DISCHARGE CHECK VALVE PROBLEMS WERE CORRECTED BEFORE RESTARTING THE PUMP. THE SEAL REPAIR WAS COMPLETED AND THE UNIT RETURNED TO DISPATCHERS AT 09:15.
2017-09-29 08:50 | YES | NO | 19940204 | 1994-08-08 | 2337 | CHEVRON PIPELINE CO | NO | 1994-07-01 | 1230 | TX | JEFFERSON | BEAUMONT | NO |  | NO | ROUTE 3, BOX 330, BEAUMONT, TEXAS 77705 |  | TANK FARM | PIPE |  | 1952 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5999.7281 | 12103.8749 | CRUDE OIL | 1 | 500 | 498 | NO | NO | 10 | 0.38 | 0 | WELDED |  | 250 | 0 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | LACK OF FLOW IN PIPE. | NO DATA |  | Null | NO DATA |  | Null | Null | PHILLIP C. DEPRANG | 7133637128 | THE LEAK WAS DUE TO INTERNAL CORROSION. ALL FREE OIL WAS PICKED UP WITH VACUUM TRUCKS AND RETURNED TO THE SYSTEM. THE LINE WAS REPAIRED WITH A REPAIR CLAMP AND THE PIPE WILL BE REPLACED AT A LATER DATE. ALL OILY SOIL WAS REMOVED TO A REMEDIATION AREA ON-SITE.
2017-09-29 08:50 | YES | NO | 19940205 | 1994-07-31 | 2337 | CHEVRON PIPELINE CO | YES | 1994-07-13 | 2300 | TX | MIDLAND | MIDLAND | NO |  | NO | 3400 EAST HIGHWAY 80, MIDLAND TEXAS 79701 |  | TANK FARM | TANK |  | 1927 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 749966.0095 | 1512984.3644 | NOT GIVEN | 1 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | LEO J. DELANEY | 7133637126 | AT APPROXIMATELY 11:40 P.M. ON JULY 13, 1994, TANK 1585 AT MESA MIDLAND STATION WAS STRUCK BY LIGHTNING AND IGNITED INSTANTLY BURNING IN THE SEAL AREA. THE FIRE DEPARTMENT WAS NOTIFIED IMMEDIATELY AND FIRE PERSONNEL REPORTED ON THE SCENE AT APPROXIMATELY 11:50 P.M. DUE TO INSUFFICIENT EQUIPMENT AND A FAILED ATTEMPT TO EXTINGUISH THE FIRE, THE DECISION WAS MADE TO LET THE FIRE BURN UNTIL MORNING. AFTER RECEIVEING SUFFICIENT EQUIPMENT AND FOAM THE FIRE WAS EXTINGUISHED USING THREE FOAM CANNONS APPLYING FOAM AT A RATE OF 1,200 GPM. THEFIRE WAS OFFICIALLY OUT AT 2:25 P.M. ON JULY 15, 1994.
2017-09-29 08:50 | YES | NO | 19940206 | 1994-07-31 | 2552 | COLONIAL PIPELINE CO | YES | 1994-06-29 | 1050 | AL | BIBB |  | NO |  | NO | LINE 1, 36 INCH OD P/L; 2 INCH BLEEDER VALVE; LINE #1 STATION 4339 + 97; NEAR COFFEE CREEK, BIBB CTY, AL |  | LINE PIPE | OTHER | 2" THREADED PIPE | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | GASOLINE | 3 | 200 | 51 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | ON THE MORNING OF JUNE 29, 1994, A COMPANY CONTRACTOR, WITH A COLONIAL EMPLOYEE/INSPECTOR PRESENT, WAS EXPOSING COLONIAL'S LINE 01, A 36-INCH OD PIPELINETO INSPECT A 2 INCH BLEEDER VALVE. AFTER LOCATING THE LINE, THE BACKHOE OPERATOR DUG TO THE SIDE OF THE LINE UNTIL IT WAS EXPOSED. AFTER EXPOSING THE SIDE OF THE PIPELINE, THE OPERATOR BEGAN SLOUGHING DIRT OFF THE TOP OF THE LINE USING THE BUCKET BACKSIDE. IT WAS DURING THIS OPERATION THAT THE 2-INCH THREADED PIPE CONNECTING THE BLEEDER VALVE TO BECOM SEPARATED FROM THE PIPELINE WHICH RESULTED IN A STREAM OF GASOLINE SPRAYING FROM THE PIPELINE. THERE IS NO EVIDENCE THAT THE BACKHOE BUCKET ACTUALLY STRUCK THE BLEEDER VALVE; IT IS SURMISED THAT SUFFICIENT PRESSURE WAS EXERTED THROUGH THE SOIL TO DISLODGE THE VALVE. THE INCIDENT OCCURRED AT APPROXIMATELY 1050, CDT. THE COLONIAL INSPECTOR IMMEDIATELY EVACUATED THE CREW FROM THE AREA AND RADIOED THE OPERATOR AT PELHAM TANK FARM, THE NEAREST MANNED STATION, AND REQUESTED THE PIPELINE SHUT DOWN. ALL UPSTREAM PUMPING UNITS WERE SHUT DOWN AND THE LINE WAS BLOCKED AT VANCE STATION, THE FIRST UPSTREAM STATION, AT 1056, CDT. THE DOWNSTREAM PUMPINGUNITS WERE KEPT RUNNING TO PULL PRODUCT FORM THE SITE. ONCE THESE UNITS SHUTDOWN BECAUSE OF LOW SUCTION PRESSURE, THE LINE WAS BLOCKED DOWNSTREAM OF THEINCIDENTS. AFTER DETERMINING THE SAFETY OF ALL EMPLOYEES PRESENT, THE COLONIAL INSPECTOR ESTABLISHED A HOT ZONE AROUND THE LEAK SITE AND DISPATCHED PERSONNEL TO BLOCK TRAFFIC ON NEARBY STATE HIGHWAY 27 AND TO EVACUATE A NEARBY NEIGHBOR. LOCAL FIRE AND POLICE AUTHORITIES WERE NOTIFIED AT 1113, CDT. EMERGENCY RESPONSE PERSONNEL WERE DISPATCHED TO THE INCIDENT SITE AND BEGAN ARRIVING SHORTLY AFTER, 1200 CDT. THE NATIONAL RESPONSE CENTER WAS NOTIFIED OF THE INCIDENT AT 1135, CDT, REPORT NO 246688. THE ALABAMA DEPARTMENT OF ENVIRONMENTALMANAGEMENT AND THE EPA REGION IV WERE ALSO NOTIFIED OF THE INCIDENT. A COURTESY NOTIFICATION CALL WAS MADE TO THE SOUTHERN REGION OF THE OFFICE OF PIPELINE SAFETY. A REPRESENTATIVE OF THE OFFICE OF PIPELINE SAFETY ARRIVED AT THE SITE AT APPROXIMATELY 2000, CDT, ON THE 29TH. THE ESCAPED GASOLINE STREAM WAS CONTAINED BY THE PLACEMENT OF EARTHEN DAMS AND COLLECTION PITS IN A DITCH LOCATED DOWNSTREAM OF THE LEAK SITE. RECOVERY OPERATIONS COLLECTED 51 BARRELS OFTHE APPROXIMATE 200 BARRELS OF PRODUCT THAT IS ESTIMATED TO HAVE ESCAPED FROM THE PIPELINE. THE REMAINDER OF THE SPILLED PRODUCT EITHER EVAPORATED OR SATURATED INTO THE SURROUNDING SOIL. AFTER ALL THE FREE PRODUCT SURROUNDING THE INCIDENT SITE WAS COLLECTED AND THE AREA WAS MONITORED AND DETERMINED TO BE SAFE, THE THREADS ON THE 2-INCH THREAD-O-LET WERE RE-TAPPED AND A THREADED PLUG WAS INSTALLED IN THE PIPELINE. AN EXAMINATION OF THE PIPELINE REVEALED THATNO OTHER DAMAGE EXISTED AND THE LINE WAS RESTARTED AT 1756, CDT. CONTAMINATED SOIL HAS BEEN STOCKPILED ON PLASTIC ENVELOPES FOR DISPOSAL AT SOME LATER DATE. THE ENVIRONMENT SECTION IS PRESENTLY CONDUCTING TEST TO DETERMINE IF ADDITIONAL CONTAMINATION EXISTS.
2017-09-29 08:50 | YES | NO | 19940207 | 1994-08-04 | 809 | ARCO PIPE LINE CO | YES | 1994-07-12 | 1310 | NM | LEA |  | NO |  | NO | AT THE INTERSECTION OF STATE HWY 18 AND MARLAND BLVD, IN HOBBS, NEW MEXICO, GO 1.7 MILES E. ON MARLAND BLVD.; S1/4 OF SEC.36, T-18-S, R-38-E,LEA CNTY, NM |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22498.9803 | 45389.5309 | CRUDE OIL | 1 | 317 | 120 | NO | NO | 6 | 0.22 | 24000 | WELDED |  | 770 | 20 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RICHARD L. TRANTHAM | 9156822576 | DOZER BELONGING TO WASTE MANAGEMENT OF SOUTHEAST NEW MEXICO STRUCK LINE WITHBLADE DAMAGING PIPELINE. LINE WAS MARKED. MARKERS LOCATED NEAR SECTION THAT WAS DAMAGED.
2017-09-29 08:50 | YES | NO | 19940208 | 1994-08-03 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1994-06-30 | 1830 | MN | ITASCA |  | NO |  | NO | LAKEHEAD MILEPOST 997.7 APPROXIMATELY 1/4 MILE NORTH OF U.S. HIGHWAY 2 AND 2 MILES EAST OF DEER RIVER, MINNESOTA IN ITASCA COUNTY |  | LINE PIPE | LONGITUDINAL WELD |  | 1967 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 374983.0048 | 756492.1822 | CRUDE OIL | 1 | 50 | 5 | NO | NO | 34 | 0.34 | 52000 | WELDED |  | 611 | 340 | YES | 8 | 816 | 9 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD A. SANDALL | 2187250102 | LAKEHEAD PERSONNEL BASED AT THE COMPANY'S DEER RIVER, MN PUMP STATION WERE NOTIFIED OF AN ODOR BY A LANDOWNER AT 18:30 MST, JUNE 30, 1994. THE CONTROL CENTER WAS IMMEDIATELY NOTIFIED AND ALL THREE LINES IN THE AREA WERE SHUTDOWN AND ISOLATED AT 18:34 MST. LAKEHEAD PERSONNEL INVESTIGATED AND VISUALLY CONFIRMED THE LEAK AT 19:30 MST. A CRACK IN THE LONGITUDINAL WELD ON LAKEHEAD'S 34"LINE 3 WAS THE CAUSE OF THE LEAK WHICH OCCURRED IN A LOW LYING SWAMP. FLUMESWERE INSTALLED TO PREVENT FURTHER OIL MIGRATION AND ABSORBENT PADS WERE USEDTO RECOVER FREE OIL. A PLIDCO REPAIR SLEEVE WAS INSTALLED ON JULY 1, 1994. ACONTROLLED BURN OF THE RESIDUAL OIL WAS PERFORMED ON JULY 2, 1994, WITH THE APPROVAL OF THE MINNESOTA POLLUTION CONTROL AGENCY. THE FAILED JOINT WAS CUT-OUT AND REPLACED ON JULY 4, 1994. THE FAILED SECTION WILL UNDERGO METALLURGICAL ANALYSIS TO DETERMINE CAUSE, AND ACCORDINGLY, TOTAL PROPERTY DAMAGES REFLECT THIS DECISION. THE NATIONAL RESPONSE CENTER AND MINNESOTA STATE DUTY OFFICER WERE INITIALLY NOTIFIED OF THE INCIDENT. ADDITIONAL DETAILS WERE PROVIDED IN COMMUNICATIONS WITH THE OFFICE OF PIPELINE SAFETY - CENTRAL REGION.
2017-09-29 08:50 | NO | NO | 19940209 | 1994-08-29 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1994-07-15 | 1810 | CA |  |  | NO |  | NO | MARINE TERMINAL #2 1300 PIER B STREET LONG BEACH, CA 90813 |  | LINE PIPE | PIPE |  | 1938 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 720 | 0 | YES | 4 | 900 | 11 | 89 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT A. PFANNSTIEL | 3104289453 | INTERNAL CORROSION LEAK ON BOTTOM SECTION OF PIPE. AFFECTED SECTION OF PIPE W
2017-09-29 08:50 | YES | NO | 19940210 | 1994-10-24 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-09-23 | 1847 | IA | MONONA |  | NO |  | NO | SECTION 17,T83N,R46, MONONA COUNTY,IOWA |  | NO DATA | SCRAPER TRAP |  | 1968 | OTHER | O-RING SPLIT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 206.2407 | 416.0707 | ANHYDROUS AMMONIA | 2 | 13 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH | 9185811800 | CENTRAL DISPATCHER NOTIFIED MAPL PERSONNE OF A POSSIBLE RELEASE NEAR A.M. 271. UPON INVESTIGATION, IT WAS DETERMINED THE O-RING SEAL OF THE SCAPER TRAP CLOSURE HAD FAILED DUE TO MECHANICAL DAMAGE CAUSED BY THE CLOSURE. THE SYSTEM WAS ISOLATED, DEPRESSURIZED AND THE O'RING REPLACED.
2017-09-29 08:50 | YES | NO | 19940211 | 1994-10-24 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-09-20 | 1040 | IA | CLINTON |  | NO |  | NO | SECTION 29,T81N,R6E, CLINTON COUNTY,IOWA, FOUR MILES W OF CLINTON, IOWA |  | LINE PIPE | OTHER | FILTER POT (VESSEL) | 1993 | OTHER | FIRE CAUSED FROM AUTO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14.9993 | 30.2597 | NOT GIVEN | 3 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY D. SMITH | 9185811800 | DURING ROUTINE FILTER ELEMENT REPLACEMENT OF METER RUN FILTERS, AUTO-IGNITION CAUSED USED FILTER ELEMENTS TO IGNITE AS A RESULT OF EXPOSURE TO AIR. THE FIRE WAS EXTINGUISHED AND NEW FILTERS WERE INSTALLED.
2017-09-29 08:50 | YES | NO | 19940212 | 1994-09-26 | 1044 | WESTTEX 66 PIPELINE CO | YES | 1994-08-26 | 1130 | NM | LEA |  | NO |  | YES | LINE 80-11 EX.-STA.877+90 - ARTESIA TO LEA SECTION 29,T17S,R32E APPROXIMATELY 10 MILES SOUTH OF MALJAMAR, NM |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 9283 | 6961.9345 | 14045.0339 | NATURAL GAS LIQUID | 2 | 593 | 0 | NO | NO | 3.5 | 0.12 | 35000 | WELDED |  | 1350 | 400 | YES | 8 | 1920 | 11 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.R. DUBOIS | 9186616267 | A BACKHOE STRUCK LINE 80-11 EXT. WHILE EXCAVATING ANOTHER COMPANY'S CRUDE OILLINE. LINE 80-11 EXT. LINE MARKERS WERE LOCATED NEARBY. THE CONTRACTOR FAILED TO MAKE A "ONE-CALL"NOTIFICATION. LINE 80-11 EXT. WAS NOT FLOWING AT THE TIME OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19940213 | 1994-10-17 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1994-09-13 | 350 | IL | GRUNDY |  | NO |  | NO | 4755 EAST ROUTE 6 ,MORRIS, IL |  | TANK FARM | OTHER | RELIEF VALVE ON TANK | 1975 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 680000 | 509976.8865 | 1028829.3678 | NATURAL GAS LIQUID | 3 | 500 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GEORGE ROOD | 7138537876 | ON TUESDAY MORNING SEPTEMBER 13, 1994 AT APPROXIMATELY 0355 HRS. AN ABOVE GOUND STORAGE SPHERE CONTAINING NATURAL GASOLINE OVERFILLED AND DISCHARGED THROUGH A RELIEF VALVE AT ENRON LIQUIDS PIPELINE STORAGE FIELD AT MORRIS, ILLINOIS. NATURAL GASOLINE WAS BEING DELIVERED INTO THE SPHERE FROM ELPC'S 105 PIPELINE A FLOW RATE OF APPROXIMATELY 1700 BPH. THE OPERATOR ON DUTY WS AT THE COMPUTER CONTROLS WAITING FOR THE HIGH LEVEL ALARM INDICATING TO SWITCH THE FLOWFROM THE NG SPHERE TO ELP'S 107 PIPELINE TO LEMONT, ILLINOIS. THE ALARM NEVERCAME. THE SENSING LINE TO A PRESSURE TRANSMITTER USED IN THE LEVEL DETECTIONSYSTEM WAS CLOGGED AND THEREFORE THE LEVEL SYSTEM DID NOT DETECT THE "FULL"CONDITION. THE SPHERE OVERFILLED RELEIVING NATURAL GASOLINE THROUGH TWO 6 INCH RELIEF VALVES TO GRADE INSIDE A DIKE AROUND THE SPHERE. THE NATURAL GASOLINE VAPORS SPREAD AND ACTIVATED A HAZARDOUS ATOMSPHERE MONITOR (HAM). WHILE THEOPERATOR WAS INVESTIGATING THE CAUSE FOR THE HAM ALARM THE VAPORS WERE IGNITED BY A SALT BATH HEATER. THE NG FIRE HEATED A NEARBY METHANOL TANK CAUSING FAILURE OF THE TANK AND IGNITED APPROXIMATELY 6,000 GALLONS OF THE METHANOL. IN ADDITION, THE SALT BATH HEATER WAS DAMAGED AND SEVERAL OTHER PIPELINE COMPONENTS WERE EXPOSED TO EXTREME HEAT. THERE WERE NO DEATHS OR INJURIES AS A RESULTS OF THIS ACCIDENTS. DAMAGE IS ESTIMATED TO BE $200,000. SUPPLEMENTALREPORT 5/22/95 INCIDICATES A CHANGE IN TOTAL PRPTY DAMAGE, FROM 200,000 TO$680,000. THERE IS ALSO A CHANGE IN THE TOTAL AMOUNT OF COMMODITY SPILLED,WHICH WAS ORIGINALLY REPORTED AS 0. IT IS NOW 500 BARRELS. (NATURAL GASOLINE).
2017-09-29 08:50 | NO | NO | 19940214 | 1994-09-29 | 18273 | SHELL PIPELINE CORP | YES | 1994-08-26 | 915 | TX |  |  | YES | X-2,764,088,Y-140,023 | NO | SOUTH PASS 70C PLATFORM GULF OF MEXICO |  | LINE PIPE | PIPE |  | 1977 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 34000 | 25498.8443 | 51441.4684 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 8 | 0.5 | 42000 | WELDED |  | 1440 | 400 | YES | 24 | 2164 | 0 | 77 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132
2017-09-29 08:50 | YES | NO | 19940215 | 1994-09-06 | 2337 | CHEVRON PIPELINE CO | YES | 1994-08-06 | 1300 | TX | BORDEN | GAIL | NO |  | NO | MILE 115.20 ON THE SNYDER TO WINK LINE. |  | LINE PIPE | LONGITUDINAL WELD |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20500 | 15374.3032 | 31016.1795 | CRUDE OIL | 1 | 437 | 280 | NO | NO | 10.75 | 0.25 | 1953 | WELDED |  | 1200 | 1145 | YES | 8 | 1500 | 0 | 81 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | LEO J. DELANEY | 7133637126 | ON SATURDAY, AUGUST 6,1994, A CPL DISPATCHER NOTICED A DROP IN PESSURE AND INCREASED FLOW RATE AT NORTH SNYDER STATION. AT THE SAME TIME, THE DISPATCHER DISCOVERED A DECREASE IN FLOW AT THE RECEIVING STATION AT WINK. THE DISPATCHER IMMEDIATELY SHUT THE SYSTEM DOWN AND IMPLEMENTED EMERGENCY CALL OUT PROCEDURES. A PATROL PLANE WAS CALLED TO FLY THE LINE AND SUBSEQUENTLY A SPILL WAS DISCOVERED. THE SPILL WAS DUE TO LOCALIZED EXTERNAL CORROSION ALONG A LONGITUDINAL WELD WHICH WEAKENED THE SEAM CAUSING AN EIGHT FOOT SPLIT DOWN THE WELD. THE BAD SECTION OF PIPE WAS REPLACED WITH PRETESTED COATED PIPE AND THE LINE RETURNED TO SERVICE. A SECTION OF THE PIPE WAS EXAMINED BY A METALLURGIST WHOCONFIRMED THE CAUSE TO BE LOCALIZED CORROSION IN THE WELD.
2017-09-29 08:50 | YES | NO | 19940216 | 1994-08-30 | 13131 | CONOCO INC | YES | 1994-08-16 | 1100 | WY | PLATTE |  | NO |  | NO | T26N, R65W,SECTION |  | TANK FARM | PIPE |  | 1949 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18749.1502 | 37824.6091 | CRUDE OIL | 1 | 350 | 340 | NO | NO | 12 | 0.25 | 25000 | WELDED |  | 150 | 15 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W. BEGGS | 3036494090 | DURING DAILY INSPECTION OF GUERNSEY STATION, CRUDE OIL WAS NOTICED POOLED INTHE TANK DIKE AREA NEAR TANK #71. ONCE THE CRUDE HAD BEEN DISCOVERED IN THE TANK DIKE, ALL OPERATIONS WERE SUSPENDED TO BEGIN CLEANUP OF CRUDE FROM THE TANK DIKE AREA WITH VACUUM TRUCKS. UPON EXCAVATING THE LINE, A SMALL PIN-HOLE LEAK WAS DISCOVERED IN THE 12-INCH FILL LINE TO TANK 71. THE SECTION OF PIPE CONTAINING THE PIN-HOLE WAS REMOVED AND REPLACED WITH A NEW PIECE OF LINE PIPE
2017-09-29 08:50 | YES | NO | 19940217 | 1994-09-07 | 15674 | PLANTATION PIPE LINE CO | YES | 1994-08-08 | 2004 | GA | GWINNETT |  | NO |  | NO | 146 FEET EAST OF ROYAL PALM COURT |  | LINE PIPE | PIPE |  | 1951 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 380000 | 284987.0836 | 574934.0585 | DIESEL FUEL | 3 | 450 | 431 | NO | NO | 14 | 0.38 | 35000 | WELDED |  | 1165 | 1163 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK | 4043645916 | AT APPROXIMATELY 8:04 P.M. EDT ON AUGUST 8, 1994, A LEAK WAS DISCOVEED ON PLANTATION'S 14-INCH, 0.375" WALL THICKNESS, GRADE B, PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN BREMEN, GEORGIA AND GREENSBORO, NORTH CAROLINA. THELEAK OCCURRED IN AN INDUSTRIAL DISTRICT OF THE METROPOLITAN ATLANTA AREA. THE SECTION OF THE PIPE THAT FAILED HAD A LONGITUDINAL CRACK APPROXIMATELY TWO INCHES LONG AT THE 4 O'CLOCK POSITION. THE PIPE FAILURE WAS CAUSED BY AN APPARENT MILL DEFECT. THE FAILED PIPE IS BEING ANALYZED BY A CONSULTANT. THE PIPELINE WAS REPAIRED BY REPLACING APPROXIMATELY 41 FEET OF EXISTING PIPE WITH NEW HYDROSTATICALLY TESTED PIPE. THE LEAK WAS REPORTED TO THE NATIONAL RESPONSECENTER AS REPORT NO.254285.
2017-09-29 08:50 | YES | NO | 19940218 | 1994-10-06 | 11237 | T E PRODUCTS PIPELINE COMPANY, L P | YES | 1994-08-26 | 1500 | AR | UNION |  | NO |  | NO | UNION COUNTY, ARKANSAS, SECTION 28,TOWNSHIP 19S,RANGE 16W-APPROXIMATELY 3.5 MILES S.E. OF JUNCTION CITY, ARKANSAS. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 14699.3338 | 29654.4935 | GASOLINE | 1 | 111 | 103 | NO | NO | 4 | 0.24 | 1986 | WELDED |  | 650 | 30 | YES | 8 | 1162 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO |  | 7137593636 | AT APPROXIMATELY 1500 HOURS, CDT, AUGUST 26,1994, A LEAK WAS DISCOVERED ON OUR 4" SYSTEM IN UNION COUNTY, ARKANSAS. PERSONNEL WERE IMMEDIATELY DISPATCHEDTO THE LOCATION OF THE LEAK. AFTER ISOLATION OF THE SITE, IT WAS DETERMINED TIMBER CLEARING EQUIPMENT OPERATING ON THE RIGHT-OF-WAY HAD DRIVEN OVER THE PIPELINE AND HAD DEFORMED THE PIPE. THIS RESULTED IN A PIN HOLE FAILURE IN ANSAREA WHICH ALSO EXHIBITED EVIDENCE OF SURFACE CORROSION. REMOVAL OF THIS SECTION AND INSTALLATION OF NEW PIPE WAS COMPLETED AUGUST 2,1994. CLEAN-UP OPERATIONS WERE CONCLUDED AND THE SYSTEM RESTARTED AUGUST 27, 1994.
2017-09-29 08:50 | YES | NO | 19940219 | 1994-09-13 | 4906 | EXXON PIPELINE CO | YES | 1994-08-19 | 2130 | TX | PASADENA |  | NO |  | NO | EPC PASADENA STATION, 3403 PASADENA FREEWAY PASADENA, TEXAS 77503. |  | TANK FARM | TANK |  | 1977 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1499.932 | 3025.9687 | DIESEL FUEL | 1 | 285 | 285 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | YES | G.G. PERSYN | 7136565521 | EMERGENCY HIGH TANK LEVEL ALARM ON ABOVE GROUND DIESEL FUEL STORAGE TANK FAILED, CAUSING THE TANK TO OVERFLOW TEMPORARILY, UNTIL SHUT DOWN BY STATION OPERATOR. RELEASED PRODUCT WAS CONTAINED ON-SITE WITHIN THE TANK FIREWALL, AND WAS RECOVERED AND RETURNED BACK INTO THE PIPELINE SYSTEM.
2017-09-29 08:50 | YES | NO | 19940220 | 1994-09-12 | 2337 | CHEVRON PIPELINE CO | YES | 1994-08-22 | 700 | TX | ECTOR | GOLDSMITH | NO |  | NO | GOLDSMITH STATION |  | TANK FARM | BOLTED FITTING |  | 1962 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 749.966 | 1512.9844 | CRUDE OIL | 1 | 260 | 255 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LEO J. DELANEY | 7133637126 | HUMAN ERROR WAS THE CAUSE OF THE SPILL. THE FIELD GAUGER PREPARED TO RECEIVEOIL FROM ANOTHER COMPANY BUT FAILED TO OPEN THE RECEIVING TANK VALVE. WHEN PUMPING STARTED, THE LINE PRESSURE CAUSED THE PIPE TO PULL OUT OF THE DRESSERSLEEVE CAUSING THE SPILL. ALL OIL WAS CONTAINED INSIDE THE TANK BERM. A NEWDRESSER SLEEVE WAS INSTALLED AND PROCEDURES FOR RECEIVING OIL HAVE BEEN REVIEWED WITH THE GAUGER.
2017-09-29 08:50 | YES | NO | 19940221 | 1994-09-16 | 19226 | TEXACO PIPELINE INC | YES | 1994-08-27 | 930 | OK | PAYNE |  | NO |  | NO | NW 1/4,SECITON 36,T18N,R5E,PAYNE COUNTY,OK FROM THE INTERSECTION OF STATE HWY 33 AND HARMONY RD IN CUSHING,OK, GO 3/4 MILE, NORTH AND 400 FEET EAST. |  | LINE PIPE | OTHER | WELD ON ENCIRCLEMENT SLEE | 1979 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 7199.6737 | 14524.6499 | CRUDE OIL | 1 | 200 | 190 | NO | NO | 20 | 0.25 | 60000 | WELDED |  | 1080 | 1030 | YES | 24 | 1493 | 9 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | VICE PRESIDENT | 9185853344 | PIPELINE HAD BEEN PREVIOUSLY DAMAGED BY OUTSIDE FORCE IN 1979. A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED OVER THE DAMAGED SECTION OF PIPE IN MARCH OF 1979. ON 08/27/94, A RURAL RESIDENT NOTICED CRUDE OIL ODOR AND NOTIFIED APPROPRIATE PERSONNEL. LEAK WAS DISCOVERED AT 0930 AND LINE SHUT DOWN. AFTER PIPELINE WAS EXPOSED, A SMALL CRACK IN THE LONGITUDAL WELD OF THE PREVIOUSLY INSTALLEDFULL ENCIRCLEMENT SLEEVE WAS DISCOVERED. LINE WAS DRAINED AND REPAIRED USING14'-6" SECTION OF NEW PRETESTED PIPE.
2017-09-29 08:50 | YES | NO | 19940222 | 1994-09-20 | 22610 | WILLIAMS PIPELINE CO | YES | 1994-08-20 | 1445 | NE | WASHINGTON |  | NO |  | NO | SW 1/4,S3 1/4, SECITON 18,TOWNSHIP 18N, RANGE 12E IN WASHINGTON COUNTY,NE . |  | LINE PIPE | PIPE |  | 1951 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 3 | 0 | 0 | YES | NO | 12.75 | 0.31 | 42000 | WELDED |  | 1100 | 200 | YES | 8 | 1650 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | NOT GIVEN | YES | YES | STEVEN S. BALL | 9185883850 | A CONTRACTOR WAS HIRED TO REMOVE CASING FROM THE CARRIER PIPE UNDER AN ABANDONED RAILROAD CROSSING WHICH WAS INSPECTED BY A THIRD PARTY INSPECTION FIRM HIRED BY WILLIAMS PIPE LINE COMPANY (WPL). THE CONTRACTOR'S PERSONNEL FIRST EXCAVATED THE SOIL FROM AROUND THE CASING TO EXPOSE THE CASED CROSSING. AFTER EXPOSING THE CROSSING, THE CONTRACTOR BEGAN REMOVAL OF THE CASING WITH AN ACETYLENE CUTTING TORCH. AFTER APPROX. 50' OF CASING WAS REMOVED AT 14:45 HOURS, THE CONTRACTOR'S WORKER BURNED A PINSIZED HOLE THROUGH THE CARRIER PIPE RELEASING FUEL OIL AND PRODUCING A SMALL FIRE WHICH WAS QUICKLY EXTINGUISHED. CONTAINER VESSELS WERE QUICKLY PLACED AT THE END OF THE CASING WHERE THE PRODUCT DRIPPING FROM THE CARRIER PIPE WAS COLLECTED. WPL'S OPERATIONS CONTROL CENTERWAS IMMEDIATELY NOTIFIED AND DISPATCHED WPL FIELD MAINTENANCE PERSONNEL TO THE SITE FOR REPAIR. AT APPROX. 16:45 HOURS, THE MAINTENANCE CREW ARRIVED AT THE SITE TO CLAMP-OFF THE LEAK AND WELD A 6" PATCH OVER THE HOLE WHICH WAS COMPLETED BY APPROX. 22:30 HOURS. AT APPROX. 08:30 ON AUGUST 21, A NON DESTRUCTIVE TEST FIRM TESTED THE PREVIOUS DAY'S WELD REPAIR. THE WELD WAS DETERMINED TO BE SATISFACTORY AND AT 09:30 ON AUGUST 21, 1994, THE OPERATION OF THE PIPELINE WAS GIVEN BACK TO THE WPL OPERATIONS CONTROL CENTER.
2017-09-29 08:50 | YES | NO | 19940223 | 1994-09-20 | 10313 | KOCH PIPELINE INC | YES | 1994-08-30 | 1038 | MO | HARRISON | EAGLEVILLE | NO |  | NO |  |  | TANK FARM | OTHER | TANK SUMP | 1980 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 59997.2808 | 121038.7492 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHRIS WILKINS | 6124592424 | KOCH PIPELINES PERSONNEL DISCOVERED & RESPONDED TO CRUDE OIL FOUND NEAR TANK33 AT THE BETHANY TANK FARM. THE TANK WAS IMMEDIATELY ISOLATED, ALONG WITH AN ENHANCED PUMPING RATE TO HASTEN PROUCT REMOVAL. AN INTERNAL INSPECTION WAS CONDUCTED WITH A SMALL CORROSION PIT FOUND IN THE TANK SUMP AREA. THE TANK WILL BE PUT BACK IN SERVICE FOLLOWING REPAIR AND FURTHER COMPREHENSIVE INTERNALINSPECTION.
2017-09-29 08:50 | YES | NO | 19940224 | 1994-09-21 | 12628 | MOBIL PIPELINE CO | YES | 1994-08-24 | 1415 | TX | WISE |  | NO |  | NO | 1862 FROM VENT MARKER ON COUNTY LINE ROAD. OFF FM 407. |  | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 187491.5024 | 378246.0911 | CRUDE OIL | 3 | 4329 | 4172 | NO | NO | 16 | 0.25 | 42000 | WELDED |  | 800 | 293 | YES | 8 | 1001 | 2 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | NOT GIVEN | YES | NO | T.P. MURPHY | 2146583869 | KELLY-COPPEDGE INC., A CONTRACTOR FOR NATURAL GAS PIPELINE OF AMERICA WAS USING TRENCHING MACHINE TO LAY A 4" NATURAL GAS LINE. THE MACHINE HIT MOBIL'S 16" CRUDE OIL LINE AT APPROXIMATELY 14:15 ON AUGUST 24, 1994. NATURAL GAS PIPELINE CALLED IN THE LEAK AT 14:30. DISPATCHING CALLED CORSICANA. RAY PEARSON AT HEALDTON, DISPATCHED PERSONNEL TO THE LEAK SITE. CORISCANA PERSONNEL WERE DISPATCHED. VACUUM TRUCKS WERE DISPATCHED AT 16:06. THE NATIONAL RESPONSE WAS NOTIFIED. ALL REMEDIAL WORK TO BE HANDLED BY NATURAL GAS PIPELINE. CLEANUP ISTO BE TO MOBIL AND TRRC SPECIFICATION.
2017-09-29 08:50 | YES | NO | 19940225 | 1994-09-27 | 809 | ARCO PIPE LINE CO | YES | 1994-08-31 | 2140 | OK | OSAGE |  | NO |  | NO | 12 MILES WEST OF SKIATOOK, OKLAHOMA ON HIGHWAY 20, SOUTH 5 MILES ON RANCH ROAD. SECTION 12, TOWNSHIP 21 NORTH, RANGE 9 EAST. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 104995.2413 | 211817.811 | GASOLINE | 2 | 1493 | 161 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 720 | 300 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY E. GRAVES | 9156822576 | WATER HAD WASHED THE SOIL AWAY FROM THE TOP OF PIPE, LEAVING ONLY GRAVEL ANDROCKS AS COVER. TOP OF PIPE WAS EXPOSED TO ATMOSPHERE RESULTING IN ATMOSPHERIC CORROSION.
2017-09-29 08:50 | YES | NO | 19940226 | 1994-09-26 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-08-22 | 1500 | NE | LANCASTER |  | NO |  | NO | T10N,R8E,SECITON 34 LANCASTER COUNTY,NEBRASKA |  | LINE PIPE | GIRTH |  | 1968 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 3940 | 2954.8661 | 5961.1584 | ANHYDROUS AMMONIA | 2 | 7 | 0 | NO | NO | 8.63 | 0.16 | 46000 | WELDED |  | 1198 | 900 | YES | 24 | 1520 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.D. SMITH | 9185811800 | LANDOWNER REPORTED A DEAD SPOT IN VEGETATION. UPON INVESTIGATION, A PINHOLE LEAK WAS DISCOVERED. A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19940227 | 1994-10-03 | 22907 | WYCO PIPE LINE CO | YES | 1994-09-12 | 947 | SD | PENNINGTON | RAPID CITY | NO |  | NO | 3225 ELGIN ST RAPID CITY, SOUTH DAKOTA SECTION 33, TOWNSHIP 2N, RANGE 8N. |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 37498.3005 | 75649.2182 | GASOLINE | 1 | 147 | 30 | NO | NO | 4 | 0.15 | 50 | WELDED |  | 50 | 50 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | TO BE ANALIZED | NO DATA |  | Null | NO DATA |  | Null | Null | ADAMS | 3032866401 | WHILE CONDUCTING MONITORING WELL INSPECTION PRODUCT WAS FOUND IN OBSERVATIONWELL #1. THE SOURCE WAS FOUND TO BE 3 LEAKING LINES UNDER THE WEST DIKE WALLOF TANK #4. THESE LEAKS HAVE BEEN REPAIRED.
2017-09-29 08:50 | YES | NO | 19940228 | 1994-10-11 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-09-08 | 734 | IA | WOODBURY |  | NO |  | NO | T87N R47W SECTION 31, WOODBURY COUNTY,IOWA APPROXIMATELY 2.5 MILES WEST OF SALIX, IOWA. |  | PUMPING STATION | VALVE |  | 1993 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 269.9878 | 544.6744 | ANHYDROUS AMMONIA | 2 | 12 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.D. SMITH | 9185811800 | THERMAL RELIEF VALVE ON A PRODUCT FILTER VESSEL RELEVED AND THEN FAILED TO SEAT PROPERLY. RELIEF VALVE WAS REPLACED AND FILTER VESSEL WAS RETURNED TO SERVICE. SUPPLEMENTAL REPORT 1/19/95 INDICATES CHANGE IN PART F - ESTIMATED TOTALPROPERTY DAMAGE. THE AMOUNT OF LOSS IS AMENDED FROM 9 BARRELS TO 11.88 (12)BARRELS AT $20.00/BARREL = 237.60 PLUS 122 RELIEF VALVE REPLACEMENT. PARTG.3 - AMENDING LOSS FROM 9 BARRELS TO 11.88 (12) BARRELS.
2017-09-29 08:50 | YES | NO | 19940229 | 1994-10-11 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-09-08 | 550 | TX | CARSON |  | NO |  | NO | SECTION 129,I&GN RR5 SURVEY CARSON COUNTY,TEXAS |  | LINE PIPE | PIPE |  | 1967 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4021 | 3015.6133 | 6083.7101 | NATURAL GAS LIQUID | 2 | 220 | 0 | YES | NO | 6.63 | 0.14 | 42000 | WELDED |  | 1210 | 480 | YES | 24 | 1696 | 2 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL | PIPELINE WARNING SIGNS | Null | Null | L.D. SMITH | 9185811800 | ORIGINAL REPORT WAS A GRASS FIRE SET BY A LIGHTNING STORM. AFTER THE GRASS FIRE WAS EXTINGUISHED, ONE AREA CONTINUED TO BURN. UPON INVESTIGATION, IT WAS DISCOVERED THAT LIGHTNING HAD HIT IN THE VICINITY OF THE PIPELINE AND BURNED A SMALL HOLE IN THE LINE. THE LINE WAS BURIED APPROXIMATELY 3-1/2 TO 4FT. IN LIMESTONE SOIL. HE SECTION OF PIPE WAS SENT TO A METALLURGIST FOR EVALUATION AND VERIFICATION.
2017-09-29 08:50 | YES | NO | 19940230 | 1994-10-11 | 11237 | T E PRODUCTS PIPELINE COMPANY, L P | YES | 1994-09-11 | 1530 | TX | ORANGE |  | NO |  | NO | MANSFIELD FERRY ROAD, LAT.N30 3' 33.5", W 94 1' 47.6" |  | TANK FARM | TANK |  | 1977 | OTHER | ROOF TANK TO DEFLECT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | KEROSENE | 1 | 4965 | 4565 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593636 | SEPTEMBER 11, 1994, AT APPROXIMATELY 1530 HOURS CDT, AN UNAUTHORIZED RELEASEOF JET "A" KEROSENE FROM A TANK WAS DETECTED BY T.E. PRODUCTS PIPELINE COMPANY PERSONNEL. THE RELEASE RESULTED FROM A COMBINATION OF FACTORS. A HEAVY RAIN CAUSED THE CENTER OF THE TANK ROOF TO DEFLECT AND AN IMMPROPERLY SECURED MANWAY COVER ALLOWED PRODUCT TO ESCAPE THROUGH THE ROOF DRAIN. THERE WAS APPROXIMATELY 4,565 BARRELS OF PRODUCT TRANSFERRED FROM THE CONTAINMENT DIKE AREA TO TANKAGE, WITH THE REMAINDER LOST TO ABSORPTION INTO THE CONTAINMENT DIKE AREA. ALL PRODUCT WAS CONTAINED WITHIN THE TANK DIKE. IN-SITE REMEDIATION OF ALL AFFECTED SOIL IS UNDERWAY.
2017-09-29 08:50 | NO | NO | 19940231 | 1994-10-11 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1994-09-13 | 2315 | CA | IMPERIAL | NILAND | NO |  | NO | NILAND STATION AT 404 E. NOFFSINGER, NILAND, CA 92257 |  | PUMPING STATION | PUMP |  | 1973 | OTHER | LEAKING SEAL SURGE PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22498.9803 | 45389.5309 | DIESEL FUEL | 3 | 8 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | SPILL OCCURED ON SEPT 13,1994 AT 2310 HOURS AT THE NILAND STATION. DISCOVERED BY LUPE GARCIA, OPERATOR AT THE TERMINAL, WHO ARRIVED FOR NORMAL WORK DAY. TECHNICIAN REPLACED LEAKING SEAL ON SEPT. 14, 1994.
2017-09-29 08:50 | NO | NO | 19940232 | 1994-10-12 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1994-09-12 | 900 | CA | SAN BERNARDINO | BLOOMINGTON | NO |  | NO | SFPP COLTON STATION AT 2359 S. RIVERSIDE AVENUE BLOOMINGTON, CA 92316 |  | NO DATA | TANK |  | 1958 | OTHER | TANK C-9 CRACK IN WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN M. ABBOUD | 2134867720 | THE INITIAL LEAK WAS DISCOVERED BY A CHEVRON PERSONNEL AT APPROXIMATELY 0900AND WAS THOUGHT TO BE A CHEVRON OWNED VALVE AND GASKET. FURTHER INVESTIGATION DETERMINED THIS TO ACTUALLY BE A SFPP VALVE AND GASKET. THE SECOND LEAK WASDISCOVERED APPROXIMATELY 1200 WAS AROUND TANK C-9" REINFORCEMENT PLATE. THISWAS DEFINITELY DETERMINED TO BE A SFPP PROBLEM AND REPORTING WAS INITIATED AT THIS POINT. LEAK STOPPED AT 1600 ON SEPT 12, 1994. VALVE AND GASKED REPLACED AND REPAIR WAS DONE ON TANK REINFORCEMENT PLATE.
2017-09-29 08:50 | YES | NO | 19940233 | 1994-09-07 | 443 | AMOCO PIPELINE CO | YES | 1994-08-04 | 1145 | OK | LINCOLN |  | NO |  | NO | SE 1/4 OF NE 1/4 SECTION 9,T15N, R6E |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 12749.4222 | 25720.7342 | CRUDE OIL | 1 | 65 | 60 | NO | NO | 12 | 0.34 | 1360 | WELDED |  | 836 | 150 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | P.J. MCGANNON | 9184913565 | ON AUGUST 4, 1994 AT 11:20 A.M., A POTENTIAL LEAK WAS REPORTED BY AMOCO PIPELINE COMPANY'S AERIAL PATROL PILOT. A MAINTENANCE CREW CONFIRMED THE LEAK AT 1:30 P.M. APL NOTIFIED THE NRC AT 12:30 P.M. THE NRC ISSUED REPORT NO. 253630FOR THIS INCIDENT. TEMPORARY REPAIRS WERE MADE BY 4:50 P.M. WITH PERMANENT REPAIRS TO FOLLOW.
2017-09-29 08:50 | YES | NO | 19940235 | 1994-10-18 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-09-14 | 245 | MN | DAKOTA |  | NO |  | NO | T27N,R22W, SECTION 13, DAKOTA COUNTY, MINNESOTA. |  | TANK FARM | TANK |  | 1962 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 7250 | 5437.2536 | 10969.1366 | L. P. G. | 2 | 500 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.D. SMITH | 9185811800 | AN EMPLOYEE AT A NEARBY FACILITY NOTIFIED THE AREA OPERATOR BY TELEPHONE THAT A TANK RELIEF VALVE WAS VENTING. CENTRAL DISPATCH WAS NOTIFIED AND BLOCKED IN THE TERMINAL. A POST INCIDENT INVESTIGATION DETERMINED THE RELIEF VALVE HAD MALFUNCTIONED,ACTIVATED PREMATURELY AND FAILED TO RESEAT. THE RELIEF VALVE WAS REPLACED.
2017-09-29 08:50 | YES | YES | 19940236 | 1994-11-21 | 2552 | COLONIAL PIPELINE CO | YES | 1994-10-20 | 831 | TX | HARRIS |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1979 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 925 | 0 | 925 | 10000000 | 7499660.0952 | 15129843.6438 | GASOLINE | 3 | 20000 | 0 | YES | NO | 40 | 0.34 | 60000 | WELDED |  | 743 | 238 | YES | 24 | 939 | 0 | 79 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412404 | ON THURSDAY, OCTOBER 20, 1994, A PRESSURE DROP AND SIGNIFICANT RATE INCREASEON LINE 01, WERE NOTED AT HOUSTON STATION BY THE LOCAL STATION OPERATOR AND BY THE LINE CONTROLLER IN ATLANTA,GA AT APPROXIMATELY 0831 CDT. THE LINE WAS IMMEDIATELY SHUT DOWN AND COMPANY PERSONNEL BEGAN SEARCHING FOR A POSSIBLE LEAK. PERSONNEL WERE ALSO DISPATCHED TO CLOSE BLOCK VALVES BETWEEN HOUSTON STATION AND SHILOH STATION. AT 0937 CDT GASOLINE WAS FOUND IN A NEW CHANNEL CREATED BY FLOOD WATERS OF THE SAN JACINTO RIVER, APPROXIMATELY 12.5 MILES DOWNSTREAM OF HOUSTON STATION. THE PIPELINE WAS SEVERED NEAR THE WEST BANK OF THE NEW CHANNEL. SHORTLY AFTER THE DISCOVERY OF THE LOCATION OF THE LEAK, THE GASOLINE FUMES IGNITED NEAR THE RIVER ROAD AREA OF CHANNELVIEW, TX. TELEPHONIC NOTICE WAS MADE TO THE NRC AT 0924 CDT ON 10/20/1994, REPORT NO. 266190. IT IS ESTIMATED THAT 20,000 BARRELS OF GASOLINE ESCAPED FROM THE SEVERED PIPELINE, ALL OF WHICH WAS CONSUMED BY THE FIRE OR LOST TO EVAPORATION. WHILE AT THE PRESENT TIME THE ESTIMATED TOTAL PROPERTY DAMAGES ARE UNDETERMINED,THE COMBINED COSTS FOR THE LINE 01, LINE 02 AND THE TEXACO CRUDE OIL LINE BREAKS ARE EXPECTED TO EXCEED $10,000,000. THIS INCIDENT IS UNDER INVESTIGATION BY THE NTSB. THE NUMBER OF PERSON (1851) INJURIED IS A COMBINED TOTAL WITH LINE 02 BREAK AND TEXACO CRUDE OIL LINE SEE REPORT #940237 FOR LINE 2 INFORMATION.
2017-09-29 08:50 | YES | YES | 19940237 | 1994-11-21 | 2552 | COLONIAL PIPELINE CO | YES | 1994-10-20 | 1400 | TX | HARRIS |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 926 | 0 | 926 | 0 | 0 | 0 | DIESEL FUEL | 3 | 10000 | 0 | YES | NO | 36 | 0.38 | 46000 | WELDED |  | 690 | 185 | YES | 24 | 740 | 0 | 63 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412404 | ON THURSDAY MORNING, OCTOBER 20, 1994, THE HOUSTON TO SHILOH STATIONSEGMENT OF LINE 02 WAS DOWN DUE TO NORMAL SCHEDULING. AFTER THE FAILURE OFLINE 01, THE SHUTDOWN OF THIS SEGMENT OF LINE 02 WAS CONTINUED AND THEBLOCK VALVE AT SHILOH STATION WAS CLOSED AS A PRECAUTIONARY MEASURE.SHORTLY AFTER 1400 CDT, THE LINE CONTROLLER NOTED THAT A SHARP PRESSUREDROP IN THIS SEGMENT HAD OCCURRED, SUGGESTING THAT A LEAK EXISTED.TELEPHONIC CALLS WERE MADE TO THE NRC AT 1455 CDT, REPORT NO. 266278 AND AT1808 CDT, REPORT NO. 266312. AFTER THE FLOOD WATERS OF THE SAN JACINTORIVER SUBSIDED, IT WAS FOUND THAT THE 36-INCH, LINE 02 HAD ALSO BEENSEVERED IN THE NEW CHANNEL ADJACENT TO THE BREAK OF THE 40-INCH, LINE 01,WHICH OCCURRED EARLIER ON 10/20/94 AT 0831 CDT. IT IS ESTIMATED THAT 10,000BARRELS OF LOW SULFUR DIESEL OIL ESCAPED FROM THE SEVERED LINE, MUCH OFWHICH WAS CONSUMED IN THE FIRE THAT STARTED AFTER THE LINE 01 BREAK. ANYRECOVERED PRODUCT WOULD HAVE BEEN MIXED WITH THE CRUDE OIL FROM THE TEXACOBREAK AND HENCE CANNOT BE SEPARABLY MEASURED. WHILE AT THE PRESENT TIME THEESTIMATED TOTAL PROPERTY DAMAGES ARE UNDETERMINED, THE COMBINED COSTS FORTHE LINE 01, LINE 02, AND THE TEXACO CRUDE OIL LINE BREAKS ARE EXPECTED TOEXCEED $10,000,000. THIS INCIDENT IS UNDER INVESTIGATION BY THE NTSB. SEEREPORT #940236 FOR LINE 1 INFORMATION B: #INJURED IN 1851, A COMBINED TOTALWITH LINE 01 BREAK AND TEXACO CRUDE OIL LINE.
2017-09-29 08:50 | YES | NO | 19940238 | 1994-11-28 | 19226 | TEXACO PIPELINE INC | YES | 1994-10-21 | 1140 | TX | HARRIS | HIGHLANDS | NO |  | NO | NEAR SAN JACINTO RIVER |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 4489020 | 3366612.416 | 6791817.0714 | CRUDE OIL | 1 | 5350 | 2900 | YES | NO | 20 | 0.31 | 46000 | WELDED |  | 720 | 0 | YES | 8 | 914 | 2 | 91 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | OTHER | TEXAS EXCAVATION SAFETY | Null | Null | B.L. LEDNICKY | 7134323401 | THE TEXACO PIPELINE INC. (TPLI) CRUDE OIL PIPELINE LOCATED IN HARRIS COUNTY NEAR THE SAN JACINTO RIVER WAS RUPTURED DURING SEVERE FLOODING AT A POINT 1550' WEST OF THE WEST BANK OF THE SAN JACINTO RIVER (MILE POST 12.07). THE BREAK WAS DISCOVERED ON THE ABOVE INDICATED DATE AND TIME WHEN TPLI PERSONNEL OBSERVED WHAT THEY BELIEVED TO BE CRUDE OIL ON THE FLOOD WATER NEAR THE TPLI 20"PIPELINE. THIS WAS VERIFIED ON SATURDAY, OCTOBER 22ND WHEN THE FLOOD WATER RECEDED SUFFICIENTLY TO ALLOW THE SEVERED 20" PIPE TO BE OBSERVED. AT THE TIMEOF THE PIPELINE BREAK THE PIPELINE WAS SHUT-IN WITH BLOCK VALVES CLOSED ON EITHER SIDE OF THE RIVER (AND BREAK) AT MILE POST 8.27 AND MILE POST 36.7. AT THIS TIME THE PIPELINE HAS NOT BEEN REPAIRED AND THEREFORE REMAINS OUT OF SERVICE ACROSS THE SAN JACINTO RIVER. PART F- ESTIMATED TOTAL TEXACO PROPERTY DAMAGE (TOTAL DAMAES ARE UNKNOWN) $4,489,020 (ESTIMATE) DAMAGE TO PIPELINE -$900,000 (EST.) LOST CRUDE OIL @16.961/BBL. 90,739. 100% TEXACO COST (CLEANUP) 3,498,281(EST.) TOTAL- $4,489,020. *APPROX. 2900 BBLS. OF DECANTED HYDROCARBONS RECOVERED TO DATE.
2017-09-29 08:50 | YES | NO | 19940239 | 1994-11-28 | 9175 | JAYHAWK PIPELINE CORP | NO | 1994-11-04 | 830 | KS | GREENWOOD |  | NO |  | NO | NW NW SECTION 23 - TOWNSHIP 22- RANGE 10E, GREENWOOD COUNTY, KANSAS 7 MILES WEST OF MADISON, KANSAS. |  | TANK FARM | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | CRUDE OIL | 1 | 1065 | 643 | NO | NO | 6.63 | 0.25 | 35000 | WELDED |  | 275 | 20 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | JAYHAWK PIPELINE'S GAUGER DISCOVERED THE SPILL AT 0830, NOVEMBER 4, 1994. OIL WAS CONTAINED INSIDE DIKE WALL AND VACUUM TRUCKS WERE USED TO RECOVER OIL. THE REMAINING 422 BARRELS WERE CALCULATED IN 9,480 CUBIC FEET OF SOIL. SOIL REMEDIATION WILL BE DONE ON SITE FOR FINAL CLEAN UP. THE PIPE WAS REMOVED AND REPLACED WITH 3 FEET OF PRETESTED PIPE BY 1800 HOURS, NOVEMBER 4, 1994.
2017-09-29 08:50 | YES | NO | 19940240 | 1994-11-22 | 30658 | KERN OIL & REFINING CO. | NO | 1994-11-05 | 1300 | CA | KERN |  | NO |  | NO | 500 FEET EAST OF COMANCHE DR. ON N. SIDE OF HERMOSA RD 7 MILES NORTH OF ARVIN,CA |  | LINE PIPE | PIPE | WELDING FITTING | 1934 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5624.7451 | 11347.3827 | CRUDE OIL | 1 | 110 | 100 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 450 | 50 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | UNDERGROUND SERV. ALERT | NO | NO | KENNETH HIGH | 8058450761 | BROKEN BY FIELD RIPPER $7500 PROPERTY DAMAGE INCLUDES COST OF REPAIR.
2017-09-29 08:50 | YES | NO | 19940241 | 1994-11-17 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1994-10-20 | 1606 | OR | MULTNOMAH | PORTLAND | NO |  | NO | LS 14 AT PORTLAND ST. LOCATED AT 6565 NWST. HELENA RD, PORTLAND, OR 97210 NEAREST RDWAY APPROX. 16 FT NW OF SPILL WITH 6-FOOT HIGH CONTAINMENT WALL BETWEEN SPIL |  | PUMPING STATION | OTHER | SUMP TANK | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 74996.601 | 151298.4364 | GASOLINE | 3 | 15 | 8 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | OPERATOR WAS PERFORMING MAINTENANCE CHECK ON MOTOR OPERATOR FUNCTION ON THE MAINLINE BLOCK VALVE. THE MAINLINE BLOCK VALVE MOTOR OPERATOR RESPONDED TO A COMMAND TO OPEN ELECTRICALLY. WHEN THE VALVE OPENED, PRODUCT BEGAN ENTERING THESCRAPER TRAP (THE SCRAPER TRAP DRAIN IS NORMALLY OPEN TO THE SUMP). THE OPERATOR ISSUED A COMMAND TO THE MAINLINE BLOCK VALVE MOTOR TO CLOSE - THE MOTOROPERATOR DID NOT RESPOND TO THE COMMAND. BY THE TIME THE VALVE WAS CLOSED (VIA HAND WHEEL), ENOUGH PRODUCT HAD ENTERED THE SUMP VIA THE SCRAPER TRAP DRAINTO CAUSE THE OVERFLOW. SFPP'S ENVIRONMENTAL HEALTH & SAFETY DEPARTMENT WILLDIRECT CLEANUP OF SITE. ANY PRODUCT COLLECTED WILL BE REMOVED BY VACUUM TRUCK.
2017-09-29 08:50 | YES | NO | 19940242 | 1994-11-18 | 4906 | EXXON PIPELINE CO | NO | 1994-10-19 | 1945 | TX | HARRIS | HIGHLANDS | NO |  | NO | SAN JACINTO RIVER, JUST SOUTH OF INTERSTATE HIGHWAY 10, HIGHLANDS, HARRIS COUNTY, TX. |  | LINE PIPE | PIPE |  | 1937 | FAILED PIPE | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 610000 | 457479.2658 | 922920.4623 | NOT GIVEN | 2 | 492 | 0 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1471 | 286 | YES | 24 | 1839 | 8 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | NO | NO | G.G. PERSYN | 7136565521 | SAN JACINTO RIVER WAS ABOVE FLOOD STAGE AND WASHED OUT AROUND THE CROSSING, RESULTING IN PIPE FAILURE.
2017-09-29 08:50 | YES | NO | 19940243 | 1994-11-17 | 2552 | COLONIAL PIPELINE CO | YES | 1994-10-17 | 1610 | TX | HARRIS | PASADENA | NO |  | NO | COLONIAL PIPELINE COMPANY'S HOUSTON STATION. |  | PUMPING STATION | OTHER | COPPER TUBING | 1979 | OTHER | FAILED CIRCUIT BREAKER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 149.9932 | 302.5969 | GASOLINE | 3 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | ON MONDAY, OCTOBER 17, 1994, AT 1610 CDT A CIRCUIT BREAKER (OCB) IN THE ELECTRICAL SUBSTATION AT COLONIAL'S HOUSTON STATION EXPLODED, SPILLING AN ESTIMATED 5 BARRELS OF TRANSFORMER OIL. THE EXPLOSION KNOCKED OUT ALL ELECTRICAL POWER TO THE FACILITY AND IGNITED A FIRE WITHIN THE SUBSTATION. AT THE SAME TIME,A SMALL FIRE OCCURRED IN THE GASOLINE SAMPLE BUILDING LOCATED NEARBY, WITHINTHE FACILITY GROUNDS. IT IS SURMISED THAT GROUND CURRENT FLOWING FROM THE CIRCUIT BREAKER FAILURE CAUSED AN ARC BURN IN A PIECE OF BARE COPPER TUBING LOCATED IN THE SAMPLE HOUSE AND IGNITED THE ESCAPING GASOLINE VAPORS. A COLONIALEMPLOYEE WAS IN THE SAMPLE BUILDING AT THE TIME AND IMMEDIATELY EXTINGUISHEDTHE FIRE. IT IS ESTIMATED THAT APPROXIMATELY 5 GALLONS OF GASOLINE WAS RELEASED,MOST OF WHICH WAS RECOVERED. THE NATIONAL RESPONSE CENTER WAS NOTIFIED OFTHE INCIDENT (REPORT NO. 265759) AT 2000 CDT. THE TEXAS GENERAL LAND OFFICEAND THE TEXAS WATER COMMISSION WERE ALSO NOTIFIED OF THE INCIDENT.
2017-09-29 08:50 | YES | NO | 19940244 | 1994-10-28 | 1004 | KOCH HYDROCARBON COMPANY | NO | 1994-09-29 | 843 | OK | CREEK |  | NO |  | NO | SW 1/4 SEC 33 T 17N R11E CREEK COUNTY, OK 2 MILES SOUTH AND 3 1/2 EAST OF KELLYVILLE, OK |  | LINE PIPE | PIPE |  | 1986 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 56247.4507 | 113473.8273 | NATURAL GAS LIQUID | 2 | 2996 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1440 | 600 | YES | 18 | 2150 | 0 | 86 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES H. ELMORE | 4053952377 | THIRD PARTY DOZER OPERATOR BUILDING POND ON LAND STRUCK KOCH'S PIPELINE AND CAUSED RELEASE OF PRODUCT.
2017-09-29 08:50 | YES | NO | 19940245 | 1994-10-28 | 18718 | SUN PIPELINE CO | YES | 1994-09-21 | 1650 | MI | OAKLAND | ROCHESTER HILLS | NO |  | NO | AVON TOWNSHIP,W1/2, NW1/4, SECTION 34, T.3N., R11E. 17 FT E. OF THE CENTERLINE OF LIVERNOIS RD, 1898 FT S. OF THE CENTERLINE OF ABURN RD,CTY OF ROCHESTER HLS,MI |  | LINE PIPE | PIPE |  | 1950 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 99820 | 74861.6071 | 151026.0993 | OIL AND GASOLINE | 2 | 18 | 0 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1200 | 468 | YES | 24 | 1500 | 10 | 58 | NO DATA | Null | YES | OTHER | UNDER INVESTIGATION | NO DATA |  | Null | NO DATA |  | Null | Null | CHRIS | 3132929841 | 0900, SEPTEMBER 19, 1994 SUN PIPE LINE REGION III OFFICE RECEIVED A CALL FROM A PROPERTY OWNER COMPLAINING OF PETROLEUM ODOR COMING FROM A DRAINAGE DITCHNEAR HIS HOUSE. A FOREMAN INVESTIGATIED THE SITE AND AT 1300 DETERMINED A POSSIBLE LEAK EXISTED. THE LPGS IN THE LINE SEGMENT WERE DISPLACED WITH UNLEADED GASOLINE ON 9/20. EXCAVATION TO LOCATE THE LEAK COMMENCED ON 9/21. THE EXCAVATED SOIL, POTENTIALLY IMPACTED WITH PETROLEUM PRODUCTS, WAS REMOVED AND STORED IN ENVIRONMENTAL ROLL OFF BOXES UNDER THE GUIDANCE OF MDNR. AT 1650 A PINHOLE LEAK WAS LOCATED AND A MECHANICAL LEAK CLAMP INSTALLED. ON 9/22 THE LINEWAS REEXCAVATED AND PERMANENT REPAIRS COMPLETED AND THE LINE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19940246 | 1994-11-25 | 1047 | AMERADA HESS CORP NORTH JERSEY PUBLIC SVC PIPELINE | NO | 1994-10-08 | 1525 | NJ | HUDSON | KEARNY | NO |  | NO | DISCHARGE OCCURRED ON PROPERTY OF BELLEZZA CONSTRUCTION, INC. IN CLOSE PROXIMITY TO WHERE THE PIPELINE CROSSES HACKENSACK RIVER. |  | LINE PIPE | VALVE | ASSOCIATED DRAIN LINE | 1977 | OTHER | VALVE NOT FULLY CLOSED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 121000 | 90745.8872 | 183071.1081 | FUEL OIL | 1 | 95 | 95 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PETER HAID | 9087506555 | ON OCTOBER 8, 1994, AMERADA HESS COPORATION HAD A DISCHARGE OF RESIDUAL OIL FROM ITS NORTH JERSEY PUBLIC SERVICE PIPELINE. THE DISCHARGE OCCURRED FROM A VALVE PIT ON THE PROPERTY OF BELLEZZA CONSTRUCTION, INC. THE VALVE PIT CONTAINS TWO VALVES, ONE A MAINLINE BLOCK FOR THE HACKENSACK RIVER AND THE OTHER A SPUR VALVE INSTALLED FOR A POTENTIAL TIE-IN TO SERVICE A LOCAL CUSTOMER. BOTHVALVES WERE SERVICED PRIOR TO THE EVENT. UPON REMOVING THE OIL FROM THE VALVEPIT, IT WAS DISCOVERED THAT THE SPUR VALVE WAS NOT FULLY CLOSED DESPITE IT'SM ARKINGS SHOWING THAT IT WAS. THIS VALVE HAS A DRAIN LINE AND TWO GREASELINES SO THAT THE VALVE CAN BE PROPERLY MAINTAINED. THE DRAIN LINE IS OPEN TOLINE PRESSURE WHEN THE VALVE IS NOT FULLY CLOSED. EXCAVATION OF THE DRAIN LINESH OWED A SMALL HOLE IN THE LINE.
2017-09-29 08:50 | NO | NO | 19940247 | 1994-11-16 | 1046 | PENNZOIL PETROLEUM COMPANY | NO | 1994-11-03 | 900 | LA |  |  | YES | 29-31-21 N AND 92-50-30 W | YES | EAST CAMERON 23 "A" PLATFORM, OCS G-2853 |  | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | CONDENSATE | 1 | 0 | 0 | NO | NO | 4.5 | 0.24 | 35000 | WELDED |  | 1440 | 300 | YES | 28 | 2160 | 7 | 81 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.C. GILMORE | 3182694330 | ON 11/03/94, PENNZOIL PETROLEUM COMPANY WAS CONTACTED BY MMS, PIPELINE DIVISION, THAT A LIGHT SHEEN WAS REPORTED IN THE AREA OF THE PENNZOIL 4" LINE. CONACTED SONAT EXPLORATION COMPANY (OPERATOR OF EAST CAMERON 23). THEY PROVIDED TRANSPORTATION AND PERSONNEL TO FIND AND REPAIR 1/8" HOLE IN THE 4" LINE. THEDIVERS LOCATED HOLE AND INSTALLED PLIDCO CLAMP. ON 11/04/1994 LINE WAS PRESSURED UP AND DIVERS FOUND NO MORE LEAKS. LINE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19940248 | 1994-11-14 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-10-11 | 1110 | KS | MCPHERSON |  | NO |  | NO | TOWNSHIP 19 SOUTH RANGE 5 WEST SECTION24 |  | PUMPING STATION | VALVE | 1" NIPPLE AND VALVE | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3800 | 2849.8708 | 5749.3406 | L. P. G. | 2 | 300 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | UNDER MAPL SUPERVISION | YES | YES | L.D. SMITH | 9185811800 | A BACKHOE OPERATOR STRUCK A 1" NIPPLE AND VALVE CONNECTED TO A PRODUCT LINE,CAUSING A PRODUCT RELEASE TO THE ATMOSPHERE. THE LINE WAS ISOLATED AND THEREMAINING PRESSURE WAS RELIEVED TO THE FLARE SYSTEM. REPAIRS WERE MADE AND THELINE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19940249 | 1994-11-14 | 9175 | JAYHAWK PIPELINE CORP | YES | 1994-10-25 | 1515 | KS | KIOWA |  | NO |  | NO | NE 1/4 SECTION 8 - TOWNSHIP 29 S. RANGE 17 W., KIOWA CNTY, KANSAS 5 MILES E. AND 4 1/2 MILES S. OF GREENSBURG, KANSAS. |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5999.7281 | 12103.8749 | CRUDE OIL | 1 | 2267 | 2245 | NO | NO | 12.75 | 0.25 | 46000 | WELDED |  | 1290 | 250 | YES | 8 | 1612 |  | 58 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | ALLEN R. WILKERSON | 3162419270 | JAYHAWK PIPELINE WAS NOTIFIED BY TELEPHONE AT 1530, OCTOBER 25, 1994, BY CECIL TEDDER OF FLINT ENGINEERING AND CONSTRUCTION THAT THEIR DITCHER HAD HIT OURPIPELINE WHILE IN THE PROCESS OF LAYING A GAS LINE. THE LEAK LOCATION WAS INA RURAL AREA IN KIOWA COUNTY 5 MILES EAST AND 4 1/2 MILES SOUTH OF GREENSBURG, KANSAS, PIPELINE "WARNING" MARKERS WITH THE COMPANY IDENTIFICATION AND EMERGENCY TELEPHONE NUMBER WERE ON EACH SIDE OF ROAD NORTHEAST OF ACCIDENT LOCATION. WE HAD RESPONDED TO THE ONE CALL AND FLAGGED OUR PIPELINE, THE CONTRACTORCALLED AND SAID HE WOULD MEET JAYHAWK AT 1000 HOURS, OCTOBER 26, 1994 TO UNCOVER OUR PIPELINE. THE LINE WAS SHUT DOWN BY 1600 HOURS, BLOCK VALVES WERE CLOSED BY 1800 HOURS, DAMAGED PIPE WAS REMOVED AND REPLACEMENT JOINT 40' OF PRETESTED 12" PIPE WAS INSTALLED OCTOBER 26, 1994.
2017-09-29 08:50 | YES | NO | 19940250 | 1994-11-03 | 4805 | EXPLORER PIPELINE CO | YES | 1994-09-30 | 300 | TX | JEFFERSON | PORT NECHES | NO |  | NO | STAR ENTERPRISE EAST PORT NECHES TERMINAL, 100 EAST PORT NECHES AVE., PORT NECHES, TEXAS 7765 |  | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 112494.9014 | 226947.6547 | FUEL OIL | 3 | 222 | 198 | NO | NO | 12 | 0.22 | 52000 | WELDED |  | 1286 | 600 | YES | 24 | 1622 | 2 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | R.E. SANDS | 9184935106 | AT 03:03 ON SEPTEMBER 30, 1994 AN EMPLOYEE OF STAR ENTERPRISE EAST TERMINAL IN PT. NECHES, TEXAS CALLED EXPLORER'S CONTROL CENTER IN TULSA, OKLAHOMA TO ADVISE OF A FUEL OIL SMELL IN THE VICINITY OF EXPLORER'S 12" PIPELINE THAT TRANSVERSES THROUGH THE STAR ENTERPRISE FACILITY. THE PIPELINE WAS IMMEDIATELY SHUT DOWN ANED ISOLATED. EXPLORER PERSONNEL WERE NOTIFIED AND ARRIVED AT THE SITE AT 04:05. IT WAS DETERMINED THERE HAD BEEN A RELEASE OF FUEL OI FROM EXPLORER'S 12" PIPELINE THAT WAS COMPLETELY CONTAINED IN EXISTING DITCHES AT THE SPILL SITE AND DID NOT PRESENT A SAFETY HAZARD. VACUUM TRUCKS AND EVACUATION EQUIPMENT WERE DISPATCHED TO THE SITE. EVACUATION OF THE PIPE REVEALED THREE 1/2" WIDE BY 33" LONG LONGITUDINAL DENTS/ SCRATCHES HAD BEEN MADE ON THE PIPEBY THIRD PARTY EQUIPEMENT. THE FUEL OIL ESCAPED FROM A 7" LONG CRACK THAT DEVELOPED IN THE CENTER SCRATCH. THE DAMAGE APPEARED TO BE OLD , BUT IT IS NOT KNOWN WHEN IT WAS DONE OR BY WHOM. REPAIRS WERE MADE WITH A 48" LONG FULL ENCIRCLEMENT SLEEVE WELDED ON BOTH ENDS. THE PIPELINE WAS REPAIRED AND PLACED BACK INTO SERVICE AT 17:00 OCTOBER 1, 1994. CONTAMINATED SOIL HAS BEEN EXCAVATED, REMOVED FROM THE SITE, AND IS BEING DISPOSED OF UNDER THE DIRECTION OF THETEXAS NATURAL RESOURCES CONSERVATION COMMISSION.
2017-09-29 08:50 | YES | NO | 19940251 | 1994-11-14 | 15490 | PHILLIPS PIPE LINE CO | YES | 1994-10-13 | 1718 | TX | HUTCHINSON |  | NO |  | NO | BEAVER-BORGER LINE -MP 45-45+50 8 MILES NORTH, 7 MILES EAST OF STINNETT, TX |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 5249.7621 | 10590.8906 | CRUDE OIL | 1 | 300 | 68 | NO | NO | 8.63 | 0.28 | 30000 | WELDED |  | 1200 | 450 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS | 9186616267 | LINE FLYER REPORTED LIQUID ON RIGHT-OF-WAY. PIPE SECTION WAS REPLACED. FREE LIQUID WAS PICKED UP. THE REMAINING OIL WAS CLEANED UP WITH A CONTROLLED BURN.
2017-09-29 08:50 | NO | NO | 19940252 | 1994-10-31 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-09-29 | 1810 | NE | SAUNDERS |  | NO |  | NO | TOWNSHIP 13 NORTH RANGE 9 EAST SECTION 9 SAUNDERS COUNTY, NEBRASKA 1 MILE ENE OF MEMPHIS, NEBRASKA |  | LINE PIPE | PIPE | GIRTH WELD | 1968 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 541 | 405.7316 | 818.5245 | ANHYDROUS AMMONIA | 2 | 2 | 0 | NO | NO | 8.63 | 0.16 | 46000 | WELDED |  | 1198 | 939 | YES | 24 | 1530 | 11 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.D. SMITH | 9185811800 | THIRD PARTY (FARMER) CALLED TO REPORT AN ODOR. UPON INVESTIGATION, A PINHOLELEAK IN A WELD WAS FOUND. THE LINE WAS SHUT DOWN, A FULL ENCIRCLEMENTSLEEVE I NSTALLED, AND THE LINE WAS THEN RETURNED TO SERVICE.
2017-09-29 08:50 | NO | NO | 19940253 | 1994-10-28 | 10312 | GULF CENTRAL PIPELINE CO | YES | 1994-09-29 | 800 | LA | ST CHARLES |  | NO |  | NO | RANGE 20E, TOWNSHIP 13S, SECTION 81 NEAR BOUTEE, LA .2 MILE ON CANAL ROAD, OFF HWY 3127 |  | LINE PIPE | OTHER | 1/2" VALVE ON TOP OF 2" | 1970 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22498.9803 | 45389.5309 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 1103 | Null | 0 | 0 |  |  | EXTERNAL | Null | Null | OTHER | OPEN 2" BLOWDOWN VALVE | NO DATA |  | Null | NO DATA |  | Null | Null | JIM L. NORVELL | 3144865488 | 08:00 (APPROX) COMPANY EMPLOYEE RECEIVED CALL FROM LANDOWNER CONCERNING POSSIBLE VAPORS FROM VALVE LOCATED ON HIS PROPERTY. EMPLOYEE NOTIFIED PIPELINECONTROL CENTER TO SHUT DOWN INJECTION PLANTS IN AREA. NO PRESSURE REDUCTIONSSEE N ON CONTROL CENTER MONITORING SCREENS. 08:50 TELEPHONE NOTIFICATION MADETO LOUISIANA STATE POLICE AND LOCAL LEPC OF MINOR RELEASE. 09:30 EMPLOYEESFOUND PARTIALLY OPENED BLOWDOWN VALVE ON TOP OF 6" VALVE. VALVE LOCATED INSIDECAN BELOW GROUND. ALL PRODUCT EXCEPT FOR SOME VAPORS CONTAINED INSIDE CAN.10:13 NOTIFIED NRC (263114) AND DOT REGIONAL OFFICE IN HOUSTON. 16:00REPAIRS MAD E USING A BLIND FLANGE, AND NEW BLOW-DOWN VALVE. PARTIALLY OPEN 2"BLOWDOWN V ALVE ALLOWED PRODUCT TO CORRODE FITTING AND 1/2" VALVE CAUSINGFAILURE OF THE 1/2" VALVE. APPROXIMATE PRODUCT LOSS ESTIMATED AT 400 POUNDS.SOIL CONTAMINA TION FROM PRODUCT WAS LOCALIZED AROUND THE VALVE AREA. OPTIONSARE BEING INVE STIGATED AS TO THE BEST METHOD FOR DISPOSAL OF CONTAMINATEDSOIL. FRESH SOIL WILL BE BROUGHT INTO THE CONTAMINATED AREA.
2017-09-29 08:50 | YES | NO | 19940254 | 1994-10-27 | 9175 | JAYHAWK PIPELINE CORP | YES | 1994-10-12 | 1635 | OK | KAY |  | NO |  | NO | NW OF NE 1/4 SECTION 17, TOWNSHIP 28N., RANGE 1W., KAY COUNTY, OKLAHOMA APPROXIMATELY 1 MILE SOUTH OF BRAMAN, OKLAHOMA. |  | LINE PIPE | PIPE |  | 1925 | FAILED PIPE | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 749.966 | 1512.9844 | CRUDE OIL | 1 | 80 | 70 | NO | NO | 4.5 | 0.24 | 35000 | WELDED |  | 1000 | 420 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | EXTERNAL CORROSION ON 4" GATHERING LINE ON JAYHAWK'S PROPERTY BEING BRAMAN STATION. THE LINE WAS SHUT DOWN AND 40 FEET OF NEW PRE-TESTED, COATED PIPE WASINSTALLED.
2017-09-29 08:50 | YES | NO | 19940255 | 1994-11-29 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-10-23 | 418 | KS | MCPHERSON |  | NO |  | NO | TOWNSHIP 19 SOUTH RANGE 5 WEST SECTION 24 |  | PUMPING STATION | OTHER | RELIEF VALVE | 1994 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 634 | 475.4785 | 959.2321 | ANHYDROUS AMMONIA | 2 | 18 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.T. CRONK | 9185811800 | THE FAILURE OF PRESSURE CONTROL VALVE TO THE CLOSED POSITION RESULTED IN THEACTIVATION OF A 1/2" FILTER RELIEF VALVE. THE FILTER WAS ISOLATED AND THECONTROL VALVE REPLACED. SUPPLEMENTAL INFORMATION CORRECTING AMOUNT OF LOSSFROM 15 BARRELS TO 18.15 BARRELS IN PARTS F AND G. REPORT SUBMITTED BY SIDRUETER (918) 581-1800.
2017-09-29 08:50 | YES | NO | 19940256 | 1994-11-30 | 4805 | EXPLORER PIPELINE CO | YES | 1994-11-01 | 800 | TX | FANNIN |  | NO |  | NO | 1.8 MILES NORTH OF U.S. HIGHWAY 69, LEONARD, TEXAS. |  | LINE PIPE | PIPE |  | 1971 | FAILED PIPE | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 224989.8029 | 453895.3093 | FUEL OIL | 3 | 113 | 25 | NO | NO | 28 | 0.28 | 52000 | WELDED |  | 751 | 384 | YES | 24 | 1055 | 2 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | R.E. SANDS | 9184935106 | AT APPROXIMATELY 08:00 NOVEMBER 1, 1994, A CONTRACTOR FOR EXPLORER PIPELINECOMPANY PERFORMING ROUTINE CATHODIC PROTECTION SURVEY WORK DISCOVERED A FUELOIL STAIN ON THE PIPELINE RIGHT OF WAY APPROXIMATELY TWO MILES NORTH OFLEONARD, TEXAS. EXPLORER PERSONNEL RESPONDED IMMEDIATELY TO THE SITE TOINVESTIGATE. A SMALL AMOUNT OF FUEL OIL WAS ALSO FOUND ON TWO WATER PONDSAPPROXIMATELY 150 FEET FROM THE PIPELINE. EXPLORER'S SPILL RESPONSECONTRACTOR, MAINTENANCE CONTRACTOR, AND VACUUM TRUCKS WERE DISPATCHED TO THESITE TO INSTALL SPILL CONTAINMENT BOOMS, RECOVER SPILLED PRODUCT, AND BEGINEXCAVATING THE PIPELINE TO LOCATE THE SOURCE OF THE RELEASE. THE SOURCE WASDETERMINED TO BE A SEEP OF PRODUCT COMING FROM A SMALL CRACK IN THEBOTTOM OF THE PIPELINE WHERE IT HAD BEEN RESTING ON A SHARP ROCK. THE PIPELINEWAS SHUTDOWN AT 14:23 ON NOVEMBER 2, 1994 AND A PLIDCO SPLIT SLEEVE BOLTEDAND WELDED IN PLACE TO REPAIR TH E FAILURE. THE PIPELINE WAS RESTARTED AT10:25 NOVEMBER 3, 1994. A TOTAL OF 25 BARRELS WAS RECOVERED FROM THE SITE.REMOVAL OF CONTAMINATED SOIL TO AN APPROVED DISPOSAL SITE IS IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19940257 | 1994-11-15 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1994-10-15 | 1558 | CT | NEW HAVEN | NEW HAVEN | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1961 | OTHER | PIPELINE SEGMENT REPLACED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1499932.019 | 3025968.7288 | TRANSMIX (PART. REFINED PETRO) | 3 | 300 | 230 | NO | NO | 12 | 0.22 | 42000 | WELDED |  | 720 | 350 | YES | 24 | 104 | 9 | 93 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER | 6108208300 | PETROLEUM PRODUCT WAS OBSERVED IN THE AREA OF THE LITTLE RIVER, NEW HAVEN, CTBY THE US COAST GUARD. THIS APPARENT RELEASE WAS REPORTED TO BUCKEYEPIPELINE'S CONTROL CENTER AT MACUNGIE, PA ON OCTOBER 15, 1994 BY COASTGUARD. THE MACUNGIE DISPATCHER CONTACTED THE NEW HAVEN STATION OPERATOR WHOIMMEDIATELY SHUT DOWN THE PIPELINE. CREWS WERE DISPATCHED TO INVESTIGATE,LOCATE AND CONTAIN THE RELEASE. THE RELEASE AREA WAS ISOLATED TO A 2000 FOOTPIPELINE SEGMENT BETWEEN QUINNIPIAC AVE. AND LITTLE RIVER AND NEXT TO ANAMTRACK HIGH SPEED PA SSENGER RAILWAY. THE EXACT LOCATION OR CAUSE OF THERELEASE HAS NOT BEEN DETE RMINED. HOWEVER, THE ENTIRE 2000 FEET OF PIPELINESEGMENT WAS ABANDONED IN PL ACE. A NEW REPLACEMENT PIPELINE SEGMENT WASCONSTRUCTED AND THE JET LINES SYS TEM RETURNED TO NORMAL SERVICE ON OCTOBER31, 1994 AT 14:30. BUCKEYE CONTINUE S TO REMEDIATE THE EFFECTS OF THE RELEASEUNDER THE DIRECTION OF FEDERAL, STATE AND LOCAL AUTHORITIES.
2017-09-29 08:50 | YES | NO | 19940258 | 1994-11-28 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1994-10-26 | 1400 | TX | NUECES |  | NO |  | NO | 1/2 BLOCK NORTH OF UP RIVER RD.; 1/2 BLOCK EAST OF TEXAS FUEL & ASPHALT TERMINAL |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | CRUDE OIL | 1 | 67 | 3 | NO | NO | 8 | 0 | 24000 | WELDED |  | 550 | 0 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW | 7138777370 | LEAK WAS DISCOVERED BY A THIRD PARTY WHILE LINE WAS DOWN FROM STAIN ON SOIL.SOUTHWESTERN. REFINERY BLOCKED THE LINE IN WHILE PUMPING TO THEM AND THE SURGE OF PRESSURE IS BELIEVED TO HAVE OPENED UP A CORROSION PIT. A TEMPORARY LEAK CLAMP WAS INSTALLED AND CONTAMINATED SOIL WAS EXCAVATED FROM THE SITE.
2017-09-29 08:50 | YES | NO | 19940259 | 1994-12-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1994-11-05 | 930 | NM | SAN JUAN |  | NO |  | YES | SECTION 2, TOWNSHIP 27N, RANGE 11WEST, SAN JUAN COUNTY, NEW MEXICO |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 132488 | 99361.4967 | 200452.2725 | NATURAL GAS LIQUID | 2 | 7237 | 0 | NO | NO | 12.75 | 0.22 | 65000 | WELDED |  | 1608 | 570 | YES | 24 | 2172 | 11 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | PIPELINE WARNING SIGNS | NO | NO | LARRY D. SMITH | 9185811800 | A THIRD PARTY CONTRACTOR WORKING ON THE INSTALLATION OF A NEW PIPELINE WHICHPARALLELED MID-AMERICA PIPELINE COMPANY'S LINE, STRUCK THE LINE WITH A DOZERCAUSING A RUPTURE. THE EMERGENCY ACTION PLAN WAS INITIATED, THE PIPELINE SHUT DOWN AND BLOCKED IN. THE DAMAGED PIPE WAS REPLACED AND THE LINE RETURNED TOSERVICE.
2017-09-29 08:50 | NO | NO | 19950001 | 1994-12-23 | 26134 | MOBIL PIPELINE CO - MOBIL WEST COAST PIPELINE | NO | 1994-12-01 | 408 | CA | LOS ANGELES | LOS ANGELES | NO |  | NO | BERTH 176 L.A. HARBOR, NEAREST CROSS STREETS ARE FRIES AVENUE AND HERMOSA STREET |  | LINE PIPE | PIPE |  | 1973 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11249.4901 | 22694.7655 | OIL AND GASOLINE | 1 | 1 | 0 | NO | NO | 10 | 0.25 | 52000 | WELDED |  | 960 | 375 | YES | 4 | 1200 | 5 | 93 | EXTERNAL | Null | YES | OTHER | CONCENTRATION CELL | NO DATA |  | Null | NO DATA |  | Null | Null | MR. SALLES | 3105480939 | THE EXTERNAL CORROSION LEAK OCCURRED INSIDE A 30' SECTION OF 14" CASING PIPE.EXTERNAL CORROSION RESULTED FROM PROTECTIVE COATING DAMAGED. DURING THE PIPELINE INSTALLATION FIBERGLASS INSULATORS ARE INSTALLED ON THE 10" PIPELINE AT INTERVALS TO KEEP THE CARRIER AND CASING PIPE INSULATED. THE LEAK OCCURRED UNDERNEATH ONE OF THE 10"X14" CASING SPACERS. REASONS AS TO HOW THE PROTECTIVE COATING WAS DAMAGED AT THE INSULATOR LOCATION ARE UNKNOWN. GROUND WATER IN ADDITION TO A HIGH WATER TABLE ALSO CONTRIBUTED TO THE CORROSION. PIPELINE IN CASING WAS REMOVED AND REPLACED.
2017-09-29 08:50 | YES | NO | 19950002 | 1994-12-28 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1994-11-21 | 422 | PA | ALLEGHENY |  | NO |  | NO |  |  | TANK FARM | TANK | BUCKEYE BREAK OUT TANK | 1977 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7499.6601 | 15129.8436 | TURBINE FUEL | 3 | 900 | 885 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DEAN R. MOYER | 6107704000 | ON NOVEMBER 2, 1994 AT 04:22, TANK 202, LOCATED AT BUCKEYE PIPE LINE'SCORAOPOLIS, PA TERMINAL, WAS FILLED ABOVE THE TANK OVERFLOW FILL HEIGHTRESULTING IN THE RELEASE OF APPROXIMATELY 900 BARRELS OF TURBINE FUEL. THERELEASE WAS CONFINED ENTIRELY TO THE FACILITY'S SECONDARY CONTAINMENT SYSTEM.THE RELEASED AVIATION TURBINE FUEL DID NOT POSE ANY THREAT TO PUBLIC SAFETY/HEALTH OR THE ENVIRONMENT. NO SURFACE WATERS WERE IMPACTED. THE DIRECT CAUSEOF THE INCID ENT WAS THE FAILURE TO RESET THE TANK #202'S ALARM LEVELSSUBSEQUENT TO THE INSTALLATION OF AN INTERNAL FLOATING ROOF.
2017-09-29 08:50 | YES | NO | 19950003 | 1994-12-22 | 19223 | SUN PIPE LINE CORPORATION - GENERAL WASH BLDG | NO | 1994-11-15 | 1330 | PA | PHILADELPHIA | PHILADELPHIA | NO |  | NO | PT BREEZE PUMP STATION, LOCATED ON PASSYUNK AVENUE |  | PUMPING STATION | OTHER | NIPPLE | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 56247.4507 | 113473.8273 | GASOLINE | 1 | 138 | 117 | NO | NO | 12 | 0.38 | 35000 | WELDED |  | 800 | 700 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | NOT GIVEN | NO | YES | ALAN D. GILLE | 2159773344 | A CONTRACTOR WAS EXCAVATING AT THE PT. BREEZE PUMP STATION AS PART OF ACONSTRUCTION PROJECT. OUR INSPECTOR HAD MARKED THE LINE, AND OUR SITE PROGRAMREQUIRED THE CONTRACTOR TO NOTIFY THE INSPECTOR OR THE PROJECT MANAGER IFTHEY WERE GOING TO MOVE THE BACKHOE TO EXCAVATE ELSEWHERE. THE CONTRACTORMOVED TO A NOTHER AREA AND BEGAN TO EXCAVATE WITHOUT INFORMING OUR COMPANYPERSONNEL. THE BACKHOE STRUCK A NIPPLE THAT WAS THREADED INTO A WELDEDTHREAD-O-LET, AND BROKE IT OFF. GASOLINE WAS RELEASED, THE FACILITY WASIMMEDIATELY EVACUATED AND EMERGENCY RESPONSE PLANS WERE IMPLEMENTED. NO ONEWAS INJURED.
2017-09-29 08:50 | YES | NO | 19950004 | 1994-12-21 | 12127 | MARATHON PIPE LINE CO | YES | 1994-11-21 | 1535 | IL | IROQUOIS | L'ERABLE | NO |  | NO | SECTION 16, T28N,R13W,IROQUOIS COUNTY,ILLINOIS APPROXIMATELY ONE HALF MILE EAST OF L'ERABLE. |  | LINE PIPE | BOLTED FITTING |  | 1970 | OTHER | MECH FAILURE OF GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 310000 | 232489.463 | 469025.153 | GASOLINE | 3 | 10 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 15:35 CENTRAL STANDARD TIME ON NOVEMBER 21, 1994, THE MARATHON PIPELINECOMPANY (MPL) OPERATIONS CENTER IN FINDLAY, OHIO RECEIVED TELEPHONENOTIFICATION OF A POSSIBLE RAINBOW SHEEN IN PRAIRIE CREEK, JUST EAST OFL'ERABLE, IROQUOIS COUNTY, IL BY A LOCAL RESIDENT. THE WABASH 12" PRODUCTSPIPE LINE WAS SHUT DOWN BY THE OPERATIONS CENTER AT 15:42, AND THE LOCALOPERATIONS FOREMAN AT GRIFFITH, IN WAS NOTIFIED. MPL RESPONDED WITH BOTH MPLPERSONNEL AND CONTRACTORS TO THE SCENE. NO SIGN OF A RELEASE COULD BE FOUNDON NOVEMBER 21; HOWEVER, EARLY ON THE MORNING OF NOVEMBER 22 A SHEEN WASNOTED ON PRAIRIE CREEK IN THE VICINITY OF THE PIPE LINE BY MPL PERSONNEL. MPLAND ITS CONTRACTORS RESPONDED BY DEPLOYING NUMEROUS BOOMS ON PRAIRIE CREEKAND THE IROQUOIS RIVER TO CONTAIN THE SHEEN, AND REMOVING ACCUMULATED PRODUCTWITH ABSORBENTS AND VACUUM TRUCK. NO EFFECT ON FISH OR WILDLIFE WAS NOTED.THE PIPELINE WAS EXCAVATED AND A LEAKING STOPPLE FITTING WAS UNCOVERED, ANDREPAIRED BY REPLACING THE GASKET. THE PIPE LINE WAS RETURNED TO SERVICE ONNOVEMBER 23, 1994 AT APPROXIMATELY 15:00. MPL AND ITS CONTRACTORS CONTINUE TOWORK ON REMEDIATION OF THE SITE, AND REPORT PROGRESS TO THE ILLINOISENVIRONMENTAL PROTECTION AGENCY.
2017-09-29 08:50 | YES | NO | 19950005 | 1994-12-14 | 2552 | COLONIAL PIPELINE CO | YES | 1994-11-10 | 1530 | GA | GWINNETT |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S DACULA PUMP STATION |  | PUMPING STATION | VALVE |  | 1963 | OTHER | FAILED CHECK VALVE SEALS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1929408 | 1446990.4185 | 2919164.1365 | TRANSMIX (PART.REFINED PETRO) | 3 | 0 | 71 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J.L. GAMBRELL | 4018412402 | ON NOVEMBER 10, 1994, AT APPROXIMATELY 1530 EST, A SMALL PRODUCT SHEEN WASDISCOVERED ON THE SURFACE OF HOPKINS CREEK JUST EAST OF DACULA PUMP STATIONIN GWINNETT COUNTY, GEORGIA. AT 1651 EST THE NATIONAL RESPONSE CENTER WASNOTIFIED OF THE INCIDENT, REPORT NO. 269217. AT APPROXIMATELY THE SAME TIME,THE GEORGIA ENVIRONMENTAL PROTECTION DIVISION (EPD) WAS ALSO NOTIFIED OF THEINCIDENT. AN INVESTIGATION IS CURRENTLY UNDERWAY TO DETERMINE THE SOURCE ANDTHE EXTENT OF CONTAMINATION. A SUPPLEMENTAL REPORT WILL BE FILED ONCE THEINVESTIGATION IS COMPLETE.
2017-09-29 08:50 | YES | NO | 19950006 | 1994-12-20 | 18273 | SHELL PIPELINE CORP | YES | 1994-11-27 | 427 | TX | HARRIS |  | NO |  | NO | BLOCK A-395, SURVEY HT & BB RANCHO 24-INCH PIPELINE. |  | LINE PIPE | PIPE |  | 1952 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 420000 | 314985.724 | 635453.433 | CRUDE OIL | 1 | 210 | 130 | NO | NO | 24 | 0.38 | 52000 | WELDED |  | 960 | 689 | YES | 12 | 1150 | 0 | 53 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132 | THE RELEASE WAS CAUSED BY DEFECTIVE PIPE (HARD SPOT), AS DETERMINED BY THIRDPARTY METALLURGICAL LABORATORY.
2017-09-29 08:50 | YES | NO | 19950007 | 1994-12-14 | 26303 | UNOCAL PIPELINE CO - EASTERN REGION | NO | 1994-11-24 | 540 | CA | SAN LUIS OBISPO |  | NO |  | NO | SANTA MARGARITA PUMP STATION LOCATED 1 MILE NORTH OF THE TOWN OF SANTA MARGARITA ON EL CAMINO REAL. |  | PUMPING STATION | VALVE | RELIEF VALVE OVERFILLED | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 8999.5921 | 18155.8124 | OIL AND GASOLINE | 3 | 130 | 120 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK ARMSTRONG | 8059348266 | AT APPROXIMATELY 5:40 A.M. A RELIEF VALVE OPENED UP AND DISCHARGED GAS OIL TOA CONCRETE SUMP VIA DRAIN PIPING. THE LEVEL SWITCH ON THE SUMP FAILED TOACTUATE AND START A SUMP PUMP. THE SUMP OVERFILLED AND SPILLED 130 BARRELS OFGAS-OIL TO PRIMARILY ASPHALT AND CONCRETE COVERED AREAS OF THE STATION. SOMESOIL WAS IMPACTED. ALL PRODUCT WAS CONTAINED TO STATION PROPERTY; NO WATER WASIMPACTED. APPROXIMATELY 120 BARRELS OF PRODUCT WAS RECOVERED. THE PIPELINEWAS OPERATING AT 950 PSI AT THE TIME OF THE INCIDENT. THE RELIEF VALVE WASCALIBRATED FOR 1200 PSI.
2017-09-29 08:50 | YES | NO | 19950008 | 1994-12-28 | 443 | AMOCO PIPELINE CO | YES | 1994-11-30 | 1410 | WY | GOSHEN |  | NO |  | NO | SECTION 23, TOWNSHIP 26N, RANGE 64W AMOCO PUMPING STATION LOCATED 1/2 MILE EAST OF FT. LARAMIE, WYOMING. |  | PUMPING STATION | VALVE |  | 1955 | OTHER | VALVE FAILURE (MECHANICAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 60 | 59 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. PETERSON | 3038305067 | DURING A CONSTRUCTION OPERATION AT PUMPING STATION, A 16" LINE HAD BEEN CUT & DRAINED IN PREPARATION FOR REPLACEMENT. WHILE UNLOADING THE CRUDE FROM THE DRAIN-UP THRU STATION TRANSFER PIPING, A VALVE CONNECTED BETWEEN THE TRANSFERPIPING & THE OPEN LINE LEAKED. 60 BBLS CRUDE WAS SPILLED ONTO STATION GROUNDS. THE OIL WAS RECOVERED, CLEANUP OPERATION COMPLETED BY 1800 MST 11/30/94.
2017-09-29 08:50 | YES | NO | 19950009 | 1994-12-28 | 443 | AMOCO PIPELINE CO | YES | 1994-12-09 | 1235 | ND | BURKE |  | NO |  | NO | NW 1/4 NW 1/4, SECTION 26, TOWNSHIP 162N, RANGE 92W. |  | PUMPING STATION | TANK |  | 1985 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | CRUDE OIL | 1 | 560 | 550 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. PETERSON | 3038305067 | TANK #7396 SIDELINE GAUGE HUNG UP RESULTING IN TANK OVERFLOW. ALL OIL WAS CONTAINED IN TANK DIKE. THE NRC WAS NOTIFIED, FILE #272627
2017-09-29 08:50 | YES | NO | 19950010 | 1994-12-27 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1994-11-10 | 1230 | TX |  |  | YES | NUECES BAY (INLAND) | NO | 1 MILE NORTH OF SOUTH BANK OF NUECES BAY |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22498.9803 | 45389.5309 | GASOLINE | 3 | 50 | 0 | NO | NO | 12.75 | 0.25 | 42000 | WELDED |  | 1000 | 900 | YES | 8 | 1260 | 10 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW | 7138777370 | A SHEEN WAS SPOTTED ON NUECES BAY BY A KOCH PIPELINE PATROL PILOT. COASTALSTATES CRUDE GATHERING COMPANY PERSONNEL VERIFIED LEAK AND SHUT THE PIPELINEDOWN. THE LINE WAS PURGED OF PRODUCT WITH NITROGEN TO LOCATE LEAK AND BEGINREPAIRS. A SPLIT SLEEVE CLAMP WAS INSTALLED ON THE LINE. THE SHEEN WASOBSERVED TO HAVE DISSIPATED RAPIDLY. THERE APPEARS TO HAVE BEEN NO DAMAGE TOTHE SHORELINE OR ANY OTHER MARINE HABITAT.
2017-09-29 08:50 | NO | NO | 19950011 | 1995-01-04 | 12913 | MURPHY OIL USA INC | NO | 1994-12-18 | 2300 | WI | DOUGLAS | SUPERIOR | NO |  | NO | 6 FEET WEST OF MARYLAND AVE, 500 YARDS SOUTH OF WINTER STREET EAST OF AMOCO TERMINAL IN THE CITY OF SUPERIOR WI. |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2249.898 | 4538.9531 | DIESEL FUEL | 1 | 20 | 20 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 540 | 65 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BRUCE KRENZ | 7153983533 | TRUCK DRIVER NOTICED OIL ON ROAD LEADING FROM TERMINAL NOTIFIED AMOCO PERSONNEL . AMOCO INVESTIGATED OIL, CALLED MURPHY OIL, MURPHY OIL SHUTDOWN & SECURED PIPELINE, NOTIFIED ALL PARTIES ON CALL LIST CALLED OUT MANPOWER & EQUIPMENTTO CONTAIN & CLEAN UP SPILL. PIPELINE WAS BLOWN OUT WITH NITROGEN AND LOCKEDOUT TAGGED OUT. OIL AND CONTAMINATED SOIL WERE REMOVED TO DISPOSAL SITE. DAMAGED SECTION OF PIPELINE WAS REPLACED AND LINE PUT BACK IN SERVICE ON 12/21/94
2017-09-29 08:50 | YES | NO | 19950012 | 1994-12-27 | 18280 | SHELL OFFSHORE INC - COASTAL DIVISION | NO | 1994-11-22 | 1300 | LA |  |  | YES | X=2,151,237 Y=134,284 | YES | SHIP SHOAL BLOCK 281 - GULF OF MEXICO | 270654 | LINE PIPE | PIPE |  | 1988 | OUTSIDE FORCE DAMAGE | FISHING OPERATIONS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 187491.5024 | 378246.0911 | CONDENSATE | 1 | 4200 | 0 | NO | NO | 4 | 0.24 | 42000 | OTHER |  | 300 | 275 | YES | 1 | 400 | 1 | 90 | NO DATA | Null | Null | NO DATA |  | FISHING OPERATIONS |  | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132 | THIS RELEASE WAS THE RESULT OF A CRACK IN THE PIPELINE. DIVERS INSPECTING THEPIPELINE FOUND A SHRIMP NET HUNG ON FLANGE BOLTS NEAR THE CRACK. FORCEAPPLIED TO THE PIPE BY THE NET APPEARED TO HAVE CAUSED THIS FAILURE. THEPIPELINE WAS REPAIRED BY REMOVING THE DAMAGED PIPE AND REPLACING IT WITH ASPOOL PIECE . THE EXACT TIME THE LINE WAS DAMAGED IS NOT KNOWN. THIS RELEASEWAS FIRST REPORTED TO THE NRC BY SHELL PIPE LINE CORPORATION ON NOVEMBER 22AND WAS ASSIGNED NUMBER 270654. ON NOVEMBER 23, SHELL OFFSHORE INC.DETERMINED THAT THE RELEASE WAS FROM THEIR LINE, AND CALLED THE NRC. SHELLOFFSHORE'S NOVEMBER 23 CALL ASSIGNED NUMBER 270732 BY THE NRC. THE NOVEMBER23 CALL ESTIMATED THE RELEASED VOLUME AS 10 BARRELS. ON DECEMBER 14, SHELLOFFSHORE AGAIN CALLED THE NRC TO CHANGE THE ESTIMATED VOLUME TO 4207 BARRELS,THE REVISED VOLUME MAY HAVE BEEN ASSIGNED TO REPORT 270654. CORRESPONDENCERECEIVED 1/5/95 INDICATES A REINSTATEMENT OF TELEPHONIC NOTIFICATION #270654,WITH THE RELEASE VOLUME CONFIRMED AT 4,200 BARRELS. THIS CORRESPONDENCE WILLBE ATTACHED TO ORIGINAL ACCIDENT REPORT (950012).
2017-09-29 08:50 | YES | NO | 19950013 | 1994-12-27 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1994-12-10 | 1428 | MN | CLEARWATER |  | NO |  | NO | LAKEHEAD MILEPOST 920.5 APPROXIMATELY 1/2 MILE WEST OF COUNTY RD 3 AND 1/2 MILE N. OF COUNTY RD 86 IN CLEARWATER COUNTY, MINNESOTA. |  | LINE PIPE | WELDING FITTING |  | 1967 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 112494.9014 | 226947.6547 | CRUDE OIL | 1 | 210 | 200 | NO | NO | 34 | 0.31 | 52000 | WELDED |  | 687 | 295 | YES | 8 | 863 | 10 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICK C. SANDAHL | 2187250102 | ON DECEMBER 10, 1994, 14:20 MST, LAKEHEAD CONTROL CENTER PERSONNEL RECEIVED ACALL FROM A LANDOWNER REPORTING OIL ON THE GROUND NEAR LEONARD,MINNESOTA. LINE WAS SHUT DOWN AT 14:28 MST. COMPANY PERSONNEL WEREIMMEDIATELY DISPATCHED TO THE AREA AND ON SITE AT 15:30 MST. THE LEAK WASCONFIRMED ON LINE 3 WITH APPROXIMATELY 210 BARRELS RELEASED, OF WHICH 200BARRELS WERE RECOVERED. EXCAVATION REVEALED A CRACK IN FILLET WELL ON STOPPLEFITTING ATTRIBUTABLE TO STRESS CAUSED BY UNEVEN SETTLEMENT OCCURRINGSUBSEQUENT TO THE REPAIR OF A PREVIOUS INCIDENT AT THIS LOCATION. (SEEACCIDENT REPORT OF MAY 17, 1994.)THE SECTION OF PIPE WAS CUT OUT FOR FUTUREANALYSIS AND A NEW JOINT INSTALLED. THE LINE WAS RETURNED TO SERVICE ONDECEMBER 12, 1994 AT 14:00 MST. THE NATIONAL RESPONSE CENTER AND MPCA STATEDUTY OFFICER WERE NOTIFIED OF THE INCIDENT ON DECEMBER 10, 1994.
2017-09-29 08:50 | YES | NO | 19950014 | 1994-12-27 | 450 | AMOCO PRODUCTION CO | NO | 1994-11-29 | 1330 | TX | HARRIS |  | NO |  | NO | HUFFSMITH STATION, 1703 E. HUFFSMITH RD, HUFFSMITH, TEXAS |  | PUMPING STATION | BOLTED FITTING |  | 0 | OTHER | FAILED GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 250 | 250 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DONNA NELLIGAN | 4099386930 | PRIOR TO INCIDENT, AFFECTED STATION PIPING HAD BEEN ISOLATED FROM LINEPRESSURE TO FACILITATE MAINTENANCE WORK. UPON COMPLETION OF SAID WORK, THEPIPING WAS RE-ALIGNED FOR NORMAL OPERATIONS. UPON RE-ALIGNMENT, A GASKET ON ABLINDED FLANGE WITHIN THE MANIFOLD PIPING/VALVE BOX FAILED. OUTAGE WAS FULLYCONTAINED WITHIN THE MANIFOLD PIPING/VALVE BOX AT APL'S HUFSMITH STATION.TOTAL RELEASE WAS FULLY RECOVERED.
2017-09-29 08:50 | YES | NO | 19950015 | 1995-01-04 | 19223 | SUN PIPE LINE CORPORATION - GENERAL WASH BLDG | NO | 1994-11-30 | 1600 | OK | GARFIELD |  | NO |  | NO | SW4 SEC 26 21N 6W, GARFIELD COUNTY, OK |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 9749.5581 | 19668.7967 | CRUDE OIL | 1 | 200 | 200 | NO | NO | 8.63 | 0.16 | 1519 | WELDED |  | 745 | 60 | YES | 24 | 1190 | 5 | 78 | INTERNAL | Null | YES | OTHER | REDUCING BACTERIAL CORR. | NO DATA |  | Null | NO DATA |  | Null | Null | E.F. COEN | 9183524363 | LEAK OCCURRED AT SIX O'CLOCK LOCATION IN PIPELINE. PIPELINE WAS LOCATED IN LOW SPOT AT BOTTOM OF A CREEK.
2017-09-29 08:50 | YES | NO | 19950016 | 1994-12-27 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1994-11-17 | 1500 | TX | SAN PATRICIO |  | NO |  | NO | APPROXIMATELY 500 YARDS WEST OF COUNTY ROAD 67 AND 500 YARDS SOUTH OF COUNTY ROAD 74 IN SAN PATRICIO COUNTY, TEXAS. |  | LINE PIPE | PIPE |  | 1991 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 1478 | 1149 | NO | NO | 10 | 0.19 | 60000 | WELDED |  | 1440 | 975 | YES | 8 | 1936 | 5 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS TELEPHONE # | NO | NO | JAY LONGFELLOW | 5122425529 | TENNESSEE PIPELINE CO. RUPTURED PIPELINE WITH TRENCHER WHILE DIGGING NEW PIPELINE DITCH FOR DIAMOND SHAMROCK
2017-09-29 08:50 | YES | NO | 19950017 | 1994-12-27 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1994-10-08 | 400 | TX | SAN PATRICIO |  | NO |  | NO | 1 MILE WEST OF INTERSECTION CO RD 79 AND CO RD 72 ON CO RD 72 IN SAN PATRICIO COUNTY, TX. |  | LINE PIPE | PIPE |  | 1948 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | OTHER | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2151 | 381 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1050 | 1250 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | INCLEMENT WEATHER | Null | NO DATA |  | Null | Null | JAY LONGFELLOW | 5122425527 | INCLEMENT WEATHER CAUSED MOTOR OPERATED VALVE TO CLOSE ON FLOWING PIPELINE.OVERPRESSURE CAUSED PIPELINE TO RUPTURE.
2017-09-29 08:50 | YES | NO | 19950018 | 1995-01-10 | 10318 | KOCH REFINING CO | YES | 1994-12-02 | 816 | WI | PORTAGE |  | NO |  | NO | LEGAL DESCRIPTION NW 1/4 - SEC.20 - T23N - R8E, PORTAGE COUNTY, WISCONSIN |  | LINE PIPE | VALVE |  | 1987 | OTHER | CHECK VALVE O-RING FAILUR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 149993.2019 | 302596.8729 | GASOLINE | 1 | 2619 | 2619 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.A. RALSTON | 6124584845 | PIPELINE CONTROL DETECTED A SMALL IMBALANCE ON THE LEAK DETECTION SYSTEM.CREWS WERE DISPATCHED TO INVESTIGATE AND DISCOVERED THE PROBLEM. A FAULTYO-RING ON A BURIED CHECK VALVE WAS DISCOVERED TO BE THE CAUSE OF THESITUATION. SUPPLEMENTAL REPORT 5/10/1995 INDICATED CHANGE IN AMOUNT SPILLED,FROM 476 TO 2619. TOTAL AMOUNT RECOVERED IS 2619.
2017-09-29 08:50 | YES | NO | 19950019 | 1995-01-06 | 15674 | PLANTATION PIPE LINE CO | YES | 1994-12-07 | 1520 | GA | CARROLL | BREMEN | NO |  | NO | TANK 65 AT PLANTATION'S BREMEN TANK FARM |  | TANK FARM | TANK |  | 1947 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 360000 | 269987.7634 | 544674.3712 | GASOLINE | 3 | 3672 | 47 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK | 4043645916 | WHILE INSTALLING MONITORING WELLS AND EXTRACTING SOIL GAS SAMPLES AS PART OFA SUBSURFACE CONTAMINATION SOURCE IDENTIFICATION PLAN AT PLANTATION'S BREMENTANK FARM, A THIRD PARTY HYDROLOGY/ENVIRONMENTAL ENGINEERING FIRMENCOUNTERED SUBSURFACE, FREE PHASE GASOLINE. FURTHER EXPLORATION AND DATAGATHERING IDENTIFIED TANK 65 AS THE MOST LIKELY SOURCE OF CONTAMINATION. AT15:20 EST ON DECEMBER 7, 1994, THE TANK WAS REMOVED FROM SERVICE FOR CLEANINGAND INSPECTION. ON DECEMBER 9, 1994, A 3"-LONG CRACK IN THE FLOOR-TO-SUMP WELDON THE WESTERLY SIDE OF THE SUMP WAS DISCOVERED. THE ENTIRE TANK FLOOR WILL BEREPLACED. A COMPREHENSIVE PLAN WILL BE DEVELOPED AND IMPLEMENTED TO RECOVERTHE LOST PRODUCT AND REMEDIATE CONTAMINATED SOILS AND GROUNDWATER.
2017-09-29 08:50 | YES | NO | 19950020 | 1994-01-18 | 26065 | NATIONAL COOP REFINERY ASSCO | YES | 1995-01-05 | 1030 | KS | RILEY |  | NO |  | NO | NCRA PRODUCTS PIPELINE MILE POST #80N.-SE1/4,SECTION 25,T8S,R4E,RILEY CNTY,KS,FROM LEONARDVILLE KS W3 MILES ON HW.24,S. 3 MILES ON HWY 82 W. .25 MILES ON GRAVEL |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 29375.5825 | 59262.4151 | FUEL OIL | 3 | 350 | 340 | NO | NO | 6.63 | 0.25 | 35000 | WELDED |  | 1440 | 700 | YES | 24 | 1000 | 0 | 41 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DOUGLAS D. GRAUER | 9133637781 | ON JANUARY 5, 1995 AT 10:30AM, THE BLUE RAPIDS, KANSAS PUMP STATION WENT DOWNON A LOW SUCTION ALARM. AT THE TIME, THE PRODUCTS PIPELINE (PPL) HAD ALL FOURPUMP STATIONS RUNNING. THE DISPATCHER AT MCPHERSON, KS CLEARED THE ALARM ANDRE-STARTED THE BLUE RAPIDS PUMP STATION AT 10:35AM. THE CONTROL VALVE AT BLUERAPIDS WOULD NOT OPEN BACK UP TO 47%. IT CONTINUED TO PINCH DOWN. WE DECIDEDTO SHUT DOWN THE FOUR PPL PUMP STATIONS: MCPHERSON, KS PUMP STATION - MP 0 -SHUTDOWN AT 10:44AM; ABILENE, KS PUMP STATION - MP 49 - SHUTDOWN AT 10:46AM;BLUE RAPIDS, KS PUMP STATION - MP 109 - SHUTDOWN AT 10:47AM; TECUMSEH, NE PUMPSTATION - MP 167 - SHUTDOWN AT 10:48AM. AT 10:50AM, WILLIAM PETERSON CALLEDTHE PPL OFFICE AT BLUE RAPIDS AND TOLD US THAT ONE OF HIS CATERPILLAR D8HDOZERS HAD HIT THE PPL SOUTHWEST OF LEONARDVILLE, KS. WILLIAM PETERSONCONSTRUCTION WAS BUILDING A POND IN A PASTURE FOR THE LANDOWNER, WESLEYLLEWELYN. WILLIAM GAVE US THE LOCATION OF THE ACCIDENT: FROM LEONARDVILLE, KSGO 3 MI WEST, 3 MI. SOUTH, AND .25 MI WEST. WILLIAM TOLD US THAT PRODUCT WASSPILLING OUT OF OUR PIPELINE AND WAS CONTAINED IN THE POND. WE DECIDED THELOCATION WAS NCRA PPL MP 80. AT 10:52AM, PPL PERSONNEL LEFT BLUE RAPIDSSTATION TO CLOSE VALVES ON EACH SIDE OF THE PUNCTURE. WINKLER VALVE - MP 94,WAS CLOSED AT 11:14AM. N. WAKEFIELD VALVE - MP 74 WAS CLOSED AT 11:34AM.PRODUCTS PIPELINE PERSONNEL ARRIVED AT THE ACCIDENT SITE AT 11:45AM. 350BARRELS OF #2 FUEL OIL (BATHC #44) HAD SPILLED INTO THE POND AND WASCONTAINED. NCRA ENVIRONMENTAL, HEALTH AND SAFETY PERSONNEL RESPONDED TO THEACCIDENT. TWO NCRA CRUDE PIPELINE TANK TRUCKS (8,000 GALLON CAP) WERE CALLEDIN TO VACUUM UP THE SPILLED #2 FUEL OIL. 340 BARRELS OF PRODUCT WERERECOVERED. 19 4FT BAGS OF SPHAG SORB WERE PLACED IN THE POND AREA TO SOAK UPTHE SMALL POCKETS OF PRODUCT THAT COULD NOT BE VACUUMED UP. A 3 FT 6INCHSECTION OF DAMAGED PIPE WAS CUT OUT OF THE PPL USING COLD CUTTERS. IN TALKINGWITH WILLIAM PETERSON DURING THE AFTERNOON, WE FOUND OUT THAT HE HAD NOTATTEMPTED TO CALL THE KS ONE-CALL SYSTEM, INC. AT 1-800 DIG-SAFE. ALSO HE HADNOT ATTEMPTED TO CALL US AT NCRA PPL AT 1-316-241-6611 OR 1-913-363-7781.WESLEY LLEWELYN, THE LANDOWNER, HAD TOLD WILLIAM THAT THE PIPELINE WAS 200YDS FURTHER NORTH OF THE POND OR ACCIDENT SITE. IT IS ALSO INTERESTING TONOTE THAT WILLIAM PETERSON CONSTRUCTION DROVE RIGHT BY ONE OF OUR AERIALMARKERS TO GET INTO THE PASTURE. THE MARKER IS TEN FEET WEST OF THE ENTRANCEROAD INTO THE PASTURE. JAN 6, 1995... A QUALIFIED WELDER ARRIVED TO REPAIRTHE PRODUCTS PIPELINE. THE 3FT 6INCH SECTION OF PIPE WAS REPLACED WITHPRE-TESTED PIPE. PIPE SPECIFICATIONS ARE AS FOLLOWS: 6.625 IN. O.D.; .432 IN.W.T.; API 5L GRADE B; SEAMLESS; TESTED ON 5/5/81 AT 1800 PSIG FOR FOUR HOURS.TWO BUTT WELDS WERE PERFORMED. THE TWO WELDS WERE X-RAYED BY A CERTIFIEDX-RAY TECHNICIAN. THE WELDS PASSED X-RAY. PPL PERSONNEL OPENED VALVES AT MP74 AND MP 94. THE GAUGER OPENED THE VALVE AT THE COUNCIL BLUFFS TERMINAL.MCPHERSON PUMP STATION WAS STARTED AT 7:30 PM. BLUE RAPIDS PUMP STATION WASSTARTED AT 8:28 PM. JAN. 9, 1995.... 12FT - 1 INCH OF COATING WAS REPLACEDWITH ROYSTON PRIMER AND ROYSTON GREENLINE TAPE. THE PPL WAS LOWERED 38 INCHESAT THE ACCIDENT SITE. 275 FEET OF TRENCH WAS DUG. THE PRESSURE IN THE PPL WAS380 PSIG. AT 1:00PM WHEN THE PIPELINE WAS LOWERED. NCRA PPL PERSONNEL WORKEDWITH THE KS DEPT OF HEALTH AND ENVIRONMENT- KDHE - SCOTT LANG TO CLEAN UP THESPILL. 280 CUBIC YARDS OF #2 FUEL OIL SATURATED SOIL WAS REMOVED FROM THEBOTTOM OF THE POND AND SURROUNDING AREA. THE SATURATED SOIL WAS STOCKPILED ON
2017-09-29 08:50 | YES | NO | 19950021 | 1995-01-12 | 25133 | TEXACO TRADING & TRANSPORTATION INC | Null | 1994-12-22 | 1100 | CA | KERN |  | NO |  | NO |  |  | TANK FARM | NO DATA |  | 0 | OTHER | EXPANSION COUPLER LOOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3749.83 | 7564.9218 | CRUDE OIL | 1 | 550 | 515 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. KELLEY | 8053282331 | COMPRESSION TYPE EXPANSION JOINT CAME LOOSE WHILE MAKING TANK SWITCH.
2017-09-29 08:50 | YES | YES | 19950022 | 1995-01-17 | 402 | AMERICAN CENTRAL GAS CO INC | NO | 1994-12-23 | 1140 | TX | PANOLA |  | NO |  | NO | NE CORNER OF MATHEW PARKER SURVEY A-257 ON PANOLA CNTY RD 115A AND APPROX. 1000' S. OF INTERSECTION OF CNTY RD 116 ON WEST SIDE OF RD. |  | TANK FARM | TANK |  | 1994 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 1 | 0 | 1 | 40000 | 29998.6404 | 60519.3746 | CONDENSATE | 1 | 0 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES E. LIND | 9187496776 | ON DECEMBER 23, 1994, DURING ROUTINE PIGGING OPERATIONS OF ACG'S 12" GATHERING LINE TO THE STATION INVOLVED IN THE ACCIDENT (ACG OXY STATION), A 2 1/2" FISHER LIQUID LEVEL CONTROL VALVE ON THE INLET GAS/LIQUID SEPARATOR HUNG OPEN CAUSING OVERPRESSURE OF ONE 210 BBL CONDENSATE STORAGE TANK. THE STORAGE TANKROOF RUPTURED IGNITING TWO ADJACENT 210 BBL CONDENSATE TANKS AND ONE 100 BBLFIBERGLASS WATER TANK WITHIN THE DIKE, ONE NATURAL GAS DEHYDRATION UNIT'S CONTROL INSTRUMENTATION WATER WELL PIPING, AN ELECTRICAL SWITCHRACK, AND PROPERTY OPERATED BY OXY USA ON THE EAST SIDE OF THE ROAD INCLUDING APPROXIMATELY 25 PINE TREES, TIN BUILDING MATERIAL, AND CONDENSATE TANK VENTS. CAUSE OF THE VALVE HANGING OPEN WAS FOUND TO BE ONE 1/8" THICK BY 1 3/8" LONG METAL "SLAG"MATERIAL LEFT IN THE INLET SEPARATOR AFTER ITS INITIAL CONSTRUCTION IN JUNE 1994. THE ONLY INJURY REPORTED WAS TO AN OXY USA RELIEF PUMPER WHO WAS IN AN OFFICE APPROXIMATELY 250 YARDS FROM THE ACCIDENT SITE AND STRAINED HIS LOWER BACK WHEN GETTING OUT OF HIS CHAIR TO DETERMINE THE NATURE OF THE EXPLOSION.
2017-09-29 08:50 | YES | NO | 19950023 | 1995-01-17 | 1682 | BP OIL PIPELINE CO | YES | 1994-12-29 | 1415 | IL | CLAY | FLORA | NO |  | NO | 3' SOUTH OF TANK 1096 & FLORA PUMP STATION STATION #1593+90 |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 196 | 193 | NO | NO | 10.75 | 0.37 | 35000 | WELDED |  | 800 | 750 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | PERTIFIER | NO DATA |  | Null | ONE CALL |  | Null | Null | G.D. FITZGERALD | 6187756413 | AT APPROXIMATELY 1415 HRS ON 12/29/94, BP PIPELINE EMPLOYEE R.D. JONESDISCOVERED OIL ON GROUND SURFACE NEAR TANK 1096 AT FLORA STATION, FLORA,ILLINOIS. IT WAS DETERMINED THAT THE SOURCE OF THE RELEASE WAS THE SALEM-STOY10" CRUDE LINE AND IT WAS IMMEDIATELY SHUT DOWN. THE PIPE WAS EXCAVATED AND ASMALL CORROSION PIT WAS LOCATED ON THE TOP (1200 POSITION). THE PIPE WASFURTHER INSP ECTED AFTER THE COATING WAS REMOVED AND A 1 1/4" LONG GOUGE WADDISCOVERED WITH SOME CORROSION ALSO PRESENT. ANOTHER GOUGE WAS LOCATED IN THESAME AREA AND WAS 1/2" IN LENGTH. THE AREA HAD BEEN COATED AND WRAPPED OVERTHE GOUGHES SOMETIME IN THE PAST. TEMPORARY REPAIRS WERE COMPLETED ON 12/29BY CLAMPING A 6"X6" PATCH OVER THE HOLE AND THE LINE WAS RESTARTED AT 1810HRS. APPROXIMATELY 195 BARRELS OF CRUDE OIL WAS PICKED UP FROM THE DIKE AREAWITH VACUUM TRUCKS AND HAULED TO SALEM STATION TANK #1201. ON 12/30 PERMANENTREPAIRS WERE COMPLETED BY WELDING THE 6"X6" PATCH ON THE HOLE AND A 3"X3"PATCH ON THE ADJACENT 1/2"GOUGE. THE PIPE WAS COATED AND WRAPPED. CLEAN-UP OFTHE AREA CONTINUED ON 12/30.
2017-09-29 08:50 | YES | NO | 19950024 | 1995-01-19 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1994-12-20 | 1353 | LA | RED RIVER |  | NO |  | NO | APPROXIMATELY 5 MILES NORTHWEST OF THE COMMUNITY OF POWHATTAN; RED RIVER M.P. 166.5. |  | LINE PIPE | PIPE |  | 1944 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 1027700 | 770740.068 | 1554894.0313 | GASOLINE | 3 | 3181 | 0 | NO | NO | 20 | 0.5 | 35000 | WELDED |  | 690 | 400 | YES | 24 | 1119 | 0 | 57 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | ONE CALL |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | AT 1353 HOURS CST DECEMBER 20, 1994, TEPPCO PERSONNEL IDENTIFIED A SHUT DOWNOF TWO REMOTE PUMPING FACILITIES ON THE COMPANY'S 20" P-2 PIPELINE. THEEMERGENCY PLAN WAS IMMEDIATELY IMPLEMENTED. LOCAL AUTHORITIES BETWEEN THE TWOPUMP STATIONS WERE NOTIFIED OF THE POTENTIAL FOR A PIPELINE RELEASE AND THESYSTEM WAS BLOCKED IN. THE OPA 90 SPILL RESPONSE PLAN WAS IMMEDIATELYIMPLEMENTED UPON CONFIRMATION OF THE RELEASE LOCATION. BASED ON A REPORT FROMLOCAL AUTHORITIES, IT WAS DETERMINED THAT THE RED RIVER CROSSING HAS FAILED.AT THE TIME OF THE FAILURE, THE RED RIVER WAS IN HIGH FLOW CONDITION, WHICHHAMPERED EFFORTS TO VISUALLY INSPECT THE RIVER CROSSING. THE PIPELINE FAILEDDUE TO A WASHOUT OF COVER AROUND THE LINE, HOWEVER, THE EXACT CAUSE OF THEFAILURE IS UNKNOWN. THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY DECLAREDCLEAN-UP OF THE INCIDENT SITE COMPLETE DECEMBER 22, 1994. INSTALLATION OF ANEW BORED CROSSING WAS BEGUN ON DECEMBER 24 AND THE LINE WAS PLACED BACK INTOSERVICE ON JANUARY 5, 1995.
2017-09-29 08:50 | YES | NO | 19950025 | 1995-01-23 | 2552 | COLONIAL PIPELINE CO | YES | 1994-12-16 | 1923 | MD | HARFORD | FOREST HILL | NO |  | NO | COLONIAL PIPELINE COMPANY'S ABERDEEN JCT. |  | TANK FARM | VALVE |  | 1965 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 3783046 | 2837155.9124 | 5723689.4477 | FUEL OIL | 3 | 1750 | 48 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J.L. GAMBRELL | 4048412402 | DURING A GASOLINE DELIVERY INTO ABERDEEN JUNCTION ON THE EVENING OF DECEMBER16, 1994, THE LOCAL OPERATOR ON DUTY RECEIVED A "HIGH" SUMP ALARM AND THEN AFEW MINUTES LATER, A SUMP "MAXFILL" ALARM. THE OPERATOR IMMEDIATELY ADVISEDTHE LINE 03 CONTROLLER TO SHUT DOWN THE DELIVERY. A CHECK OF THE STATIONREVEALED THAT PRODUCT HAD SPILLED OUT OF THE SUMP AND INTO THE STATION YARD.APPROXIMATELY 121 BARRELS OF PRODUCT WAS PICKED UP AND RETURNED TO THE SYSTEM.ALL PRODUCT SPILLED WAS CONTAINED WITHIN THE STATION YARD. AT 2210 EST ONDECEMBER 16, 1994, THE NATIONAL RESPONSE CENTER WAS NOTIFIED OF THE INCIDENT,REPORT NO. 273543. THE MARYLAND DEPARTMENT OF ENVIRONMENT AND THE OFFICE OFPIPELINE SAFETY WERE ALSO NOTIFIED OF THE INCIDENT. THE CAUSE OF THE LEAK WASFOUND TO BE A 3-INCH DRAIN VALVE ON THE PROVER LOOP INADVERTENTLY LEFTOPEN. SUPPLEMENTAL REPORT 2/3/95 INDICATES THAT AFTER EXTENSIVE SOIL TESTING,COLONIAL'S ENVIRONMENTAL TEAM HAS NOW DETERMINED THAT THE ESTIMATED AMOUNT OFCOMMODITY SPILLED IS 140 BARRELS.
2017-09-29 08:50 | YES | NO | 19950026 | 1995-01-24 | 25133 | TEXACO TRADING & TRANSPORTATION INC | Null | 1995-01-05 | 900 | CA | LOS ANGELES | CARSON | NO |  | NO | 2160 SEPULVEDA, CARSON, CALIFORNIA |  | NO DATA | OTHER | TRUCK UNLOADING | 0 | OTHER | WASHOUT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 510000 | 374538.6766 | 755595.7928 | CRUDE OIL | 1 | 5 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | NO DATA |  | Null | Null | RICHARD E. KELLEY | 8053282331 | TRUCK UNLOADING RACK SUMP FLOODED WITH WATER AND RELEASED APPROXIMATELY FIVE(5) BARRELS OF CRUDE IN FLOODED AREA.
2017-09-29 08:50 | NO | NO | 19950027 | 1995-01-27 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1994-11-23 | 1800 | TX | LEE |  | NO |  | NO | ONE MILE ESE OF FM 180 & FM 1697 INTERSECTION |  | LINE PIPE | PIPE |  | 1985 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 35 | 34 | NO | NO | 4 | 0.19 | 0 | WELDED |  | 150 | 100 | Null | 0 | 0 |  |  | NO DATA | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID FRITSCHE | 4095354855
2017-09-29 08:50 | YES | NO | 19950028 | 1995-01-27 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1994-12-06 | 1225 | TX | LEE |  | NO |  | NO | 200 YARDS EAST NORTH EAST OF FM 141 AND CR 430 INTERSECTION. |  | LINE PIPE | PIPE |  | 1983 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 180 | 176 | NO | NO | 4 | 0.19 | 0 | NO DATA |  | 150 | 100 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.T. LARD | 4095354855
2017-09-29 08:50 | YES | NO | 19950029 | 1995-01-27 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1994-12-24 | 1940 | TX | GALVESTON |  | NO |  | NO | 3/4 MI. W. OF S. H. 146; 1/2 MILE SOUTH OF INDUSTRIAL ROAD. |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 112494.9014 | 226947.6547 | NATURAL GAS LIQUID | 1 | 2434 | 243 | NO | NO | 6.63 | 0.25 | 2641 | WELDED |  | 1440 | 1260 | YES | 8 | 1850 | 12 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | P.L MARKERS COMM AWARENES | NO | NO | W.D. PARTLOW | 7138777370 | WHILE PUMPING FROM ALMEDA TERMINAL TO TEXAS CITY AND ON TO THE AMOCO CHEMICALS PLANT AT CHOCOLATE BAYOU, A VALVE WAS ABRUPTLY BLOCKED-IN AT AMOCO CAUSINGTHE PIPELINE TO PRESSURE-UP TO 1260# AND IMMEDIATELY FALLING TO 0#. UPON EXCAVATING THE PIPELINE LEAK SITE, IT WAS DISCOVERED THAT THE RUPTURE HAD OCCURRED WHER THE PIPELINE HAD BEEN DAMAGED BY AN OUTSIDE FORCE. APPROXIMATELY 16' OF 6" PIPE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19950030 | 1995-01-27 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1994-11-29 | 1947 | TX | KLEBERG |  | NO |  | NO | KING RANCH; 2 MILES SOUTHWEST OF FM 1355; 3 MILES NORTH ON FM 101 |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | L. P. G. | 2 | 25 | 0 | NO | NO | 12.75 | 0.25 | 42000 | WELDED |  | 720 | 400 | YES | 24 | 945 | 0 | 81 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW | 7138777370 | LEAK WAS INITIALLY IDENTIFIED BY EXXON PIPELINE PATROL PILOT AND REPORTED TOCOASTAL. THIS IS A LEASED PIPELINE FROM EXXON PIPELINE COMPANY AND THERE AREPIPELINES ADJACENT TO THIS SYSTEM. LEAK CREATED ICE BALL OVER AREA AND, ONCEDISSIPATED, A SPLIT SLEEVE CLAMP WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19950031 | 1995-01-30 | 879 | CHEMOIL REFINING | NO | 1994-12-25 | 25 | CA |  | LONG BEACH | NO |  | NO | INTERSECTION OF 23RD STREET AND SANTA FE AVENUE |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 56247.4507 | 113473.8273 | FUEL OIL | 1 | 1 | 1 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 720 | 600 | YES | 4 | 900 | 0 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID J. DARAGT | 3109213581 | THE OIL LEAK WAS DISCOVERED BY THE CITY OF LONG BEACH FIRE DEPARTMENT. THEOIL HAD COME UP THROUGH THE PAVEMENT AT THE INTERSECTION OF 23RD STREET ANDSANTA FE AVENUE. THE LEAK WAS REPORTED TO CHEMOIL VIA THE OIL SPILL "CALLWHEEL RESPONSE SYSTEM". CHEMOIL PERSONNEL CONTACTED A CLEANUP AND REPAIRCOMPANY T O BEGIN CLEANUP OF THE STREET AND UNCOVER THE 10" PIPELINE WHICH WASSUSPECTED OF BEING THE SOURCE OF THE LEAK. CHEMOIL ALSO CONTACTED GOLDEN WESTREFINING COMPANY, THE OWNER OF THE PIPELINE, WHO ALSO DISPATCHED PERSONNEL TOTHE SITE OF THE LEAK. LESS THAN 1 BARREL OF PRODUCT HAD SURFACED ON THESTREET. THE SITE OF THE LEAK AS WELL AS THE SURROUNDING STREET INTERSECTIONWAS CLEANED UP WITHIN 16 HOURS. THE LEAK WAS DUE TO EXTERNAL CORROSION CAUSEDBY THE FAILU RE OF THE PROTECTIVE PIPE RAP MATERIAL. APPROXIMATELY 6 FEET OFPIPE HAD BEEN REPLACED WITH PRETESTED PIPE AND THE LINE HAS BEEN RESTORED TOAN OPERATING CONDITION. COMPLETE REMEDIATION OF THE SITE INCLUDING PAVINGREPAIRS WAS ACCOMPLISHED BY JANUARY 13, 1995. PER CONVERSATION WITH D. DARAGTON 2/16/95, CLARIFICATION WAS MADE ON THE ESTIMATED TPD (PART F), WHICH ISLISTED ON THE FORM AS 75M... CLARIFIED AS $75,000, NOT 75 MILLION. CHANGEMADE IN SYSTEM.(CB) REQUESTED SUBMISSION OF SUPPLEMENTAL 2/16/95 TO DOCUMENTTHIS CLARIFICATION...(CB)
2017-09-29 08:50 | YES | NO | 19950032 | 1995-02-03 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1994-12-21 | 800 | CA | SAN JOAQUIN |  | NO |  | NO | CORRAL HOLLOW LAND FILL LOCATED AT CORRAL HOLLOW ROAD AND INTERSTATE I-580 |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2249.898 | 4538.9531 | CRUDE OIL | 1 | 550 | 535 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 940 | 300 | YES | 5 | 1175 | 1 | 90 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | G.G. HOHNSTEIN | 8053270110 | CORRAL HOLLOW LAND FILL AUTHORIZED SCS FIELD SERVICES TO DRILL TEST HOLESALONG PERIMETER OF LAND FILL TO TEST FOR METHANE GAS. A ONE-CALL ALERT WASISSUED AND RESPONDED TO BY TEXACO TRADING AND TRANSPORTATION INC'S MR. JOHNGUERRERO. (PLEASE REFER TO MR. GUERRERO'S LETTER ON 12/24/94). ANINVESTIGATION OF THE CAUSE OF THE ERRATIC SIGNAL FOUND IT WAS CAUSED BYMETALLIC OBJECTS BURIED IN THE DUMP, I.E., CABLE , BED SPRINGS, ETC. SCSDRILLING RIG SET UP OVER OUR PIPELINE AND DRILLED AT 1/2" HOLE IN THE TOP OFTHE PIPELINE. UNCONTROLLED LEAKAGE WAS ESTIMATED AT 50 BARRELS, WITHCONTROLLED DRAIN-UP AT 500 BARRELS . 535 BARRELS WERE RECOVERED AND RETURNEDTO THE PIPELINE SYSTEM. THE REMAINING 15 BARRELS WERE CONTAINED IN THE SOILWHICH WAS EXCAVATED AND WILL BE DISPOSED OF OFF-SITE. REPAIRS WEREACCOMPLISHED WITH A RUBBER PATCH OVER THE HOLE WITH A FULL ENCIRCLEMENT REPAIRSLEEVE WELDED TO THE PIPE. THE AREA WAS RETURNED TO IT'S ORIGINAL CONDITION.
2017-09-29 08:50 | YES | NO | 19950033 | 1995-02-05 | 737 | ASHLAND PIPELINE CO | YES | 1995-01-04 | 700 | KY | FAYETTE | LEXINGTON | NO |  | NO | JUDDMONTE HORSE FARM LOCATED ON WALNUT HILL RD APPROXIMATELY 2.5 MILES SOUTH OF RICHMOND ROAD. |  | LINE PIPE | OTHER | NOT GIVEN | 1973 | OTHER | NOT GIVEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 91798.6952 | 185195.0473 | CRUDE OIL | 1 | 27 | 27 | NO | NO | 24 | 0.25 | 1083 | WELDED |  | 780 | 759 | YES | 24 | 1083 | 0 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES O. SIMPSON | 5026832485 | THE ASHLAND CONTROL CENTER, IN ASHLAND KENTUCKY, RECEIVED A PHONE CALL FROMMR. BILL MALEY, WIMBLETON HORSE FARM, AT APPROXIMATELY 6:40 AM CST, JANUARY4, 1995, EXPLAINING THAT HE COULD SMELL WHAT HE THOUGHT WAS A STRONG ODOR OFCRUDE OIL OR DIESEL FUEL. THE COMPLAINT WAS FORWARDED TO FIELD PERSONNEL FOREVALUATION. THE PIPELINE WAS SHUT DOWN AT APPROXIMATELY 7:OO AM. A PIPELINECREW WAS DISPATCHED FROM LEBANON JUNCTION AND THE PIPELINE AERIAL PATROLCONTRACT OR WAS DISPATCHED TO FLY THE SECTION OF LINE IN QUESTION. THE CRUDEOIL LEAK WAS VERIFIED AT APPROXIMATELY 8:30 AM BY THE LEBANON JUNCTIONMAINTENANCE CRE W. ADDITIONAL CREWS AND EQUIPMENT WERE DISPATCHED FROMOWENSBORO AND GRAYSON. THE MAINTENANCE CREWS BUILT AN UNDERFLOW DAM DOWN THEHILL FROM THE LEAK TO CONTAIN THE OIL SHOULD IT START RAINING. THE MAINTENANCECREW EXCAVATED THE PIPELINE AND DISCOVERED THAT THE PIPELINE WAS LAYING ON AROCK LEFT IN THE BACKFILL DURING CONSTRUCTION CAUSING A DENT WHICH DEVELOPEDA SMALL CRACK. INITIAL LEAKAGE FROM THE PIPELINE WAS STOPPED AND THE PIPELINERESTARTED AT 11:00 PM, JANARY 4, 1995. THE PERMANENT PIPELINE REPAIR WASCOMPLETED THURSDAY, JANUARY 5, 1995 AT APPROXIMATELY 7:30 AM, WITH A 24" X36"PLIDCO REPAIR SLEEVE. SUBSEQUENT TO PLACING THE LINE BACK IN SERVICE ANDCOMPLETION OF THE INITIAL CLEANUP HEAVY RAINS CAUSED ADDITIONAL CRUDE OIL TOLEACH TO THE SURFACE REQUIRING FURTHER CLEANUP EFFORTS. ONCE THE INITIALCLEANUP EFFORT IS COMPLETED, THE LEAK SITE WILL BE MONITORED 2 TO 3 TIMES AWEEK, BY ASHLAND PERSONNEL, FOR FURTHER LEACHING OF CRUDE OIL. REMEDIATIONEFFORTS WILL CONTINUE UNTIL SUCH TIME AS CRUDE OIL LEACHING CEASES. INADDITION, THIS SECTION OF PIPE WILL BE SCHEDULED FOR FUTURE REPLACEMENT.
2017-09-29 08:50 | YES | NO | 19950034 | 1995-02-09 | 11537 | LIQUID ENERGY CORP | NO | 1994-12-25 | 230 | TX | BRAZOS | BRYAN | NO |  | NO | 3747 OLD RELIANCE ROAD BRYAN, TX 77808 |  | LINE PIPE | OTHER | RELIEF VALVE | 1990 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 95 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BRAD MARTIN | 4097782744 | AT APPROXIMATELY 2:00 AM ON DECEMBER 25TH, THE BRYAN HICKS FACILITY SHUTDOWN.THE PIPELINE PUMPS AT BRYAN HICKS COULD NOT BE RESTARTED. THE OPERATOR ATBRYAN HICKS CALLED THE MADISON PLANT TO TELL THEM TO SHUTDOWN THEIR PUMPS BUTCOULD NOT GET AN ANSWER. SOON, THE RELIEF VALVE ON THE METER SKID RELIEVED(SET AT 530) CAUSING A LPG VAPOR CLOUD TO BE RELIEVED INTO THE AIR. THEOPERATORS AT BRYAN-HICKS CALLED 911, GAS CONTROL, AND THE MADISON PLANT SUPT.AFTER APPROX. 30 MINUTES, THE PRESSURE ON THE PIPELINE WENT BELOW RELIEF VALVESETTING PRESSURE. PLANT OPERATOR WENT TO THE RELIEF VALVE AND RESTARTED IT.THE VAPOR CLOUD DISAPPEARED. EMERGENCY PERSONNEL ARRIVED, BUT THE SITUATIONWAS CLEAR AND WERE SENT HOME. A REPORT WAS SENT TO THE TNRCC FOR EXCESSEMISSIONS. A TELEPHONE REPORT WAS GIVEN TO THE RAILROAD COMMISSION, AND AFORMAL REPORT WILL BE SENT TO THE RAILROAD COMMISSION WITHIN 30 DAYS OF THEINCIDENT. THERE WERE NO INJURIES OR EQUIPMENT DAMAGE. THE CAUSE OF THEINCIDENT IS BEING INVESTIGATED. THERE WERE NO INJURIES OR EQUIPMENT DAMAGE.SEVERAL OF THE CAUSES HAVE ALREAD BEEN FIXED.THE PROBABILITY OF THIS INCIDENT RECURRING IS VERY SMALLBECAUSE THE PIPELINE WILL BE REPLACED WITHIN A FEW WEEKS AND MANY OF THECAUSES OF INCIDENT HAVE BEEN FIXED.
2017-09-29 08:50 | YES | NO | 19950035 | 1995-02-01 | 26350 | TEXACO TRADING & TRANSPORTATION INC | YES | 1995-01-02 | 1600 | OK | LINCOLN |  | NO |  | NO | NW 1/4, SEC 22, T 17 N, R 5 E LINCOLN CTY, OK FROM THE INTERSECTION OF HWY 33 AND HWY 18 IN CUSHING OK GO 3 MI S, 1/2 MI. E, AND 150' S. TO LOCATION. |  | TANK FARM | TANK |  | 1946 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 41500 | 30477.1668 | 61484.7557 | CRUDE OIL | 1 | 30000 | 29500 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOYD BRATIL | 9182253469 | TANK #320 AT THE TEXACO TERMINALS, INC. TANK FARM IN CUSHING, OKLAHOMA FAILEDAT THE CONNECTION LOCATED BETWEEN TANK SHELL AND SUCTION/FILL LINE. FAILUREWAS ATTRIBUTED TO TANK SETTLEMENT WHICH PLACED EXCESSIVE STRESS ON SUCTION/FILL LINE WHICH HAD ADEQUATE SUPPORT. TANK FAILURE ACTIVATED ALARM SYSTEM FORIDLE TANKS WHICH SIGNIFIED TANK FAILURE. COMPANY PERSONNEL REROUTED CONTENTSOF FAILED TANK TO ADDITIONAL STORAGE TANKS. OIL NOT RECOVERED BY TRANSFERRINGPROCESS SPILLED INTO PRIMARY CONTAINMENT DIKE. THE PRIMARY DIKE OVERFILLEDWHICH ROUTED OIL INTO COMPANY OWNED CATCHMENT BASIN WHERE IT WAS CONTAINED.ALL OIL SPILLED WAS CONTAINED ON TEXACO PROPERTY AND WAS NEVER IN DANGER OFREA CHING "WATERS OF THE STATE".
2017-09-29 08:50 | YES | NO | 19950036 | 1995-02-14 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-01-12 | 900 | OH | BUTLER |  | NO |  | NO | CORNER OF TODUNTER RD AND YANKEE RD; N 39 27" 38.4", W84 23" 48.9" |  | TANK FARM | OTHER | COIL,DIRECT FIRED HEATER | 0 | OTHER | COIL DIRECT FIRED HEATER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8600 | 6315.7502 | 12741.4193 | L. P. G. | 2 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | AT APPROXIMATELY 0900 HOURS, CST, JANUARY 12,1995, A COIL IN A DIRECT FIRED HEATER FAILED RESULTING IN A FIRE INSIDE THE HEATER FIRE BOX AT THE TODHUNTERTERMINAL. TERMINAL PERSONNEL IMMEDIATELY ENACTED EMERGENCY PROCEDURES AND ISOLATE THE DIRECT FIRED HEATER. THE FIRE WAS PERMITTED TO EXTINGUISH ITSELF UNDER A SUPERVISED CONTROLLED BURN. THE HEATING COIL WAS REPLACED AND THE UNIT RESTARTED JANUARY 13, 1995.
2017-09-29 08:50 | NO | NO | 19950037 | 1995-02-14 | 30658 | KERN OIL & REFINING CO. | NO | 1995-01-30 | 1600 | CA | KERN | BAKERSFIELD | NO |  | NO | ON N. SIDE REDBANK RD APPROX 200 FEET WEST OF WEEDPATCH HWY (STATE HWY 184). (EAST OF BAKERSFIELD SOUTH OF HWY 58.) |  | LINE PIPE | PIPE |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | FAILED PIPE | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2937.5582 | 5926.2415 | CRUDE OIL | 1 | 35 | 35 | NO | NO | 5 | 0.26 | 24000 | WELDED |  | 700 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | YES | KEN HIGH | 8058450761
2017-09-29 08:50 | NO | NO | 19950038 | 1995-02-14 | 30658 | KERN OIL & REFINING CO. | NO | 1995-01-31 | 800 | CA | KERN | LAMONT | NO |  | NO | IN CENTER OF SEC 9 TBLS-R29E KERN CTNY SECTION BOUNDED BY DIGEORIO RD ON N. MALAGA DR. ON E. BUENA VISTA BLVD ON S. AND EDISON RD ON W. |  | LINE PIPE | PIPE |  | 1934 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 440.6337 | 888.9362 | CRUDE OIL | 1 | 15 | 10 | NO | NO | 6 | 0.28 | 24000 | WELDED |  | 700 | 0 | YES | 0 | 1100 |  | 77 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | KEN HIGH | 8058450761 | 7
2017-09-29 08:50 | YES | NO | 19950039 | 1995-02-21 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-01-17 | 1130 | KS | HARPER |  | NO |  | NO | TOWNSHIP 35 SOUTH RANGE 5 WEST, SECTION 10, HARPER CNTY, KANSAS TRACT NO.64-K-HA-63. |  | LINE PIPE | PIPE |  | 1973 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 3818.8257 | 7704.114 | ANHYDROUS AMMONIA | 2 | 30 | 0 | NO | NO | 8.63 | 0.16 | 46000 | WELDED |  | 1198 | 200 | YES | 24 | 1592 | 1 | 74 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SID P. RUETER | 9185811800 | THIRD PARTY (FARMER) CALLED TO REPORT A DEAD SPOT IN VEGETATION. UPON INVESTIGATION A PINHOLE WAS DISCOVERED IN THE LONGITUDINAL SEAM OF THE 8" ERW PIPE. THE LINE WAS SHUT DOWN, PRESSURE PULLED DOWN AND BLOCKED IN. THE LINE WAS PERMANENTLY REPAIRED BY INSTALLING A FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19950040 | 1995-02-22 | 26125 | CALNEV PIPELINE CO | YES | 1995-02-09 | 900 | CA | SAN BERNARDINO |  | NO |  | NO | COLTON TERMINAL 2051 E. SLOVER AVE COLTON, CA, 92316-2423 |  | TANK FARM | TANK |  | 1961 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 734.3896 | 1481.5604 | DIESEL FUEL | 1 | 70 | 65 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BRIAN J. MCGUIRE | 9093879509 | COLTON TERMINAL DRAIN DRY TANK #133 WAS TAKEN OUT OF SERVICE FOR INSPECTION/REPAIR. THE TANK SUCTION/FILL LINE WAS BLINDED OFF AT THE TANK VALVE. AFTER COMPLETING THE INSPECTION/REPAIRS, THE BLIND WAS REMOVED AND THE SPOOL PIECE FLANGE RECONNECTED TO THE TANK. WHILE REFILLING THE TANK IT WAS DISCOVERED THATTHE FLANG WAS NOT TIGHT AND SEATED PROPERLY. THE DIESEL FUEL ESCAPED FROM THESUCTION/FILL LINE. APPROXIMATEY 65 BBLS WERE RECOVERED OF THE 70BBLS RELEASED.
2017-09-29 08:50 | YES | NO | 19950041 | 1995-02-24 | 12626 | MOBIL PIPELINE CO - EMPIRE | NO | 1995-02-02 | 1600 | TX | NAVARRO | CORSICANA | NO |  | NO | 1/4 MILE WEST OF SOUTH 15TH ON MAIN TANK FARM RD, 150' WEST OF MAIN TANK AND 75' WEST OF #7 BOOSTER PUMP. |  | LINE PIPE | BOLTED FITTING |  | 1953 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NOT GIVEN | 3 | 0 | 0 | YES | NO | 24 | 0.25 | 35000 | WELDED |  | 50 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | M.A. HAMRICK | 2146583414 | ON THURSDAY, FEBRUARY 2, 1995, CONTRACT EMPLOYEES UNDER THE SUPERVISION OFMOBIL, WERE INSTALLING A 24" CHECK VALVE IN THE CRUDE SUCTION LINE ATCORSICANA TANK FARM. CONTRACT EMPLOYEES HAD COLD CUT THE LINE AND THE WELDERHAD INSTALLED WELDED FLANGES NECESSARY TO INSTALL THE CHECK VALVE.SUBSEQUENTLY, WHILE POSITIONING THE CHECK VALVE INTO PLACE A FLASH FIREOCCURRED. SIX CONTRACT EMPLOYEES EVACUATED THE IMPACTED AREA. THE FLAMES WEREEXTINGUISHED WITHIN 2.5 MINUTES, UTILIZING A 30# DRY CHEMICAL FIREEXTINGUISHER. NO MEDICAL TREATMENT WAS REQUIRED OR SOUGHT BY AFFECTEDEMPLOYEES, AND THERE WAS NO PROPERTY DAMAGE. THE ROOT CAUSE OF THE INCIDENTWAS AN ELECTRICAL ARC DUE TO RECTIFIERS NOT BEING TURNED OFF AND BONDING ANDGROUNDING CABLES NOT BEING UTILIZED. THIS PROVIDED A SOURCE OF IGNITION WHENTHE 24" VALVE TOUCHED THE OPEN ENDED LINES.
2017-09-29 08:50 | YES | NO | 19950043 | 1995-03-02 | 808 | ARCO TERMINAL SERVICES CORP | NO | 1995-02-01 | 650 | UT | SAN JUAN | MONTEZUMA | NO |  | NO | INTERSECTION OF UTAH HWY.262 AND NAVAJO HWY. NO 35 |  | LINE PIPE | PIPE |  | 1992 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 367194.781 | 740780.1891 | CRUDE OIL | 1 | 500 | 160 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1168 | 150 | YES | 4 | 1460 | 6 | 92 | INTERNAL | Null | YES | OTHER | 1/2 DIAMETER INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. BARRETT | 3104289000 | ON FEBRUARY 1, 1995, A LEAK WAS DISCOVERED IN LINE 91, THE 16 INCH SOUTH SIDE GATHERING LINE, IN THE ANETH GATHERING SYSTEM. THE LEAK WAS CAUSED BY INTERNAL CORROSION IN A 130FT SECTION OF LINE THAT WAS REPLACED IN 1992.
2017-09-29 08:50 | YES | NO | 19950044 | 1995-03-02 | 15674 | PLANTATION PIPE LINE CO | YES | 1995-02-14 | 447 | NC | GUILFORD | GREENSBORO | NO |  | NO | ACCIDENT OCCURRED AT EXXON COMPANY, U.S.A. GREENSBORO TERMINAL. THE ACCIDENT INVOLVED A BOOSTER PUMP OWNED BY PLANTATION PIPE LINE COMPANY. |  | TANK FARM | PUMP |  | 1966 | OTHER | BOOSTER PUMP FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2203.1687 | 4444.6811 | GASOLINE | 1 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK | 4043645880 | ON FEBRUARY 14, 1995, AT 4:47 A.M. EDT, A SMALL FIRE OCCURRED AT A BOOSTER PUMP OWNED BY PLANTATION BUT LOCATED WITHIN EXXON COMPANY'S PROPERTY AT GREENSBORO, NORTH CAROLINA. A BALL BEARING SUPPORTING THE HORIZONTAL PUMP SHAFT FAILED CAUSING THE SPINNING SHAFT TO DROP AND RUB ON THE BEARING OIL DEFLECTOR AND BEARING COVER. THE SHAFT MISALIGNMENT AND VIBRATION CAUSED A MISALIGNMENTOF THE MECHANICAL SEAL FACES. THIS MISALIGNMENT CAUSED THE SEAL TO LEAK GASOLINE VAPORS WHICH WERE IGNITED BY HEAT GENERATED FROM THE SHAFT SPINNING ON THE BEARING COVER. THE RESULTING SMALL FIRE WAS SEEN BY A TERMINAL ATTENDANT AND THE PUMP WAS TURNED OFF. WHEN THE PUMP STOPPED, THE GASOLINE VAPOR LEAK STOPPED AND THE FIRE WENT OUT IMMEDIATELY. ALL VAPORS RELEASED WERE BURNED AND NO PRODUCT WAS RELEASED TO THE ENVIRONMENT. THE AMOUNT OF GASOLINE VAPOR RELEASED IS ESTIMATED TO A SMALL FRACTION OF A GALLON.
2017-09-29 08:50 | YES | NO | 19950045 | 1995-03-06 | 2337 | CHEVRON PIPELINE CO | YES | 1995-02-08 | 1430 | TX | BORDEN | GAIL | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 29500 | 21664.4921 | 43706.0312 | CRUDE OIL | 1 | 1400 | 1000 | NO | NO | 10 | 0.25 | 3780 | WELDED |  | 1000 | 900 | YES | 0 | 1760 | 0 | 81 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | K.C. CROWELL | 7133637123 | THE LEAK WAS CAUSED BY EXTERNAL CORROSION. THE LINE WAS REPAIRED WITH A REPAIR CLAMP. THIS SECTION OF LINE IS SCHEDULED FOR FUTURE REPLACEMENT. OIL RECOVERY IS ONGOING IN THE AREA AND REMEDIATION HAS BEEN STARTED.
2017-09-29 08:50 | YES | NO | 19950046 | 1995-03-09 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1995-02-01 | 544 | CA | PLACER | ROCKLIN | NO |  | NO | MARLEE WAY, WEST OF FAIRWAY DRIVE IN ROCKLIN, CA 95677 LINE SECTION 64, 8-INCH PIPE |  | LINE PIPE | PIPE |  | 1988 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 734389.562 | 1481560.3781 | DIESEL FUEL | 3 | 413 | 295 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1380 | 1220 | YES | 8 | 1805 | 2 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.M. ABBOUD | 2134867720 | OPERATOR DETECTED ABNORMAL CONDITIONS ON THE PIPELINE. PIPELINE WAS SHUT DOWNAND FIELD OPERATIONS PERSONNEL DISPATCHED TO INSPECT THE RIGHT-OF-WAY. ALEAK WAS FOUND AND RESPONSE AND REPAIR ACTIVITIES CONDUCTED. EXCAVATION OFTHE LINE INDICATE A THIRD PARTY DAMAGE. IN THE MEANTIME, THE FIRE DEPARTMENTWAS NOTIFIED OF A RELEASE. DAMAGE BY OTHERS WAS BELIEVED TO HAVE OCCURRED INLATE '88 BEFORE THE LOCATION WAS PAVED. REMOVED SECTION OF PIPE HAS BEEN SENTIN FOR LAB ANALYSIS.
2017-09-29 08:50 | YES | YES | 19950047 | 1995-03-13 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-02-16 | 1750 | KS | MCPHERSON |  | NO |  | NO | RANGE 5W, TOWNSHIP 19S, SE-1/4, SECTION 23, MCPHERSON COUNTY, KANSAS. |  | TANK FARM | PIPE |  | 1976 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.P. RUETER | 9185811800 | A 10" BUTANE LINE WAS EXCAVATED AND PREPARED FOR REVISIONS. THE LINE WAS BLOWN DOWN AND COLD CUT. WHILE PREPARING THE PIPE FOR WELDING. SPARKS FROM A BEVELING MACHINE IGNITER CAUSED VAPORS IN THE DITCH TO FLASH.
2017-09-29 08:50 | NO | NO | 19950048 | 1995-03-16 | 567 | ARCO OIL AND GAS COMPANY | NO | 1995-01-06 | 900 | TX | COOKE |  | NO |  | NO | 200 FT N. OF SOUTH SURVEY LINE IN GIDEON-ROSE SURVEY, 8 MILES NORTH OF CALLISBURG, TEXAS. |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | CRUDE OIL | 1 | 4 | 3 | NO | NO | 3 | 0.22 | 150 | WELDED |  | 300 | 150 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH W. STUTEVILLE | 4052735151
2017-09-29 08:50 | YES | NO | 19950049 | 1995-03-16 | 567 | ARCO OIL AND GAS COMPANY | YES | 1995-01-09 | 1445 | OK | CARTER |  | NO |  | NO | SECTION 18 5 S. 3 W. MIDDLE OF SOUTH 1/2, 2.5 MILES S. OF RINGLING ON HWY, 89, THEN ONE MILE EAST ON SECTION LINE. |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | CRUDE OIL | 1 | 50 | 49 | NO | NO | 12.75 | 0.38 | 50 | WELDED |  | 250 | 50 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | KEN W. STUTEVILLE | 4052735151
2017-09-29 08:50 | YES | NO | 19950050 | 1995-03-23 | 12626 | MOBIL PIPELINE CO - EMPIRE | NO | 1995-02-19 | 930 | TX |  | KILGORE | NO |  | NO | 16.7 MILES WEST OF KILGORE, 7/10 MILES WEST OF COUNTY RD.233 |  | LINE PIPE | OTHER | NOT GIVEN | 1931 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 160000 | 117502.3299 | 237049.6605 | CRUDE OIL | 1 | 800 | 800 | NO | NO | 12 | 0.25 | 30000 | WELDED |  | 550 | 75 | YES | 8 | 837 | 4 | 86 | INTERNAL | Null | YES | OTHER | NOT GIVEN | NO DATA |  | Null | NO DATA |  | Null | Null | M.A. HAMRICK | 2146583414 | ON SATURDAY FEBRUARY 18TH AT 21:00, DISPATCHERS NOTED A SHORT IN THE SUBJECTLINE. GAUGERS WERE DISPATCHED TO DETERMINE METER READINGS AND AIR PATROL WASNOTIFIED TO FLY THE LINE ON SUNDAY, 09:30 SUNDAY, AIR PATROL VERIFIED A LEAK.THE LINE WAS SHUT DOWN AND MAINTENANCE PERSONNEL WERE DISPATCHED TO ISOLATETHE LINE. THIS WAS COMPLETED BY 10:30. THE LEAK WAS CONTAINED IN A CREEK APPROXIMATELY TWO FEET WIDE AND .5 MILES LONG; THICK BRUSH AND DEBRIS TRAPPED THECRUDE PREVENTING IT FROM SPREADING FURTHER. MAINTANCE CREWS RESPONDED TO THESCENE AND REPAIRED THE 3/8" HOLE WITH A WRAP OVER THE BELL-WELD ANDBACKFILLED THE SUBJECT AREA BY LATE EVENING. SUPPLEMENTAL REPORT 5/25/1995INDICATES A CHANGE IN THE TOTAL AMOUNT OF COMMODITY SPILLED, FROM 1500 TO 800.THE SUPPLEMENTAL REPORT ALSO INCLUDED A CHANGE IN THE PROPERTY DAMAGE FROM$100,000 TO $160,000. QUESTIONS RELATED TO THESE CHANGES CAN BE REFERRED TOD.G. SCOTT (214) 658-5914
2017-09-29 08:50 | YES | NO | 19950051 | 1995-03-23 | 10319 | KOCH GATHERING SYSTEMS INC | NO | 1995-02-27 | 2300 | OK | CARTER |  | NO |  | NO | KOCH GATHERING SYSTEMS. "CHEROKEE TUSSY STATION" SE/4 SECTION 7-TIS-R3W, CARTER COUNTY OKLAHOMA |  | PUMPING STATION | PUMP |  | 0 | OTHER | PUMP PACKING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2203.1687 | 4444.6811 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVE WRIGHT | 4052257151 | PUMP PACKING FAILURE RESULTING IN SUMP OVER-FLOW.
2017-09-29 08:50 | YES | NO | 19950052 | 1995-03-21 | 809 | ARCO PIPE LINE CO | NO | 1995-02-20 | 1215 | TX | HARRIS |  | NO |  | NO | 8280 SHELDON ROAD, NEAR THE INTERSECTION OF SHELDON AND WALLISVILLE ROAD CHANNELVIEW, TX |  | PUMPING STATION | PUMP |  | 1977 | OTHER | FAILURE ON BOOSTER PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2937.5582 | 5926.2415 | BENZENE/BENZOL | 2 | 30 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W. CRISS DOSS | 7139865364 | THE LOW SUCTION PRESSURE SWITCH ON THE #4 BENZENE BOOSTER PUMP HAD A DIAPHRAGM FAILURE. THE DIAPHRAGM FAILURE CAUSED PRODUCT TO BE RELEASED ON THE GROUND. THE DEFECTIVE PRESSURE SWITCH AND DIAPHRAGM WERE REPLACED ON RE-PIPED/RE-LOCATED OVER PUMP CONTAINMENT WALL. THIS SHOULD CONTAIN PRODUCT BETTER. BENZENEWAS DISPOSED OF USING INSULATION, ROCK, SOIL & BENZENE ABSORBENT PADS. PLACED IN FOUR CONTAINMENT DRUMS. RESEARCH IS CURRENTLY BEING CONDUCTED TO DETERMINE APPLICABLE USE OF THIS PARTICULAR SWITCH FOR BENZENE SERVICE
2017-09-29 08:50 | YES | NO | 19950053 | 1995-03-20 | 30686 | UNOCAL SOUTHERN CALIFORNIA DIV PIPELINE | NO | 1995-02-20 | 1416 | CA | LOS ANGELES | NORWALK | NO |  | NO | WEST SIDE OF RAILROAD, SOUTH IMPERIAL HIGHWAY, EAST OF BLOOMFIELD ROAD THOMAS BROTHERS ATLAS, LOS ANGELES COUNTY PAGE 737, GRID A1 |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3500000 | 2570363.4669 | 5185461.3234 | CRUDE OIL | 1 | 1000 | 800 | NO | NO | 10 | 0.38 | 1630 | WELDED |  | 460 | 200 | YES | 4 | 900 | 4 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | HUGH W. CRADDOCK | 3109038336 | OPERATOR OF KRUSE & KRUSE CONSTRUCTION, WORKING FOR METROLINK ( AN AREA MASS-TRANSIT AGENCY), STRUCK THE PIPELINE WITH A TRACKED-LOADER PUNCTURING THE LINE AT A FIELD BEND. THE LEAK WAS DETECTED BY THE PIPELINE CONTROL CENTER IN SANTA FE SPRING, AND THE PUMPING OPERATION WAS SHUT DOWN WITHIN 6 MINUTES. ELEVATION DIFFERENCE BETWEEN THE PUMP STATION AND THE LEAK SITE CONTINUED PRESSURE THE RELEASE UNTIL OPERATION PERSONNEL RESPONDED THE CLOSED THE NEAREST UPSTREAM VALVE. APPROXIMATELY 1000 BARRELS WERE RELEASED, RESULTING IN A SIGNIFICANT ENVIRONMENTAL CLEAN UP EFFORT.
2017-09-29 08:50 | YES | NO | 19950054 | 1994-05-09 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | 400 FEET WEST OF SIERRA HIGHWAY INTRACT 2703, LOT 14 RANCHO SAN FRANCISCO GRANT, SANTA CLARITA FCPL-LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 101000 | 75746.567 | 152811.4208 | CRUDE OIL | 1 | 183 | 20 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 822 | 50 | YES | 4 | 1020 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD | 3104289217 | FAILURE AT WELD DUE TO EARTHQUAKE REPAIRED/REPLACED DAMAGED PIPELINE REMOVEDCONTAMINATED FOLIAGE AND SOIL FROM AFFECTED CREEK AREA.
2017-09-29 08:50 | NO | NO | 19950055 | 1994-05-09 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | LEAK WAS LOCATED ON THE PROPERTY OF THE DEPARTMENT OF WATER & POWER, NORTHWEST OF TELFAIR AVENUE AND OLDEN STREET CITY OF LOS ANGELES FCPL-LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 6749.6941 | 13616.8593 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 720 | 100 | YES | 4 | 900 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD | 3104289217 | FAILURE OF ACETYLENE WELD DURING EARTHQUAKE, REPAIRED/REPLACED DAMAGED PIPELINE. REMOVED CONTAMINATED SOIL FROM AFFECTED AREA IN THE DEPARTMENT OF WATER & POWER YARD.
2017-09-29 08:50 | YES | NO | 19950056 | 1994-05-09 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | CORNER OF O'MELVENY STREET AND SAN FERNANDO MISSION BLVD. CITY OF SAN FERNANDO FCPL - LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1600000 | 1199945.6152 | 2420774.983 | CRUDE OIL | 1 | 561 | 100 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 624 | 150 | YES | 4 | 800 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD | 3104289217 | FAILURE AT WELD DUE TO EARTHQUAKE. REPAIRED/REPLACED DAMAGED PIPELINE. VACUUMED RECOVERABLE CRUDE OIL, STEAM CLEANED AFFECTED AREAS AND REPAIRED AFFECTEDAREAS. COMBINED COSTS FOR THIS LEAK AND A LEAK SEPARATELY REPORTED ON LINE 1AT WOLFSKILL ST AND AMBOY AVE (REPORT #950057) IN CITY OF LOS ANGELES, ARE 3.2MILLION. CLEANUP EXPENSES CANNOT BE EXPLICITLY SEGREGATED FOR THIS INDIVIDUALLEAK BECAUSE THE TWO LEAK SITES ARE CLOSE TOGETHER AND CLEANUP WAS MANAGED ASA JOINT PROJECT.
2017-09-29 08:50 | YES | YES | 19950057 | 1994-05-09 | 5522 | FOUR CORNERS PIPELINE CO | NO | 1994-01-17 | 431 | CA | LOS ANGELES |  | NO |  | NO | CORNER OF WOLFSKILL STREET AND AMBOY AVENUE CITY OF LOS ANGELES FCPL - LINE 1 |  | LINE PIPE | PIPE |  | 1925 | OUTSIDE FORCE DAMAGE | EARTHQUAKE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 1 | 0 | 1 | 1600000 | 1199945.6152 | 2420774.983 | CRUDE OIL | 1 | 561 | 100 | YES | YES | 10 | 0.37 | 35000 | WELDED |  | 624 | 150 | YES | 4 | 800 | 5 | 90 | NO DATA | Null | Null | NO DATA |  | EARTHQUAKE |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD | 3104289217 | FAILURE AT WELD DUE TO EARTHQUAKE, REPAIRED/REPLACED DAMAGED PIPELINE.VACUUMED RECOVERABLE CRUDE OIL AND STEAM CLEANED AFFECTED AREA AND REPAIREDAFFECTED AREA. COMBINED COSTS FOR THIS LEAK AND A LEAK SEPARATELY REPORTED ONLINE 1 AT O'MELVENY ST AND SAN FERNANDO MISSION BLVD (SEE REPORT #950056),CITY OF SAN FERNANDO, ARE 3.2 MILLION. CLEANUP EXPENSES CANNOT BE EXPLICITLYSEGREGATED FOR THIS INDIVIDUAL LEAK BECAUSE THE TWO LEAK SITES ARE CLOSETOGETHER AND CLEANUP WAS MANAGED AS A JOINT PROJECT.
2017-09-29 08:50 | NO | NO | 19950058 | 1994-05-09 | 5522 | FOUR CORNERS PIPELINE CO | YES | 1994-02-12 | 100 | CA | SAN BERNARDINO |  | NO |  | YES | SHEEPHOLE PASS, BRISTOL LAKE SW CALIFORNIA SECTION 27,T2N,R2E,APM 163.50 FCPL - LINE 90. |  | NO DATA | OTHER | VACUUM TRUCK HOSE VENT | 0 | OTHER | DEFECTIVE HOSE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14999.3202 | 30259.6873 | CRUDE OIL | 1 | 2 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DANIEL C. REYNEVELD | 3104289217 | DURING A VENTING OPERATION RELATED TO LINE REPAIR TO TWO-INCH CONNECTING LINE 90 TO A VACUUM TRUCK BURST. THE HOSE WAS FOUND TO BE DEFECTIVE.
2017-09-29 08:50 | YES | NO | 19950059 | 1995-03-28 | 20133 | UNION PACIFIC RESOURCES CO | NO | 1995-03-06 | 830 | TX | NUECES | BISHOP | NO |  | NO | V.P.L.P. INC'S HARLAN TANK FARM - BISHOP, TX FM 666 (5 MILES WEST OF DRISCOLL, TX ON FM 665, 1 MILE SOUTH ON FM 666) |  | TANK FARM | TANK |  | 1941 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 517 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CINDY L. MUNOZ | 5125843521 | OPERATOR ERROR IN GAUGES RECORDED ON BUTANE TANKS 121 & 122. OPERATOR ASSUMED (DUE TO ERRONEOUS GAUGES) THAT THESE TWO TANKS HAD ENOUGH ROOM TO RECEIVE THE WEEKENED RECEIPTS. BUTANE THEN RELEASED THROUGH RELIEF VALVES ON TOP OF TANKS. AT 0830 ON 03/06/95, TANKS 121 & 122 THEN EQUALIZED INTO TANK 321 TO CONTROL PRESSURE AND VOLUMES. TANK 121 & 122 WERE THEN ISOLATED SO THAT NO MORE PRODUCT COULD BE RECEIVED INTO THEM. TANKS 121 & 122 TO BE PUMPED DOWN ON 03/06/95 AT 8:00 P.M.
2017-09-29 08:50 | YES | NO | 19950060 | 1995-03-28 | 10318 | KOCH REFINING CO | YES | 1995-03-05 | 1130 | WI | EAU CLAIRE |  | NO |  | NO | EAU CLAIRE PUMP STATION, INTERSECTION OF US HWY 93 AND SPRUCE ROAD. |  | PUMPING STATION | OTHER | THERMAL RELIEF LINE | 1993 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 183597.3905 | 370390.0945 | GASOLINE | 1 | 100 | 22 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT SHAFFER | 6124592424 | THE ACCIDENT WAS CAUSED BY THE FAILURE OF A 1/2 INCH STAINLESS STEEL THERMALRELIEF LINE LOCATED NEAR BOOSTER PUMP #1, EAU CLAIRE PUMP STATION.
2017-09-29 08:50 | YES | NO | 19950061 | 1995-04-04 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1995-03-07 | 600 | IL | MARION | PATOKA | NO |  | NO | 1 MILE SOUTH OF VERNON, IL IN PATOKA TOWNSHIP ON MOBIL OIL CORP. PROPERTY PATOKA TANK FARM, TANK NO.2519. |  | TANK FARM | TANK |  | 1948 | OTHER | ROOF DRAIN HOSE ON TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | CRUDE OIL | 1 | 200 | 196 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.A. HAMRICK | 2146583414 | ON MARCH 7, 1995 AT O6:00, THE DALLAS DISPATCHER NOTIFIED THE PATOKA OPERATOR THAT ACCORDING TO HIS MONITOR HE WAS LOSING 200 BARRELS PER HOUR OUT OF TANK 2519. BY 06:30 AM THE PATOKA OPERATOR HAD VERIFIED THE LEAK, ISOLATED IT AND HAS COORDINATED MAINTENANCE CREWS TO CLEAN UP THE SPILL NOTIFICATION TO THENATIONAL RESPONSE CENTER WAS MADE AT 07:30, (REFERENCE LEAK #282419).
2017-09-29 08:50 | NO | NO | 19950062 | 1995-04-05 | 809 | ARCO PIPE LINE CO | NO | 1995-03-15 | 2145 | IL | MARSHALL |  | NO |  | NO | AT CROW CREEK ON COUNTY ROAD 1700 E APPROXIMATELY 2 MILES NORTH OF WASHBURN, IL |  | LINE PIPE | OTHER | ABANDONED PIPE | 1900 | OTHER | ABANDONED PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 40391.4259 | 81485.8208 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 8 | 0 | 0 | NO DATA |  | 0 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY E. GRAVES | 9156859529 | AS OUR RECORDS BEST INDICATE, THE SECTION OF 8-INCH PIPE CROSSING CROW CREEKWHERE THE SHEEN OCCURRED WAS ABANDONED IN THE MID 1950'S. AS A PART OF THEEMERGENCY RESPONSE AND CLEAN UP ACTIVITIES, ABSORBENT PADS AND BOOMS WEREUSED TO TRY AND COLLECT THE SHEEN. VACUUM TRUCKS WERE USED TO REMOVE ANYREMAINING FREE LIQUID FROM INSIDE THE ABANDONED PIPE AND AS AN ADDITIONALPRECAUTION TO PREVENT ANY FUTURE REOCCURRENCE OF A SHEEN, THE SECTION OFABANDONED PIPE WAS FILLED WITH A CONCRETE SLURRY.
2017-09-29 08:50 | NO | NO | 19950063 | 1995-04-05 | 809 | ARCO PIPE LINE CO | YES | 1995-03-14 | 815 | NM | LEA |  | NO |  | NO | HOBBS, NEW MEXICO SANITARY LAND FILL (APPROXIMATELY 1 MILE SOUTHEST OF HOBBS, NEW MEXICO |  | LINE PIPE | GIRTH |  | 1939 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14687.7912 | 29631.2076 | CRUDE OIL | 1 | 30 | 0 | NO | NO | 6 | 0.28 | 24000 | WELDED |  | 770 | 250 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | LARRY E. GRAVES | 9156859529 | DURING NORMAL MONITORING OF PRESSURE ON THE IDLE PIPELINE, A LOSS OF PRESSUREWS NOTED. IT WAS DISCOVERED THAT A GIRTH WELD ON A PREVIOUSLY INSTALLED WHOLE SOLE SLEEVE HAD FAILED CAUSING THE RELEASE OF CRUDE OIL.
2017-09-29 08:50 | YES | NO | 19950064 | 1995-04-06 | 2326 | CHEVRON USA - WESTERN REGION PRODUCTION | NO | 1995-03-11 | 920 | CA | FRESNO | HURON | NO |  | NO | NEAR THE INTERSECTION O GALE AND BUTTE ROAD, FRESNO COUNTY, CALIFORNIA CHEVRON PIPE LINE COMPANY'S KLM PIPELINE MILE POLE 17.5 |  | LINE PIPE | GIRTH |  | 1969 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 10000000 | 7343895.6198 | 14815603.7811 | CRUDE OIL | 1 | 4000 | 0 | NO | NO | 18 | 0.38 | 35000 | WELDED |  | 1040 | 678 | YES | 4 | 1255 | 5 | 92 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | ONE CALL |  | Null | Null | MARION G. DELOUTH | 8053923181 | WATER IN EXCESS OF 100 YEARS STORM, TOOK OUT THE I-5 BRIDGE (NEAR HIGHWAY198) AND ERODED THE SOIL FROM AROUND THE PIPELINE. THE STORM WATER CARRIEDDEBRIS THAT STRUCK THE PIPELINE MOVING IT 16" OFF CENTER. AS A RESULT, A GIRTHWELD BROKE WHERE THE PIPELINE EXITED THE CREEK BANK.
2017-09-29 08:50 | YES | NO | 19950065 | 1995-04-13 | 15156 | SINCLAIR PIPELINE CO | YES | 1995-04-04 | 1527 | WY | CARBON | LAMONT | NO |  | NO | 18 MILES EAST OF LAMONT, WY |  | PUMPING STATION | PIPE |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5600 | 4112.5815 | 8296.7381 | CRUDE OIL | 1 | 280 | 270 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDALL W. DANIELSON | 3073283578 | AT 3:27PM ON 04/04/95 THE SPC CONTROL CENTER OPERATOR RECEIVED AN ALARM ON THE SCADA SYSTEM INDICATING THAT WE HAD A LOW PRESSURE OCCURANCE AT FERRIS STATION ON THE INCOMING STREAM FROM AMOCO'S WAMSUTTER PIPELINE. THE CONTROL CENTER OPERATOR DISPATCHED THE Q.I. TO FERRIS STATION AFTER RECEIVING THE ALARM. THIS SEGMENT OF THE STATION PIPING WAS NOT IN OPERATION WHEN THE LEAK OCCURED. THE Q.I. ARRIVED AT THE SITE AND BEGAN CLOSING VALVES TO ISOLATE THE PIPING. THE Q.I. CALLED AND CONFIRMED THE LEAK TO THE CONTROL CENTER AT 4:1O PM. THE SPC RESPONSE TEAM WAS ASSEMBLED AT SINCLAIR WYO AND DISPATCHED TO THE LEAK SITE. A VACUUM TRUCK WAS CALLED IN TO START RECOVERING THE SPILLED CRUDE OIL.THE RESPONSE TEAM ARRIVED AT 6:15 PM AND BEGAN EXCAVATING THE AREA OF THE LEAK. A SPLIT IN THE PIPE WAS THE CAUSE OF THE SPILL, THE CAUSE FOR THS SPLIT HAS NOT BEEN DETERMINED. APPROXIAMTELY 280BBLS. WE RECOVERED 270 BBLS. BY VAC TRUCK, THE OIL CONTAMINATED DIRT IS BEING STORED AT THE SITE UNTIL ARRANGEMENTS HAVE BEEN MADE TO HAUL IT TO AN APPROVED LANDFILL SITE.
2017-09-29 08:50 | YES | NO | 19950066 | 1995-04-17 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-03-16 | 124 | WY | UINTA |  | NO |  | YES | RANGE 112W, TOWNSHIP 18N, SECTION 10 |  | LINE PIPE | BOLTED FITTING | INSULATING GASKET | 1994 | OTHER | INSULATING GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 27417 | 20134.7586 | 40619.9409 | NATURAL GAS LIQUID | 2 | 746 | 0 | NO | NO | 6 | 0.28 | 42000 | FLANGED |  | 1440 | 700 | YES | 8 | 2185 | 12 | 94 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SID P. RUETER | 9185811800 | EMPLOYEES AT THE COASTAL BLACKS FORK FACILITY NOTIFIED MID-AMERICA PIPELINECOMPANY'S CENTRAL DISPATCH OFFICE, VIA QUESTAR GAS CONTROL IN SALT LAKE CITY,UTAH, OF A POSSIBLE RELEASE LOCATED NEAR THE PLANT CONNECTION WITH THEMAINLINE. EMERGENCY PROCEDURES WERE IMPLEMENTED IT WAS DETERMINED THAT A6"-600# INSULATING GASKET FAILED WHICH RESULTED IN THE RELEASE. THE GASKETWAS REPLACED AND THE LINE RETURNED TO SERVICE. THE FAILED GASKET IS BEING
2017-09-29 08:50 | YES | NO | 19950067 | 1995-04-17 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-03-14 | 1640 | KS | MCPHERSON |  | NO |  | NO | TOWNSHIP 19 SOUTH, RANGE 5 WEST, SECTION 24 |  | PUMPING STATION | PUMP |  | 1994 | OTHER | MECHANICAL SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SID P. RUETER | 9185811800 | DURING THE INITIAL START-UP OF A PUMP, THE INBOARD SEAL OVERHEATED ANDIGNITED THE ESCAPING PRODUCT WHICH RESULTED IN FIRE WITH A THREE-INCH FLAME.THE IMMEDIATE SHUT DOWN OF THE PUMP TERMINATED THE FUEL SOURCE ANDEXTINGUISHED THE FIRE. THE FIRE BURNED LESS THAN ONE MINUTE WITH A PRODUCTRELEASE ESTIMATED AT EIGHT FLUID OUNCES. DISASSEMBLY OF THE SEAL REVEALED THESTATIONARY EXCESS FLOW BUSHING CONTACTED THE ROTATING DRIVE SLEEVE PROVIDINGAN IGNITION SOURCE. THE MANUFACTURER WAS ADVISED OF THE PROBLEM.
2017-09-29 08:50 | YES | NO | 19950068 | 1995-04-19 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1995-03-21 | 805 | KS | HARVEY |  | NO |  | NO | SECTION 9 T-23W R-3W HARVEY COUNTY, KANSAS |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 33047.5303 | 66670.217 | L. P. G. | 2 | 3200 | 0 | NO | NO | 6.63 | 0.17 | 42000 | WELDED |  | 1440 | 100 | YES | 9 | 2275 | 12 | 66 | EXTERNAL | Null | YES | OTHER | BACTERIAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | GEORGE A. ROOD | 7138537876 | ON MARCH 21, 1995, OUR AERIAL PATROL PLANE SPOTTED WHAT APPEARED TO BE A LEAK ON OUR 104 PIPELINE.,@0805 HRS. WE CONFIRMED THE LEAK BY 0940 HRS. AND ISOLATED THE SECTION. ALL INFORMATION WAS RELEASED TO THE EMPLOYEES, AS WELL AS THE FEDERAL, STATE, AND LOCAL AUTHORITIES, AND WE BEGAN IMMEDIATE REPAIRS. A 32 FOOT SECTION OF THE PIPE WAS REPLACED, AND THE LINE WAS PUT BACK IN SERVICEON MARCH 24, 1995 AT 2230 HRS.
2017-09-29 08:50 | YES | YES | 19950069 | 1995-04-26 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1995-03-21 | 830 | IA | POLK | DES MOINES | NO |  | NO | DES MOINES STORAGE FIELD |  | TANK FARM | PIPE |  | 1990 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GEORGE A. ROOD | 7138537876 | EMPLOYEES HAD BLOWN DOWN SEGMENT OF PIPE TO FACILITATE CHANGING OUT A VALVE.THEY WERE USING NITROGEN TO PURGE THE SEGMENT TO INSURE THAT ALL THE PRODUCTWAS OUT. SEVERAL EMPLOYEES WERE STANDING CLOSE TO THE END OF THE SEGMENT WHENA SLUG OF BUTANE ESCAPED; SPEWING BUTANTE ON TWO EMPLOYEES AND GETTING INTHEIR FACE. ONE EMPLOYEE WAS TREATED BY A PHYSICIAN FOR CHEMICALCONJUNCTIVITIS ; THE OTHER WAS NOT HARMED.
2017-09-29 08:50 | YES | NO | 19950070 | 1995-04-26 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1995-03-29 | 600 | NY | ONONDAGA | SYRACUSE | NO |  | NO | MOBIL TERMINAL PRPTY LOCATED AT THE INTERSEC OF 502 SOLAR ST & BEAR. THE LEAK SITE IS AT THE PIPELINE MANIFOLD AREA LOC. ON THE E SIDE OF THE BEAR ST. BRIDG |  | LINE PIPE | OTHER | .5"DRAIN VAL. ON STRAINER | 1994 | INCORRECT OPERATION BY OPERATOR PERSONNEL | HUMAN ERROR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7343.8956 | 14815.6038 | GASOLINE | 3 | 67 | 65 | NO | NO | 6.63 | 0 | 35000 | WELDED |  | 1440 | 250 | YES | 8 | 1853 | 0 | 77 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.S. SOBEY | 7165276160 | ON MARCH 28, 1995, TWO EMPLOYEES WERE ASSIGNED THE DUTY OF CHANGING AN INTERNAL CORROSION COUPON LOCATED ON THE MAINLINE SIDE OF THE MANIFOLD SYSTEM. THIS PROCESS INVOLVED ISOLATING A 3' SECTION OF PIPE WITH VALVES ON EACH SIDE AND OPEINIG A DRAIN VALVE ON THE STRAINER TO RELIEVE PRESSURE. THE TWO ISOLATING VALVES WERE LOCKED OUT AND TAGGED, THE DRAIN VALVE WAS TAGGED, HOWEVER NOT LOCKED DUE THE NEED TO OPERATE THE VALVE FOR PRESSURE RELIEF. UPON COMPLETIONOF THE TASK, THE DRAIN VALVE WAS SUPPOSEDLY CLOSED AND THE ISOLATION VALVES WERE ERE UNLOCKED/UNTAGGED AND THE SYSTEM WAS PLACED BACK TO NORMAL. AT 0500,MARCH 29, DALLAS PLOCC OPENED THE DELIVERY VALVE AND BEGAN DELIVERY INTO SYRACUSE TANKAGE. AT 0645, AN EMPLOYEE DRIVING OVER THE BEAR STREET BRIDGE, NOTICED A GASOLINE ODOR. HE PROCEEDED ACROSS THE BRIDGE AND DROVE TO THE MANIFOLDAREA, AT WHICH TIME HE NOTICED PRODUCT ON THE GROUND INSIDE THE DIKE AREA OFTHE MANIFOLD. HE APPROACHED THE AREA TO INVESTIGATE CAUSE OF THE LEAK AND FOUND THAT THE DRAIN VALVE ON THE STRAINER WAS NOT COMPLETELY CLOSED. HE CLOSEDTHE VALVE AND OBSERVED THAT THE LEAK HAD STOPPED. HE THEN LEFT THE AREA TO GET HELP AND INITIATE SYSTEM SHUTDOWN PROCEDURES AND EMERGENCY RESPONSE EFFORTS. THE SYSTEM WAS SHUTDOWN AT 0653 BY DALLAS CONTROL CENTER. EMPLOYEES OBSERVED THAT THE LEAK WAS CONTAINED WITHIN THE DIKE AREA, BLOCKED THE ENTRANCES OFF, CONTACTED THE FIRE DEPARTMENT, AND CLEAN UP CONTRACTOR. THE CLEANUP CREW ARRIVED AT APPROXIMATELY 0745 TO BEGIN RECOVERY OPERATIONS. THE FIRE DEPARTMENT ARRIVED AT APPROXIMATELY THE SAME TIME AND BLOCKED THE BEAR STREET BRIDGE FROM TRAFFICC AS A PRECAUTION. AFTER NOTIFICATION, THE NYDEC ARRIVED ON SCENE TO EVALUATE THE SITUATION AND AGREED WITH OUR RECOVERY AND CLEANUP PLANS. AT APPROXIMATELY 1145, THE M AINFOLD AREA WAS INSPECTED BY MOBIL EMPLOYEES TO ENSURE SAFE OPERATION. THE SYSTEM WAS MANUALLY PRESSURIZED AND MOINTORED, TURNED OVER TO THE DALLAS CONTROL CENTER TO BEGIN SYSTEM DELIVERY OPERATIONS. THE AREA WAS CLOSELY MONITORED FOR ANY OTHER PROBLEMS. CLEANUP OPERATIONS CONTINUED UNTIL APPROXIMATELY 1500, AND THE AREA WAS MONITORED OVER THE THE NEXT SEVERAL DAYS.
2017-09-29 08:50 | YES | NO | 19950071 | 1995-04-26 | 2271 | CHASE TRANSPORTATION CO | YES | 1995-04-05 | 710 | KS | BUTLER |  | NO |  | NO | NE 1/4 SE 1/4 SEC. 8 T26S R5E BUTLER COUNTY, KS |  | PUMPING STATION | VALVE |  | 1973 | INCORRECT OPERATION BY OPERATOR PERSONNEL | MALFUNCTION OF CONTROL | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 73438.9562 | 148156.0378 | JET FUEL | 3 | 797 | 302 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHUCK JOHNSON | 3168327484 | BLOW DOWN VALVE ON #1 PUMP, COLORADO PIPELINE, WAS LEFT OPEN AND FAILURE INBLOW DOWN SYSTEM TO SUMP CAUSED PORTION OF PRODUCT TO SPILL ONTO GROUND INPUMP AREA. 797 BARRELS WERE SPILLED. 302 WERE RECOVERED. OF THE ESTIMATED 495BARRELS LOST, APPROXIMATELY 300 BARRELS WERE BURNED BY AUTHORIZATION OF THEKANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT & FIRE DEPARTMENT, PERCONVERSATION W/C JOHNSON 04/26/95. WE ARE CURRENTLY TALKING TO THE KANSASDEPARTMENT OF HEALTH AND ENVIRONMENT OFFICIALS REGARDING A REMEDIATION PLANFOR THE SATURATED SOIL.
2017-09-29 08:50 | NO | NO | 19950072 | 1994-07-15 | 15674 | PLANTATION PIPE LINE CO | YES | 1994-06-23 | 1100 | NC | GUILFORD | GREENSBORO | NO |  | NO | TANK 145, PLANTATION'S GREENSBORO TANK FARM 6907-A WEST MARKET STREET GREENSBORO, NC 27409 |  | TANK FARM | TANK |  | 1972 | OTHER | STRESS CRACK IN HEAT ZONE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 16499.2522 | 33285.656 | TURBINE FUEL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK | 4043645916 | ON JUNE 23, 1994, DURING A DAILY ROUTINE INSPECTION, A STAINED AREA WAS DISCOVERED IN THE DIKE AREA AROUND TANK 145 AT PLANTATION'S GREENSBORO TANK FARM. THE TANK WAS EMPTY AT THE TIME. THE TANK WAS IMMEDIATELY TAKEN OUT OF SERVICE, CLEANED ON JUNE 25, AND INSPECTED ON JUNE 26. THE INSPECTION REVEALED A 6-INCH LONG STRESS CRACK IN THE FLOOR PLATE APPROXIMATELY 3 INCHES FROM THE FILL LINE FLANGE IN THE TANK BOTTOM. THE SECTION OF FLOOR PLATE WAS REMOVED ANDREPLACED.
2017-09-29 08:50 | YES | NO | 19950074 | 1995-05-08 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1995-04-09 | 1500 | TX | MONTAGUE | RINGGOLD | NO |  | NO | 12" DISCHARGE LINE TO UNIT #2 AT RINGGOLD PUMP STATION WHICH IS LOCATED APPRX. 3 MI. N. OF THE CITY OF RINGGOLD ON US HWY 811, 1 MI. W.OFF HWY 81 ON A GRAVEL RD |  | LINE PIPE | PIPE |  | 1953 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4406.3374 | 8889.3623 | CRUDE OIL | 1 | 210 | 180 | NO | NO | 12 | 0.25 | 1312 | WELDED |  | 760 | 860 | YES | 4 | 950 | 5 | 94 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT | 2146585914 | AS A PART OF NORMAL OPERATIONS A SEGMENT OF LINES WERE ISOLATED ON SUNDAY, APRIL 9, 1995 AT 10:00 AM. IN THIS SYSTEM, THE WAY THE LINES WERE ISOLATED, THER WAS NO THERMAL RELIEF SYSTEM. SUN PRESSURE WARMED UP THE LINE, AND THE 12"DISCHARGE LINE TO UNIT #2 FAILED AT APPROXIMATELY 860 PSI AT 4:00 PM. THE FAILURE WAS APPROXIMATELY 49.5" LONG BY 1" WIDE, RESULTING IN 210 BARRELS BEINGSPILLED. THERE WERE NO INJURIES AS A RESULT OF THIS INCIDENT. OPERATION AND MAINTENANCE PERSONNEL WERE ON SITE AND IMMEDIATELY NOTIFIED THE DISPATCHER ATTHE DALLAS OPERATIONS CONTROL CENTER, COORDINATING THE CLEAN UP AND FURTHER NOTIFICATION OF THE REGULATORY AGENCIES.
2017-09-29 08:50 | YES | NO | 19950075 | 1995-05-10 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-03-29 | 825 | AR | UNION |  | NO |  | NO | APPROXIMATELY 0.25 MILES NORTH OF U.S. HIGHWAY 82 |  | LINE PIPE | PIPE |  | 1926 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 84454.7996 | 170379.4435 | DIESEL FUEL | 3 | 100 | 100 | NO | NO | 8.63 | 0.32 | 42000 | WELDED |  | 660 | 40 | YES | 24 | 1188 | 8 | 67 | EXTERNAL | Null | YES | OTHER | UNDER INVESTIGATION | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | AT APPROXIMATELY 0852 HOURS CST, MARCH 29, 1995, A LEAK WAS DISCOVERED ON OUR 8" SYSTEM IN UNION COUNTY, ARKANSAS, AS A RESULT OF A LANDOWNER'S REPORT OFA FUEL ODOR. PERSONNEL IMMEDIALTEY RESPONDED IN ACCORDANCE WITH OUR 49CFR PART 94 OIL SPILL RESPONSE PLAN. THE LINE WAS IMMEDIATELY ISOLATED AND ALL REQUIRED NOTIFICATIONS WERE MADE. THE CLEAN UP OF THE SPILLED OIL WAS MONITORED AND APPROVED BY THE ARKANSAS DEPT. OF POLLUTION CONTROL & ECOLOGY. REMOVAL OF THE LEAKING SECTION OF PIPE AND INSTALLATION OF NEW PIPE WAS COMPLETED ON MARCH 31, 1995. ON-SITE REMEDIATION OF A SMALL AMOUNT OF OIL-CONTAMINATED SOIL IS IN PROGRESS.
2017-09-29 08:50 | NO | NO | 19950076 | 1995-05-15 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1995-04-14 | 550 | CA | SAN BERNARDINO | BLOOMINGTON | NO |  | NO | COLTON TERMINAL (TANK FARM) LOCATED AT 2359 SOUTH RIVERSIDE AVENUE, BLOOMINGTON, CA 92316 |  | TANK FARM | VALVE |  | 1978 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 25703.6347 | 51854.6132 | TURBINE FUEL | 3 | 2 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | BREAKOUT TANK (C-31) WAS TAKEN OUT OF SERVICE FOR SEAL REPAIR AND MAINTENANCE. THE TANK VALVE LEAKED UPON REFILLING THE TANK,DUE TO FAILURE TO PROPERLY TIGHTEN VALVE BOLTS. THE BOLTS WERE TIGHTENED AND SOIL IS UNDER REMEDIATION.
2017-09-29 08:50 | YES | NO | 19950077 | 1995-05-16 | 22175 | WARREN PETROLEUM CO | NO | 1995-05-10 | 800 | LA | PLAQUEMINES |  | NO |  | NO | APPROXIMATELY 3 MILES SOUTHWEST OF VENICE, LA BETWEEN RED PASS AND PASS TANTE PHINE. |  | LINE PIPE | WELDING FITTING |  | 1990 | OTHER | IMPROPER PIPE SUPPORT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 25 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BRETT W.ELDRED | 5045344036 | AT APPROXIMATELY 8:00 AM,A 1/2" FITTING ON THE PLANT RAWMAKE DENSITOMETER BROKE RELEASING APPROXIMATELY 25 BBLS. ON MIXED BUTANES TO THE ATMOSPHEE THE DENSITOMETER LOOP WAS IMPROPERLY SUPPORTED AND IT IS SUSPECTED THE VIBRATIONS FROM THE POSITIVE DISPLACEMENT PRODUCT PUMP CAUSED THE FITTING TO FAIL. TELEPHONE NOTIFICATION WAS MADE TO THE NRC AT 10:10 AM #290776.
2017-09-29 08:50 | YES | NO | 19950078 | 1995-05-22 | 1044 | WESTTEX 66 PIPELINE CO | NO | 1995-04-20 | 1811 | WY | PLATTE |  | NO |  | NO | POWDER RIVER PIPELINE - MP 532-43+91 SEC.8, T22N,R67W,PLATTE CO., WY APPROX. 4 MILES NORTH OF WHEATLAND, WY, IN A VERY REMOTE PASTURE AREA. |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12250 | 8996.2721 | 18149.1146 | NATURAL GAS LIQUID | 2 | 12 | 0 | NO | NO | 6.63 | 0.16 | 52000 | WELDED |  | 1750 | 850 | YES | 24 | 2334 | 8 | 71 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS | 9186616267 | THE LINE FLYER REPORTED A LEAK AT MP 533. THE CONTROL CENTER BLOCKED THE LINE, AND A CREW WAS DISPATCHED TO THE SITE. THE CREW ISOLATED THE AFFECTED PIPELINE SECTION BY STOPPLING AND VENTED APPROXIMATELY 24 BARRELS OF NGL TO THE ATMOSPHERE TO FACILITATE REPAIRS. EXTERNAL CORROSION DUE TO A HOLIDAY IN THE COATING CAUSED A PINHOLE LEAK. THE PIPE WAS REPLACED.
2017-09-29 08:50 | NO | NO | 19950079 | 1995-05-24 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-03-25 | 1235 | IL | WILL |  | NO |  | NO | 16550 PARKER ROAD., LOCKPORT, HOMER TOWNSHIP, WILL COUNTY, ILLINOIS |  | LINE PIPE | PIPE |  | 0 | OTHER | DRILLED HOLE IN PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 63000 | 46266.5424 | 93338.3038 | L. P. G. | 3 | 14 | 0 | NO | NO | 12.75 | 0.38 | 35000 | WELDED |  | 600 | 40 | YES | 8 | 760 | 0 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON APRIL 25, 1995, TEPPCO DETERMINED AN INCIDENT WHICH OCCURRED MARCH 25,1995 WOULD EXCEED $50,000 DUE TO REMEDIATION REQUIREMENTS IMPOSED BY THEILLINOI S ENVIRONMENTAL PROTECTION AGENCY. THE INCIDENT INVOLVED A 12"PIPELINE (OWNED AND MAINTAINED BY UNOCAL PIPELINE COMPANY; OPERATED BYTEPPCO) IN WILL COUNTY, ILLINOIS WITH APPROXIMATELY 14 BARRELS OF PRODUCTUNINTENTIONALLY RELEASED DUE TO A DRILLED HOLE THAT HAD NOT LEAKED INTHE PAST. THIS HOLE WAS PRESENT PRIOR TO REFURBISHING AND THE RECOAT OF THEPIPE. THE PIPE WAS REPAIRED AND PLACED BACK INTO SERVICE ON MARCH 27 ANDINITIAL REMEDIATION AT THE SITE BEGAN WITH A FORMAL PLAN BEING SUBMITTED TOTHE ILLINOIS ENVIRONMENT PROTECTION AGENCY SHORTLY THERAFTER. TEPPCO HAD NOINDICATION THE TOTAL COST OF THE INCIDENT WOULD EXCEED $50,000 AT THIS TIME.WHEN THE FINAL APPROVED PLAN WAS RECEIVED BY TEPPCO, IT BECAME APPARENT THEADDITIONAL REQUIREMENTS IMPOSED BY THE STATE AGENCY WOULD CAUSE THE PROJECT TOEXCEED THE $50,000 THRESHOLD. CONTACT JIM MIKA WITH QUESTION 713-759-3955.
2017-09-29 08:50 | YES | NO | 19950080 | 1995-05-22 | 18718 | SUN PIPELINE CO | NO | 1995-05-12 | 1630 | OK | PONTOTOC | ADA | NO |  | NO | 1 4/10 MILES EAST OF HWY 99 AND RALETRACT RD ON NORTH SIDE, APPROX. 400 YDS NORTH OF ROADWAY. |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4406.3374 | 8889.3623 | CRUDE OIL | 1 | 350 | 340 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 775 | 111 | YES | 24 | 1025 | 7 | 94 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | EDITH F. COEN | 9185866942
2017-09-29 08:50 | YES | NO | 19950081 | 1995-05-26 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-04-27 | 835 | KS | MCPHERSON |  | NO |  | NO | SECTION 24, TOWNSHIP 19S, RANGE SW, MCPHERSON COUNTY, KANSAS. |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3616 | 2655.5527 | 5357.3223 | ANHYDROUS AMMONIA | 2 | 17 | 0 | NO | NO | 8.63 | 0.16 | 46000 | WELDED |  | 1167 | 200 | YES | 24 | 1509 | 4 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL | PIPELINE WARNING SIGNS | YES | YES | S.P. RUETER | 9185811800 | A MAPL EMPLOYEE REPORTED AN AMMONIA ODOR INSIDE MAPL'S CONWAY STATION NEAR THE BLOCK VALVE ON THE 8-INCH NH3 PIPELINE. UPON EXCAVATION OF THE LINE, A LEAK WAS FOUND IN THE LINE, ORIGINATING FROM PREVIOUS MECHANICAL DAMAGE. THE LINE WAS SHUT DOWN, PRESSURE WAS LOWERED ON THE LINE SEGMENT, AND IT WAS BLOCKEDIN. THE LINE WAS PERMANENTLY REPAIRED BY INSTALLING A FULL ENCIRCLEMENT SLEEV
2017-09-29 08:50 | YES | NO | 19950082 | 1995-05-24 | 2733 | CHEVRON PIPELINE CO - MIDLAND DIV | NO | 1995-03-13 | 1215 | TX | FORT BEND | MISSOURI CITY | NO |  | NO | APPROXIMATELY 150 FEET NORTH OF THE INTERSECTION OF LAKE OLYMPIA PARKWAY AND MISTY HOLLOW. |  | LINE PIPE | PIPE | SCREWED COLLAR | 0 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 11750.233 | 23704.966 | CRUDE OIL | 1 | 150 | 150 | NO | NO | 6.63 | 0.28 | 35000 | THREADED |  | 700 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | WILLIAM J. JASPER | 7133635922 | OIL HAS TRAVELED FROM LEAKSITE ALONG A PREVIOUS EXCAVATION THAT T&R HADMADE TO CROSS UNDER OUR CRUDE LINES WITH A 6" PVC SEWER LINE ON 3/06//95. THEOIL IS COMING OUT OF THIS LOCATIN AND HAS MOVED DOWNHILL TOWARD A LOWTREELINE AREA WITH STANDING WATER. THE T&R FORMAN, HERBERT GAMBLE, SAID THATWHEN THEY DISCOVERED THE LEAK THEY USED THEIR TRACK HOE TO BUILD LEVIESAROUND THE LOW AREAS, IN THE PATH OF THE FLOWING OIL TO PREVENT IT FROMENTERING THE SWAMP AREA. 8:00 AM TWO MCCARTY VACUUM TRUCKS REMOVING OIL FROMLEAKSITE. CREW CONTINUED TO WAS AREA AND COLLECT OIL. SORBENT TOWELS WEREREMOVED AND REPLACED IN LOW AREAS. A PILE OF TREES WERE MOVED TO ALLOW ACCESSTO THE OIL SKIM THAT HAD COLLECTED BELOW THEM. ORGANIC ABSORBENT MATERIAL WASSPREAD IN THE GRASSY AREAS. TOTAL OIL RECOVERED THIS DAY 10 BBLS. VAN MOOREWITH TRRC INSPECTED SITE AND STATED THAT WE HAD DONE A VERY GOOD JOB OFRECOVERING THE OIL AND AGREED THAT IF THE OIL ENTRAPPED IN THE SOIL AT THELEAKSITE WAS SUCCESSFULLY REMOVED THAT THE SOIL COULD BE SPREAD AND MIXEDWITH CLEAN FILL DIRT AT THE SITE AND WOULD NOT HAVE TO BE HAULED OFF. 8:00AMMIKE LAUGHLIN CHECKED SITE AND REPORTED APPROX. 20 GALS, ACCUMULATED IN THETRENCHES. 1:00PM MIKE LAUGHLIN OVERSAW REMOVAL OF APPROX. 30 GALS OF OIL FROMTHE TRENCHES. SEE REPORT FOR ADDITIONAL INFORMATION.
2017-09-29 08:50 | YES | NO | 19950083 | 1995-06-05 | 2387 | CITGO PIPELINE CO | YES | 1995-05-07 | 2010 | OK | POTTAWATOMIE | TECUMSEH | NO |  | NO | 3 MILES W. OF TECUMSEH, OK THENCE 3 MILES S. OF HWY 9 ON COKER ROAD, THENCE 300' WEST OF COKER ROAD AT DANCE CREEK. |  | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18359.739 | 37039.0095 | GASOLINE | 3 | 500 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 700 | 5 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | JAMES F. CONDUFF | 9184954119 | 5/8/95 2010 TECUMSEH POLICE DEPT. REPORTED LEAK TO US. 2015 PRESSURE LOSS INDICATED THAT WE HAD LEAK, 2044 ONE MILE AREA AROUND LEAK SITE EVACUATED. 2100 DAMAGED PIPE WAS UNDER WATER BECAUSE OF HEAVY RAIN. 2117 VALVE ON NORTH SIDE OF LEAK SITE CLOSED. 2130 VALVE ON SOUTH SIDE OF LEAK SITE CLOSED. 05/09/950400 WATER RECEDED AND WOODEN PEG WAS DRIVEN INTO BULLET HOLE. 0645 INSTALLED TEMPORARY REPAIR CLAMP.
2017-09-29 08:50 | YES | NO | 19950084 | 1995-06-02 | 22610 | WILLIAMS PIPELINE CO | YES | 1995-05-01 | 1345 | OK |  | ROCK ISLAND | NO |  | NO | SE1/4 OF SW 1/4, SECTION 27, T20N, R2E MP 175 + 3314 |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22031.6869 | 44446.8113 | NATURAL GAS LIQUID | 2 | 770 | 0 | NO | NO | 8 | 0.2 | 42000 | WELDED |  | 1300 | 400 | YES | 8 | 2233 | 10 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | LINE MAKERS VISIBLE | NO | NO | STEVEN S. BALL | 9185883850 | AT APPROX. 13:45 HOURS ON MAY 1, 1995, DISPATCHING RECEIVED A CALL FROM A LANDOWNER REPORTING A WHITE VAPOR CLOUD FROM OUR PIPELINE NEAR CORDOVA, ILLINOIS. THE LINE WAS IN A STATIC CONDITION HOLDING APPROX. 400 PSI. THE LOCAL FIRE DEPARTMENT, POLICE AND STATE PATROL RESPONDED TO OUR NOTIFICATIONS. DISPATCHING IMMEDIATELY HAD VALVES CLOSED AT MP 170 AND 221. COMPANY PERSONNEL WERE ON SITE WITHIN AN HOUR TO MANUALLY CLOSE VALVES AT MP 173 AND MP 183 FOR FURTHER LEAK ISOLATION. THE VAPOR CLOUD HAD DISPERSED BY THE TIME CREWS ARRIVED. THE DAMAGE WAS LOCATED IN THE MIDDLE OF A POTATOE FIELD, APPROX. 1/2 MILE FROM THE NEAREST ROAD. THE PIPE DAMAGE WAS CAUSED BY A DEEP TILLAGE IMPLEMENT THAT PUNCTURED THE LINE. LINE DEPTH AT THE POINT OF RUPTURE WAS APPROX. 24". THE NEAREST LINE MARKER WAS LESS THAN 100 FEET AWAY. THE LINE WAS FLARED DOWN AND APPROPRIATE REPAIRS WERE INITIATED.
2017-09-29 08:50 | YES | NO | 19950085 | 1995-06-01 | 15674 | PLANTATION PIPE LINE CO | YES | 1995-05-03 | 1600 | VA | HENRY |  | NO |  | NO | OFF FOXFIRE RD (VA ROUTE 658) BETWEEN DYERS STORE RD (VA ROUTE 657) AND BARROWS MILL RD (VA ROUTE 663) |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 58751.165 | 118524.8302 | GASOLINE | 1 | 5 | 4 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1450 | 1180 | YES | 24 | 1884 | 10 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | R.M. CROOK | 4043645916 | AT APPROXIMATELY 4:00 P.M., EDT, ON MAY 3, 1995, A LEAK WAS DISCOVERED ON PLANTATION'S 8.625 INCH O.D., O.188" WALL THICKNESS, GRADE X-52, PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN GREENSBORO, NORTH CAROLINA AND ROANOKE, VIRGINIA. THE LEAK OCCURRED IN A REMOTE AREA NEAR FOXFIRE ROAD (VA ROUTE 618)BETWEEN DYERS STORE ROAD (VA ROUTE 614) AND BARROWS MILL ROAD (VA ROUTE 663)IN HENRY COUNTY, VIRGINIA. THE SEAMLESS LINE PIPE HAD A 2-INCH LONG HAIRLINECRACK WITH A PINHOLE AT THE TWELVE O'CLOCK POSITION. THE CRACK WAS WITHIN A DENT WHICH MEASURED 0.22" IN DEPTH. DURING EXCAVATION OF THE PIPELINE LEAK, A ROCK WAS DISCOVERED RESTING ONT HE PIPE. THE PIPELINE WAS REPAIRED WITH A 4' LONG FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19950086 | 1995-05-31 | 12127 | MARATHON PIPE LINE CO | YES | 1995-04-28 | 1530 | IN | HAMILTON | SHERIDAN | NO |  | NO | THE INCIDENT OCCURRED 3 MILES NE SHERIDAN, IN ADJACENT TO US HWY 31, IN HAMILTON CTY, ADAMS TOWNSHIP, SECTION 24, T20N, R3E. |  | LINE PIPE | PIPE |  | 1952 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 128518.1733 | 259273.0662 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 22 | 0.31 | 46000 | WELDED |  | 939 | 710 | YES | 24 | 1175 | 0 | 75 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 15:38 ON APRIL 28, 1995, MARATHON PIPE LINE COMPANY'S OPERATIONS CENTER WAS NOTIFIED BY THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT THAT HYDROCARBON HAD APPEARED IN A ROADSIDE DITCH ADJACENT TO U.S. HIGHWAY 31 AT A POINTWHERE THE MPL MARTINSVILLE-LIMA 22" CRUDE PIPE LINE CROSSES UNDER THE HIGHWAY. IDEM THEN CONTACTED THE MPL AREA FOREMAN, WHO CONTACTED THE OPERATIONS CENTER AT 15:55 REQUESTING SHUTDOWN OF THE PIPELINE. SHUTDOWN OF THE PIPELINE WAS IMMEDIATELY COMMENCED. MPL PERSONNEL RESPONDED TO THE AREA, AND CONTAINED AND REMOVED THE SMALL AMOUNT OF CRUDE OIL IN THE ROADSIDE DITCH. THE PIPE LINEWAS EXCAVATED AND THE SOURCE OF THE RELEASE WAS UNCOVERED AT APPROXIMATELY 23:00 THE SAME DAY. A SMALL DENT/FLAT SPOT WAS DISCOVERED IN THE PIPE LINE INSIDE THE CASING UNDERNEATH U.S. HIGHWAY 31. IN THE CENTER OF THE DENT WAS A CRACK APPROXIMATELY 3" LONG WHICH WAS SEEPING HYDROCARBON. THE CRUDE OIL HAS SEEPED OUT AROUND THE CASING SEAL AND A SMALL AMOUNT HAD COME OUT THE CASING VENT. THE TOTAL AMOUNT OF HYDROCARBON RELEASED WAS ESTIMATED TO BE FIVE GALLONS.THE DAMAGED PIPE LINE WAS PULLED FROM THE CASING. 251 FEET OF PREVIOUSLY TESTED NEW PIPE LINE WAS INSTALLED. THE PIPE LINE WAS RETURNED TO SERVICE AT 01:15 ON MAY 2, 1995. ALL THE RELEASED CRUDE OIL WAS RECOVERED BY VACUUM TRUCK OR IN THE EXCAVATED SOIL WHICH WILL BE PROPERLY DISPOSED BY LANDFILLING.
2017-09-29 08:50 | YES | NO | 19950087 | 1995-06-02 | 10312 | KOCH INDUSTRIES INC | YES | 1995-05-10 | 1305 | LA | LA SALLE |  | NO |  | NO | T-8N,R2E,SEC7 |  | LINE PIPE | PIPE |  | 1969 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 62423.1128 | 125932.6321 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1340 | 862 | YES | 36 | 1970 | 0 | 69 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM L. NORVELL | 3144865488 | LANDOWNER RICKY COKERCHAM REPORTED A POSSIBLE RELEASE OF AMMONIA ON HIS PROPERY IN LASALLE PARISH, LA TO THE GULF CENTRAL PIPELINE CONTROL CENTER IN WICHITA, KS AT APPROXIMATELY 13:00 ON MAY 10, 1995. PRESSURE WAS REDUCED AND COMPANY PERSONNEL DISPATCHED TO SITE. CONFIRMATION OF RELEASE WAS MADE AT 13:45. CLOSEST VALVE UPSTREAM WAS CLOSED AND NEAREST PUMP DOWNSTREAM WAS STARTED TO PULL AWAY PRESSURE. INJECTION FACILITES WERE SHUT DOWN. SITE ISOLATED AT 15:37. TELEPHONE NOTIFICATION OF RELEASE WAS MADE TO THE LA STATE POLICE (95-1628) AT APPROX. 14:25 AND TO THE NRC (290861) AT APPROX. 15:20. EXCAVATION OF PIPELINE SHOWED A HAIRLINE CRACK ALONG THE SEAM OF THE PIPE. REMOVED AND REPLACED 48" OF PIPE. FAILED PIPE HAS BEEN SENT IN FOR ANALYSIS. NO CONCLUSIVE REPORTS HAVE BEEN RECEIVED TO DATE. FINAL REPAIRS MADE AND LINE RETURNED TO SERVICE AT 21:20 ON 05/13/95. REMEDIATION OF CONTAMINATED SOIL AT SITE IS BEING PLANNED. A SUPPLEMENTAL 7000-1 WILL BE FILED WHEN FINAL CLEAN-UP COSTS, DAMAGES, AND PRODUCT LOSS ARE BETTER DETERMINED.
2017-09-29 08:50 | YES | NO | 19950088 | 1995-06-15 | 12127 | MARATHON PIPE LINE CO | YES | 1994-11-30 | 1330 | MI | MUSKEGON | FRUITPORT | NO |  | NO | THREE MILES EAST OF FRUITPORT, MI. SECTION 28, T9N,R15W, FRUITPORT, TOWNSHIP. MPL R/W 1114 ON LOTTAVILL-MUSKEGON 10" PIPELINE. |  | LINE PIPE | PIPE |  | 1958 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 56247.4507 | 113473.8273 | FUEL OIL | 3 | 7 | 7 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1406 | 200 | YES | 8 | 1765 | 8 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | ON NOVEMBER 30, 1994, AT APPROXIMATELY 13:30 CST, MARATHON PIPE LINE COMPANY(MPL) WAS NOTIFIED OF A SMALL STAINED AREA OF SOIL LOCATED IN A FIELD 3 MILES EAST OF FRUITPORT, MI, NEAR THE MPL (MPL) LOTTAVILLE-MUSKEGON 10" PRODUCTS PIPE LINE. AT THE TIME OF NOTIFICATION, THE LINE WAS SHUT DOWN IN #2 FUEL OILSERVICE DUE TO AND EXCAVATED THE AFECTED AREA. A TINY PINHOLE WAS DISCOVEREDIN A LONGGITUDINAL WELD SEAM AT APPROXIMATELY 16:00 THE SAME DAY, RELEASING A PRODUCT STREAM APPROXIMATELY THE SIZE OF A STREAM FROM A HYPODERMIC NEEDLE.IT IS ESTIMATED THAT 7 BBLS. OF MIXED #2 FUEL OIL/GASOLINE WAS RELEASED. A 50" SECTION OF PIPE WAS REPLACED WITH PRE-TESTED PIPE IN THE AFFECTED AREA. ALL THE EXCAVATED CONTAMINATED SOIL WAS REMOVED AND PROPERLY DIPOSED. THE DAMAGED SECTION OF PIPE WAS ANALYZED AT MARATHON OIL COMPANY'S PETROLEUM TECHNOLOGY CENTER. NO SEVERE DEFECTS WERE OBSERVED THAT COULD ACCOUNT FOR THE REPORTEDRELEASE. AT THE TIME OF THE RELEASE, THE STATE OF MICHIGAN WAS NOTIFIED HOWEVER, THE NATIONAL RESPONSE CENTER WAS NOT NOTIFIED BECAUSE NONE OF THE REPORTABILITY CRITERIA IN 195.50 WERE MET. HOWEVER, BY THE END OF MAY 1995, IT WASNOTIED THAT ONGOING REMEDIATION COSTS AT THE SITE HAD ESCALATED THE TOTAL PROPERTY DAMAGE TO EXCEED $50,000. THE REMEDIATION WAS NECESSARY TO MITIGATE MINOR LOCALIZED GROUNDWATER CONTAMINATION.
2017-09-29 08:50 | YES | NO | 19950089 | 1995-06-12 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-03-09 | 1725 | IN | CLINTON |  | NO |  | NO | 300' EAST OF CR800 W, 1MILE SOUTH OF SR28, CLINTON COUNTY |  | LINE PIPE | GIRTH |  | 1957 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 55079.2171 | 111117.0284 | FUEL OIL | 3 | 30 | 24 | NO | NO | 14 | 0.25 | 52000 | WELDED |  | 1000 | 120 | YES | 24 | 1876 | 0 | 57 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON MAY 18, 1995, TEPPCO DETERMINED AN INCIDENT WHICH OCCURRED MARCH 9, 1995 WOULD EXCEED $50,000 DUE TO REMEDIATION REQUIREMENTS IMPOSED BY THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT. THE INCIDENT INVOLVED A 14" LINE IN CLINTON COUNTY, INDIANA WITH APPPROXIMATELY 30 BARRELS OF PRODUCT UNINTENTIONALLY RELEASED DUE TO A CRACK IN A GIRTH WELD. THE PIPE WAS REPAIRED AND PLACEDBACK INTO SERVICE ON MARCH 11 AND INITIAL REMEDIATION AT THE SITE BEGAN WITHA FORMAL PLAN BEING SUMBITTED TO THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT SHORTLY THERAFTER. TEPPCO HAD NO INDICATION TOTAL COST OF THE INCIDENT WOULD EXCEED $50,000 ON THE DATE OF THE INCIDENT. ONLY AFTER THE STATE PROVIDED THE REMEDIATION CRITERIA DID IT BECOME APPARANT THE PROJECT WOULD EXCEEDTHE $50,000 THRESHOLD.
2017-09-29 08:50 | YES | NO | 19950090 | 1995-06-20 | 9175 | JAYHAWK PIPELINE CORP | NO | 1995-06-01 | 5 | KS | BUTLER |  | NO |  | NO | SE 1/4 SECTION 27, TOWNSHIP 27 SOUTH, RANGE 4 EAST OF BUTLER, COUNTY KANSAS |  | LINE PIPE | PIPE |  | 1923 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 8500 | 6242.3113 | 12593.2632 | CRUDE OIL | 1 | 210 | 0 | NO | NO | 6.63 | 0.28 | 30000 | WELDED |  | 300 | 20 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | WASHOUT |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | JAYHAWK PIPELINE'S 6" GATHERING LINE SOUTH OF AUGUSTA, KANSAS SPANS THE WALNUT RIVER. EARLY THURSDAY MORNING JUNE 1, 1995, JAYHAWK RECIVED A TELEPHONE CALL FROM AUGUSTA DEPT. OF SAFETY CONCERNING OIL ON THE WALNUT RIVER. JAYHAWK PERSONNEL IMMEDIATELY SHUT DOWN THE PIPELINE AND BLOCKED THE LINE IN. HAZMAT RESPONSE, INC. WAS CALLED TO ASSIST IN CONTAING THE PILL. JAYHAWK PURGED AND CAPPED THE LINE ON BOTH SIDES OF THE RIVER. DUE TO FLOOD STAGE, A LOG JAM ON THE WALNUT RIVER DESTROYED JAYHAWK'S RIVER SPAN. DUE TO THIS INCIDENT AND ECONOMIC FACTORS, JAYHAWKS HAS DECIDED TO SHUT THIS GATHERING SYSTEM DOWN.
2017-09-29 08:50 | NO | NO | 19950091 | 1995-06-22 | 11032 | LACLEDE GAS CO | YES | 1995-05-21 | 645 | IL | MADISON |  | NO |  | NO | CHOUTEAU ISLAND, ILLINOIS , BETWEEN LACLEDE PROPANE PIPELINE MARKERS. 202 & 203 |  | LINE PIPE | OTHER | UNKNOWN | 1972 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | ONE CALL |  | Null | Null | PAUL B. HUNKER | 3143420528 | ON MAY 21, 1995 AT APPROXIMATELY 06:15 CDT A PORTION OF THE LEVEE PROTECTINGCHOUTEAU ISLAND, MADISON COUNTY, ILLINOIS FROM THE MISSISSIPPI RIVER NEAR MILE MARKER 192 FAILED. APPROXIMATELY 30 MINUTES LATER (06:45 CDT) A 10.75" O.D. PIPELINE LATERAL OFF OF A LIQUID PROPANT TRANSMISSION LINE FAILED. THIS LATERAL PIPELINE SECTION HAD NOT BEEN OPERATED IN OVER NINE (9) YEARS AND HAD THE LIQUID PUMPED OFF AND ISOLATION VALVES CLOSED APPROXIMATELY A YEAR PRIOR TOTHE INCIDENT. AS A RESULT, THE PIPELINE SECTION CONTAINED ONLY PROPANE VAPORAT A PRESSURE OF APPROXIMATELY 100 PSIG, WHICH VENTED TO ATMOSPHERE AND DISSIPATED ON PREVAILING S-SW WINDS. (APPROXIMATELY 122,400 CUBIC FEET OF VAPOR)
2017-09-29 08:50 | NO | NO | 19950092 | 1995-06-26 | 4902 | EXXON COMPANY, U.S.A - SOUTHWESTERN DIVISION | NO | 1995-05-19 | 240 | TX | YOAKUM |  | NO |  | NO | EXXON METER SITE ABOUT 3.5 MILES NORTH OF DENVER CITY, TEXAS ON THE WEST SIDE OF STATE HIGHWAY 214. |  | NO DATA | OTHER | RELIEF VALVE (THERMAL) | 1986 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 367.1948 | 740.7802 | CARBON DIOXIDE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.K. FLOOD | 9156886769 | AT APPROXIMATELY 2:40 AM ON MAY 19, 1995 A 3/4" X 1" THERMAL RELIEF VALVE (PSV 101B) ON A T" CARBON DIOXIDE SUPPLY PIPELINE HEADER BEGAN LEAKIN AT A RATEOF APPROXIMATELY 10 MILLION STANDARD CUBIC FEET PER DAY. THE LEAKING VALVE WAS DISCOVERED AND REPORTED TO EXXON BY A NON-EXXON OPERATOR IN THE WASSON FIELD AROUND 4 A.M. UPON NOTIFICATION, EXXON'S CORNELL UNIT PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE FACILITY TO THE FACILITY SITE. EXXON PERSONNEL FIRST VERIFED THAT THE PRESSUER (1950 PSIG) WAS NOT IN EXCESS OF THE PIPELINE'S MAOP (2160 PSIG). THEY THEN PROCEEDED (AT ABOUT 4:45 AM) TO ISOLATE THE LEAKING RELIEF VALVE AND ELIMINATE THE LEAK. APPROXIMATELY 350 BARRELS OF CO2 (AT PIPELINE CONDITIONS) WERE CALCULATED TO HAVE VENTED DURING THIS TIME. THE PSV WAS REPAIRED AND RETURNED TO SERVICE BY LATER IN THE MORNING OF MAY 19TH. THELEAKING CARBON DIOXIDE WAS ENTIRELY CONTAINED WITHIN THE EXXON FACILITY. SINCE NO DANGER TO THE PUBLIC OR EXXON PERSONNEL EXISTED. EMERGENCY CONTINGENCY PLAN PROCEDURES WERE NOT IMPLEMETNED. THIS INCIDENT WOULD NOT NORMALLY BE CONSIDERED AN "ACCIDENT", SINCE THERE WAS NO SIGNIFICATNT IMPACCT TO PUBLIC SAFETY OR THE ENVIRONMENT. IT IS REPORTABLE (WRITTEN REPORT WITHIN 30 DAYS ONLY BECAUSE THE LOST CARBON DIOXIDE EXCEEDED THE 50 BARREL LIMIT PROVIDED BY DOT REGULATION (49CFR 195.50). BASED ON AN INVESTIGATION OF THE RELIEF VALVE FAILURE IT WAS DETERJMINED THAT THE FAILURE OCCURRED BECAUSE THE FEFLON SEAT MATERIAL HAD EXTRUDED UNDER PRESSURE. IT WAS RECOMMENDED BY THE RELIEF VALVE MANUFACTURER THAT A MORE DURABLE SEAT MATERIAL BE UTILIZED TO PREVENT SUCH FAILURES IN THE FUTURE. NEW VALVES WITH THIS MORE DURABLE SEAT MATERIAL HAVE BEEN ORDERED AND WILL BE INSTALLED INPLACE OF ALL VALVES CURRENTLY UTILIZING THE TEFLON MATERIAL IN SIMILAR SERVICE CONDITIONS.
2017-09-29 08:50 | YES | NO | 19950093 | 1995-06-26 | 4906 | EXXON PIPELINE CO | YES | 1995-05-23 | 930 | TX | CHEROKEE | TROUP | NO |  | NO | AT INTERSECTION OF HWYS 135 AND 110 IN TROUP, TX GO WEST 2.4 MILES TO FM 2064, AND TURN SOUTH. PROCEED 1.5 MILES TO CR.4908 AND TURN RIGHT; 1 MI TO WHITTON FARM |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 46000 | 33781.9199 | 68151.7774 | CRUDE OIL | 1 | 480 | 478 | NO | NO | 8 | 0.32 | 30 | NO DATA |  | 700 | 170 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | ONE CALL |  | NO | NO | GEORGE PERSYN | 7136565521 | LANDOWNER REPORTED CRUDE OIL CREEK BED OF A TRIBUTARY TO MUD CREEK SOUTH OF TROUP, TEXAS IN CHEROKEE COUNTY. AT ONCE EXXON PIPELINE COMPANY (EPC) SHUT DOWN THE LINE AND DISPATCHED EPC'S RESPONSE TEAM AND CONTRACTORS. SPILL WAS CONTAINED IN THE CREEK BED BY CONTAINMENT BOOMS WHERE IT WAS RECOVERED. THERE WERE NO INJURIES OR IMPACT TO PUBLIC FROM THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 19950094 | 1995-06-23 | 15156 | SINCLAIR PIPELINE CO | NO | 1995-05-24 | 1602 | WY | NATRONA | WEST OF MILLS | NO |  | NO | NE 1/4 SEC. 8,T.33 N., R.80 W., NATRONA COUNTY, WY W. OF THE INTERSECTION OF POISON SPIDER RD AND SEVEN MILE ROAD. |  | LINE PIPE | PIPE |  | 1977 | FAILED PIPE | UNDER INVESTIGATION | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 55079.2171 | 111117.0284 | CRUDE OIL | 1 | 1500 | 1490 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1440 | 1370 | YES | 24 | 1800 | 8 | 77 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARK A. PETERSEN | 8015242852 | AT 4:02 P.M. ON MAY 24, 1995, THE OPERATIONS COORDINATOR DETECTED A SIGNIFICATN DECREASE IN DISCHARGE PRESSURE AT OUR CASPER PUMP STATION. THE PIPELINE WAS SHUT DOWN AT 4:04 P.M. AND PERSONNEL WERE CONTACTED TO INVESTIGATE THE LOSS OF PRESSURE. AT 4:23 P.M. A SINCLAIR PIPELINE EMPLOYEE FOUND THE SPILL SITEAND CLOSED THE BLOCK VALVES ON EACH SIDE OF THE AFFECTED AREA TO ISOLATE SPILL SITE. A TOTAL OF 1500 BBLS WERE SPILLED AND APPROXIMATELY 1490 BBLS. HAVE BEEN RECOVERED AS OF THIS DATE. AN EARTHEN DAM WAS CONSTRUCTED TO STOP THE FLOW OF CRUDE ABOUT 200 YARDS FROM THE ORIGIN. SOME OF THE CRUDE REACHED AN IRRIGATION DRINAGE DITCH. THE CRUDE IN THE IRRIGATION DITCH WAS CONTAINED 500 YARDS DOWNSTREAM AND RECOVERED.
2017-09-29 08:50 | YES | NO | 19950095 | 1995-06-23 | 2371 | CINIZA PIPELINE INC | NO | 1995-04-21 | 1000 | NM |  |  | NO |  | YES | SEC.33 T25N R6W NMPM |  | PUMPING STATION | OTHER | STRAINER | 1986 | OTHER | DRAIN VALVE LEFT OPEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 14109 | 10361.5023 | 20903.3354 | CRUDE OIL | 1 | 150 | 100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.L. CALVERY | 5056328006 | DRAIN VALVE WAS LEFT PARTLY OPEN ON STRAINER.
2017-09-29 08:50 | YES | NO | 19950096 | 1995-06-22 | 22442 | WEST TEXAS GULF PIPELINE CO | NO | 1995-05-27 | 800 | TX | FREESTONE |  | NO |  | NO | 1/4 MILE NORTH OF FM 27, 3 MILES EAST OF WORTHAM, TEXAS NEAR WEST TEXAS GULF PUMP STATION. |  | TANK FARM | BOLTED FITTING | STRAINER TOP | 1953 | OTHER | FAILURE OF GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 200 | 195 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | T.R. REED | 8177653261
2017-09-29 08:50 | YES | NO | 19950097 | 1995-07-05 | 737 | ASHLAND PIPELINE CO | YES | 1995-06-07 | 953 | OH | STARK |  | NO |  | NO | APPROXIMATELY 50 FT. WEST OF THE TUSCARAWAS RIVER AND 1500 FT. E OF RIVERLAND RD, BETHLEHEM TWP., STARK CO., NW QUARTER OF SECTION 22 T9N R9W. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2500000 | 1835973.9049 | 3703900.9453 | CRUDE OIL | 1 | 726 | 530 | NO | NO | 12 | 0.38 | 25000 | WELDED |  | 439 | 390 | YES | 24 | 546 | 0 | 72 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | JESSE A. BROTHERS | 6063294307 | AT APPROXIMATELY 0953 HRS., JUNE 7, 1995, WHILE DOING PREPARATTORY RIGHT-OF-WAY WORK FOR THE INSTALLATION OF A 16" REPLACEMENT LINE PARALLEL TO AND WITHIN THE SAME RIGHT-OF-WAY AS THE EXISTING 12" CRUDE OIL PIPELINE, THE CONSTRUCTION CONTRACTOR'S DOZER STRUCK AND BROKE A SHALLOWLY BURIED 4" RISER WHICH HADBEEN TAPPED ONTO THE 12" PIPELINE AT A TIME UNKNOWN TO CURRENT OPERATING PERSONNEL AND WITHOUT NOTATION OF ITS EXISTENCE ON THE SYSTEM MAPS. THE ASHLAND CONTROL CENTER IMMEDIATELY DETECTED THE CHANGE IN PRESSURE AND FLOW AND INITAITED EMERG4NCY SHUT-DOWN PROCCEDURES AT 0956 HRS.. FIELD PERSONNEL WERE IMMEDIATELY DISPATCHED TO CLOSE THE DOWNSTREAM VALVE AND VERIFY CLOSURE OF THE UPSTREAM VALVE. WITHIN 5 MINUTES, THE LINE WAS SHUT DOWN PROCEDURES AT 0956 HRS.. FIELD PERSONNEL WERE IMMEDIATELY DISPATCHED TO CLOSE THE DOWNSTREAM VALVE AND VERIFY CLOSURE OF THE UPSTREAM VALVE. WITHIN 5 MINUTES, THE LINE WAS SHUT DOWN; WITHIN 9 MINUTES (1002 HRS) THE UPSTREAM REMOTELY-OPERATED VALVE WAS CLOSED; AND WITHIN 23 MINUTES (1015 HRS) THE DOWNSTREAM MANUALLY-OPERATED VALVEWAS CLOSED. THE UPSTREAM VALVE IS APPROXIMATELY 1.1 MILES WEST OF THE LEAK SITE AND THE DOWNSTREAM VALVE IS APPROXIMATELY 0.94 MILES EAST OF THE LEAK SITE. EMERGENCY RESPONSE PERSONNEL WERE DISPATCHED TO THE TUSCARAWAS RIVER TO START PLACING BOOMS ON THE RIVER AND START CLEANUP. AT APPROXIMATELY 1150 HOURS, IT WAS DETERMINED THAT AN UNKNOWN 4" TAP RISER AND VALVE ON THE PIPELINE WAS STRUCK CAUSING THE ACCIDENT. AT APPROXIMATELY 1900 HOURS , A PLIDCO SPLIT SLEEVE WAS PLACED OVER THE OPENING LEFT IN THE DAMAGED PIPE. AT APPROXIMATELY 1915 HOURS, THE VALVE AT NAVARRE STATION WAS OPENED AND AT APPROXIMATELY 1930HOURS THE VALVE AT SHEPLER CHURCH WAS OPENED. THE SLEEVE WAS CHECKED FOR LEAKAGE AND NONE WAS FOUND. AT APPROXIMATELY 1959 HOURS, THE LINE WAS RESTARTED,AND THE SLEEVE WAS CHECKED FOR LEAKAGE AND NONE WAS FOUND.
2017-09-29 08:50 | NO | NO | 19950098 | 1995-07-05 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1995-06-05 | 1415 | CA | SAN BERNARDINO | RIALTO | NO |  | NO | COLTON TERMINAL (TANK FARM) LOCATED AT 2359 S. RIVERSIDE AVENUE, BLOOMINGTON, CA 92316 |  | TANK FARM | VALVE |  | 1969 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22031.6869 | 44446.8113 | GASOLINE | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | CONTAMINATED SOIL (APPROXIMATELY 10'X10') WAS DISCOVERED WHILE EXCAVATING BREAKOUT TANK C-27 TANK VALVE. TANK AND PIPING WERE EMPTY AND OUT SERVICE IN PREPARATION FOR TANK CLEANING AND SEAL REPLACEMENT. TANK VALVE FLANGE WAS WET INDICATING PROBABLE SOURCE OF RELEASE.
2017-09-29 08:50 | YES | NO | 19950099 | 1995-07-05 | 19226 | TEXACO PIPELINE INC | YES | 1995-06-07 | 930 | OK | KAY |  | NO |  | NO | SALT FORK RIVER CROSSING SW 1/4 SECTION 16,T 25 N, R 2 E, KAY COUNTY OKLAHOMA. |  | LINE PIPE | GIRTH | LINE FAILED AT GIRTH WELD | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 660000 | 484697.1109 | 977829.8496 | CRUDE OIL | 1 | 2526 | 80 | NO | NO | 8 | 0.32 | 24000 | WELDED |  | 490 | 100 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | BOYD URATIL | 9182253469 | SHORTLY AFTER MIDNIGHT ON JUNE 7, 1995, A SMALL DIFFERENTIAL IN THROUGHPUTVOLUMES WAS NOTICED ON THE CIMARRON CRUDE SYSTEM AND THE LINE WAS SHUT DOWN.A RELEASE WAS CONFIRMED BY AERIAL FLYOVER AFTER DAYBREAK. THE RELEASE OCCURREDBETWEEN RIVER BLOCK VALVES WHILE THE SALT FORK RIVER WAS ENCOUNTERING HIGHWATER CONDITIONS AND/OR INCREASED WATER VOLUMES. EXACT CAUSE OF FAILURE WILLBE DETERMINED ONCE RIVER CONDITIONS ALLOW ACCESS FOR INSPECTION. LINE WILLREMAIN IDLE UNTIL RIVER CROSSING IS CORRECTED. SUPPLEMENTAL REPORT RECEIVED10/13 INDICATES THAT THE LINE WAS NITROGEN PURGED AND ABANDONED DURING JULYAND AUGUST OF 1995. DECISION TO ABANDON WAS BASED ON ECONOMIC FEASIBILITY.SUPPLEMENTAL INFORMATION RECEIVED 1/31/1996 INDICATED THAT RIVER CROSSING WASINVESTIGATED. HIGH WATER CONDITIONS UNDERCUT BURIED PIPE PLACING EXCESSIVESTRESS ON PIPE. LINE FAILED AT GIRTH WELD. INCREASE IN PROP DAMAGE FROM450000 TO 660000.
2017-09-29 08:50 | NO | NO | 19950100 | 1995-06-30 | 19226 | TEXACO PIPELINE INC | YES | 1995-05-14 | 1500 | TX | JEFFERSON | PT. NECHES | NO |  | NO | INSIDE STAR ENTERPRISE PT. NECHES ASPHALT PLANT ON TPLI 22" PIPELINE. |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 44063.3737 | 88893.6227 | CRUDE OIL | 1 | 25 | 24 | NO | NO | 22 | 0.31 | 52000 | WELDED |  | 1060 | 100 | YES | 0 | 1000 | 0 | 53 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | B. KEDNEDY | 7134323401 | IN DECEMBER 1994 A CONTRACTOR FOR STAR ENTERPRISE BUILT A ROAD INSIDE THE ASPHALT PLANT OVER OUR PIPELINE. NO ONE NOTIFIED TPLI OF THIS WORK. TPLI WAS NOTIFIED ON 12/19/94 THAT THE 22" LINE WASH HIT WHILE WORKING IN VICINITY OF LINE. TPLI RESPONDED AND THERE WAS ONLY MINOR DAMAGE AT THAT TIME. TPLI THEN MARKED THE REMAINING 200-300 FEET OF LINE FOR CCOMPLETION OF ROAD. TPLI WAS ON SITE FOR NEXT THREE (3) DAYS. THE CONTRACTOR NEVER MENTIONED ADDITIONAL DAMAGE TO TPLI'S LINE. ON MAY 14, 1995 WHILE THE LINE WAS IDLE, OIL BEGAN SURFACING IN THE ROAD IN PT. NECHES PLANT. UPON INVESIGATION A SEVERELY DAMAGED SECTION OF PIPELINE WAS LOCATED IN EAST END OF ROAD. REPAIRS MADE, OIL REMOVED, OILY DIRT REMOVED.
2017-09-29 08:50 | YES | NO | 19950101 | 1995-06-30 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-05-30 | 1313 | IN | TIPPECANOE |  | NO |  | Null | 7913 STATE ROAD 43 NORTH, BATTLEGROUND INDIANA |  | PUMPING STATION | PUMP |  | 0 | OTHER | SEAL LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5507.9217 | 11111.7028 | GASOLINE | 3 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | AT APPROXIMATELY 1313 HOURS, MAY 30, 1995, THE BOOSTER PUMP AT TEPPCO'S LAFAYETTE STATION EXPERIENCED A SEAL FAILURE. THIS FAILURE RESULTED IN A SMALL RELEASE OF UNLEADED GASOLINE VAPORS WHICH IMMEDIATELY IGNITED. PERSONNEL ON-SITE IMMEDIATELY INITIATED THE EMERGENCY PLAN. THE PUMP WAS SHUT DOWN, ISOLATED AND THE SMALL FIRE AROUND THE PUMP SEAL WAS EXTINGUISHED. REPAIRS WERE MADE TO THE PUMP SEAL ASSEMBLY ON THE SAME DATE.
2017-09-29 08:50 | NO | NO | 19950102 | 1995-07-03 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-06-05 | 1521 | NE | LANCASTER |  | NO |  | NO | TOWNSHIP 11 NORTH, RANGE 8 EAST, SECTION 12 |  | PUMPING STATION | PUMP |  | 1976 | OTHER | MECHANICAL SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 4 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.P. RUETER | 9185811800 | DURING THE START-UP OF A PUMP, THE OUTBOARD MECHANICAL SEAL FAILED. LIQUIFIED ANHYDROUS AMMONIA WAS RELEASED TO THE ATMOSPHERE WHERE IF IMMEDIATELY VAPORIZED. THE PUMP UNIT WAS IMMEDIATELY SHUTDOWN AND A MOTOR OPERATED VALVE CLOSED ISOLATING THE UNIT. A BLOWDOWN HOSE WAS CONNECTED TO AID IN THE PROPER REMOVAL OF THE REMAINING PRODUCT TO A RECOVERY SYSTEM.
2017-09-29 08:50 | YES | NO | 19950103 | 1995-07-07 | 10012 | KANEB PIPELINE CO | YES | 1995-06-06 | 1535 | KS | REPUBLIC |  | NO |  | NO | NW 1/4, NW 1/4, SECTION 21, T-1-S, R-5-W |  | LINE PIPE | GIRTH |  | 1935 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7343.8956 | 14815.6038 | FUEL OIL | 3 | 50 | 7 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.LEROY ANDERSON | 3162621408 | THE LANDOWNER NOTICED STAINED SOIL ON CULTIVATED FARM GROUND. FURTHER INVESTIGATION BY THE LANDOWNER REVEALED A PETROLEUM ODOR AT THE STAIN LOCATION. SUBSEQUENTLY, THE LANDOWNER TELEPHONED THE KANEB PIPE LINE CONTROL CENTER TO REPORT THE STAINED SOIL. THE AFFECTED LINE SEGMENT WAS SHUT DOWN IMMEDIATELY UPON NOTIFICATION. PERSONNEL AND EQUIPMENT WERE MOBILIZED TO THE AREA. THE PIPELINE WAS EXCAVATED AND EXPOSED. INVESTIGATION REVEALED AN ANOMALY IN A GIRTH WELD THAT HAD DEVELOPED A SEEPING LEAK. THE PIPELINE WAS REPAIRED BY WELDING AFULL ENCIRCLEMENT SLEEVE OVER THE PROBLEM AREA. THE IMPACTED SOILS ARE UNDERGOING REMEDIATION IN COOPERATION WITH THE KANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19950104 | 1995-07-10 | 25172 | UNOCAL NORTH AMERICAN OIL & GAS DIV | NO | 1995-06-24 | 1700 | CA | KERN | MCKITTRICK | NO |  | NO | MCKITTRICK PUMP STATION ON THE SOUTH SIDE OF FRANKO WESTERN ROAD, 1.5 MILES NORTH OF REWARD ROAD. SEC 18, T 30S, R 22 E, KERN COUNTY, CALIFORNIA |  | PUMPING STATION | PUMP |  | 1980 | OTHER | MECHANICAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 55079.2171 | 111117.0284 | CRUDE OIL | 1 | 250 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDMOND C. LEE | 8053955312 | ON JUNE 24, 1995 AT APPROXIMATELY 5:00 PM, PACIFIC TIME, UNOCAL ENERGY RESOURCES PERSONNEL DROVE BY MCKITTRICK PUMP STATION AND REPORTED OIL SPRAYING FROM THE MAINLINE SHIPPING AREAS AND RUNNING ACROSS THE ROADWAY. THIS INCIDENT WAS DISPATCHED TO PIPELINE PERSONNEL WHO WAS ON CALL. AFTER LEARNING OF THE INCIDENT, ALL PUMPING ACTIVITIES IN THE STATION WERE SHUTDOWN. UPON PRELIMINARYINVESTIGATION, WE FOUND THE SPILL WAS CAUSED BY THE MECHANICAL FAILURE OF A IMO, MAINLINE SHIPPING PUMP (SCREW PUMP). THE REAR IDLER OF THE PUMP WENT THROUGH THE REAR FLANGE AND PUNCTURED A HOLE, 1 3/4" IN DIAMETER, ON THE FLANGE. THE SJVH CRUDE OIL WAS CONTAINED AND CLEANED UP BY UNOCAL, THE SATISFACTIONOF THE DEPARTMENT OF FISH AND GAME, WHO WERE THE LEADING AGENCY RESPONDING TO THE INCIDENT.
2017-09-29 08:50 | YES | NO | 19950105 | 1995-07-10 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-06-12 | 1030 | TX | HARRIS |  | NO |  | NO | 1836 VISTA ROAD, DEER PARK, TEXAS |  | PUMPING STATION | PUMP |  | 0 | OTHER | PUMP SEAL RELEASE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5507.9217 | 11111.7028 | GASOLINE | 3 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | AT APPROXIMATELY 1030 HOURS, JUNE 12, 1995, THE BOOSTER PUMP AT TEPPCO'S BATTLEGROUND PUMP STATION EXPERIENCED A SEAL FAILURE. THIS FAILURE RESULTED IN ASMALL RELEASE OF UNLEADED GASOLINE VAPORS WHICH IMMEDIATELY IGNITED. PERSONNEL ON-SITE IMMEDIATELY INITIATED THE EMERGENCY PLAN. THE PUMP WAS SHUTDOWN, ISOLATED AND THE SMALL FIRE AROUND THE PUMP SEAL WAS EXTINGUISHED REPAIRS HAVEBEEN MADE TO THE PUMP SEAL ASSEMBLY.
2017-09-29 08:50 | YES | NO | 19950106 | 1995-07-07 | 1004 | KOCH HYDROCARBON COMPANY | NO | 1995-06-06 | 1110 | OK | CLEVELAND | NORMAN | NO |  | NO | T9N-R3W SEC 34 CLEVELAND COUNTY, OK MIDDLE OF CANADIAN RIVER |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 293755.8248 | 592624.1512 | NATURAL GAS LIQUID | 2 | 1555 | 0 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 1200 | 743 | YES | 8 | 1555 | 10 | 85 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | JERRY ROGERS | 4053952377 | AT THIS TIME; CAUSE IS UNKNOWN, BUT AN ASSUMPTION IS THAT THE PIPELINE FAILED DUE TO NATURAL CAUSES CAUSED BY RIVER AND FLOODING.
2017-09-29 08:50 | YES | NO | 19950107 | 1995-07-17 | 12627 | MOBIL OIL CORP | NO | 1995-05-28 | 800 | TX | NAVARRO | CORSICANA | NO |  | NO | 1604 SOUTH 15TH STREET, CORSICANA, TEXAS APPROX. 1 MILE N. OF DOWNTOWN CORSICANA, TEXAS |  | TANK FARM | TANK | SMALL HOLE DRAIN ROOF | 1978 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11015.8434 | 22223.4057 | CRUDE OIL | 1 | 103 | 100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | ROOF DRAIN HOSE LEAK | Null | NO DATA |  | Null | Null | D.G. SCOTT | 2146585914 | APPROXIMATELY 0800 HRS. SUNDAY, MAY 28, 1995, CRUDE OIL WAS DISCOVERED LEAKING FROM THE ROOF DRAIN VALVE OF TANK #2691 AT CORSICANA TANK FARM DUE TO A SMALL HOLE IN THE ROOF DRAIN HOSE. APPROXIMATELY 103 BBLS. ESCAPED WITHIN THE TANK FIREWALL AREA THUS BEING CONTAINED.MAINTENANCE PERSONNEL WERE IMMEDIATELYNOTIFIED AND STEPS INITIATED TO BEGIN RECOVERY AND CLEANUP. APPROXIMATELY 100 BBLS. WERE RECOVERED. THE REMAINING 3 BBLS. WAS MIXED WITH FRESH DIRT AND ABSORBED INSIDE FIREWALL. THE NRC AND TRRC WERE NOTIFIED. NO INJURIES WERE ASSOCIATED WITH THIS INCIDENT. STEPS ARE BEING TAKEN TO REPLACE THE FAULTY ROOF DRAIN HOSE.
2017-09-29 08:50 | YES | NO | 19950108 | 1995-07-13 | 12127 | MARATHON PIPE LINE CO | YES | 1995-06-13 | 17 | IN | HAMILTON | SHERIDAN | NO |  | NO | APPROXIMATELY 1 MILE SOUTH OF SHERIDAN, IN, HAMILTON COUNTY, ADAMS TOWNSHIP, SECITON 5, T19N,R3E. |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 367194.781 | 740780.1891 | CRUDE OIL | 1 | 2268 | 636 | NO | NO | 22 | 0.31 | 46000 | WELDED |  | 939 | 795 | YES | 24 | 1175 | 0 | 75 | NO DATA | Null | Null | NO DATA |  | OTHER | PRIOR OUTSIDE DAMAGE. | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 00:17:07 HOURS ON JUNE 13, 1995, MARATHON PIPE LINE COMPANY'S (MPL"S) OPERATIONS CENTER RECOREDED A SUDDEN PRESSURE DROP ON THE MARTINSVILLE-LIMA 22" RCRUDE PIPELINE. SHUTDOWN OF THE PIPELINE WAS COMMENCED BY THE OPERATIONS CENTER AT 00:18:07 AND COMPLETED AT 00:20:44. MPL PERSONNEL RESPONDED TO THE GENERAL LOCATION OF THE PRESSURE DROP AND DISCOVERED A RUPTURE IN THE PIPELINE AT RIGHT-OF-WAY 1227, IN A CULTIVATED FIELD. CRUDE OIL HAD SPRAYED FROM THE RUPTUIRE AND COVERED AND AREA APPROXIMATELY 500' BY 500' IN THE FIELD WITH CRUDE OIL. OIL HAD COLLECTED IN A DRY SWALE APPROXIMATELY 600' LONG IN THE CENTER OF THE SPRAYED AREA. SOME OIL ALSO ENTERED A DRAIN TILE SYSTEM AND WAS CONVEYED TO A SMALL DRAINAGE DITCH, WHERE IT WAS CONTAINED WITH BOOMS AND SIPHON DAMS. OIL COLLECTION COMMENCED IMMEDIATELY BY VACUUM TRUCK. A SYSTEM OF TRENCHES WAS DUG IN THE CULTIVATED FIELD TO CONCENTRATE AND COLLECT THE FREE OIL. THE AFFECTED FIELD TILES WERE JETTED AND FLUSHED WITH SEVERAL THOUSAND GALLONS OF WATER TO ATTEMPT TO FLUSH OUT ANY CRUDE OIL WHICH HAD ACCUMULATED.A 55' FOOT SECTION OF PIPE WAS REMOVED AND REPLACED WITH PREVIOUSLY TESTED 22" PIPE. THE PIPELINE WAS RETURNED TO SERVICE AT 05:40 ON JUNE 14, 1995. RICK GULSTAD, OPS INSPECTOR, WAS ON SITE DURING THE MAJORITY OF THE WORK. THE DAMAGED SECTION OF PIPE WILL BE ANALYZED TO ATTEMPT TO DETERMINE THE CAUSE OF THE FAILURE. SOME SMALL DENTS AND SURFACE GOUGES WERE OBSERVED IN THE PIPELINE WHERE THE RUPTURE OCCURRED; THE PIPELINE COATING WAS ALSO DAMAGED IN THIS AREA. LONG-TERM CLEANUP AND REMEDIATION OF THE SITE BY HERITAGE ENVIRONMENTAL (MPL'S CONTRACTOR IS ONGOING.
2017-09-29 08:50 | YES | YES | 19950109 | 1995-07-17 | 12127 | MARATHON PIPE LINE CO | YES | 1995-06-16 | 1955 | OH | SUMMIT | FRANKLIN | NO |  | NO | SECT. 18,SE 1/4,T18N,R10W/FRANKLIN TOWNSHIP, SUMMIT COUNTY, OHIO. |  | TANK FARM | PIPE |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 2 | 1 | 1 | 3000000 | 2203168.6859 | 4444681.1343 | GASOLINE | 3 | 5264 | 2062 | YES | NO | 8 | 0.32 | 0 | WELDED |  | 275 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT 1920 HOURS ON JUNE 16, 1995, THE CLINTON STATION FOREMAN RECEIVED NOTICEFROM THE FRANKLIN TOWNSHIP FIRE DEPARTMENT THAT A RESIDENT ONCLEVELAND-MASSILL ON ROAD WAS COMPLAINING ABOUT STRONG GASOLINE VAPORS IN THEAREA OF THE CLINT ON STATION. THE FOREMAN CONTACTED THE MARATHON PIPE LINECOMPANY OPERATIONS CENTER TO ADVISE THEM OF THE SITUATION. LOCAL PERSONNELWERE ALSO DISPATCHED T O CLINTON STATION. AT 1934 HOURS, ALL RECEIPT ANDDELIVERY OPERATIONS AT CLIN TON STATION WERE SHUT DOWN BY THE OPERATIONSCENTER. AT 1955 HOURS, CLINTON S TATION PERSONNEL FOUND A RELEASE HAD OCCURREDFROMT HE 8" TANK LINE TO TANK 3 611. DUE TO VAPOR MIGRATION TO THE IMMEDIATELYADJACENT RESIDENTIAL AREA, THE FRANKLIN TOWNSHIP FIRE DEPARTMENT EVACUATED 24HOMES AS A SAFETY PRECAUTION. INITIALLY THE RELEASED PRODUCT WAS CONFINED TOTHE CLINTON STATION PROPERTY, HOWEVER, SUBSEQUENT SUBSURFACE MIGRATION DIDIMPACT ON ADJACENT PARCEL OF PRIVATE PROPERTY. MARATHON PIPE LINE ANDCONTRACT PERSONNEL WERE DISPATCHED TO THE SCENE WHERE PRODUCT CONTAINMENT ANDRECOVERY WAS BEGUN. A SYSTEM OF TRENCHES WERE DUG ON SITE IN THE IMPACTEDAREAS TO INTERCEPT AND CONTROL THE SUBS URFACE MIGRATION OF THE PRODUCT.TRENCHES WERE ALSO DUG ON ONE ADJACENT PARCE L. ALSO, BOOMS WERE PLACED ON THECLINTON STATION POND AND TOW PRIVATE PONDS, ADJACENT TO THE STATION, TOPREVENT PRODUCT FLOW INTO THE CREEKS DOWNSTREAM THEREOF. AS AN ADDITIONALPRECAUTION, CONTAINMENT DIKES, WITH FLUMES AND BOOMS WERE DEPLOYED ON CREEKSAND STREAMS DOWNSTREAM OF THE RELEASE AREA. ON MONDAY, JUNE 19, 1995 AT ABOUT0630 HOURS, A BACKHOE BEING USED TO CONSTRUCT A CONTAINMENT TRENCH NEAR THEPOND AREA CAUSED A SPARK WHICH IGNITED VAPORS IN TH E RENCH. THE ENSUING FIRESPREAD FROM THE TRENCH AREA TO THE POND AND THEN UP THE HILL WHERE SOME OFTHE RELEASED PRODUCT WAS SEEPING TO THE SURFACE. THE FIRE WAS CONFIEND TO THEIMMEDIATE STATION AREA. A MARATHON EMPLOYEE AND A CONTRACT EMPLOYEE RECEIVEDBURNS WHEN THE FIRE IGNITED. BOTH WERE TRANSPORTED TO A NEARBY HOSPITAL WHERTHEY WERE TREATED AND RELEASED LATER THAT MORNING. A 25 FOOT SECTION OF PIPEWAS REMOVED FROMT HE 8" TANK LINE AND REPLACED WITH NEW PIPE. THIS DAMAGEDSECTION OF PIPE IS BEING ANALYZED BY AN OUTSIDE CONSU LTANT TO DETERMINE THECAUSE OF THE PIPE FAILURE. THE REPAIRED TANK LINE WAS PRESSURE TESTED TO AMINIMUM PRESSURE OF 350 PSI, AND HELD FOR 8 HOURS, PRIOR TO RETURNING IT TOSERVICE. THE NORMAL OPERATING PRESSURE OF THIS LINE IS AP PROXIMATELY 50 PSI.THE CLINTON STATION WAS FULLY RETURNED TO SERVICE ON JUNE 23, 1995. RECOVERYAND REMEDIATION CONTINUES AT THE SITE.
2017-09-29 08:50 | YES | NO | 19950110 | 1995-07-17 | 26127 | CHEVRON PIPELINE CO | NO | 1995-06-17 | 1230 | CA | YOLO |  | NO |  | NO | AREA WAS NEAR THE INTERSECTION OF SOUTH RIVER ROAD & JEFFERSON ROAD. |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 73438.9562 | 148156.0378 | GASOLINE | 1 | 10 | 0 | NO | NO | 8 | 0.19 | 4600 | WELDED |  | 1434 | 724 | YES | 4 | 1786 | 12 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | G.N. TURNER | 5107532002 | D-7 CATIPILER WORKING FOR PORT OF SACRAMENTO HIT PIPELINE. THERE WAS NO ONE-CALL NOTIFICATION MADE CAT OPERATOR CALLED FIRE DEPARTMENT, WHO INFORMED CHEVRON PIPE LINE COMPANY DISPTACH OFFICE. DISPATCH SHUT DOWN PIPELINE.
2017-09-29 08:50 | YES | NO | 19950111 | 1995-07-17 | 2387 | CITGO PIPELINE CO | YES | 1995-07-01 | 800 | TX | HARDIN | SOUR LAKE | NO |  | NO | CITGO TANK FARM, WEST SIDE OF HWY, 326N |  | TANK FARM | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8078.2852 | 16297.1642 | CRUDE OIL | 1 | 460 | 445 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. MOSELEY | 4092873594 | LEAK WAS REPORTED BY AERIAL PATROL FLYING OVER TANK FARM. CITGO PIPELINE PERSONEL FOUND LEAK COMING FROM SUCTION LINE TO EXXON METER SKID. EXXON WAS SHUTDOWN AND LINE ISOLATED. CLEAN UP CREWS WERE CALLED OUT AND TEMPORARY REPAIR MADE TO LINE.
2017-09-29 08:50 | YES | NO | 19950112 | 1995-07-13 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-06-13 | 1530 | IA | WOODBURY |  | NO |  | NO | TOWNSHIP 86 NORTH, RANGE 47 WEST, SECTION 26 |  | LINE PIPE | GIRTH |  | 1974 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 3323 | 2440.3765 | 4923.2251 | ANHYDROUS AMMONIA | 2 | 12 | 0 | NO | NO | 4.5 | 0.14 | 2193 | WELDED |  | 1579 | 200 | YES | 24 | 2148 | 0 | 74 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHNNY CAVITT | 9185993795 | A MAPCO EMPLOYEE CONFIRMED A DEAD SPOT REPORTED BY THE LINE FLYER, AND ALSO REPORTED A SMELL OF AMMONIA VAPORS. UPON EXCAVATION OF THE LINE, A PINHOLE LEAK WAS FOUND IN A GIRTH WELD. THE LINE WAS SHUT DOWN, AND PRESSURE WAS LOWERED ON THE LINE SEGMENT. EMPLOYEES THEN CLOSED THE UPSTREAM AND DOWNSTREAM BLOCK VALVES. A PERMANENT REPAIR WAS MADE BY INSTALLING A FULL ENCIRCLEMENT SLEEVE
2017-09-29 08:50 | YES | NO | 19950113 | 1995-07-11 | 22610 | WILLIAMS PIPELINE CO | YES | 1995-06-10 | 500 | MO | AUDRAIN |  | NO |  | NO | SOUTHWEST 1/4 OF SECTION 2 IN T51N-R9W IN AUDRAIN COUNTY, MISSOURI |  | LINE PIPE | PIPE |  | 1945 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 55079.2171 | 111117.0284 | GASOLINE | 3 | 89 | 89 | NO | NO | 12.75 | 0.25 | 35000 | WELDED |  | 750 | 650 | YES | 8 | 1007 | 0 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883850 | AT APPROXIMATELY 0500 HOURS ON JUNE 10, 1995, OPERATIONS CONTROL NOTIFIED THEREGION OFFICE PERSON ON CALL THAT THE PRESSURE HAD DROPPED ON A SECTION OF THE TCS 12" LINE BETWEEN CENTRALIA, MO. (MP 401) AND MADISONVILLE, MO (MP 443). AT THE TIME OF THE DROP IN PRESSURE, THE LINE WAS HOLDING A STATIC PRESSUREOF APPROXIMATELY 650 PSI. FIELD PERSONNEL WERE DISPATCHED TO CLOSE VALVES ATMP 411 AND 421 TO FURTHER ISOLATE THE LINE. THIS CAUSED THE PRESSURE TO STABILIZE AT BOTH CENTRALIA AND MADISONVILLE. PRESSURE GAUGES WERE THEN INSTALLEDTO VERIFY PRESSURE DROPPED, FIELD PERSONNEL BEGAN WALKING THE LINE AND FLYING THE TNE MILE SECTION TO LOCATE THE LEAK. THE LEAK WAS FOUND AT APPROXIMATELY 1230 HOURS AT MP 417 +25. THE MAINTENANCE CREW BEGAN RECOVERY AND CONTAINMENT EFFORTS BY DIGGING TRENCHES DOWNGRADE OF THE LINE, WHICH PREVENTED ANY CONTAMINATION OF A NEARBY CREEK. THE LINE WAS EXCAVATED THE LEAK WAS CLAMPED OFFFOR INSTALLATION OF A 12" FULL ENCIRCLEMENT SLEEVE. THE LINE WAS EXCAVATEDAPPROXIMATELY 110 FEET ON BOTH SIDES OF THE LEAK SITE TO INSPECT THE INTEGRITY OF THE PIPE AND COATING. REPAIRS WERE MADE TO ADDITIONAL LOCALIZED CORRODEDAREAS WHICH WERE COMPLETED JUNE 11, 1995. THE LINE WAS OFFICIALLY TURNED OVERTO OPERATIONS CONTROL AT 1600 HOURS ON JUNE 12, 1995. CLEAN-UP EFFORTS INCLUDED INSITU BURNING ALONG WITH SOIL EXCAVATION AND LAND FARMING ON SITE. THISWORK WAS DONE IN COOPERATION WITH THE MISSOURI DEPARTMENT OF NATURAL RESOURCES. IT IS EXPECTED TO TAKE A COUPLE OF MONTHS FOR COMPLETE CLEAN-UP AND RESTORATION OF THE LEAK SITE.
2017-09-29 08:50 | NO | NO | 19950114 | 1995-07-11 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO., LP | YES | 1995-06-14 | 0 | IL | WILL |  | NO |  | NO | 12864 HADLEY ROAD, LOCKPORT, ILLINOIS |  | LINE PIPE | OTHER | NOT GIVEN | 0 | OTHER | 1/8" HOLE DRILLED IN PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 44063.3737 | 88893.6227 | NATURAL GAS LIQUID | 3 | 15 | 0 | NO | NO | 12.75 | 0.38 | 35000 | WELDED |  | 600 | 40 | YES | 8 | 760 | 0 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON JUNE 14, 1995, TEPPCO DETERMINED AN INCIDENT WHICH OCCURRED JUNE 10, 1995WOULD EXCEED $50,000 DUE TO REMEDIATION REQUIREMENTS. THE INCIDENT INVOLVED A 12" PIPELINE (OWNED AND MAINTAINED BY UNOCAL PIPELINE COMPANY; OPERATED BY TEPPCO) IN WILL COUNTY, ILLINOIS WITH APPROXIMATELY 15 BARRELS OF PRODUCT UNINTENTIONALLY RELEASED DUE TO A ONE-EIGHTH INCH DIAMETER DRILLED HOLE THAT HADNOT LEAKED IN THE PAST. THIS HOLE WAS PRESENT PRIOR TO RFURBISHING AND THE RECOAT OF THE PIPE. THE PIPE WAS REPAIRED AND PLACED BACK INTO SERVICE ON JUNE15 AND INITIAL REMEDIATION AT THE SITE BEGAN. TEPPCO HAD NO INDICATION THE TOTAL COST OF THE INCIDENT WOULD EXCEED $50,000 AT THE TIME. A FORMAL SITE REMEDIATION PLAN IS BEING PREPARED FOR SUBMITTAL TO THE ILLINOIS ENVIRONMETAL PROTECTION AGENCY.
2017-09-29 08:50 | YES | NO | 19950115 | 1995-07-17 | 15851 | PRIDE REFINING INC | NO | 1995-06-01 | 800 | TX | GRAY | PAMPA | NO |  | NO | 2 TO 3 MILES SOUTH OF PAMPA OFF BOWENS CITY HIGHWAY. |  | PUMPING STATION | PUMP |  | 0 | OTHER | PACKING GLAND FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1101.5843 | 2222.3406 | CRUDE OIL | 1 | 490 | 260 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON | 9156748231 | PIPELINE SCADA OPERATOR BECAME CONCERNED ABOUT A LOSS OF RATE ON THE SYSTEM SO THE PUMPS WERE SHUT DOWN AT 5:15AM AND OIL WAS DISCOVERED AT 8:00AM. INJECTION PUMP PACING GLAND HAD FAILED AND APPROXIMATELY 490 BBLS OF OIL HAD BEEN RELEASED ON COMPANY PROPERTY. PHASE I CLEAN-UP ACTIVITY WAS COMPLETED BY THE FOLLOWING MORNING. WE ARE AWAITING SOIL TEST RESULTS BEFORE FINAL CLEAN-UP/REMEDIATION IS SCHEDULED.
2017-09-29 08:50 | YES | NO | 19950116 | 1995-07-19 | 19326 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1995-06-19 | 1130 | TX | WINKLER |  | NO |  | NO | SW/SE/4 SECTION 2, BLOCK 74,APPROXIMATELY 7 1/2 MILES SUTH OF JAL STATION. |  | LINE PIPE | PIPE |  | 1955 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18359.739 | 37039.0095 | CRUDE OIL | 1 | 62 | 0 | NO | NO | 12 | 0.22 | 24000 | WELDED |  | 685 | 60 | YES | 8 | 800 | 0 | 91 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | EDWIN H. GRIPP | 9159479001 | OIL LOSS WAS REPORTED BY AIR PATROL AT 11:30 A.M. CDST ON JUNE 19, 1995. LINEWAS DOWN AT TIME OF RELEASE. CAUSE THE LEAK WAS DETERMINED TO BE INTERNAL CORROSION. LEAK WAS TEMPORARILY REPAIRED AND LINE RETURNED TO SERVICE AT 4:00 P.M. CDST ON JUNE 19, 1995. INITIAL CLEANUP WAS COMPLETED AT 12:30 P.M. CDST, JUNE 20, 1995. FINAL CLEANUP WILL BE IN ACCORDANCE WITH THE STATE OF TEXAS STATEWIDE RULE 91. PERMANENT REPAIRS WILL BE MADE BY REPLACING PIPE WITH NEW PIP
2017-09-29 08:50 | YES | NO | 19950117 | 1995-07-19 | 7614 | HOWELL CORP | NO | 1995-06-14 | 1100 | TX | WALLER |  | NO |  | NO |  |  | LINE PIPE | OTHER | COLLAR FITTING | 1925 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 88126.7474 | 177787.2454 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 500 | 278 | YES | 8 | 908 | 0 | 93 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | DANNY F. DAVIS | 7136584132 | ON JUNE 14, 1995 A HOWELL PIPELINE TEXAS (HPT) PATROL AIRPLANE REPORTED A CRUDE OIL LEAK NEAR WALLER, TEXAS ON HPT'S NAVASOTA TO SATSUMA 8" PIPELINES. THE SPILL SITE IS LOCATED SOUTH OF REID'S PRAIRIE ROAD APPROXIMATELY 1/3 MILE EAST OF FM 362. THE SPECIFIC BREAK IN HPT'S 8" LINE WAS LOCATED DIRECTLY ABOVEAQUILLA'S 30" NATURAL GAS LINE WHICH HAD BEEN INSTALLED IN LATE MAY. BECAUSEOF THE CONDITION OF AQUILLA"S CONSTRUCTION ROW, THE NATURAL GAS LINE HAD BEEN CONSTRUCTED AND BACKFILLED DURING OR IMMEDIATELY AFTER A SUBSTANTIAL RAINFALL. LARGE AND DEEP RUTS WERE NOTED THROUGHOUT THE ROW AND OVER THE BROKEN 8"PIPELINE. GIVEN THESE FACTS, OUR CONCLUSION IS THAT HAINES CONSTRUCTION, AQUILLA'S CONTRACTOR DROVE A PIECE OF HEAVY EQUIPMENT ONTO AND /OR OVER OUR CRUDE OIL PIPELINE, WHICH CAUSED THE LINE TO BREAK.
2017-09-29 08:50 | YES | NO | 19950118 | 1995-07-25 | 19522 | TOSCO CORP | NO | 1995-06-27 | 315 | NY | SUFFOLK |  | NO |  | NO | NORTH SERVICE ROAD OF THE LONG ISLAND EXPRESSWAY, 1400 FT. EAST OF ROUTE 111. |  | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 61852 | 45423.4632 | 91637.4725 | FUEL OIL | 1 | 880 | 800 | NO | NO | 16 | 0.25 | 1625 | WELDED |  | 250 | 884 | YES | 12 | 900 | 8 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | EARL ESPELAND | 5162842010 | SUPPLEMENTAL REPORT 11/29/1995 INDICATES THAT THE SUBJECT ORIGINAL PIPESECTION WAS RELOCATED IN 1989 FOR THE CONSTRUCTION OF THE NORTH SERVICE ROADOF THE LI EXPRESSWAY. SUPPLEMENTAL ALSO CHANGED PROPERTY DAMAGE FROM $0 TO$61,852.00.
2017-09-29 08:50 | YES | NO | 19950119 | 1995-07-24 | 12627 | MOBIL OIL CORP | NO | 1995-06-21 | 720 | CA | KERN |  | NO |  | NO | ROAD FROM INTERSTATE 5. |  | PUMPING STATION | VALVE |  | 1968 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7600 | 5581.3607 | 11259.8589 | CRUDE OIL | 3 | 170 | 165 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JEFF T. MILLER | 8057637600 | AT APPROXIMATELY 0730 ON JUNE 21, 1995 A MOBIL OPERATOR ENTERED THE ROSE STATION TO MAKE HIS ROUNDS WHEN HE NOTICED THE LEAK. THE OPERATOR IMMEDIATELY SHUT DOWN THE SYSTEM AND NOTIFIED THE MOBIL DISPATCH IN DALLAS, HE THEN CALLED HIS AREA MANAGER WHO THEN CALLED OES (REFERENCE #296502), CALIFORNIA STATE FIRE MARSHAL, AND FISH & GAME. MOBIL'S PIPELINE CREW IMMEDIATELY WENT TO THE SITE TO START THE CLEAN UP. OF THE 170 BARRELS SPILLED 165 WERE RECOVERED. THE GASKET WAS REPLACED THE FIRST WEEK OF JUNE 1995 BECAUSE OF SIGNS OF LEAKAGE AROUND GASKET AREA. DURING NORMAL ROUNDS, NO OTHER PROBLEMS WERE FOUND UNTIL THE DAY OF THE INCIDENT. MOBIL CONDUCTED IT'S OWN INCIDENT INVESTIGATION AND IT WAS FOUND THAT: 1). THE LEAK ACCRUED BECAUSE OF A GASKET FAILURE DUE TO A POSSIBLE MANUFACTURING FLAW FOLLOWED BY A SUBSEQUENT RECALL BY THE SAME MANUFACTURER. 2). THE GASKET WAS NOT PLIABLE ENOUGH TO WITHSTAND THE HIGH AND LOW TEMPERATURE CHANGES.3).SPARE GASKET MAY HAVE SET TO LONG. MOBIL CONTACTED THE VENDER TO MAKE THE NEW TYPE OF GASKETS AND AT THIS TIME WE SHOW NO SIGNS OF ANY OTHER PROBLEMS. MOBIL HAS ALSO STARTED AND INSPECTION OF IT'S SPARE GASKETS TO MAKE SURE THIS WILL NOT EVER HAPPEN AGAIN.
2017-09-29 08:50 | YES | NO | 19950120 | 1995-07-21 | 2552 | COLONIAL PIPELINE CO | YES | 1995-06-03 | 1500 | GA | COBB |  | NO |  | NO | COLONIAL PIPELINE COMPANY'S TANK FARM ATLANTA JUNCTION |  | TANK FARM | OTHER | SUMP | 1962 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11015.8434 | 22223.4057 | GASOLINE | 3 | 130 | 115 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | AT APPROXIMATELY 1500 ON JUNE 03, 1995. COLONIAL PIPELINE COMPANY EXPERIENCED A GASOLINE LEAK AT ITS TANK FARM AT POWDER SPRINGS, GEORGIA. APPROXIMATELY 130 BARRELS OF PRODUCT ESCAPED FROM AN OVERFILLED SUMP DURING A GASOLINE DELIVERY. THIS INCIDENT OCCURRED AFTER DRAIN VALVES ON THE STATION PROVER LOOP, WHICH DRAIN PRODUCT OT THE STATION SUMP, WERE INADVERTENTLY LEFT OPEN AFTER THE PREVIOUS METER PROVING ON MAY 15, 1995. A FAILURE OF THE SUMP OVERFLOW ALARM CONTRIBUTED TO THE SEVERITY OF THE INCIDENT. COMPANY EMPLOYEES AND CONTRACTOR PERSONNEL RESPONDED TO THE LEAK WHICH WAS CONTAINED ON THE OPERATORS PROPERTY. MOST OT THE PRODUCT ENTERED THE YARD DRAIN SYSTEM AND WAS COLLECTED IN ANEARBY CONSTRUCTION DITCH. WHEN IT BECAME APPARENT THAT MORE THAN 50 BARRELSOF PRODUCT HAD ESCAPED, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (REPORT NO. 294134) ON JUNE 04, 1995. TO DATE, 115 BARRELS OF PRODUCT HAVE BEEN RECOVERED. THE DISTRICT ENVIRONMENTAL TEAM CONTINUES TO ASSESS THE LEVEL OF CONTAMINATION AT THE FACILITY.
2017-09-29 08:50 | YES | NO | 19950121 | 1995-07-25 | 18386 | BP OIL PIPELINE CO | NO | 1995-07-08 | 1110 | OH | SUMMIT | STOW | NO |  | NO | LAKE RUN BLVD, 1/4 MILE WEST OF FISHCREEK ROAD. |  | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7343.8956 | 14815.6038 | DIESEL FUEL | 2 | 450 | 422 | NO | NO | 10 | 0.25 | 46000 | WELDED |  | 800 | 250 | YES | 24 | 1545 | 0 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | GREGORY A. DEBROCK | 2165862003 | A THIRD PARTY CONTRACTOR, A. CRANO EXCAVATION WAS OPERATING AN EARTHMOVER OVER THE AROUND THE PIPELINE TO REMOVE SOIL. A TOOTH ON THE BLADE OF THE EARTHMOVER STRUCK AND PUNCTURED THE PIPE, LEAVING A 2"X3" HOLE. THE CONTRACTOR QUICKLY DIKED THE AREA (60' X 100') AROUND THE RELEASE SITE TO CONTAIN THE PRODUCT. THE CONTRACTOR HAD BEEN WORKING IN THE AREA FOR SEVERAL WEEKS AND THE PIPELINE WAS MARKED WITH BOTH PERMANENT AND TEMPORARY MARKERS. BP CHECKED WITH THE CONTRACTOR ON SITE ON 07/07/95 AND THE CONTRACTOR GAVE NO INDICATION THAT THEY WOULD BE EXCAVATING IN THE AREA.
2017-09-29 08:50 | YES | NO | 19950122 | 1995-08-01 | 1004 | KOCH HYDROCARBON COMPANY | NO | 1995-06-28 | 1110 | OK | STEPHENS |  | NO |  | NO | NE 1/4 SEC 13 T2S R4W. 5 MILES S AND 8 MILES E OF VELMA, OK |  | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18359.739 | 37039.0095 | NATURAL GAS LIQUID | 2 | 300 | 0 | NO | NO | 4 | 0.13 | 42000 | WELDED |  | 1297 | 750 | YES | 10 | 1641 | 11 | 89 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | JERRY RODGERS | 4053952377 | THIRD PARTY OPERATOR BACK-HOE HIT OUR PIPELINE CAUSING A LEAK. ATTEMPTED TOMARK LOCATION AND UNABLE TO MAKE CONTACT WITH THIRD PARTY OPERATOR. KOCH R.O.W. MARKER 75' FROM SITE.
2017-09-29 08:50 | YES | NO | 19950123 | 1995-08-01 | 22610 | WILLIAMS PIPELINE CO | YES | 1995-06-29 | 1056 | OK | OKLAHOMA |  | NO |  | NO | NE 1/4 SEC OF SECTION 32, T12 N, R2W AND CLOSE TO INTERSECTION OF NE 10TH STREET AND SOONER ROAD |  | LINE PIPE | PIPE |  | 1973 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22031.6869 | 44446.8113 | FUEL OIL | 3 | 125 | 30 | NO | NO | 8.63 | 0.28 | 35000 | WELDED |  | 750 | 230 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883850 | SPECIFIC LOCATION: NE 1/4 IF THE NE 1/4 OF SECTION 32, T12N, R2W AND CLOSE TO THE INTERSECTION OF NE 10TH STREET AND SOONER ROAD.ON JUNE 29, 1995, AT APPROXIMATELY 0930 HOURS, AN INDIVIDUAL CONTACTED OPERATIONS CONTROL TO REPORT A POSSIBLE LEAK NEAR M.P. 1.49 ON THE #2-8" TULSA TO OKLAHOMA CITY LINE. OPERATIONS WERE IMMEDIATELY SHUT DOWN UNDER PRESSURE BETWEEN CUSHING AND OKLAHOMA CITY. OPERATIONS CONTROL CONTACTED THE SOUTHERN REGION OFFICE, WHO DISPATCHED EMPLOYEES FROM THE OKLAHOMA CITY AREA TO INVESTIGATE THE SITUATION. OPERATIONS CONTROL NOTED THAT THE STATIC PRESSURE WAS DROPPING ON THE CUSHING-OKLAHOMA CITY LINE SECTION AND PASSED THE INFORMATION ONTO THE SOUTHERN REGION OFFICE. CREWS FROM TULSA WERE MOBILIZED TO RESPOND TO THE SITUATION. UPON INSPECTION OF THE SITE, IT WAS DETERMINED THAT A SPILLHAD INDEED OCCURRED. THE TULSA AND IOLA, KANSAS, MAINTENANCE CREWS WERE DISPATCHED TO THE AREA TO REPAIR THE PIPELINE AND CLEAN UP THE SPILL.AT 1620 HOURS, THE MAINTENANCE CREW UNCOVERED THE LEAKING SECTION OF PIPE. FIVE PINHOLES WERE DISCOVERED WITHIN A 40 FOOT SECTION OF THE PIPE. THE CAUSE OF THE LEAK WAS DETERMINED TO BE EXTERNAL CORROSION, WHICH WAS CAUSED BY INTERFERENCE WITH FOREIGN PIPING AT THIS LOCATION. THE PIPELINE WAS REPAIRED AND RETURNED TO SERVICE. A CATHODIC PROTECTION INVESTIGATION WAS CONDUCTED IMMEDIATELY AND CORRECTIVE MEASURES HAVE BEEN TAKEN TO CORRECT ANY AREAS OF CONCERN.A TOTAL OF 125 BBLS. OF #2 FUEL OIL WAS SPILLED WITH APPROXIMATELY 30 BBLS. RECOVERED. WPL ENVIRONMENT PERSONNEL ARE CURRENTLY WORKING WITH THE OKLAHOMACORPORATION COMMISSION TO COMPLETE ENVIRONMENTAL REMEDIATION OF THE SPILL SIT
2017-09-29 08:50 | YES | NO | 19950124 | 1995-08-01 | 18273 | SHELL PIPELINE CORP | YES | 1995-06-24 | 855 | MS | LINCOLN |  | NO |  | NO | PEETSVILLE STATION - CAPLINE SYSTEM |  | PUMPING STATION | GIRTH |  | 1973 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 145000 | 106486.4865 | 214826.2548 | CRUDE OIL | 1 | 300 | 295 | NO | NO | 24 | 0.5 | 52000 | WELDED |  | 560 | 329 | YES | 24 | 1100 | 0 | 76 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | E.V. HENRY | 7132410132 | A HOLE WAS FOUND IN THE CIRCUMFERENTIAL WELD ON THE 24-INCH KICKER LINE.
2017-09-29 08:50 | NO | NO | 19950125 | 1995-08-01 | 15674 | PLANTATION PIPE LINE CO | YES | 1995-06-28 | 1400 | LA | EAST BATON ROUGE | BATON ROUGE | NO |  | NO | TANK 53 FILL LINE AT PLANTATION'S BATON ROUGE TANK FARM LOCATED AT 2200 BLOUNT ROAD, BATON ROUGE, LA 70807. SEE DRAWING NO. A-DOT 61. |  | TANK FARM | PIPE |  | 1951 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 51000 | 37453.8677 | 75559.5793 | GASOLINE | 3 | 25 | 20 | NO | NO | 18 | 0.38 | 35000 | WELDED |  | 285 | 40 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY M. CROOK | 4043645916 | ON THE AFTERNOON OF 27 JULY, 1995, A PLANTATION EMPLOYEE OBSERVED STRESSED VEGETATION IN THE VICINITY OF SEVEN TANK FILL LINES WITHIN PLANTATION'S TANK FARM IN BATON ROUGE, LOUISIANA. THE AREA WAS EXCAVATED AND A RELEASE WAS CONFIRMED ON THE AFTERNOON OF JUNE 28. THE AREA WAS DIFFICULT TO EXCAVATE DUE TOTHE CLOSE PROXIMITY OF THE SEVEN TANK FILL LINES. A PINHOLE WAS LOCATED AT THE 6:00 POSITION IN THE 18-INCH FILL LINE TO TANK 53 ON JUNE 30 AND REPAIREDWITH A 5-FOOT LONG FULL ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19950126 | 1995-07-31 | 12626 | MOBIL PIPELINE CO - EMPIRE | NO | 1995-06-11 | 15 | TX | NAVARRO | CORSICANA | NO |  | NO | 1604 SOUTH 15TH STREET, CORSICANA, TEXAS - APPROXIMATELY 1 MILE NORTH OF DOWNTOWN CORSICANA AT THE MOBIL OIL CORP. TAMK FARM - TANK #2690 |  | TANK FARM | TANK |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | NOT GIVEN | 1 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | D.G. SCOTT | 2146585924 | AT APPROXIMATELY 0015 HOURS ON 11 JUNE, 1995, DURING A SEVERE LIGHTNING AND THUNDERSTORM, TANK #2690 WAS STRUCK BY LIGHTNING. OPERATING PERSONNEL ON SITE AT THE TIME IMMEDIATELY NOTIFIED THE CORSICANA FIRE DEPARTMENT WHO PROMPTLYRESPONDED. OTHER PERTINENT MOBIL PERSONNEL DISPATCHED TO THE AREA IMMEDIATELY FOLLOWING FIRE DEPARTMENT NOTIFICATION. NRC & TRRC OFFICE OF PIPELINE SAFETY NOTIFIED AT 0140 HOURS. CORSICANA FIRE DEPARTMENT EXTINGUISHED THE FIRE IN ITS ENTIRETY AT 0300 HOURS. NRC & TRRC NOTIFIED. TANK #2690 IS AN EXTERNAL FLOATING ROOF TANK. THERE WERE NO DEATHS OR INJURIES ASSOCIATED WITH THISPOST ACCIDENT REVIEW CONDUCTED 6/23/95 AT CORSICANA STATION WITH KEY MOBIL PERSONNEL IN ATTENDANCE PLUS THE CORSICANA FIRE CHIEF.
2017-09-29 08:50 | YES | NO | 19950127 | 1995-07-31 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-06-29 | 1410 | KS | DICKINSON |  | NO |  | NO | 4 MILES SOUTH OF HERINGTON, KANSAS, T16S/R4E/SECTION 35 |  | PUMPING STATION | PUMP |  | 1965 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L. P. G. | 2 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHNNY L. CAVITT | 9185993795 | DURING ROUTINE MAINTENANCE, WELDING SPARKS IGNITED VAPORS FROM A MECHANICAL PUMP SEAL RESULTING IN A ONE INCH FLAME. THE FIRE WAS IMMEDIATELY EXTINGUISHED AND WORK SUSPENDED UNTIL AN INCIDENT REVIEW WAS COMPLETED. THE FIRE BURNED FOR LESS THAN ONE MINUTE WITH A PRODUCT RELEASE OF NEGLIGIBLE AMOUNT.
2017-09-29 08:50 | NO | NO | 19950128 | 1995-07-28 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1995-06-16 | 810 | AZ | YUMA | YUMA | NO |  | NO | YUMA BOOSTER STATION LOCATED AT 6471 SOUTH COUNTY 7-E, YUMA, AZ 85365. LS-114, 1/2 MILE NORTH OF GILA RIVER. |  | PUMPING STATION | PUMP |  | 1989 | OTHER | SEAL FALURES ON BSTER PMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | GASOLINE | 3 | 9 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | UNIT #1 PUMP IN BOARD SEAL FAILED. PRODUCT OVERFLOWED FROM SEAL BOX ONTO SURROUNDING SLAB AND GROUND. RELEASE DETECTED BY MAINTENANCE PERSONNEL. SEAL FAILURE SWITCH INOPERABLE DUE TO OBSTRUCTION IN INSTRUMENT PIPING.9 BBLS. LISTED AS SPILLED. REPORT CLAIMS 400-500 GALLONS (APPROXIMATELY 9 BBLS.)
2017-09-29 08:50 | YES | NO | 19950129 | 1995-08-02 | 19536 | TOTAL PIPELINE CORP | YES | 1995-06-29 | 1030 | OK | COTTON | TEMPLE | NO |  | NO | NW 1/4 SECTRION 17 TOWNSHIP 4 SOUTH - RANGE 10W COTTON COUNTY, OKLAHOMA (SEE ATTACHED MAP) |  | LINE PIPE | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 11000 | 8078.2852 | 16297.1642 | CRUDE OIL | 1 | 120 | 110 | NO | NO | 8 | 0.32 | 0 | COUPLED |  | 596 | 375 | YES | 8 | 745 | 4 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MICHAEL COOPER | 4052291638 | APPROXIMATELY 1030 HOURS ON 6/29/1995 A CALL WAS RECEIVED FROM THE COTTON COUNTY ROAD COMMISSIONERS OFFICE STATING THAT ONE OF THEIR ROAD MAINTENANCE CREWS HAD HIT A TOTAL PIPELINE WHILE CLEANING OUT A BARDITCH WITH A ROAD GRADER IN THE NW/4 OF SECTION 17 - TOWNSHIP 4 SOUTH - RANGE 10 WEST - COTTON COUNTY,OKLAHOMA, AND THAT CRUDE OIL WAS SPRAYING OUT OF THE PIPELINE.TOTAL'S 24-HOUR CONTROL CENTER WAS NOTIFIED IMMEDIATELY AND THE PIPELINE WASSHUT DOWN WITHIN MINUTES OF THE INCIDENT. TOTAL'S EMERGENCY RESPONSE TEAM FROM BOTH HEALDTON, OK, & BURKBURNETT, TX, WERE IMMEDIATELY DISPATCHED TO THE SITE TO INITIATE REPAIR AND CLEANUP PROCEDURES.ONCE EMERGENCY RESPONDERS WERE ON SITE, A SITE SAFETY EVALUATION WAS PERFORMED AND PROPER REPAIR PROCEDURES WERE INSTITUTED UTILIZING THE PROPER PERSONNEL PROTECTIVE EQUIPMENT.THE PIPELINE WAS EXCAVATED AND FOUND TO BE APPROXIMATELY 12" DEEP BELOW THE BOTTOM OF THE BARDITCH AND THAT THE ROAD GRADER HAD CUT A 1/2"X3" GASH IN THETHE PIPELINE WAS REPAIRED TEMPORARILY BY INSTALLING A WELDED HALFSOLE PATCH OVER THE AFFECTED AREA. THE PIPELINE IS TO BE PERMANENTLY REPAIRED BY REPLACING THE ENTIRE ROADWAY CROSSING WITH NEW PIPE.THE OIL WAS RECOVERED FROM THE BARDITCH AND THE DRY GULLY WITH VACUUM TRUCKS, APPROXIMATELY 100 YARDS OF OIL STAINED SOIL WAS REMOVED AND HAULED TO AN APPROVED SOIL FARM, ALL STAINED GRASS AND VEGETATION WAS CUT AND REMOVED AND DISPOSED OF.
2017-09-29 08:50 | YES | NO | 19950130 | 1995-08-09 | 25172 | UNOCAL NORTH AMERICAN OIL & GAS DIV | NO | 1995-07-18 | 1730 | CA | KERN | LOST HILLS | NO |  | NO | JUNCTION PUMP STATION ON THE SOUTH SIDE OF HIGHWAY 46, SEVEN MILES WEST OF HIGHWAY 33, SEC. 19 & 20, T26S, R19E, KERN COUNTY, CALIFORNIA |  | PUMPING STATION | SCRAPER TRAP |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OIL AND GASOLINE | 3 | 220 | 210 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDMOND C. LEE | 8053993546 | ON JULY 18, 1995 AT APPROXIMATELY 5:30 PM, PACIFIC TIME, A PM STATION OPERATOR AT THE JUNCTION PUMP STATION PREFORMED HIS ROUTINE HOURLY CHECK OF THE FACILITIES AND FOUND GAS OIL ON THE GROUND, ALONG THE EAST-WEST CONTAINMENT DIKEWALL AND IN THE GENERAL VICINITY OF THE MAINLINE PUMP HOUSE. IMMEDIATELY, THE OPERATOR CALLED THE CONTROL CENTER IN THE SANTA FE SPRINGS TO SHUT DOWN ALLINCOMING AND OUTGOING PIPELINES AND TERMINATED ALL ACTIVITIES WITHIN THE STATION. THE INCIDENT WAS REPORTED TO PIPELINE PERSONNEL WHO WAS ON CALL AND EMERGENCY RESPONSE EQUIPMENT AND PERSONNEL WERE DISPATCHED TO THE SITE. UPON PRELIMINARY INVESTIGATION, WE FOUND THE OPERATOR MISTAKENLY LEFT THE DRAIN VALVEFOR THE PIG RECEIVING TRAPPER OPEN. THIS ALLOWED THE GAS OIL TO "SLIP STREAM" INTO TANKAGE AND DRAIN AT THE SAME TIME. THE DRAIN WAS HARD PIPED TO SUMP, WHICH IS LOCATED OUTSIDE OF THE MAINLINE PUMP HOUSE. AS THE SUMP BEGAN TO FILL, THE GAS OIL TRAVELED UP THE DRAIN LINE TO THE PUMP HOUSE, PUTTING APPROXIMATELY 220 BBLS INTO THE PIPE TRENCH, WHICH IS BELOW THE FLOOR GRATING. THIS PREVENTED THE SUMP FROM OVERFLOWING AND ALLOWED THE GAS OIL TO BE CONTAINED WITHIN THE PUMP HOUSE. APPROXIMATELY 10-15 BBLS WERE SPILLED ON THE GROUND.
2017-09-29 08:50 | YES | NO | 19950131 | 1995-08-14 | 10012 | KANEB PIPELINE CO | YES | 1995-07-12 | 915 | KS | BUTLER |  | NO |  | NO | NW 1/4, SECTION 32, TOWNSHIP 25 SOUTH, RANGE 5 EAST. |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | FUEL OIL | 3 | 737 | 89 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | L.LEROY ANDERSON | 3162621408 | PIPELINE FAILED DURING NORMAL PIPELINE OPERATIONS. EXCAVATION REVEALED EXTERNAL DAMAGE THAT MOST LIKELY OCCURRED DURING THE ORIGINAL OF THE CONSTRUCTION OF THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19950132 | 1995-08-14 | 11237 | T E PRODUCTS PIPELINE COMPANY, L P | YES | 1995-07-13 | 730 | IL | SALINE |  | NO |  | NO | APPROXIMATELY 7.5 MILES NORTHWEST OF HARRISBURG, ILLINOIS NEAR THE INTERSECTION OF HARCO ROAD AND STATE ROAD 13. |  | LINE PIPE | PIPE |  | 1944 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 92000 | 67563.8397 | 136303.5548 | NATURAL GAS LIQUID | 2 | 3 | 0 | NO | NO | 20 | 0.31 | 35000 | WELDED |  | 690 | 480 | YES | 24 | 1080 | 0 | 57 | NO DATA | Null | Null | NO DATA |  | OTHER | UNABLE TO DETERMINE | Null | ONE CALL |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON JULY 13, 1995, TEPPCO DETERMINED AN INCIDENT OCCURRING THIS DATE WOULD EXCEED $50,000. THIS INCIDENT INVOLVED OUR 20" PIPELINE IN SALINE COUNTY, ILLINOIS. APPROXIMATELY 3 BARRELS OF PRODUCT WERE UNINTENTINALLY RELEASED. THE RELEASE WAS DUE TO A HAIRLINE CRACK IN AN AREA THAT HAD BEEN GOUGED BY EARTH MOVING EQUIPMENT. TEPPCO HAS NOT BEEN ABLE TO DETERMINE WHEN THE GOUGE HAD OCCURRED. THE PIPE WAS REPAIRED AND PLACED BACK INTO SERVICE ON JULY 14, 1995.
2017-09-29 08:50 | YES | NO | 19950133 | 1995-08-14 | 30661 | NORCO PIPELINE CO., INC. | YES | 1995-07-17 | 925 | IL | MARSHALL | LACON TWP | NO |  | NO | EAST BANK OF ILLINOIS RIVER - 5 1/2 MILES SOUTH OF LACON, IL WEST OF HIGHWAY #26 |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 73438.9562 | 148156.0378 | GASOLINE | 3 | 549 | 149 | NO | NO | 8 | 0.32 | 0 | WELDED |  | 740 | 40 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | SNAGGED BY DRAGLINE | Null | ONE CALL |  | NO | NO | RICK HOOD | 5014443507 | CONTRACTOR WORKING FOR STATE OF ILLINOIS, DEPARTMENT OF CONSERVATION, WASREPAIRING A LEVEE WITH DRAGLINE. CONTRACTOR FAILED TO UTILIZE ONE CALL SYSTEMAND FAILED TO OBSERVE PIPELINE MARKERS ACROSS PROPERTY. DRAGLINE REMOVED COVEROVER PIPELINE AND PUNCTURED PIPELINE WITH DRAGLINE BUCKET.
2017-09-29 08:50 | YES | NO | 19950134 | 1995-08-08 | 19226 | TEXACO PIPELINE INC | YES | 1995-07-27 | 702 | LA | TERREBONNE | HOUMA | NO |  | NO | TEXACO PIPELINE INC. - HOUMA STATION - 1617 COTEAU RD - HOUMA, LOUISIANA LA HWY 660 |  | PUMPING STATION | BOLTED FITTING |  | 1980 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 55079.2171 | 111117.0284 | CRUDE OIL | 1 | 1300 | 1300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | E.M. ROMERO | 5048765645 | THE LEAK OCCURRED IN HOUMA STATION DISCHARGE PIPING. IT WAS CAUSED BY A BREAKIN A FLANGE GASKET LOCATED ON THE DISCHARGE SIDE OF A MAIN PUMPING UNIT. ALLOF THE OIL WAS CONTAINED WITHIN HOUMA STATION'S SECONDARY CONTAINMENT SYSTEM. IT WAS RECOVERED AND PUT BACK INTO TANKAGE AT HOUMA STATION. NO OIL ESCAPEDFROM THIS SITE.
2017-09-29 08:50 | YES | YES | 19950135 | 1995-08-15 | 4493 | ENTERPRISE PRODUCTS CO | YES | 1995-08-12 | 340 | TX | LIBERTY |  | NO |  | NO | APPROXIMATELY 6 MILES NORTH OF INTERSTATE 10 ALONG FM 563 |  | LINE PIPE | OTHER | (1) 2" VENT VALVE | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 4 | 0 | 4 | 500000 | 367194.781 | 740780.1891 | L. P. G. | 2 | 1300 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | RON LABUS | 7133854241 | BASED UPON INFORMATION FROM THE TEXAS DEPARTMENT OF PUBLIC SAFETY, AN AUTOMOBILE TRAVELING IN EXCESS OF 85 MPH LOST CONTROL: THE DRIVER SKIDDED OFF FM 563, PENETRATED A CYCLONE PERIMETER FENCE ALONG PRIVATELY OWNED PROPERTY, PROCEEDED TO SKID ANOTHER 45 FEET ENTERING THE PIPELINE CORRIDER, AND THEN THROUGHTHE CYCLONE SECURITY FENCE AROUND ENTERPRISE'S VALVE STATION #3. THE VEHICLECAME TO REST UPON THE ABOVE-GROUND MAINLINE VALVE STATION. PRELIMINARY REVIEW INDICATES THE VEHICLE IMPACT SHEARED-OFF A 2" VENT VALVE AND TWO 3/4" INSTRUMENT VALVES FROM THE 4" MAINLINE VALVE STATION.
2017-09-29 08:50 | YES | NO | 19950136 | 1995-08-17 | 300 | ALL AMERICAN PIPELINE CO | YES | 1995-08-03 | 350 | NM | HIDALGO | LORDSBURG | NO |  | NO | APPROXIMATELY 9 MILES EAST OF LORDSBURG NEW MEXICO AND 2 MILES NORTH OF INTERSTATE 10 (MILE MARKER 33). |  | PUMPING STATION | OTHER | CRUDE OIL DIRECT FIRED | 1986 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | PROGRAMMABLE LOGIC MALFUN | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 367194.781 | 740780.1891 | CRUDE OIL | 1 | 108 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JORDAN JANAK | 8053985345 | A PROGRAMMABLE LOGIC CONTROLLER (PLC) WHICH CONTROLS THE OPERATION OF THE CRUDE OIL HEATER APPARENTLY MALFUNCTIONED CAUSING AN UNCOMMANDED START UP OF THE ISOLATED HEATER. EXCESSIVE HEAT CAUSED A TUBE FAILURE (S) WHICH RESULTED INA FIRE. REMEDIAL ACTION TO DATE: THE GAS SUPPLY VALVES TO ALL HEATERS, NOT IN SERVICE, HAVE BEEN CLOSED. THE ALL AMERICAN PIPELINE SYSTEM WAS SHUTDOWN DIMMEDIATELY AFTER THE FIRE WAS DISCOVERED. BECAUSE THE HEATER PIPING WAS ISOLATED AND THE FIRE IN THE HEATER WAS LOCATED A SUFFICIENT DISTANCE FROM ABOVEGROUND PIPING, THIS INCIDENT DID NOT AFFECT THE ALL AMERICAN MAINLINE. PIPELINESYSTEM OPERATIONS RECOMMENCED AT 15:35 (PDT). AN INVESTIGATION TO DETERMINE THE CAUSE OF THE PLC MALFUNCTION IS BEING CONDUCTED.
2017-09-29 08:50 | YES | NO | 19950137 | 1995-08-11 | 15851 | PRIDE REFINING INC | NO | 1995-07-05 | 1400 | TX | GRAY |  | NO |  | NO | THE LEAK OCCURRED ON THE KADE MATTHEWS RANCH |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | CRUDE OIL | 1 | 300 | 0 | NO | NO | 6 | 0.28 | 25000 | WELDED |  | 770 | 0 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON | 9156748231 | A LEAK WAS REPORTED ON 07/05/95 BY PRIDE'S PIPELINE PATROL PLANE. CREWS WEREDISPATCHED TO THE AREA FOR SPILL CONTAINMENT AND TO CLAMP THE LINE. A SECTION OF THE 6" PIPELINE WAS REPLACED WITH NEW PIPE. SATURATED SOIL WAS REMOVED FROM THE AREA TO PRIDE'S ALANREED STATION AND IS NOW AWAITING DISPOSAL. SOIL SAMPLES ARE BEING TAKEN OF THE REMAINING ARE TO DETERMINE FINAL CLEAN TO RULE 91.
2017-09-29 08:50 | YES | NO | 19950138 | 1995-08-11 | 3527 | DOW PIPELINE CO | NO | 1995-07-14 | 1608 | TX | CHAMBERS |  | NO |  | NO | 0.4 MILES WEST OF SH-146 ON WINFREE ROAD IN MONT BELVIEU, TEXAS LOCATED APPROXIMATELY 1.65 MILES NORTH OF I-10. |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 28900 | 21223.8583 | 42817.0949 | L. P. G. | 2 | 2364 | 25 | NO | NO | 8 | 0.38 | 52000 | WELDED |  | 2160 | 1850 | YES | 24 | 4099 | 4 | 71 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D. BRIAN LACY | 7134719440 | THE LEAK OCCURRED INSIDE A CASING. THE CASING WAS ACROSS A SMALL OIL FIELD ROAD. GENERALIZED CORROSION WAS FOUND ON THE BOTTOM QUARTER OF THE LINE PIPE AT THE SOUTH END OF THE CASING. THE CORRODED AREA WAS ABOUT 7"X11". A PIT HAD DEVELOPED IN THIS AREA AND CORRODED THROUGH THE PIPE. THE LINE WAS BREACHED BY A 3/32" HOLE. THE AREA WAS QUICKLY SECURED THE LINE CLEARED AND REPAIRS MADE. THE PIPELINE WAS RETURNED TO SERVICE.
2017-09-29 08:50 | NO | NO | 19950139 | 1995-08-23 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-07-24 | 930 | NE | GAGE |  | NO |  | NO | TOWNSHIP 3 NORTH RANGE 6 EAST SECTION 122 MILES SE OF THE TOWN OF BEATRICE, 1 MILE S. OF BEATRICE, TURN LEFT ON GRAVEL RD FOR 3-1/8 MILES, ON NORTH SIDE OF RD. |  | LINE PIPE | VALVE |  | 1968 | OTHER | VALVE STEM PACKING FAILUR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHNNY CAVITT | 9185993795 | VAVLE STEM PACKING FAILED, RESULTING IN A RELEASE.
2017-09-29 08:50 | YES | NO | 19950140 | 1995-08-25 | 22610 | WILLIAMS PIPELINE CO | YES | 1995-07-03 | 1705 | OK | PAYNE |  | NO | NA | NO | SOUTHEAST 1/4 OF THE SOUTHWEST 1/4 OF SECTION 7, TOWNSHIP 17W, RANGE 6E |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9500 | 6976.7008 | 14074.8236 | CRUDE OIL | 1 | 50 | 12 | NO | NO | 12.75 | 0.3 | 35000 | WELDED |  | 750 | 70 | YES | 8 | 960 |  | 95 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL, SENIOR VICE PRES. & GENERAL MANAGER | 9185883850 | AT APPROXIMATELY 15:45 HOURS ON JULY 3, 1995, THE WPL PATROL PILOT REPORTED APOSSIBLE SPILL AT M.P. 60.42 ON THE CUSHING-TULSA JUNCTION LINE SECTION. THETULSA MAINTENANCE CREW WAS IMMEDIATELY DISPATCHED TO THE SPILL SITE WHERE THELEAK WAS CONFIRMED AT 17:05 HOURS. AT APPROXIMATELY 20:30 HOURS, THE LEAKWAS CLAMPED OFF AND REPAIRED WITH A PATCH.THE PINHOLE SIZE LEAK WAS THE RESULT OF LOCALIZED EXTERNAL CORROSION CAUSEDBY A SUSPECTED INTERFERENCE PROBLEM. THE INTERFERENCE PROBLEM WAS SUSPECTEDSINCE THE PIT WAS ON THE SIDE OF THE PIPE FACING A PARALLEL FOREIGN PIPELINEIN THE SAME RIGHT-OF-WAY. BEFORE THE END OF THE YEAR, THE CORROSION DEPARTMENT HAS SCHEDULED THE INSTALLATION OF NEW GROUND BEDS IN THE SPILL AREA AND THE PERFORMANCE OF A CLOSE INTERVAL SURVEY.THE SPILL RESULTED IN A LEAK OF APPROXIMATELY 50 BARRELS OF CRUDE OIL OF WHICH 12 BARRELS WERE RECOVERED. WPL ENVIRONMENTAL PERSONNEL HAVE BEEN COORDINATING THE CLEAN-UP WITH THE OKLAHOMA CORPORATION COMMISSION, WHICH WILL CONSISTOF INSITU LANDFARMING BY THE TILLING OF HAY IN THE LEAK SITE AREA.
2017-09-29 08:50 | YES | NO | 19950141 | 1995-08-25 | 10012 | KANEB PIPELINE CO | YES | 1995-07-19 | 1205 | NE | FILLMORE |  | NO |  | NO | NE 1/4, SECTION 25, TOWNSHIP 7 NORTH, RANGE 3 WEST |  | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | GASOLINE | 3 | 602 | 157 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | L. LEROY ANDERSON, MANAGER OF REGULATORY AFFAIRS | 3162621408 | AN IRRIGATION WELL DRILLING CONTRACTOR WAS EXCAVATING A DRILLING MUD PIT WITHA FRONT END LOADER WHEN HE HIT AND RUPTURED THE PIPELINE IN THE PROCESS.
2017-09-29 08:50 | YES | NO | 19950142 | 1995-08-25 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1995-07-27 | 1135 | AR | GARLAND |  | NO |  | NO | MOBIL PIPE LINE COMPANY'S #1-20" CRUDE OIL PIPELINE SYSTEM, MILE POST 263.1. APPROXIMATELY 1.5 MILES NORTHEAST OF MT. PINES, ARKANSAS |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 110158.4343 | 222234.0567 | CRUDE OIL | 1 | 600 | 580 | NO | NO | 20 | 0.31 | 42000 | WELDED |  | 899 | 540 | YES | 8 | 1124 | 8 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D. G. SCOTT, MANAGER, MAINLINE CRUDE & NGL OPERATIONS | 2146585914 | MOBILE PIPELINE ROAD CROSSING SIGN AT ACCIDENT LOCATION.GARLAND COUNTY, STATE OF ARKANSAS, MAINTENANCE CREW WAS DOING ROUTINE ROADWORK AND CLEANING OUT DITCHES APPROXIMATELY 1.5 MILES NORTHEAST OF MT. PINES,ARKANSAS WHEN THEIR ROAD GRADER OPERATOR HIT MOBIL PIPE LINE COMPANY'S #1-20"CRUDE OIL PIPELINE AT MILE POST 263.1. THE BLADE OF THE ROAD GRADER CUT A 2"GASH IN THE STEEL PIPELINE CAUSING CRUDE OIL TO ESCAPE. THE ROAD GRADER OPERATOR IMMEDIATELY WENT DOWNSTREAM OF THE PIPELINE AND CONSTRUCTED A BERM TOCONTAIN THE OIL. MOBIL PIPE LINE COMPANY OPERATIONS CONTROL PERSONNEL INDALLAS WERE NOTIFIED BY THE GARLAND COUNTY MAINTENANCE DEPARTMENT OF THEACCIDENT AND PIPELINE SHUTDOWN PROCEDURES WERE IMPLEMENTED.MOBIL PIPE LINE COMPANY HAD A PIPELINE ROAD CROSSING SIGN DIRECTLY ADJACENTTO THE ACCIDENT SITE.MOBIL'S LONGVIEW, TEXAS MAINTENANCE CREW WAS NOTIFIED BY DALLAS AND DISPATCHED TO SCENE. RECOVERY AND CLEAN-UP PROCEDURES INITIATED. PERMANENT REPAIRSWERE MADE BY REPLACING APPROX. 44' OF TESTED 20" PIPE.ALL FEDERAL AND STATE AGENCIES WERE NOTIFIED WITHIN 2 HOURS OF ACCIDENT. THEARKANSAS ONE-CALL SYSTEM WAS NOT NOTIFIED BY GARLAND COUNTY MAINTENANCE DEPARTMENT, THUS MOBIL NEVER RECEIVED ANY ONE-CALL NOTIFICATION.
2017-09-29 08:50 | YES | NO | 19950143 | 1995-08-29 | 2387 | CITGO PIPELINE CO | YES | 1995-07-27 | 1145 | OK | CARTER |  | NO |  | NO | APPROXIMATELY 22 MILES NORTHWEST OF ARDMORE, OKLAHOMA |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 62423.1128 | 125932.6321 | GASOLINE | 3 | 400 | 80 | NO | NO | 12.75 | 0.38 | 35000 | COUPLED |  | 440 | 250 | YES | 8 | 550 |  | 91 | INTERNAL | Null | YES | NO DATA |  | OTHER | BELOW GROUND | Null | NO DATA |  | Null | YES | JIM SANDERS, MANAGER SAFETY AND ENVIRONMENTAL | 9184954786 | THE LEAK WAS CAUSED BY INTERNAL CORROSION. IT WAS DISCOVERED BY A THIRDPARTY WHO NOTICED A STRONG ODOR IN THE AIR AND CALLED THE EMERGENCYTELEPHONE NUMBER ON CITGO'S PIPELINE MARKER.
2017-09-29 08:50 | YES | NO | 19950144 | 1995-08-30 | 4805 | EXPLORER PIPELINE CO | YES | 1995-07-17 | 1600 | LA | CALCASIEU |  | NO |  | NO | 8 MILES WEST OF GUM COVE FERRY ROAD (HWY381) AND 2 1/2 MILES EAST OF SABINE RIVER (SEE ATTACHED MAPS) |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 110158.4343 | 222234.0567 | FUEL OIL | 3 | 17 | 17 | NO | NO | 12 | 0.22 | 52000 | WELDED |  | 1286 | 560 | YES | 24 | 1620 | 2 | 71 | EXTERNAL | Null | YES | OTHER | MICROBIOLOGICALLY INDUCED | NO DATA |  | Null | NO DATA |  | Null | Null | R. W. FLEMING, MANAGER - FIELD OPERATIONS | 9184935100 | THIS ACCIDENT REPORT IS BEING FILED AS A RESULT OF ADDITIONAL INFORMATIONAVAILABLE RELATING TO AN ACCIDENT THAT OCCURRED ON 7/17/95. IT HAS BEENDETERMINED THAT REPAIR COSTS WILL NOW EXCEED $50,000 AS A RESULT OFUNANTICIPATED SOIL REMOVAL/DISPOSAL COSTS FROM THE REMOTE ACCIDENT SITE.TELEPHONIC NOTIFICATION WAS MADE AT THE TIME OF DISCOVERY OF THE ACCIDENT BUTNONE OF THE CONDITIONS LISTED IN PARAGRAPH 195.50 REQUIRING WRITTEN NOTICEEXISTED OR WERE ANTICIPATED. THE FOLLOWING IS AN ACCOUNT OF THE ACCIDENT:AT APPROXIMATELY 1600 HRS ON 7/17/95 EXPLORER'S AIR PATROL PILOT REPORTED ANAREA OF DEAD GRASS ON THE PIPELINE ROW NEAR MP 22.7 ON THE LAKE CHARLES,LOUISIANA TO PT ARTHUR, TEXAS 12" PIPELINE. THE SYSTEM WAS SHUT DOWN ANDISOLATED. RESPONSE CREWS WERE IMMEDIATELY DISPATCHED TO THE SITE. ATAPPROXIMATELY 1730 HRS EXPLORER PERSONNEL ARRIVED AND LOCATED A SMALL AMOUNTOF DARK FUEL OIL IN A PASTURE FLOATING ON WATER CONTAINED IN A 12 FT. DIAMETER MUD PUDDLE ON A PIPELINE/POWER TRANSMISSION LINE CORRIDOR. THE NATIONAL RESPONSE CENTER AND LOUISIANA STATE AGENCIES WERE NOTIFIED. BECAUSE OF THE REMOTE LOCATION AND LACK OF ROADS, REPAIR EQUIPMENT HAD TO BE BARGED ON THE INTRACOASTAL WATERWAY TO THE VICINITY OF THE REPAIR SITE. REPAIR/CLEANUP CREWS AND EQUIPMENT WERE MOVED IN AND BEGAN CLEANUP AND EXCAVATION OPERATIONS AT 1200 HRS ON 7/18/95. APPROXIMATELY ONE BARREL OF FUEL OIL WAS RECOVERED FROM THE SURFACE OF THE MUD PUDDLE WITH SORBENT PADS. A PINHOLE LEAK WAS DISCOVEREDAND TEMPORARY REPAIRS WERE MADE BY INSTALLING A PLIDCO SPLIT SLEEVE. THE PIPELINE WAS RETURNED TO NORMAL OPERATIONS AT 1615 HRS ON 7/19/95. PERMANENT REPAIRS WERE COMPLETED ON 8/1/95 BY WELDING THREE FULL ENCIRCLEMENT SLEEVES OVER LOCALIZED CORROSION PITS. FOLLOWING SAMPLING AND TESTING OF THE CONTAMINATED SOIL, IT WAS DETERMINED THAT THE CONTAMINATED SOIL HAD TO BE REMOVED AND BARGED/TRUCKED TO A LICENSED INDUSTRIAL LAND FILL SITE. CLEAN FILL DIRT WAS BARGED INTO THE SITE TO REPLACE THE REMOVED SOIL.
2017-09-29 08:50 | YES | NO | 19950145 | 1995-08-30 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1995-08-02 | 1430 | NM | LEA |  | NO |  | NO | MOBIL PIPE LINE COMPANY'S CROSSROADS TO SEMINOLE 8" LOOP LINE. APPROXIMATELY 15 MILES EAST OF LOVINGTON, NM |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 1835.9739 | 3703.9009 | CRUDE OIL | 1 | 75 | 0 | NO | NO | 8 | 0.19 | 42000 | WELDED |  | 800 | 99 | YES | 20 | 1640 | 1 | 68 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT, MGR., MAINLINE CRUDE & NGL PIPELINE OPERATIONS | 2146585914 | MPLCO.'S CROSSROAD TO SEMINOLE 8" LOOP LINE BETWEEN MILE POSTS 22.15 AND 30.93 WAS INACTIVE AND ISOLATED. COMPANY PERSONNEL WERE IN THE PROCESS OF DISPLACING THE LINE WITH NITROGEN WHEN LEAK OCCURRED. ALL ESCAPED OIL WAS CONTAINED AND CLEAN UP & REPAIR PROCEDURES WERE IMMEDIATELY INITIATED. THE STATE OFNEW MEXICO OIL CONSERVATION COMMISSION AND THE NATIONAL RESPONSE CENTER WERENOTIFIED.NO CRUDE OIL REACHED ANY CREEKS, STREAMS, PONDS, OR LAKES.
2017-09-29 08:50 | YES | NO | 19950146 | 1995-08-31 | 7614 | HOWELL CORP | NO | 1995-07-30 | 1900 | MS | JEFFERSON DAVIS |  | NO |  | NO | GWINVILLE JCT TO GWINVILLE STATION 8" LINE, R-18W T-9N 9MILES N. OF PRENTICE, MS OFF OF WILLIAMSON MILL RD IN OPEN FIELD. |  | LINE PIPE | PIPE |  | 1970 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 29375.5825 | 59262.4151 | CRUDE OIL | 1 | 100 | 91 | NO | NO | 8 | 0.2 | 52000 | WELDED |  | 727 | 30 | YES | 24 | 2160 | 5 | 70 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDDIE STUTTS | 6017292430 | EXXON CONTROL CENTER AT HOUSTON NOTIFIED EDDIE STUTTS WITH HOWELL AT 7:00 PM07/30/95 OF REPORTED LEAK. MAINLINE PUMPS WERE SHUT DOWN. STUTTS CONTACTED LANDOWNER AND VERIFED LEAK & OIL ON POND. STUTTS CONTACTED LOCAL COMPANY PERSONNEL TO RESPOND ALONG WITH LOCAL CONTRACTOR. ALSO NOTIFIED HOWELL PERSONNEL IN HOUSTON. CHECKED LEAK SITE & CLOSED MAINLINE BLOCK VALVES. EXCAVATE LEAK SITE AND FOUND HOLE IN BOTTOME OF 8" PIPE-APPEARED TO BE INTERNAL CORROSION. REPAIRED PIPE WITH 8" PLIDCO SPLIT SLEEVE CLAMP AND PUT LINE BACK INTO SERVICE.CONTRACTOR CONTINUED WITH CLEANUP. CONTACTED GANER ENVIRONMENTAL SERVICES ON07/31/95 TO RESPOND AND ASSIST WITH CLEANUP. SITE WORK COMPLETED ON 08/01/95.
2017-09-29 08:50 | YES | NO | 19950147 | 1995-09-06 | 22610 | WILLIAMS PIPELINE CO | YES | 1995-08-05 | 430 | OK | OSAGE |  | NO |  | NO | LOCATED WITHIN THE FENCE BOUNDARY OF THE BARNSDALL PUMP STATION IN SECTION 32 OF TOWNSHIP 25N AND RANGE 11E IN OSAGE COUNTY, OKLAHOMA. |  | LINE PIPE | WELDING FITTING |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18359.739 | 37039.0095 | Q-GRADE | 1 | 75 | 75 | NO | NO | 8.63 | 0.2 | 35000 | WELDED |  | 900 | 820 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | STEVEN S. BALL | 9185883850 | AT APPROXIMATELY 0300 HOURS ON AUGUST 5, 1995, WILLIAMS PIPE LINE (WPL) PERSONNEL ARRIVED AT THE BARNSDALL PUMP STATION TO INVESTIGATE A PROBLEM WITH ONEOF THE PUMP UNITS. AT 0506 HOURS, WPL PERSONNEL NOTICED A STRONG PETROLEUM ORDER AND DISCOVERED THAT A LEAK HAD OCCURRED ON THE #1-8" LINE. THEY IMMEDIATELY SHUT DOWN THE PUMP UNIT AND CONTACTED OPERATIONS CONTROL. AT APPROXIMATELY 0535 HOURS, THE WPL PERSONNEL CLOSED THE NEAREST MAINLINE GATE VALVE, THUS ISOLATING THE LEAK BETWEEN THE MAINLINE GATE VALVE AND PUMP STATION. AT 0620 HURS,AFTER LOCATING THE LEAK SITE, WPL PERSONNEL ON SITE CONTACTED THE TULSA MAINTENANCE CREW AND VARIOUS CONTRACTORS FOR VACUUM TRUCKS AND EXCAVATING EQUIPMENT. AT 0637 HOURS, WPL PERSONNEL WENT TO INVESTIGATE THE EXTENT OF THE SPILL IN ORDER TO BE PREPARED FOR THE ARRIVAL OF THE RESPONSE CREWS. AT APPROXIMATELY 0800 HOURS, THE TULSA MAINTANCE CREW ARRIVED TO BEGIN REPAIR OF THE LINE. BY 0930 HOURS, AND UNDERFLOW DAMN HAD BEEN CONSTRUCTED IN THE ROAD DITCH OUTSIDE THE PUMP STATION PROPERTY PREVENTING THE PRODUCT FROM FLOWING INTO NEARBY BIRD CREEK. VACUUM TRUCKS WERE UTILIZED TO PICK UP THE SPILLED PRODUCT WHICH WAS DETERMINED BY OPERATION CONTROL TO BE 75 BARRELS. THE LEAK WAS THE RESULT OF A MECHANICAL FAILURE OF A 3/4" NIPPLE THAT HAD BEEN WELDED ON THE LINE FOR A SAMPLE CONNECTION. THE SAMPLE CONNECTION VALVE HAD BEEN CLOSED, PLUGGED, BURIED AND ABANDONED MANY YEARS AGO. THE SAMPLE TAP WAS CUT OUT OF THE LINE AND REPLACED WITH A FLANGED CONNECTION BY 1830 HOURS. REMEDIATITON OF THESPILL CONSISTED OF VACUUM TRUCKS REMOVING THE PRODUCT FROM THE SURFACE OF THE WATER IN THE ROAD DITCH AND INSITUBURNING OF THE PRODUCT. INSITU BURNING WAS APPROVED BY THE OKLAHOMA CORPORATION COMMISSION AT APPROXIMATELY 1315 HOURS.
2017-09-29 08:50 | YES | NO | 19950148 | 1995-09-06 | 2371 | CINIZA PIPELINE INC | NO | 1995-08-15 | 1200 | NM | RIO ARRIBA |  | NO |  | Null | ON PIPE LINE RIGHT-OF-WAY .5 MILE S. OF LYBROOK, NEW MEXICO. SEC. 15,T23N,R7W, IN RIO ARRIBA COUNTY, NEW MEXICO. |  | LINE PIPE | OTHER | NOT GIVEN | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7168 | 5264.1044 | 10619.8248 | CRUDE OIL | 1 | 200 | 2 | NO | NO | 4 | 0.16 | 1760 | WELDED |  | 650 | 500 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL | AIR PATROL | YES | YES | ROY ARMENTA | 5056328024 | DAMAGE TO 4" PIPE WAS CAUSED BY EQUIPMENT BACK FILLING NEW PIPE LINE BEING INSTALLED PARALLEL TO EXISTING LINE.
2017-09-29 08:50 | YES | NO | 19950149 | 1995-09-12 | 10012 | KANEB PIPELINE CO | YES | 1995-08-09 | 1500 | NE | NUCKOLLS |  | NO |  | NO | N 1/2, SE 1/4, SECTION 25, TOWNSHIP 1 NORTH, RANGE 7 WEST |  | TANK FARM | TANK |  | 1935 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | FUEL OIL | 3 | 900 | 45 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.LEROY ANDERSON | 3162621408 | OPERATOR PERSONNEL INCORRECTLY IDENTIFIED A VALVE AS BEING IN THE CLOSED POSITION AND SUBSEQUENT OPERATION PUMPED PRODUCT TO A TANK THAT HAD THE MANWAY REMOVED FOR CLEANING PURPOSES.
2017-09-29 08:50 | YES | NO | 19950150 | 1995-09-12 | 395 | AMOCO OIL CO | NO | 1995-08-23 | 725 | WY | JOHNSON |  | NO |  | NO | S9-T42N-R79W |  | LINE PIPE | PIPE |  | 1965 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 367.1948 | 740.7802 | CRUDE OIL | 1 | 160 | 152 | NO | NO | 10 | 0.28 | 52000 | WELDED |  | 1310 | 995 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. PETERSON | 3038305067 | THIS ACCIDENT OCCURED ON 08/23/95 AT ABOUT 7:25 A.M. LOCAL TIME. THE NRC REPORT NUMBER IS 304955. THIS ACCIDENT RESULTED FROM A SEAM FAILURE AT A PRESSURE WHICH PRODUCED A HOOP STRESS OF ABOUT 55% OF THE SPECIFIED MINIMUM YIELD STRENGTH. APPROXIMATELY 160 BARRELS WERE RELEASED WITH 152 BARRELS RECOVERED. THE RESPONSE CREW WAS AT THE SCENE PROMPTLY.
2017-09-29 08:50 | YES | NO | 19950151 | 1995-09-12 | 26041 | GATX TERMINALS CORP | NO | 1995-08-11 | 1600 | CA |  | CARSON | NO |  | NO | 900 BLOCK OF 233RD STREET - CARSON, CA - 1/2 MILE WEST OF WILMINGTON AVENUE |  | LINE PIPE | PIPE |  | 1975 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 118000 | 86657.9683 | 174824.1246 | JET FUEL | 3 | 5 | 3 | NO | NO | 10 | 0.25 | 2160 | WELDED |  | 1200 | 30 | YES | 8 | 1504 | 1 | 95 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID J. KINGSTON | 3105187705 | RECEIVED A CALL FROM A THIRD PARTY INFORMING GATX THAT THE GRASS APPEARED TOBE DEAD NEAR OUR PIPELINE MARKER. AFTER INVESTIGATING, THE SOIL APPEARED TO HAVE A PETROLEUM ODOR. EXCAVATIO OF THE AREA REVEALED A PIPELINE LEAK IN THE CASING UNDER THE ROAD. THE OLD PIPE WAS REMOVED AND APPROXIMATELY 130 FEET OFNEW PIPE WAS REPLACED THROUGH THE CASING.
2017-09-29 08:50 | YES | NO | 19950152 | 1995-09-11 | 13131 | CONOCO INC | YES | 1995-08-28 | 1630 | TX | HOPKINS | SULPHUR SPRINGS | NO |  | NO | 1.75 MILES SOUTH OF SULPHUR SPRINGS, TX AND 1/4 MILE WEST OF STATE HIGHWAY 154. |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 146877.9124 | 296312.0756 | DIESEL FUEL | 1 | 183 | 130 | NO | NO | 6.63 | 0.16 | 42000 | WELDED |  | 1450 | 789 | YES | 8 | 1813 | 3 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | CONTRACTOR EDUCATION | YES | YES | JAMES J. JONES | 3184974813 | THIRD PARTY PIPELINE COMPANY WAS LAYING LINE PARELLEL TO CONOCO PIPELINE CO.6 5/8 OD PIPELINE. CPL PIPELINE WAS WELL MARKED WITH YELLOW FLAGS AND COMMUNICATED TO CONSTRUCTION CREW. CPL PIPELINE WAS PROBED FOR DEPTH AND FLAGGED AT50 TO 100 FT. INTERVALS. THIRD PARTY WAS EXCAVATING BELL HOLE FOR TIE IN A PI WHEN BACKHOE DUG INTO CPL PIPELINE AND PUNCTURED PIPELINE WITH TOOTH ON BACKHOE BUCKET. THE BACKHOE WAS PARKED ACROSS THE CPL PIPELINE. PRODUCT WAS RELEASED INTO THE BELL HOLE AND ASSOCIATED DITCH FOR THE NEW PIPELINE. ALL PRODUCT WAS CONTAINED WITHIN THE DITCH AND BELL HOLE EXCEPT THE INITIAL SPRAY CREATED PRIOR TO CPL SHUT DOWN AND RESULTING PRESSURE DROP. SOIL CONTENT PRIMARILY PRIMARILY TIGHTLY COMPACTED MOTLED CLAY, ALLOWING VERY SMALL AMOUNT OF PRODUCT LOSS THRU SATURATION. SATURATED SOILS OCCURRED PRIMARILY IN THE AREA AFFECTED BY THE SPRAY PRIOR TO DEPRESSURIZATION. ONE-CALL SYSTEM WAS UTILIZED BY THIRD PARTY FOR DAMAGE PREVENTION, BUT MARKING WAS IGNORED. CPL REPRESENTATIVE CONTACTED CONSTRUCTION CREW THROUGH OUT THE DAY BUT WAS NOT PRESENT AT THE SITE WHEN CONTACT WITH THE PIPELINE WAS INITIATED. CPL REPRESENTATIVE WAS NOTNOTIFIED OF THIRD PARTY INTENT TO EXCAVATE BELL HOLE OVER CPL LINE. ALL CONTAMINATED SOIL ABOVE 500 PPM THPH WAS REMOVED AND TRANSPORTED TO LAND FILL FORTREATMENT AND DISPOSAL. ALL NON-CONTAINTAED MATERIAL AND MATERIAL WITH CONSENTRATION LESS THAN 500 PPM TPH WAS UTILIZED AS BACKFILL. ADDITIONAL CLEAN BACKFILL WAS TRANSPORTED TO THE SCENE AND UTILIZED TO RETURN THE TOPOGRAPHY AND SURFACE LAND UTILIZATION TO PRE-SPILL CONDITION.
2017-09-29 08:50 | YES | NO | 19950153 | 1995-09-21 | 2733 | CHEVRON PIPELINE CO - MIDLAND DIV | YES | 1995-08-16 | 730 | TX | ECTOR | GOLDSMITH | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1945 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4406.3374 | 8889.3623 | CRUDE OIL | 1 | 548 | 548 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 750 | 580 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | K.C. CROWELL | 7133637123 | THE LEAK WAS DUE TO EXTERNAL CORROSION IN A CALICHE ROAD CROSSING UPON NOTIFICATION OF THE LEAK, THE LINE WAS BLOCKED IN AND A SUCTION WAS PUT ON THE LINE. CLEANUP WAS PERFORMED TO RCT RULE 91 SPECIFICATIONS. THE CORRODED SECTIONOF PIPE WAS REPLACED WITH 206 OF COATED NEW PIPE.
2017-09-29 08:50 | NO | NO | 19950154 | 1995-09-14 | 26088 | SIGMOR PIPELINE CO | NO | 1995-07-10 | 1130 | TX | SAN PATRICIO | MATHIS | NO |  | NO | 4 MILES DUE NORTH OF THE CITY OF MATHIS, TEXAS 1/4 MILE NORTHWEST OF COUNTY ROAD NO.3 A-338, J.P. BORDEN SURVEY, SAN PATRICIO COUNTY, TEXAS. |  | LINE PIPE | PIPE |  | 1957 | OUTSIDE FORCE DAMAGE | CORROSION, EXTERNAL | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 26300 | 19314.4455 | 38965.0379 | TRANSMIX (PART. REFINED PETRO) | 3 | 0 | 0 | NO | NO | 6 | 0.19 | 35000 | WELDED |  | 819 | 0 | YES | 24 | 1000 | 11 | 77 | EXTERNAL | Null | YES | OTHER | FOREIGN PIPELINE CP INTER | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | GERALD CHILDERS | 8063783583 | AT APPROXIMATELY 1130 HOURS ON JULY 10, 1995, DURING AN INTEGRITY TEST OF OUR 6" CCORPUS CHRISTI REFINED PRODUCTS PIPELINE, A SUSPECT LEAK WAS ISOLATED AND DETERMINED TO BE IN AN 8 MILE SEGMENT OF LINE BETWEEN ARGENTA BLOCK VALVE AND MATHIS STATION. PERSONNEL WALKED PIPELINE TWICE THEN CALLED IN CONSULTANTWITH ELECTRONIC SNIFFERS AGAIN A LEAK WAS NOT FOUND. THE LEAK WAS FINALLY DISCOVERED ON JULY 12, 1995 BY PURGING THE LINE WITH NITROGEN WHICH FORCED VAPORS UP FOR SNIFFER TO DETECT, HOWEVER PRODUCT NEVER SURFACED. INVESTIGATION HAS SHOWN OUR LINE HAD BEEN STRUCK BY EXCAVATING EQUIPMENT DIGGING OUT A FOREIGN LINE CROSSING ABOVE OUR LINE APPARENTLY MANY YEARS AGO. FURTHER STUDY APPEARS TO SHOW TH FOREIGN PIPELINE OPERATOR WAS RUNNING HIGH CP CURRENT OUTPUT WHICH CAUSING CP INTERFERENCE AND ALLOWING EXTERNAL CORROSION ON OUR LINE IN THE AREA OF PREVIOUSLY DAMAGED COATING. THE DAMAGED PIPE WAS REPLACED WITH 24 FEET OF PRE-TESTED LINE PIPE AND RETURNED TO SERVICE WITHOUT INCIDENT.
2017-09-29 08:50 | YES | NO | 19950155 | 1995-09-20 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-08-17 | 1641 | KS | MCPHERSON |  | NO |  | NO | T-19-S/R5-W, 8 MILES WEST OF MCPHERSON, KS ON STATE HIGHWAY 56, CONWAY STATION |  | NO DATA | OTHER | BRINE TUBING SALT CAVERN | 1986 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2203.1687 | 4444.6811 | L. P. G. | 2 | 10 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | JOHNNY CAVITT | 9185993795 | COLLAPSE OF A SHALE LEDGE WITHIN A BEDDED SALT CAVERN CAUSED DAMAGE TO THE BRINE TUBING. THE DAMAGE ALLOWED PRODUCT (PROPANE) TO ENTER THE BRINE SYSTEM. THE DEGASIFIER/FLARE SYSTEM CONTAINED THE RELEASED; HOWEVER, A SMALL QUANTITYWAS RELEASED TO THE ATMOSPHERE THROUGH THE BRINE PIT.
2017-09-29 08:50 | YES | NO | 19950156 | 1995-09-18 | 19226 | TEXACO PIPELINE INC | YES | 1995-08-26 | 200 | ND | BILLINGS |  | NO |  | YES | ONE MILE EAST, 1/2 MILE NORTH OF FRYBURG EXIT ON INTERSTATE 94 |  | PUMPING STATION | PIPE |  | 1993 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | CRUDE OIL | 1 | 100 | 85 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GARY QUINN | 4066873304 | A XX-HEAVY 1" NIPPLE THAT IS USED TO DRAIN THE PUMP BODY CRACKED ALLOWING OIL TO LEAK.
2017-09-29 08:50 | YES | NO | 19950157 | 1995-09-22 | 26095 | STEUART PETROLEUM CO | NO | 1995-09-03 | 1004 | MD | ST MARYS | PINEY POINT | NO |  | NO | FROM RT. 5 TAKE RT. 249 SOUTH, THE TERMINAL IS SEVEN MILES ON THE RIGHT HAND SIDE. STEUART PETROLEUM CO., RT. 249, PINEY POINT, MD 20674 MAP FROM SPCC. |  | TANK FARM | OTHER | HEAT EXCHANGERS | 1995 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 47500 | 34883.5042 | 70374.118 | FUEL OIL | 3 | 83 | 71 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CLIFTON R. BALLAME | 0 0 0 | ON TH MORNING OF SEPTEMBER 3, 1995, STEUART PETROLEUM COMPANY WAS FINISHING APIPELINE DELIVERY OF 1% #6 FUEL OIL TO PEPCO'S CHALK POINT FACILITY. DUE TO THE PHYSICAL PROPERTIES OF #6 FUEL OIL, IT IS NECESSARY TO DISPLACE THE #6 OIL FROM THE PIPELINE WITH #2 OIL AFTER A DELIVERY TO CHALK POINT IS COMPLETED.THIS IS ACCOMPLISHED BY SECURING THE PIPELINE TRANSFER FROM PINEY POINT, GAUGING TANKS, AND REALIGNING VALVES AT BOTH PINEY POINT AND CHALK POINT. ONCE THIS IS COMPLETED, A PRE-TRANSFER CONFERENCE IS HELD BETWEEN THE SPC OPERATORSLOCATED AT CHALK POINT AND PINEY POINT PRIOR TO TRANSFER COMMENCEMENT. THE PINEY POINT OPERATOR FAILED TO PROPERLY ALIGN VALVES IN ACCORDANCE WITH STANDARD OPERATING PROCEDURES, RESULTING IN MAIN LINE PRESSURE BEING PLACED ON THE HEAT EXCHANGERS LOCATED ON THE SUCTION SIDE OF THE PUMPS AT THE PINEY POINT TERMINAL. THIS CAUSED GASKET FAILURE IN THE HEAT EXCHANGERS RESULTING IN APPROXIMATELY 3,500 GALLONS OF THE #6 FUEL OIL BEING SPILLED ONTO AN IMPERVIOUS CLAY SURFACE IN AND NEAR THE TANK DIKE AREA.
2017-09-29 08:50 | YES | NO | 19950158 | 1995-09-28 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1995-09-03 | 1624 | MN | CLEARWATER |  | NO |  | NO | UNDER POWERLINES |  | LINE PIPE | PIPE |  | 1950 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 50 | 0 | YES | NO | 18 | 0.28 | 46000 | WELDED |  | 831 | 541 | YES | 24 | 1055 | 9 | 73 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS | MECHANICAL DAMAGE | Null | ONE CALL |  | Null | Null | R.C. SANDAHL | 2187250102 | THE LEAK WAS DETECTED BY ODOR SUNDAY NIGHT BY LAKEHEAD EMPLOYEES AT CLEARBROOK TERMINAL. THE LEAK WAS CONFIRMED BY STAFF AND REPORTED TO THE LINE 1 OPERATOR AT 1624 MST/O3. THE LINE WAS SHUT DOWN AT 1625 MST/O3. LAKEHEAD PERSONNELISOLATED THE AREA AND BEGAN ASSESSING THE EXTENT OF THE LEAK. BEMIDJI DISTRICT MANAGEMENT AND PLM WERE NOTIFIED OF THE SITUATION AND BEGAN MOBILIZING TO THE SITE. THE FEDERAL EMERGENCY RESPONSE CENTER AND MINNESOTA STATE DUTY OFFICER WERE NOTIFIED OF THE SITUATION. AFTER VERIFYING PERSONNEL SAFETY, THE AREA WAS INTENTIONALLY IGNITIED WITH A FLARE GUN. TO FACILITATE REPAIRS, CRUDE OIL WAS MOVED INTO THE PIPE TO REPLACE THE NGL. PLM COMPLETED INSTALLATION OF A STOPPLE TOWER. THE FIRE WAS EXTINGUISHED WITH FOAM AND REPAIRS MADE. THE JOINT CONTAINING THE DEFECT WAS REMOVED AND SENT FOR ANALYSIS. LINE WAS RETURNED TO SERVICE 1350 MST ON SEPTEMBER 6, 1995.
2017-09-29 08:50 | YES | NO | 19950159 | 1995-09-28 | 15851 | PRIDE REFINING INC | NO | 1995-08-30 | 1100 | TX |  |  | NO |  | NO | APPROX. 24 MILE W. OF THE TOWN OF ALANREED TX, ON INTERSTATE 40 TO FM RD 2477 TURN N. GO APPROX. 13 MILES . LEAK WAS LOCATED ON THE W.SIDE OF FM 2477 3/4 MILES |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 367.1948 | 740.7802 | CRUDE OIL | 3 | 100 | 0 | NO | NO | 10.75 | 0.37 | 25000 | WELDED |  | 600 | 305 | YES | 8 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON | 9156748231 | LEAK WAS REPORTED BY PRIDE'S PIPELINE PATROL PLANE. CREWS WERE DISPATCHED TOTHE AREA FOR SPILL CONTAINMENT AND TO CLAMP THE LINE. SOIL SAMPLES ARE BEINGTAKEN AND A SUITABLE CLEAN-UP PLAN FOR RULE 91 IS BEING DEVELOPED.
2017-09-29 08:50 | NO | NO | 19950160 | 1995-09-28 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1995-08-29 | 1300 | TX | NUECES |  | NO |  | NO | 5032 UPRIVER ROAD CORPUS CHRISTI,TX |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | GASOLINE | 3 | 0 | 5 | NO | NO | 12.75 | 0.25 | 42000 | WELDED |  | 1000 | 890 | YES | 8 | 1260 | 10 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS PUMP STATION | NO | NO | W.D. PARTLOW | 7138777370 | LEAK WAS ORIGINALLY THOUGHT TO BE A COASTAL REFINERY LEAK ON 08/26/95. ON 8/29/95 BLOCKED IN HOUSTON 12" BLOCK VALVE ON SOUTH SIDE OF CORPUS SHIP CHANNEL- PRESSURED UP ON LINE AND WOULD NOT HOLD; CONTINUED EXCAVATION COASTAL REFINERY HAD INITIATED IN SEARCH OF LEAK. FOUND LEAK EARLY A.M. 08/30/95; ATTEMPTED TO INSTALL SPLIT SLEEVE CLAMPS BUT WOULD NOT HOLD DUE TO DAMAGE OF THE PIPE; INSTALLED HALF WRAP CLAMP WHICH HELD UNTIL PERMANENT PIPE REPLACEMENT WAS MADE ON 09/12/95.
2017-09-29 08:50 | NO | NO | 19950161 | 1995-09-28 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1995-08-19 | 2200 | TX | BEE |  | NO |  | NO | PETTUS PIPELINE STATION ALONG FM ROAD 623 |  | PUMPING STATION | BOLTED FITTING |  | 1960 | OTHER | GASKET BLEW /STRAINER POT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14687.7912 | 29631.2076 | DIESEL FUEL | 3 | 30 | 10 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW | 7138777370 | GASKET BLEW OUT OF STRAINER POT IN PETTUS STATION. VOLUNTEER FIRE DEPARTMENTWAS CALLED TO ASSIST IN WASHING DIESEL OFF OF HIGHWAY AS VACUUM TRUCKS RECOVERED PRODUCT.
2017-09-29 08:50 | YES | NO | 19950162 | 1995-09-25 | 2371 | CINIZA PIPELINE INC | NO | 1995-09-02 | 330 | NM | MCKINLEY |  | NO |  | YES | STANDING ROCK STATION, 23.1 MILES WEST OF CROWNPOINT, NEW MEXICO. SEC.22, TWP - 19N, RGE 15W |  | PUMPING STATION | PUMP |  | 1992 | OTHER | THREADS FAILED ON PIPELIN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 17240 | 12660.876 | 25542.1009 | CRUDE OIL | 1 | 400 | 262 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY ARMENTA | 5056328006 | THREADS ON STUFFING BOX FAILED, PACKING GLAND PULLED AWAY FROM STUFFING BOX ALLOWING OIL TO ESCAPE THROUGH PACKING AREA. THREADS ON PACKING GLAND FAILED ON PIPELINE PUMP.
2017-09-29 08:50 | YES | YES | 19950163 | 1995-10-02 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1995-08-30 | 2332 | TX | EL PASO | EL PASO | NO |  | NO | EL PASO STATION (SAMPLE SHELTER BUILDING) LOCATED AT 6850 MARKET AVENUE, EL PASO, TEXAS 79915 |  | NO DATA | OTHER | FIRE/PRODUCT TESTING | 0 | OTHER | FIRE IN SAMPLE BUILDING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 15000 | 11015.8434 | 22223.4057 | GASOLINE | 3 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | FIRE IN SAMPLE TESTING BUILDING RESULTING IN SMALL SPILLAGE OF PRODUCT TO THE GROUND.
2017-09-29 08:50 | YES | NO | 19950164 | 1995-10-04 | 2387 | CITGO PIPELINE CO | YES | 1995-09-04 | 1500 | TX | HARDIN | SOUR LAKE | NO |  | NO | 1.5 MILES NORTH OF STATE HIGHWAY 105 AT THE END OF FANNIN STREET |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | CRUDE OIL | 1 | 115 | 110 | NO | NO | 12.75 | 0.25 | 42000 | WELDED |  | 720 | 500 | YES | 8 | 988 |  | 90 | EXTERNAL | Null | YES | GALVANIC |  | OTHER | GALVANIC CORROSION | Null | NO DATA |  | Null | Null | JIM SANDERS | 9184954786 | BYROU DAVIS OF APACHE PRODUCTION FOUND THE LEAK. RICK DAVIS OF CITGO RESPONDED AND HAD THE PIPELINE CONTROL CENTER IN TULSA SHUT DOWN THE LINE. A CITGO RESPONSE CREW CLAMPED THE LEAK AND BEGAN CLEAN UP. LEAKAGE WAS CONTAINED WITHIN A TEXACO TANK BERM. APPROXIMATELY 100 BARRELS WERE RECOVERED BY NIGHTFALL ON MONDAY. AN ADDITIONAL 100 BARRELS WERE RECOVERED ON TUESDAY. REMAINING CRUDE OIL CONTAMINATION WILL BE REMEDIATED IN PLACE UNDER APPROVAL OF THE TEXAS RAILROAD COMMISSION. THE LINE WAS SUBSEQUENTLY REPAIRED WITH FULL ENCIRCLEMENTSLEEVES.
2017-09-29 08:50 | NO | NO | 19950165 | 1995-10-04 | 10318 | KOCH REFINING CO | YES | 1995-08-30 | 1430 | WI | DODGE |  | NO |  | NO | T12N,R14E,SEC21, DODGE COUNTY, WISCONSIN NEAR INTERSECTION OF BREEZY POINT AND JUNIPER ROAD. |  | LINE PIPE | VALVE |  | 1987 | OTHER | THREADED UNION LEAKING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | FUEL OIL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.A. RALSTON | 6124584845 | DURING THE INSTALLATION OF A FIBERGLASS INSPECTION CANISTER AROUND AND 8" MAINLINE VALVE, A SMALL DRIP LEAK WAS OBSERVED AROUND A THREADED BELOW GROUND UN
2017-09-29 08:50 | YES | NO | 19950166 | 1995-10-05 | 20133 | UNION PACIFIC RESOURCES CO | NO | 1995-09-06 | 1555 | TX | NUECES | BISHOP | NO |  | NO | SAUH FRACTIONAL 1/2 OF FRACTIONAL SECTION 206 OF THE F2 BISHOP PALO ALTO SUBDIVISION (OFF OF CO RD 16 EAST OF FM 70 BY VPRC'S OFFICE PRODUCTION). |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 734.3896 | 1481.5604 | NATURAL GAS LIQUID | 2 | 707 | 0 | NO | NO | 2.38 | 0.13 | 2526 | WELDED |  | 672 | 125 | YES | 8 | 840 | 4 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CINDY L. MUNOZ | 5125843521 | NOTICED DROP IN PRESSURE AND SUSPECTED A LEAK . EVACUATED PRODUCT (MIXED BUTANE) FROM PIPELINE AND FILLED LINE WITH WATER TO PRESSURE TEST. SEVERAL (6) PINHOLE LEAKS DETECTED ON 09/06/95 AND 09/07/95. PIPELINE WILL BE REPLACED BEGINNING ON OR ABOUT 09/18/95.
2017-09-29 08:50 | YES | NO | 19950167 | 1995-10-06 | 808 | ARCO TERMINAL SERVICES CORP | YES | 1995-09-13 | 1130 | CA | LONG BEACH |  | NO |  | NO | INTERSECTION AT FASHION AVENUE AND 16TH STREET |  | LINE PIPE | GIRTH |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 66095.0606 | 133340.434 | CRUDE OIL | 1 | 20 | 10 | NO | NO | 12 | 0.3 | 46000 | WELDED |  | 720 | 25 | YES | 8 | 900 | 0 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GUY S. CASTRO | 3104992353 | LEAK SURFACED AT PAVED INTERSECTION OF FASHION AVENUE AND 16TH STREET IN LONGBEACH. PIPE WAS EXCAVATED AND A CORROSION PIT WAS FOUND IN A WELD.SUPPLEMENTAL REPORT INDICATES CORROSION AS CAUSE, BUT ADDS OTHER, AS WELL,CITING "WELD FAILURE AND EXTERNAL CORROSION." COMMENTS CONTINUE BY ADDINGTHAT UPON FURTHER INVESTIGATION, IT WAS FOUND THAT IN THE ORIGINALFABRICATION THERE EXISTED AN IMPROPER WELD FUSION.
2017-09-29 08:50 | YES | NO | 19950168 | 1995-10-11 | 10313 | KOCH PIPELINE INC | YES | 1995-09-11 | 800 | LA | AVOYELLES |  | NO |  | NO | T-2N,R3E,SEC 26. NEAR TOWN OF FIFTH WARD |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 110158.4343 | 222234.0567 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 10.75 | 0.25 | 1407 | WELDED |  | 1340 | 948 | YES | 32 | 1960 | 7 | 69 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | JIM L. NORVELL | 3144865488 | ETED FINAL REPAIRS ON 09/15/95 BY REPLACING DAMAGED PIPE WITH HYDROSTATICALLY TESTED REPAIR PIPE. KOCH CONTRACTOR'S ALSO X-RAYED THE REPAIRED PIPE SEGMENT ON 09/15/95. KOCH CONTRACTORS REMOVED THE CONTAMINATED SOIL TO A LICCENSED LANDFILL UNDER DIRECTION OF THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY. KOCH CONTRACTORS BROUGHT CLEAN SOIL TO THE SITE FOR FILL.
2017-09-29 08:50 | NO | NO | 19950169 | 1995-10-12 | 10318 | KOCH REFINING CO | YES | 1995-09-14 | 1830 | WI | DODGE |  | NO |  | NO | 3 MILE EAST OF BEAVER DAM, WI ON COUNTY ROAD "E" |  | LINE PIPE | VALVE |  | 1987 | OTHER | 1/2 UNION OF SEAL PIPING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | FUEL OIL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICK RALSTON | 6124584845 | LINE VALVE, A SMALL DRIP LEAK WAS OBSERVED AROUND A THREADED BELOW GROUND UNION.
2017-09-29 08:50 | NO | NO | 19950170 | 1995-10-18 | 10318 | KOCH REFINING CO | YES | 1995-09-20 | 940 | WI | DANE |  | NO |  | NO | SEE MAP |  | LINE PIPE | VALVE |  | 1987 | OTHER | THREADED UNION LEAKING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | FUEL OIL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICK RALSTON | 6124584845 | DURING THE INSTALLATION OF A FIBERGLASS INSPECTION CANISTER AROUND AN 8" MAINLINE VALVE, A SMALL DRIP LEAK WAS OBSERVED AROUND A 1/2" THREADED BELOW GROUND UNION.
2017-09-29 08:50 | NO | NO | 19950171 | 1995-10-16 | 14194 | OILTANKING OF TEXAS PIPELINE CO | NO | 1995-09-27 | 905 | TX | HARRIS |  | NO |  | NO | CHANNELVIEW TX VIA 24" LINE ACROSS HOUSTON SHIP CHANNEL NEAR WASHBURN TUNNEL TO LYONDELL REFINERY ON HWY 225. |  | LINE PIPE | OTHER | NOT GIVEN | 1977 | INCORRECT OPERATION BY OPERATOR PERSONNEL | VALVE CLOSURE | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NOT GIVEN | 3 | 0 | 0 | NO | NO | 24 | 0.28 | 1090 | WELDED |  | 530 | 620 | YES | 24 | 785 | 3 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHUCK THOMPSON | 7134577900 | AT 0905 27 SEPT 95, OIL TANKING WAS TRANSFERRING CRUDE OIL TO LYONDELL-CITGOREFINING ON HWY 225. LCR PERSONEL MADE A TANK SWITCH WITHOUT WALKING OUT LINEUP. ONE VALVE WAS LEFT CLOSED, CAUSING OIL TANKINGS REMOTE PRESSURE SWITCH TO DROP OUT BOOSTER PUMP & OPENING A BYPASS ON MAIN PUMPS. OIL TANKING PERSONNEL SHUT SYSTEM DOWN & TELEPHONED LCR. FOREMAN. O920 LCR PERSONNEL (ARMSTRONG)ADVISED TO START BACK SLOWLY OT. PERSONNEL WERE RIDING R.O.W. & CHECKING VALVESITES & CHANNEL CROSSING AT REDUCED RATE. RATE WAS NOT INCREASED TO MAX UNTIL 1000 29 SEPT 95 WITH OIL TANKING ON R.O.W.
2017-09-29 08:50 | YES | NO | 19950172 | 1995-10-16 | 26023 | COASTAL STATES CRUDE GATHERING CO | YES | 1995-09-20 | 2130 | TX | BEE |  | NO |  | NO | 3.9 MI NORTH FM 623 3/4 MI SOUTH CO RD #743 2 MI EAST OF HIGHWAY #181 |  | LINE PIPE | PIPE |  | 0 | OTHER | NOT GIVEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 2510 | 0 | NO | NO | 12 | 0.23 | 0 | WELDED |  | 1025 | 900 | Null | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | OTHER | NOT GIVEN | Null | Null | CLIF GROTE | 5128873953 | WHILE STARTING PIPE LINE UP FROM CORPUS LINE BLEW OUT.
2017-09-29 08:50 | NO | NO | 19950173 | 1995-10-13 | 21038 | VALERO MARKETING CO | NO | 1995-08-28 | 800 | TX | BEXAR |  | NO |  | NO | 4.6 MILES SOUTH OF VALERO'S SAN MARTIN PLANT |  | LINE PIPE | PIPE |  | 1981 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | TRANSMIX (PART. REFINED PETRO) | 3 | 2 | 0 | NO | NO | 6 | 0.16 | 42000 | WELDED |  | 1424 | 1020 | YES | 24 | 1831 | 4 | 81 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN SOMMER | 2102462395 | WHILE VALERO'S LEAK DETECTION SPECIALIST WAS CONDUCTING THE INSPECTION OF THEPIPELINE RIGHT OF WAY A SPOT OF DEAD VEGETATION WAS FOUND. THE PIPELINE WAS EXCAVATED AND A PIN HOLE LEAK WAS FOUND IN A GIRTH WELD.
2017-09-29 08:50 | YES | NO | 19950174 | 1995-10-16 | 12626 | MOBIL PIPELINE CO - EMPIRE | NO | 1995-09-09 | 800 | TX | NAVARRO |  | NO |  | NO | 1604 SOUTH 15TH STREET CORSICANA, TEXAS, APPROX. 1 MILE NORTH OF DOWNTOWN CORSICANA, TEXAS. |  | TANK FARM | WELDING FITTING | 8" NIPPLE ON HEADER OF 24 | 1948 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11015.8434 | 22223.4057 | CRUDE OIL | 1 | 536 | 508 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 30 | 30 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT | 2146585914 | AT APPROXIMATELY 0800 HRS. SEPT.9, 1995 LEAK WAS DISCOVERED ON THE BOTTOM PART OF 8" NIPPLE ON HEADER OF 24" SUCTION/FILL LINE TO STORAGE TANK #2619. THE8" NIPPLE HAD A DENT ON BOTTOM SIDE WHERE LEAK OCCURRED. INTERNAL CORROSION WAS CAUSE OF LEAK APPROX. 526 BBLS. OF CRUDE OIL ESCAPED WITH 508 BBLS RECOVERED. TEMPORARY REPAIR WAS MADE BY INSTALLING 8" CLAMP AND PLATE ON LEAK AREA.PERMANENT REPAIR WAS MADE 09/15/95 BY COMPLETELY REMOVING THE HEADER WERE LEAK OCCURRED. THIS HEADER HAD BEEN PREVIOUSLY ISOLATED FROM MAIN SUCTION/FILL LINE AND BEEN IDLE FOR MANY YEARS. CLEAN-UP PROCEDURES WERE IMMEDIATLEY INITIATED. THE OILY SOIL WAS MIXED WITH FRESH SOIL AND BLENDED TOGETHER. THE ENTIRE AREA WAS TURNED OVER AND DISC WITH TRACTOR. ALL SOIL WAS MIXED AND 13-13-13FERTILIZER ADDED TO ENHANCE BIOREMEDIATION PROCESS WITH TILLING AND WATERING. THE NRC AND TRRC WERE NOTIFIED.
2017-09-29 08:50 | YES | NO | 19950175 | 1995-10-20 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1995-09-27 | 50 | MN | CLEARWATER |  | NO |  | NO | LAKEHEAD'S CLEARBROOK, MINNESOTA TERMINAL |  | PUMPING STATION | BOLTED FITTING |  | 1994 | OTHER | GASKET ON HEADER FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | CRUDE OIL | 1 | 50 | 47 | NO | NO | 24 | 0 | 600 | FLANGED |  | 960 | 837 | YES | 4 | 2160 | 10 | 94 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.G. SANDAHL | 2187250102 | AT APPROXIMATELY 00:50 MST, A TERMINAL GAUGER WITNESSED THE RELEASE OF CRUDEOIL COMING FROM HEADER PIPING ON LINE 2 PUMP STATION. THE CONTROL CENTER WASCONTACTED IMMEDIATELY TO SHUTDOWN AND ISOLATE LINE 2. A LEAK OF APPROXIMATELY 50 BBLS. WAS SUSTAINED AND CONFINED TO THE STATION PROPERTY. APPROXIMATELY 95% OF THE OIL WAS RECOVERED WITH THE VACUUM TRUCKS. THE REMAINING CONTAMINATED SOIL WAS STOCKPILED AND WILL BE INCINERATED ALONG WITH THE CURRENT INCINERATION PROGROM AT CLEARBROOK. THE CAUSE OF THE ACCIDENT HAS BEEN ATTRIBUTED TOFAULTY INSTALLATION AND BOLT-UP OF A 24" FLANGE CONNECTION INSTALLED DURING THE 1994 CONSTRUCTION YEAR.
2017-09-29 08:50 | YES | NO | 19950176 | 1995-10-26 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-09-29 | 830 | IA | WOODBURY |  | NO |  | NO | T-87-N R-47-W SECTION 30,1/2MILE FROM TERRA PORT NEAL PLANT |  | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20048 | 14723.0419 | 29702.3225 | ANHYDROUS AMMONIA | 3 | 266 | 76 | NO | NO | 4.5 | 0.14 | 35000 | WELDED |  | 1160 | 100 | YES | 24 | 2092 | 0 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | LINE MARKERS | NO | NO | SID RUETER | 9185811538 | A THIRD PARTY RUPTURED MAPL'S NH3 LINE WITH A BACKHOE. THE LINE WAS REPAIREDBY REPLACING THE DAMAGED SECTION. SUPPLEMENTAL REPORT RECEIVED 1/30/1996INDICATED A CORRECTION TO THE TOTAL LOSS OF PRODUCT/COMMODITY SPILLED. THETOTAL LOSS OF PRODUCT WAS 266 BARRELS, HOWEVER, ONLY 190 BARRELS WENT TO THEATMOSPHERE BECAUSE WE TRANSFERRED 76 BARRELS OF PRODUCE IN THE PIPE TO A TRUCKTRANSPORT TRAILER USING NITROGEN DISPLACEMENT. SUPPLEMENTAL REPORT SUBMITTEDBY JOHNNY CAVITT, MANAGER OF QUALITY DEVELOPMENT.
2017-09-29 08:50 | YES | NO | 19950177 | 1995-10-26 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-09-26 | 2024 | KS | OTTAWA |  | NO |  | NO | T-12-S R-1-W SECTION 34, 2 MILES NORTH AND 2-1/2 MILES WEST OF SOLOMON, KANSAS APPROX. 1/4 MILE SOUTH-WEST OF AM 47 |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 19730 | 14489.5061 | 29231.1863 | L. P. G. | 2 | 1059 | 0 | NO | NO | 8 | 0.16 | 52000 | WELDED |  | 1350 | 926 | YES | 24 | 1800 | 9 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | LINE MARKERS | NO | NO | SID RUETER | 9185811537 | A FARMER, PLOWING A LOW SPOT, RUPTURED AN 8" PIPELINE. EMERGENCY PROCEDURES WERE INITIATED. THE LINE SEGMENT WAS ISOLATED AND REPAIRED WITH A FULL ENCIRCLEMENT SLEEVE. SUPPLEMENTAL REPORT SUBMITTED 2/13/1996 BY JOHNNY CAVITTCHANGED ORIGINAL PROPERTY DAMAGE FROM $11000 TO $19370.
2017-09-29 08:50 | YES | NO | 19950178 | 1995-10-26 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1995-09-28 | 2015 | NM | SAN JUAN |  | NO |  | NO | SECTION 21 T-26-N R-10-W, MP-399 HIGHWAY 44 AT MILE MARKER 133, STATION IS BESIDE HIGHWAY |  | PUMPING STATION | OTHER | FLARE SYSTEM SPARK ARREST | 1992 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 367.1948 | 740.7802 | NATURAL GAS LIQUID | 2 | 1 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SID RUETER | 9185811538 | DURING A MAINLINE FILTER CHANGING OPERATION, PRODUCT WAS DIRECTED TO THEFLARE SYSTEM. DIRT AND DEBRIS FROM RECENT PIGGING OPERATIONS PLUGGED THEFLAME ARRESTOR, CAUSING THE BODY GASKET ON THE FLAME ARRESTOR TO LEAK,RESULTING IN A PRODUCT RELEASE TO THE ATMOSPHERE. FIRE FROM THE BURING FLAREIGNITED THE ESCAPING PRODUCT AT THE FLAME ARRESTOR. MAPL PERSONNEL ISOLATEDTHE FLARE SYSTEM AND THE SMALL FIRE WAS IMMEDIATELY EXTINGUISHED. THEARRESTOR WAS REMOVED, CLEANED, AND THE GASKET WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19950179 | 1995-11-06 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1995-09-22 | 1100 | TX | BEE |  | NO |  | NO | 4 MILES NORTHEAST OF PETTUS, TEXAS |  | LINE PIPE | PIPE |  | 1960 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 91798.6952 | 185195.0473 | GASOLINE | 3 | 2510 | 0 | NO | NO | 12.75 | 0.22 | 42000 | WELDED |  | 1050 | 830 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.D. PARTLOW | 7138777370 | A PRESSURE DROP OCCURRED AT 2104 HRS. ON 09/20/95 ON THE 12" SEGMENT OF THE SAN ANTONIO REFINED PRODUCTS PIPELINE SYSTEM BETWEEN THE NORMANA AND KARNES CITY PUMP STATIONS. THE LINE HAD JUST RETURNED TO SERVICE JUST PRIOR TO THE NOTED PRESSURE DROP. COASTAL PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE AREA WHERE THE LEAK WAS SUSPECTED TO HAVE OCCURRED. DUE TO INCLEMENT WEATHER (THUNDERSTORMS) AND THE RURAL LOCATION OF THE PIPELINE, THE LEAK WAS NOT ACTUALLY LOCATED UNTIL 1100 HRS. ON 09/22/95. A 10' SPLIT, 2" WIDE IN THE 12" PIPE WASFOUND UPON EXCAVATION OF THE SITE. SUBSEQUENTLY, THE MOP AND OPERATING PRESSURES WERE LOWERED ON THE SYSTEM AND A METALLURGICAL ANALYSIS OF THE FAILED PIPE IS BEING CONDUCTED.
2017-09-29 08:50 | YES | NO | 19950180 | 1995-11-06 | 12627 | MOBIL OIL CORP | NO | 1995-10-03 | 857 | TX | LIBERTY |  | NO |  | NO | APPROXIMATELY 2 MILES WEST OF HULL TEXAS AT MOBIL PIPE LINE MILE POST 181 |  | LINE PIPE | PIPE |  | 1924 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 165237.6514 | 333351.0851 | CRUDE OIL | 1 | 1000 | 700 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 400 | 915 | YES | 8 | 500 | 11 | 92 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT | 2146585914 | AT 0815 HRS. ON OCT 3, 1995, COMPANY PERSONNEL BEGAN LINE DISPLACEMENT OF APPROX 1500 BBLS. OF CRUDE OIL WITH NITROGEN FOR TIE-IN OF NEW TRINITY RIVER CROSSING. OPERATIONS CONTROLLER HAD PREVIOUSLY COMPLETED A DELIVERY DOWNSTREAM OF DISPLACEMENT AREA AND FAILED TO PROPERLY REALIGN VALVES FOR DISPLACEMENT OPERATIONS. PIPELINE BECAME OVERPRESSURED AND 0857 HRS, DROP IN PRESSURE OCCURRRED. OPERATIONS CONTROLLER CONTACTED FIELD PERSONNEL AND HAD THEM INVESTIGATEFOR POSSIBLE LEAK. AT O914 HRS CONTROLLER DISCOVERED THAT HE HAD FAILED TO OPEN A DOWNSTREAM MAINLINE BLOCK VALVE, THUS CAUSING THE PRESSURE BUILDUP. FIELD PERSONNEL DID NOT DISCOVER A LEAK DURING THEIR INVESTIGATION. COMPANY PILOT WAS DISPATCHED TO AREA AND HE TOO DID NOT DISCOVER ANY LEAK OR DISCREPANCIES. AT 1130 HRS. ON OCTOBER 4, 1995, OPERATIONS CONTROLLER RECEIVED A TELEPONE CALL FROM FARMER IN AREA OF THE PREVIOUS DAYS LINE DISPLACEMENT NOTIFYING HIM OF A PETROLEUM ODOR. CONTROLLER NOTIFIED FIELD PERSONNEL IN AREA TO INVESTIGATE. A HELICOPTER WAS ALSO DISPATCHED TO AREA AND AT APPROX. 1330 HRS. ALEAK WAS DISCOVERED AT MILE POST 181 ON THE LINE THAT HAD BEEN DISPLACED WITH NITROGEN THE DAY BEFORE. CREWS WERE DISPATCHED TO THE AREA AND REPAIR AND CLEAN UP PROCEDURES INITIATED. THE OPERATIONS CONTROLLER RESPONSIBLE FOR THISINCIDENT WAS SUSPENDED FROM DUTY ON 0CT 4, 1995 AND DRUG TESTED PER IN-HOUSEINVESTIGATION BY MANAGEMENT PERSONNEL REVEALED DISCREPANCIES IN PROCEDURES AND COMMUNICATION. CORRECTIVE ACTION HAS BEEN IDENTIFIED AND IS IN THE PROCESSOF BEING CORRECTED.
2017-09-29 08:50 | YES | NO | 19950181 | 1995-11-06 | 2170 | CENEX PIPELINE | YES | 1995-10-04 | 1614 | ND | MOUNTRAIL |  | NO |  | NO | NORTH SIDE OF HIGHWAY 23, APPROX 4 MILES WEST OF NEW TOWN NORTH DAKOTA, AND 1/4 MILE EAST OF FOUR BEARS BRIDGE. |  | LINE PIPE | PIPE |  | 1995 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 165237.6514 | 333351.0851 | GASOLINE | 3 | 1136 | 330 | NO | NO | 8 | 0.25 | 2435 | WELDED |  | 1200 | 500 | YES | 8 | 1850 | 9 | 95 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | S MICHEL STAHLY | 4066285209 | ON OCTOBER 4, 1995, AT APPROXIMATELY 4:14 P.M. MOUNTAIN DAYLIGHT TIME, A STATE CONTRACTOR WORKING FOR THE STATE OF NORTH DAKOTA ON A STATE HIGHWAY CONSTRUCTION PROJECT, HIT AN 8" DIAMETER PETROLEUM PRODUCTS PIPELINE OWNED AND OPERATED BY CENEX PIPELINE, INC. AT A LOCATION APPROXIMATELY 4 MILES WEST OF NEW TOWN, NORTH DAKOTA. THE IMPACT OF THE EARTH-MOVING EQUIPMENT CAUSED THE STEEL PIPEINE TO RUPTURE, RELEASING UNLEADED GASOLINE TO THE GROUND, AND POSSIBLY ASMALL QUANTITY TO LAKE SAKAKAWEA. A DETAILED DESCRIPTION OF THE INCIDENT LOCATION IS: NORTH OF HIGHWAY 23, APPROXIMATELY 4 MILES WEST OF NEW TOWN, NORTH DAKOTA, AND 1/4 MILE EAST OF FOUR BEARS BRIDGE, SECTION 14, T152N, R93W, MONTRAIL COUNTY, NORTH DAKOTA. A TOTAL OF 1136 BARRELS (47,712 GALLONS) OF UNLEADED GASOLINE WAS LEAKED; APPROXIMATELY 330 BARRELS (13,860 GALLONS) OF WHICH WAS RECOVERED AND TRANSPORTED TO THE CENEX PIPELINE TERMINAL IN MINOT, NORTH DAKOTA. THE LOSS OF PIPELINE PRESSURE RESULTING FROM THE RUPTURE WAS IMMEDIATELY DETECTED AT THE PIPELINE CONTROL CENTER IN LAUREL, MONTANA, AND THE PIPELINE WAS SHUT DOWN BY 4:16 P.M. THE STAT CONTRACTOR USED EARTH-MOVING EQUIPMENTON SITE TO CONSTRUCT BERMS WHICH CONTAINED THE GASOLINE, AND MINIMIZED THE VOLUME REACHING NEARBY LAKE SAKAKAWEA. BLOCK VALVES LOCATED ON EACH SIDE OF THERUPTURE WERE CLOSED, ISOLATING THE SECTION OF PIPELINE. FEDERAL AND STATE GOVERNMENTAL AGENCIES WERE NOTIFIED THROUGH THE NATIONAL RESPONSE CENTER. CENEXRESPONSE CREWS WERE DISPATCHED TO THE SCENE, WORKING THROUGH THE NIGHT TO PUMP THE CONTAINED GASOLINE INTO TANK TRUCKS,AND TO INSURE THAT NONE OF IT REACHED THE WATER. SORBENT MATERAILS AND CONTAINMENT BOOMS WEREDEPLOYED NEAR THE SHORE OF LAKE SAKAKAWEA AS A PECAUTIONARY MEASURE IN THEEVENT THAT SEEPA GE OF GASOLINE TO THE LAKE SHOULD OCCUR. VISUAL ON-GROUNDINSPECTIONS OF THE SHORELINE ADJACENT TO THE RUPTURE CONDUCTED THROUGHOUT THEFIRST NIGHT DID NO T DETECT THE PRESENCE OF MEASURABLE OIL ON THE WATERSURFACE. A 3" - TO 4" - WIDE SHEEN WAS OBSERVED, WHICH EXTENDED FORAPPROXIMATELY 20 FEET OF THE SHOR ELINE ADJACENT TO THE RUPTURE. ON THEMORNING OF OCTOBER 5, THE SHORELINES NE AR THE SITE WERE INSPECTED BY AIRCRAFTAND BY BOAT TO VERIFY THAT GASOLINE WAS NOT REACHING THE WATER. FOLLOWINGRECOVERY OF THE CONTAINED GASOLINE, TRENC HES WERE EXCAVATED TO RECOVERADDITIONAL GASOLINE AND IMPACTED GROUNDWATER. THE DAMAGED SECTION OF PIPELINEWAS REPLACED BY OCTOBER 6. APPROXIMATELY 5,570 CUBIC YARDS OFGASOLINE-IMPACTED SOIL WAS EXCAVATED FROM THE SITE, AND REMOV ED TO ASTATE-APPROVED LANDFARM FACILITY FOR TREATMENT DURING THE DAYS FOLLOW ING THEINCIDENT. SAMPLES WERE COLLECTED FROM SOIL REMAINING AT THE EXCAVATIO NSURFACES TO VERIFY THE ACHIEVED CLEANUP LEVELS. CLEAN SOILS FROM THE HIGHWA YCONSTRUCTION PROJECT WERE USED TO BACKFILL THE EXCAVATIONS. THE CLEANUP WASCOMPLETED ON WEDNESDAY, OCTOBER 18, 1995. AN ENVIRONMENTAL GEOLOGIST FROM TH ENORTH DAKOTA DIVISION OF WATER QUALITY WAS ON SITE DURING MOST OF THE CLEAN UPEFFORT. THE SITE CLEANUP WAS ALSO MONITORED BY REPRESENTATIVES OF THE STAT EDEPARTMENT OF TRANSPORTATION, MONTRAIL COUNTY, AND FORT BERTHOLD INDIAN RESERVATION.
2017-09-29 08:50 | YES | NO | 19950182 | 1995-11-09 | 18273 | SHELL PIPELINE CORP | YES | 1995-10-07 | 910 | TX |  |  | YES | X-2747580.86,Y-216682.40 | NO | COBIA 12-INCH PIPELINE, MAIN PASS BLOCK 70 |  | LINE PIPE | GIRTH |  | 1968 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 367194.781 | 740780.1891 | CRUDE OIL | 1 | 3 | 0 | NO | NO | 12 | 0.41 | 52000 | WELDED |  | 1440 | 0 | YES | 24 | 1800 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132 | COBIA PIPELINE WAS BEING PRESSURE TESTED BEFORE RETURNING TO SERVICE AFTERHURRICANE OPAL. HURRICANE OPAL CAUSED UNKNOWN STRESS RESULTING IN RELEASE ATGIRTH WELD. PROPERTY DAMAGE IS ESTIMATED ON THIS REPORT. WILL BE FILINGSUPPLEMENTAL.
2017-09-29 08:50 | NO | NO | 19950183 | 1995-11-10 | 443 | AMOCO PIPELINE CO | YES | 1995-10-11 | 1800 | IN | LAKE | EAST CHICAGO | NO |  | NO | PIPELINE VALVE NORTH AND WEST OF INDIANA HARBOR CANAL IN AMOCO WHITING REFINERY MARINE DOCKS FACILITY. |  | LINE PIPE | BOLTED FITTING |  | 1953 | OTHER | LOOSE FLANGE BOLT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 62500 | 45899.3476 | 92597.5236 | TRANSMIX (PART. REFINED PETRO) | 1 | 20 | 15 | NO | NO | 12 | 0.34 | 42000 | WELDED |  | 1440 | 1350 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD WHITE | 7089906105 | ON OCTOBER 11, 1995, AT 1800 AMOCO OIL COMPANY WHITING REFINERY EMPLOYEES BECAME AWARE OF A SHEEN ON THE INDIANA HARBOR CANAL. THE NRC WAS NOTIFIED AT 1900 AND THE REPORT #310546 WAS ISSUED. INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMANT WAS NOTIFIED AT 1920 AND ISSUED INCIDENT #9510072. AMOCO EMPLOYEES HAD BOOMED OFF THE CANAL AND BEGUN PICKING UP PRODUCT BY 2100. AMOCO THEN BEGANSYSTEMATICALLY SEARCHING FOR THE SOURCE OF THE PRODUCT. ON OCTOBER 12, 1995 IT BECAME APPARENT THAT THE SOURCE OF THE LEAK WAS A PIPELINE OPERATED BY AMOCO PIPELINE COMPANY. AT 1230 AN AMOCO PIPELINE EMPLOYEE IDENTIFIED THE SOURCEAS A BOLTED FLANGE ON THE INTERSTATE PIPELINE. PIPELINE EMPLOYEES UPDATED THE NRC, IDEM, AND MSO CHICAGO OF THE NEW SOURCE OF THE PRODUCT BETWEEN 1615 AND 1625. GEO PROBES WERE UTILIZED TO DEFINE THE BOUNDARIES OF THE PRODUCT AND 3 SUMPSHAVE EXTRACTED APPROXIMATELY 15 BARRELS OF PRODUCT. A SOIL VAPOR EXTRACTION UNIT HAS ALSO BEEN INSTALLED AND WILL BE ENERGIZED SOME TIME NEXT WEEK.THE INITIAL PIPELINE REPAIR INVOLVED THE TIGHTENING OF THE FLANGE BOLTS. EVENTUALLY A SECONDARY CONTAINMENT VAULT WILL BE INSTALLED TO FACILITATE THE FUTURE INSPECTION OF THE FLANGE.
2017-09-29 08:50 | YES | NO | 19950184 | 1995-11-20 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-10-22 | 1200 | TX | HARRIS | BAYTOWN | NO |  | NO | CORNER OF DECKER DRIVE (LOOP 330) AND BAKER ROAD: 4225 DECKER DRIVE |  | TANK FARM | OTHER | NOT GIVEN | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | KEROSENE | 1 | 75 | 71 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | OF A JET A KEROSOSENE TANK. UPON DISCOVERY, THE OPERATOR IMMEDIATELY SHUT OFF FLOW TO THE TANK AND STOPPED THE OVERFLOW OF PRODUCT. THERE WERE APPROXIMATELY 4 BARRELS LOST TO ABSORPTION INTO THE CONTAINMENT DIKE AREA. THIS AREA ISCURRENTLY BEING REMEDIATED IN-SITU.
2017-09-29 08:50 | YES | NO | 19950185 | 1995-11-20 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-10-23 | 2036 | TX | JEFFERSON |  | NO |  | NO | HIGHWAY 69 NORTH, JEFFERSON COUNTY IN NEDERLAND, TEXAS |  | TANK FARM | OTHER | NOT GIVEN | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 19800 | 14540.9133 | 29334.8955 | GASOLINE | 1 | 951 | 597 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | OF AN UNLEADED REGULAR GASOLINE TANK. UPON DISCOVERY, THE OPERATOR IMMEDIATELY SHUT OFF FLOW TO THE TANK AND STOPPED THE OVERFLOW OF PRODUCT. THERE WERE APPROXIMATELY 597 BARRELS OF PRODUCT TRANSFERED FROM THE CONTAINMENT DIKE AREA TO AN ADJACENT STORAGE TANK, APPROXIMATELY 354 BARRELS WERE LOST TO EVAPORATION AND ABSORPTION INTO THE CONTAINMENT DIKE AREA. THIS AREA IS CURRENTLY BEING REMEDIATED IN-SITU.
2017-09-29 08:50 | YES | NO | 19950186 | 1995-11-22 | 12127 | MARATHON PIPE LINE CO | YES | 1995-10-24 | 1611 | IL | BOND |  | NO |  | NO | 1/2 MILE E. OF SORENTO, IL - BOND COUNTY, LAGRANGE TOWNSHIP, SECTION 7 T6N, R3W |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 128000 | 94001.8639 | 189639.7284 | OIL AND GASOLINE | 3 | 70 | 59 | NO | NO | 10.75 | 0.31 | 0 | WELDED |  | 1204 | 880 | YES | 10 | 1510 | 8 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOSEPH A. FISHER | 4194213201 | AT 16:11 CDT OCTOBER 24, 1995, THE MPL OPERATIONS CENTER DETECTED A SUDDEN PRESSURE DROP ON THE MARATHON PIPE LINE COMPANY (MPL) #1-10" PIPELINE BETWEEN SORENTO AND ALTAMONT, IL. SHUTDOWN WAS INITIATED AT 16:13 AND THE LIN WAS COMPLETELY SHUTDOWN BY 16:15. ALSO AT APPROXIMATELY 16:13, THE MPL OPERATIONS CENTER IN FINDLAY, OH RECEIVED A PHONE CALL FROM A PROPERTY OWNER ONE-HALF MIL EAST OF SORENTO WHO INFORMED MPL THAT A BULLDOZER DOING DRAINAGE WORK ON HIS PROPERTY HAD STRUCK AND RUPTURED THE PIPELINE. MPL PERSONNEL MOBILIZED TO THESITE OF THE DAMAGED PIPELINE. THE AFFECTED AREA WAS SECURED AND ALL FREE PRODUCT (LIGHT CAT CYCLE OIL) WAS RECOVERED BY VACUUM TRUCK AND RETURNED TO THEPIPELINE SYSTEM AT WOOD RIVER, IL. THE DAMAGED SECTION OF PIPE WAS REPAIRED OCTOBER 25 WITH A TWO-FOOT TYPE B FULL-ENCIRCLEMENT SLEEVE. AFTER A 50-MINUTESTATIC TEST THE PIPELINE WAS RETURNED TO ACTIVE SERVICE AT 19:52 ON OCTOBER 25. OCTOBER 24-27, MUCH OF THE CONTAMINATED SOIL WAS EXCAVATED AND IS PRESENTLY STOCKPILED AWAITING REMEDIATION OR DISPOSAL. VEGETATION AFFECTED BY THE INCIDENT WAS COLLECTED AND BURNED AFTER RECEIVING PERMISSION FROM THE ILLINOIS EPA. MPL IS PRESENTLY NEGOTIATING AN AGREEMENT ON FUTURE RESPONSIBILITY FOR CLEANUP WITH THE CONTRACTOR RESPONSIBLE FOR THE DAMAGE.
2017-09-29 08:50 | NO | NO | 19950187 | 1995-11-21 | 22387 | WEST EMERALD PIPE LINE CORP | YES | 1995-10-16 | 1520 | NM | QUAY |  | NO |  | NO | 17 MILES EAST OF TUCUMCARI, NEW MEXICO SECTION 35, TWN 11-N,RNG 28-E, QUAY COUNTY, NEW MEXICO |  | LINE PIPE | LONGITUDINAL WELD |  | 1958 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 20800 | 15275.3029 | 30816.4559 | GASOLINE | 3 | 0 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1440 | 700 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD CHILDERS | 8063783583 | AT APPROXIMATELY 1520 HOURS ON OCTOBER 16, 1995, WEST EMERALD EXPERIENCED A LEAK IN ITS 6" PRODUCTS PIPELINE BETWEEN AMARILLO, TEXAS AND TUCUMCARI, NEWMEXICO. THE LINE WAS IMMEDIATELY SHUT DOWN AND BLOCK VALVES CLOSED IN THEAREA OF THE LEAK. THERE WERE NO INJURIES, FIRE OR EVACUATION DURING THEINCIDENT I NVESTIGATION OF THE PIPE SHOWED A 1/2" SPLIT ALONG THE LONGITUDINALWELD SEAM APPROXIMATELY 1/8" WIDE. THE FULL JOINT OF PIPE WAS SLEEVED TOPREVENT ANY F UTHER OCCURRENCE OF LEAKAGE AND RETURNED TO SERVICE WITHOUT
2017-09-29 08:50 | YES | NO | 19950188 | 1995-11-27 | 4493 | ENTERPRISE PRODUCTS CO | YES | 1995-11-02 | 1437 | AL | BALDWIN |  | NO |  | NO | SOUTH OF I-65 AND WEST OF HWY 287 BALDWIN COUNTY, ALABAMA |  | LINE PIPE | PIPE |  | 1981 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 16300 | 11970.5499 | 24149.4342 | NATURAL GAS LIQUID | 2 | 0 | 0 | YES | NO | 6.63 | 0.16 | 52000 | WELDED |  | 1440 | 600 | YES | 24 | 2160 | 0 | 81 | NO DATA | Null | Null | NO DATA |  | OTHER | POSSIBLE LIGHTNING | Null | NO DATA |  | Null | Null | PARIS WALTMAN | 3346758562 | NOVEMBER 2, 1995 AT 1437 REPORT WAS CALLED IN TO BAY MINETTE FIRE DEPT. BY INDIVIDUAL. NO PERSONAL INJURY'S AND NO APPRECIABLE PROPERTY DAMAGE TO SURROUNDING PROPERTY. INDIVIDUAL REPORTED TO LOCAL FIRE DEPT. WHAT SEEMED TO BE A BRUSH FIRE DURING A HEAVY LIGHTING STORM. UPON INVESTIGATION BY LOCAL FIRE DEPT. THE FIRE WAS DETERMINED TO BE A PIPELINE LEAK. LOCAL PIPELINE OPERATORS WERE NOTIFIED TO DETERMINE SOURCE OF LEAK. UPON NOTIFICATION OUR PIPELINE WAS SHUT IN AND DEPRESSURIZED AT THIS TIME. OUR EMERGENCY PROCEDURES WERE IMPLEMENTED. ONCE ENTERPRISE DETERMINED IT WAS OUR PIPELINE WE COMMENCED TO DISPLACE THE PRODUCT WITH NITROGEN IN AN EFFORT TO MINIMIZE PRODUCT LOST TO THE ATMOSPHERE. WE ESTIMATE A TOTAL OF 30 GALLONS OF LIQUID BUTANE LOST TO ATMOSPHERE, WHILE BURNING.
2017-09-29 08:50 | YES | NO | 19950189 | 1995-11-27 | 18273 | SHELL PIPELINE CORP | YES | 1995-10-24 | 800 | TX | GAINES |  | NO |  | NO | WASSON-HOBBS 12 INCH, SECTION 19, BLOCK A9 |  | LINE PIPE | PIPE |  | 1948 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14687.7912 | 29631.2076 | CRUDE OIL | 1 | 3000 | 2250 | NO | NO | 12 | 0.28 | 30000 | WELDED |  | 924 | 354 | YES | 8 | 1155 | 0 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | J.M. KORPAL | 7132410132 | PIPE FAILED AT A DENT CAUSED BY UNKNOWN THIRD PARTY EQUIPMENT INSIDE A CATTLE FEED LOT.
2017-09-29 08:50 | YES | NO | 19950190 | 1995-12-04 | 12628 | MOBIL PIPELINE CO | YES | 1995-11-10 | 115 | NJ | GLOUCESTER | GIBBSTOWN | NO |  | NO | REFER TO ATTACHED MAP |  | PUMPING STATION | BOLTED FITTING |  | 1990 | INCORRECT OPERATION BY OPERATOR PERSONNEL | GASKET FAILURE | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 55079.2171 | 111117.0284 | DIESEL FUEL | 2 | 107 | 107 | NO | NO | 12 | 0.37 | 35000 | FLANGED |  | 1009 | 1000 | YES | 8 | 1262 | 9 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM R. DURHAM II | 6092245057 | A VALVE ALIGNMENT DURING A BATCH CHANGE AT THE MALVERN PUMP STATION (MALVERN, PA) CAUSED AN INCREASE IN PRESSURE ON THE MALVERN MANIFOLD. THE INCREASE INPRESSURE CAUSED VALVE #1 (HEADGATE VALVE) AT MALVERN TO GO IN TRANSIT TO THECLOSED POSITION. UPON CLOSURE, SYSTEM PRESSURE BACK TO THE PAULSBORO PUMP STATION (GIBBSTOWN, NJ) INCREASED. THE INCREASE IN PRESSURE CAUSED TWO EVENTS: 1-UNIT 2 (TURBINE PUMP) WAS LOCKED OUT, AND 2-RUPTURE OF A GASKET AT THE PAULSBORO STATION. APPROXIMATELY 107 BARRELS OF LOW SULFUR DIESEL WERE RELEASED FROM THE FLANGE.
2017-09-29 08:50 | YES | NO | 19950191 | 1995-12-01 | 2271 | CHASE TRANSPORTATION CO | YES | 1995-10-30 | 730 | KS | BUTLER |  | NO |  | NO | 3510 SW 20TH STREET EL DORADO, KS |  | TANK FARM | TANK |  | 1977 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 6700 | 4920.4101 | 9926.4545 | FUEL OIL | 1 | 700 | 550 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHUCK JOHNSON | 3163216380 | ON OCTOBER 29, 1995, TANK GAUGE ON TANK #403 MALFUNCTIONED, SHOWING LESSPRODUCT THAN ACTUALLY WAS IN THE TANK. DELIVERY INTO TANK WAS AT 700 BBLS.PER HOUR MORE THAN WHAT WAS BEING TAKEN OUT OF TANK CAUSING TANK TO FILL ANDOVERFLOW, AT 7:30 A.M. ON 10/30/1995 ALL PRODUCT WAS CONTAINED WITHIN THEDIKED AREA AROUND THE TANK.
2017-09-29 08:50 | YES | NO | 19950192 | 1995-12-04 | 12106 | MAPCO INC | YES | 1995-11-04 | 1624 | TX | GAINES |  | NO |  | NO | 17 MI. WEST OF SEMINOLE, TEXAS ON HWY 62/180, THEN 3-1/2 MILES NORTH ON COUNTY ROAD 237, SEMINOLE, TX 79360 |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 33559 | 24645.3793 | 49719.6847 | L. P. G. | 2 | 1473 | 0 | NO | NO | 6.63 | 0.22 | 42000 | WELDED |  | 1440 | 800 | YES | 24 | 2311 | 12 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL | PERMANENT LINE MAKERS | NO | Null | JOHNNY L. CAVITT | 9185993795 | THIRD PARTY STRUCK AND RUPTURED MAPL'S SAN ANDRES 6" PIPELINE WITH A BACKHOE, CAUSING A RELEASE OF PRODUCT TO THE ATMOSPHERE. THE LINE WAS REPAIRED WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 19950193 | 1995-12-04 | 12106 | MAPCO INC | YES | 1995-11-09 | 1448 | IL | HANCOCK |  | NO |  | NO | SECTION 15,T-7-N,R-7-W 3 MILES SOUTH AND 1-1/2 MILES WEST OF DALLAS CITY ILLINOIS |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 46600 | 34222.5536 | 69040.7136 | L. P. G. | 2 | 1264 | 0 | NO | NO | 8.63 | 0.16 | 1881 | WELDED |  | 1350 | 250 | YES | 24 | 1741 | 0 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | LINE MARKERS | NO | NO | JOHNNY L. CAVITT | 9185993795 | THIRD PARTY TILING CONTRACTOR PUNCTURED 8" LINE. A 56' SECTION OF LINE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19950194 | 1995-12-04 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1995-11-01 | 1205 | TX | HARRIS | BAYTOWN | NO |  | NO | BAYTOWN, HARRIS COUNTY, TEXAS; CORNER OF DECKER DRIVE AND BAKER ROAD |  | TANK FARM | TANK |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 425000 | 312115.5638 | 629663.1607 | GASOLINE | 1 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES | LIGHTING STRIKE | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON NOVEMBER 1, 1995 AT APPROXIMATELY 1205 HOURS, LIGHTING STRUCK A BREAKOUT STORAGE TANK AT TEPPCO'S BAYTOWN TERMINAL. THE TANK WAS IN UNLEADED GASOLINE SERVICE. IT WAS CONSIDERED TO BE FULL AT THE TIME OF THE INCIDENT, WITH LESS THAN 1,000 BARRELS OF STORAGE SPACE AVAILABLE. THIS TANK IS EQUIPPED WITH AN INTERNAL FLOATING ROOF, WHICH EFFECTIVELY ACTED AS A VAPOR BARRIER AND LIMITEDTHE FIRE TO THE SEAL AREA ONLY. IMMEDIATELY UPON DISCOVERY OF THE FIRE, TERMINAL PERSONNEL BEGAN EMERGENCY PROCEDURES. UPON TEPPCO'S REQUEST, LOCAL MUNICIPAL AND INDUSTRY MUTUAL-AID FIRE FIGHTING UNITS RESPONDED TO THE SCENE. AT APPROXIMATLEY 1500 HOURS THE FIRE WAS EXTINGUISHED. ALL PRODUCT LOSS WAS A RESULT OF BURNING VAPORS WITH NO PRODUCT ESCAPING TO THE GROUND. NO PRODUCT WASSPILLED - 146 BARRELS OF GASOLINE WAS LOST DUE TO COMBUSTION.
2017-09-29 08:50 | YES | NO | 19950195 | 1995-12-04 | 22610 | WILLIAMS PIPELINE CO | YES | 1995-11-08 | 934 | OK | CRAIG |  | NO |  | NO | SOUTHEAST QUARTER OF THE NORTHWEST QUARTER OF SECTION 14, TOWNSHIP 29N, RANGE 20N IN CRAIG COUNTY, OKLAHOMA. |  | LINE PIPE | WELDING FITTING |  | 1929 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 29375.5825 | 59262.4151 | GASOLINE | 3 | 126 | 126 | NO | NO | 12.75 | 0.3 | 30000 | WELDED |  | 750 | 420 | YES | 8 | 968 | 7 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | STEVEN S. BALL | 9185883850 | AT APPROX. 09:37 HOURS ON 11/08/95 A SPILL OCCURRED AT M.P. 178.8 ON THE #3-12" TULSA JCT. HEYWORTH LINE SECTION. APPROX. 126 BARRELS OF N-GRADE WERE RELEASED. WPL MAINTENANCE PERSONNEL WERE EXCAVATING THE PIPELINE IN PREPARATION FOR REPLACEMENT OF A MAINLINE GATE VALVE AT THIS LOCATION WHEN THE BACKHOE STRUCK A 3" TAP AND VALVE WHICH WAS CONNECTED TO THE LINE. THE CONNECTION BETWEEN THE TAP AND THE PIPELINE FAILED RESULTING IN THE SPILL. MAINTENANCE PERSONNEL IMMEDIATELY CONTACTED THE OPERATIONS CONTROL CENTER AND THE PIPELINE OPERATIONS WERE SHUT DOWN. THE OPERATIONS CONTROL CENTER CONTACTED THE SOUTHERN REGION OFFICE AND EMERGENCY RESPONSE PERSONNEL AND EQUIPMENT WERE DISPATCHED TO THE SITE. THE WPL PERSONNEL ON SITE SECURED THE AREA AND UTILIZED EQUIPMENTTHAT WAS ON-SITE TO CONTAIN THE RELEASED PRODUCT. ADDITIONAL RESPONSE PERSONNEL AND EQUIPMENT ARRIVED ON SITE AND RECOVERED 35 BARRELS OF FREE PRODUCT. THE REMAINING PRODUCT WAS REMEDIATED THROUGH SOIL EXCAVATION AND BIO-REMEDIATION TECHNIQUES. ENVIRONMENTAL RESPONSE EFFORTS WERE COORDINATED WITH THE OKLAHOMA CORPORATION COMMISSION.
2017-09-29 08:50 | YES | NO | 19950196 | 1995-12-05 | 2170 | CENEX PIPELINE | YES | 1995-11-05 | 1940 | ND | WARD |  | NO |  | NO | CENEX PIPELINE TERMINAL, 3 MILES WEST OF MINOT, NORTH DAKOTA ON NORTH DAKOTA HIGHWAY 2 AND 52. |  | TANK FARM | OTHER | PRESSURE RELIEF LINE | 1991 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22031.6869 | 44446.8113 | GASOLINE | 3 | 83 | 0 | NO | NO | 1 | 0.13 | 7080 | THREADED |  | 1440 | 1400 | YES | 4 | 1800 | 0 | 91 | NO DATA | Null | Null | NO DATA |  | OTHER | VIBRATION | Null | ONE CALL |  | Null | Null | S. MICHEL STAHLY | 4066285209 | ON NOVEMBER 5, 1995, AT APPROXIMATELY 7:40 P.M. CENTRAL TIME, A STEEL FITTINGON A 1 INCH-DIAMETER PRESSURE RELIEF LINE FAILED DUE TO VIBRATION AT THE CENEX PIPELINE TERMINAL NEAR MINOT, NORTH DAKOTA. THE FAILURE RESULTED IN THE DISCHARGE OF A FINE SPRAY OF UNLEADED GASOLINE INTO THE AIR. A SOUTHWESTERLY WIND PREVAILED AT THE TIME, WHICH CAUSED A MIST OF GASOLINE TO BE CARRIED TOWARD THE NORTHEAST AWAY FROM THE SOURCE. WIND-BLOWN GASOLINE WAS DEPOSITED ON THE GROUND IN THE APPROXIMATE LOCATIONS. NO OVERLAND FLOW OF GASOLINE OCCURRED.THE LINE WAS SHUT DOWN, AND THE DISCHARGE ELIMINATED WITHIN APPROXIMATELY 10MINUTES OF THE FAILURE. AN ESTIMATED 2,000 TO 4,000 GALLONS OF UNLEADED GASOLINE WAS RELEASED DURING THE INCIDENT. UPON NOTIFICATION OF THE RELEASE, CENEX EMPLOYEES WERE DISPATCHED TO THE SITE. THEY IMMEDIATELY OPERATED VALVES TOSTOP THE DISCHARGE OF GASOLINE. NOTIFICATIONS WERE GIVEN THROUGH THE 911 SYSTEM, AND TO THE NATIONAL RESPONSE CENTER. LOCAL AND STATE RESOURCES RESPONDINGINCLUDED WARD COUNTY EMERGENCY MANAGEMENT, WARD COUNTY SHERIFF'S OFFICE, MINOT POLICE DEPARTMENT, MINOT RURAL FIRE DEPARTMENT, BURLINGTON RURAL FIRE DEPARTMENT, ND DIVISION OF EMERGENCY MANAGEMENT, ND HIGHWAY PATROL, ND STATE RADIO COMMUNICATION, ND FIRE MARSHALL'S OFFICE, ND DEPARTMENT OF TRANSPORTATION,AND ND STATE HEALTH DEPARTMENT. GROUND RECONNAISSANCE WAS PERFORMED TO INITIALLY EVALUATE THE EXTENT OF THE IMPACTED AREA. AS A SAFETY PRECAUTION, ND HIGHWAY 2 & 52 WAS CLOSED TO TRAFFIC FOR APPROXIMATELY TWO AND ONE-HALF HOURS, AND THE ROAD WAS SANDED. AIR MONITORING WAS CONDUCTED TO VERIFY THE NON-EXISTENCE OF EXPLOSION HAZARD. SOME RESIDENCES WERE TEMPORARILY EVACUATED. THE EXTENT OF IMPACTED SURFACE SOIL WAS DETERMINED ON NOVEMBER 6 AND 7, USING HAND-HELD FIELD PHOTOIONIZATION DETECTOR METHODS. SOIL SAMPLES WERE ALSO COLLECTED ATTHAT TIME FOR LABORATORY ANALYSIS. A LIMITED SOIL REMOVAL IS SCHEDULED FOR NOVEMBER 30, 1995. THE NORTH DAKOTA DEPARTMENT OF HEALTH IS OVERSEEING THE SOIL CLEANUP. THE FAILED LINE HAS BEEN REDESIGNED AND RECONSTRUCTED TO PREVENT FUTURE FAILURE.
2017-09-29 08:50 | YES | NO | 19950197 | 1995-12-07 | 10012 | KANEB PIPELINE CO | YES | 1995-11-08 | 600 | KS | BUTLER |  | NO |  | NO | NW 1/4, SECTION 10, TOWNSHIP 26 SOUTH, RANGE 5 EAST (1624 SUNSET ROAD, EL DORADO, KS 67042) |  | TANK FARM | TANK |  | 1953 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 22031.6869 | 44446.8113 | FUEL OIL | 3 | 452 | 315 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.LEROY ANDERSON | 3162621408 | OPERATOR PERSONNEL INCORRECTLY CALCULATED FILL TIME AND OVERFILLED TANK.
2017-09-29 08:50 | YES | NO | 19950198 | 1995-12-15 | 30903 | ARCO PIPE LINE COMPANY | YES | 1995-11-15 | 1230 | CA | SAN BERNARDINO |  | NO |  | YES | SECTION 28, TOWNSHIP 8 NORTH, RANGE 19 EAST APPROXIMATELY 15 MILES EAST OF ESSEX, CA |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 268000 | 196816.4026 | 397058.1813 | CRUDE OIL | 1 | 80 | 0 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1170 | 335 | YES | 12 | 1463 | 10 | 77 | EXTERNAL | Null | YES | GALVANIC | LOW POTENTIALS | NO DATA |  | Null | NO DATA |  | Null | Null | DAN T. HISEY | 3104289000 | EXTERNAL CORROSION CAUSED PITTING AND A HOLE OF APPROXIMATELY 1/2" DIAMETER,AT THE 6 O'CLOCK POSITION. THE LEAK WAS DISCOVERED BY OUR LINERIDER DURING HIS ROUTINE PATROL OF THE RIGHT-OF-WAY. NO FREE OIL WAS RECOVERED-OIL HAD ABSORBED INTO THE SAND/SOIL AND WILL BE REMOVED FROM THE SITE FOR TREATMENT AND DISPOSAL.
2017-09-29 08:50 | YES | NO | 19950199 | 1995-12-13 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1995-11-12 | 917 | NY | NASSAU |  | NO |  | NO | INWOOD TERMINAL ON HEAD OF BAY, NASSAU COUNTY, NY |  | TANK FARM | TANK |  | 1952 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 88126.7474 | 177787.2454 | TRANSMIX (PART. REFINED PETRO) | 3 | 110 | 102 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL C. LARKIN | 6107704507 | ON NOVEMBER 12, 1995, SHORTLY AFTER 0800, A MANIFOLD VALVE TO TRANSMIX TANK 2WAS INADVERTENTLY OPENED DURING A DELIVERY AS A RESULT OF A PARTIAL POWERLOSS. TRANSMIX TANK 2 ALARM DEVICE WAS INCORRECTLY WIRED AND WAS NOT SET ATTHE CORRECT LEVEL TO PREVENT THE TANK OVERFLOW. IMPROPERLY WIRED ALARM ANDLEVEL SETTING WERE PROPERLY CORRECTED BEFORE TRANSMIX TANK 2 TO SERVICE.ALL APPLICABLE AGENCIES WERE NOTIFIED AND ALL RELEASED PRODUCT WAS CONTAINEHE DIKE AREA. RECOVERY AND CLEANUP ACTIVITIES WERE DONE UNDER THE SUPERVISIONWITHIN THE DIKE AREA. RECOVERY AND CLEANUP ACTIVITIES WERE DONE UNDER THE SOF THE NYDEC, THE NASSAU COUNTY FIRE MARSHALL, AND THE OWNER OF THE TRANSMIX,SUPERVISION OF THE NYDEC, THE NASSAU COUNTY FIRE MARSHALL, AND THE OWNER OFTHE TANK, STAR ENTERPRISE.
2017-09-29 08:50 | YES | NO | 19950200 | 1995-12-12 | 809 | ARCO PIPE LINE CO | YES | 1995-11-27 | 1750 | TX | GAINES |  | NO |  | NO | 8 MI E OF NM/TX STATE LINE ON HWY 180 TURN N ON FM 3306 AND GO APPROX. 3 MI TURN W ON GRAVEL RD & PROCEED TO ARCO ROF, TURN LEFT ON ROF & GO APPROX. 1/4 MILE |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11015.8434 | 22223.4057 | CRUDE OIL | 1 | 278 | 210 | NO | NO | 6 | 0.28 | 24000 | WELDED |  | 770 | 225 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | LARRY E. GRAVES | 7134574054 | DOZER WAS CLEARING BRUSH FROM PASTURE LAND. WHILE MOVING FROM ONE AREA TO ANOTHER HE PROCEEDED OVER AN ELEVATED AREA. WHEN HE WENT OVER THE ELEVATED AREA, THE DOZER BLADE TILTED DOWNWARD INTO THE SOIL CAUSING THE BLADE TO STRIKE THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19950201 | 1995-12-12 | 4906 | EXXON PIPELINE CO | YES | 1995-11-15 | 1810 | TX | TITUS | MOUNT PLEASANT | NO |  | NO | GO N TO MT.PLEASENT ON HWY.271 TURN W ON CTY RD 43 CROSS RR TRACKS, TURN R ON DR GO 1/4 MI TURN LEFTINTO PASTURE,GO 300 YRD TURN LEFT GO TO P/L ROW SITE IS ON L |  | LINE PIPE | PIPE |  | 1936 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 11015.8434 | 22223.4057 | CRUDE OIL | 1 | 385 | 380 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 570 | 170 | YES | 8 | 713 | 12 | 93 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | G.G. PERSYN | 7136565521 | DAMAGE BY OUTSIDE FORCES (3RD PARTY). LANDOWNER WAS CLEARING PROPERTY WHEN THE PIPELINE WAS STRUCK BY A GRADER. THE PIPELINE PUMPS WERE SHUT IN AND EPC DISPATCHED IT'S OIL SPILL RESPONSE TEAM TO THE SITE. THE CRUDE OIL WAS CONTAINED IN THE AREA OF THE DAMAGED PIPE BY BERMS WHERE IT WAS RECOVERED BY EPC. THE DAMAGED SECTION OF PIPE BY BERMS WHERE IT WAS RECOVERED BY EPC. THE DAMAGEDSECTION OF PIPE WAS REPLACED. THERE WERE NO INJURIES OR EXPLOSIONS AS A RESULT OF THIS EVENT. NRC REPORT NO. 314369.
2017-09-29 08:50 | YES | NO | 19950202 | 1995-12-12 | 9175 | JAYHAWK PIPELINE CORP | NO | 1995-11-20 | 1215 | KS | RUSSELL |  | NO |  | NO | SE 1/4, SECTION 30, TOWNSHIP 15 SOUTH, RANGE 13 WEST OF RUSSELL COUNTY, KANSAS, 6 MILES EAST OF MILBERGER |  | LINE PIPE | PIPE |  | 1938 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | CRUDE OIL | 1 | 150 | 145 | NO | NO | 6.63 | 0.19 | 1986 | WELDED |  | 50 | 0 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419271 | THIS GATHERING LINE DELIVERS OIL INTO JAYHAWK'S TRAPP STATION. THE LINE SPANSSELLENS CREEK. JAYHAWK RECEIVED A TELEPHONE CALL FROM KAW PIPELINE'S GAUGER SAYING WE HAD A LEAK ON SELLENS CREEK. JAYHAWK PERSONNEL IMMEDIATELY RESPONDED TO THIS LOCATION AND CLAMPED OFF THE LEAK. A VACUUM TRUCK WAS SENT TO THE SPILL SITE AND CLEAN-UP OPERATION COMMENCED. AFTER CLEAN-UP, JAYHAWK WILL REPAIR THE LINE AND INSTALL CORROSION COUPONS TO MONITOR INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19950203 | 1995-12-15 | 4805 | EXPLORER PIPELINE CO | YES | 1995-11-17 | 1509 | TX | HARRIS | PASADENA | NO |  | NO | JEFFERSON AND BEARL STREET, PASADENA, TEXAS |  | PUMPING STATION | VALVE |  | 1971 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 33047.5303 | 66670.217 | JET FUEL | 3 | 230 | 217 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.W. FLEMING | 9184935112 | AT 1509 ON NOVEMBER 17, 1995 EXPLORER'S PASADENA STATION TERMINAL OPERATOR INITIATED A START-UP OF THE 28" PIPELINE SYSTEM ORIGINATING JET FUEL FROM LOCAL TERMINAL TANKAGE TO EXPLORER'S HOUSTON PUMP STATION. DURING START UP, A PUMP UNIT SEAL FAILURE ALARM AND SUMP HIGH LEVEL ALARM SAFETY DEVICES CAUSED THEPUMP UNITS TO SHUT DOWN AT 1514. THE TERMINAL OPERATOR ON DUTY MADE A VISUALINSPECTION OF THE STATIONS GROUND AREA AND FOUND THE UNDERGROUND SUMP TANK HAD OVERFLOWED JET FUEL. THE TERMINAL OPERATOR INITIATED EXPLORER'S EMERGENCY RESPONSE CASCADE SYSTEM OF NOTIFICATION AND INSTALLED PLYWOOD BARRIERS AND SORBENT BOOMS IN THE STREET DITCHES ADJACENT TO THE STATION TO PREVENT FURTHER MIGRATION OF THE PRODUCT. MAINTENANCE CONTRACTORS, VACUUM TRUCKS, AND EMTECH ENVIRONMENTAL SERVICES CONTRACTOR WERE DISPATCHED TO THE SITE FOR CLEAN-UP.FEDERAL AND STATE AGENCIES WERE NOTIFIED AS REQUIRED. INITIAL CLEAN-UP WAS COMPLETED AND THE STATION RESTARTED BY 0258 ON NOVEMBER 18, 1995. IT WAS DETERMINED THAT THE SUMP TANK OVERFLOW OCCURRED AS A RESULT OF TWO UNDERGROUND 4" STATION/PUMP DRAIN VALVES CONNECTED TO THE SUMP THAT HAD BEEN OPENED FOR A MAINTENANCE WORK THE PREVIOUS DAY AND NOT COMPLETELY RECLOSED, ALLOWING RAPID FLOWINTO THE SUMP DURING START-UP. WIRING MODIFICATIONS TO THE HIGH SUMP LEVEL SWITCH WERE MADE TO INITIATE CLOSURE OF ALL MANIFOLD VALVES TO IN ADDITION TO PUMP UNIT SHUTDOWN. THIS WILL PREVENT GRAVITY FLOW INTO THE SUMP FOLLOWING A HIGH SUMP LEVEL ALARM.
2017-09-29 08:50 | YES | NO | 19950204 | 1995-12-18 | 4906 | EXXON PIPELINE CO | YES | 1995-11-20 | 1600 | TX | LIBERTY | HULL | NO |  | NO | LIBERTY COUNTY, BETWEEN SOUR LAKE AND HULL STATIONS, IN ISOLATED AREA. IN DAISETTA, TEXAS, TAKE RIGHT ON 834 TO HULL. AT RR TRACKS, TURN RIGHT, AND PARALLEL THE |  | LINE PIPE | PIPE |  | 1917 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 110158.4343 | 222234.0567 | CRUDE OIL | 1 | 40 | 39 | NO | NO | 8 | 0.32 | 25000 | THREADED |  | 496 | 300 | YES | 8 | 620 | 9 | 85 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | NO | G.G. PERSYN | 7136565521 | THIRD PARTY ON HORSEBACK REPORTED LEAK; SYSTEM SHUT-IN AT TIME LEAK REPORTED. EPC PERSONNEL RESPONDED, DETERMINED LOCATION OF LEAK, PLACED BOOM TO PREVENT SPREAD OF CRUDE- CRUDE WAS CONFINED TO BAR DITCH AND SURROUNDING ROW. CLEANUP AND REPAIRS HAVE BEEN COMPLETED. NRC REPORTED NO.314885.
2017-09-29 08:50 | NO | NO | 19950205 | 1995-12-18 | 10313 | KOCH PIPELINE INC | NO | 1995-11-13 | 1600 | OK | PAYNE |  | NO |  | NO | SPILL CONTAINED ALL ON KOCH PROPERTY NE 1/4 SEC 15-17 N-5E PAYNE COUNTY |  | TANK FARM | PIPE |  | 1992 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6572 | 4826.4082 | 9736.8148 | CRUDE OIL | 1 | 45 | 25 | NO | NO | 10 | 0.38 | 24000 | WELDED |  | 40 | 30 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | SCOTT CLARK | 9182256867 | THIS IS A RELIEF LINE, ONLY IN THE EVENT THAT A PRESSURE RELIEF VALVES OPENSWILL THERE BE FLOW, THEREFORE FLUID IS STATIC AND PRESSURE IS APPROX. 40 TANK HEAD PRESSURE.
2017-09-29 08:50 | YES | NO | 19950206 | 1995-12-15 | 19536 | TOTAL PIPELINE CORP | YES | 1995-11-18 | 1130 | OK | MURRAY | WYNNEWOOD | NO |  | NO | TRACT OF LAND IN THE 1/2 OF THE NW 26-T2N-R1E MURRAY COUNTY, OKLAHOMA |  | TANK FARM | VALVE |  | 1975 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 2 | 2242 | 1287 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL JOHN COOPER | 4052291638 | ON SATURDAY, NOVEMBER 18, 1995, AT APPROXIMATELY 11:30 AM, STATION OPERATORDISCOVERED LOW SULFUR DIESEL FUEL IN THE DIKE AROUND TANK 101 AT WYNNEWOODSTATION. WYNNEWOOD STATION IS A PRODUCT TERMINAL LOCATED ON THE SOUTH SIDE OFWYNNEWOOD OK. IT IS USED TO STORE AND PUMP REFINED PRODUCTS INTO THE WILLIAMSPIPELINE SYSTEM. THE STATION HAS TWO 90,000 BARREL STORAGE TANKS EACH OF THETANK HAS AN EXTERNAL FLOATING ROOF AND IS 116' IN DIAMETER BY 48' HIGH. TANK101 (THE WEST TANK) HAD PREVIOUSLY BEEN TAKEN OUT OF SERVICE TO REPLACE THESUCTION NOZZLE WITH A DIFFERENT DESIGN. THE OLD SUCTION NOZZLE WAS CAUSINGMOISTURE FROM THE BOTTOM OF THE TANK TO BE ENTRAINED IN THE PRODUCT AS IT WASPUMPED FROM THE TANK. THE OLD SUCTION NOZZLE WAS RELACED WITH A DIFFUSER INORDER TO ELIMINATE THIS PROBLEM. WHILE THE TANK WAS OUT OF SERVICE, IT WASALSO CLEANED, A SECONDARY SEAL WAS INSTALLED ON THE FLOATING ROOF, AND THEROOF DRAIN WAS CHECKED FOR LEAKAGE (NONE FOUND). ON NOV 15, OPERATORPERSONNEL WERE SENT TO THE STATION TO RE-INSTALL THE MANWAY PLATE AND TOINSTALL A FILTER DRUM. THE PLAN WAS TO TRANSFER DIESEL FUEL FROM TANK 102 (THEEAST TANK) TO TANK 101 AND THE FILTER WOULD REMOVE SUSPENDED PARTICLES FROMTHE DIESEL DURING THE TRANSFER. ON THE MORNING OF NOV 17, OPERATOR PERSONNELWERE SENT TO THE SITE TO VACUUM THE SUMP TANK AND STARTED THE PRODUCT TRANSFERAROUND 9:30AM. OPERATOR PERSONNEL WERE TOLD TO STAY AT THE SITE TO CHECK FORLEAKS AND TO ENSURE THAT THE TRANSFER WAS PROGRESSING SMOOTHLY. STATIONOPERATOR WAS REQUESTED TO MAKE PERIODIC STATION CHECKS ON THE TRANSFER. THEPRIMARY EMPHASIS BEING ON THE TRANSFER PUMP, FILTER DRUM, AND HOSES FORLEAKAGE. A CHECK WAS MADE AT 3 PM ON NOV 17 AND FOUND THE PACKING ON THETRANSFER PUMP WAS LEAKING. HE TIGHTENED THE PACKING AND STOPPED THE LEAK.ADDITIONAL CHECKS WERE MADE BY THE STATION OPERATOR AT 9:00 THAT EVENING ANDAGAIN AT 3:30AM AND 11:30AM THE NEXT DAY. THE SPILL WAS DISCOVERED DURING THE11:30AM CHECK. UPON DISCOVERY OF THE SPILL, THE STATION OPERATOR FOUND THESOURCE TO BE THE WATER DRAW VALVE ON THE SOUTHWEST SIDE OF TANK 101. THISVALVE WAS OPEN. HE IMMEDIATELY CLOSED THE VALVE AND SHUT OFF THE PRODUCTTRANSFER PUMP. THE TANK VALVES USED FOR THE TRANSFER WERE CLOSED AND THETANKS ISOLATED. THE DENVER PIPELINE CONTROL CENTER WAS THEN NOTIFIED AND ACALL WAS MADE TO EMERGENCY PERSONNEL FOR SPILL RESPONSE ASSISTANCE. THEDIVISION RESPONSE TEAM ARRIVED AT THE SITE AT 1:15 PM, 1:25 PM AND 1:45PMRESPECTIVELY. THE FIRST VACUUM TRUCK ARRIVED AROUND 1:30PM WITH THE SECONDONE ARRIVING AROUND 4:00PM. A TOTAL TRANSPORT ARRIVED ABOUT 3 PM. TOTAL'SVACUUM TRUCK ARRIVED ABOUT 6PM. A SITE ASSESSMENT WAS DONE UPON ARRIVAL TOENSURE SAFE WORKING CONDITIONS BEFORE CLEANUP EFFORTS WERE STARTED. THENNOTIFICATIONS WERE MADE TO THE PROPER AUTHORITIES. ALL FREE PRODUCT WAS THENPICKED UP WITH THE VACUUM TRUCKS.
2017-09-29 08:50 | NO | NO | 19950207 | 1995-12-19 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1995-11-17 | 1445 | IL | WILL |  | NO |  | NO | 1.5 MILES NORTH OF ROUTE 7, 200 YARDS EAST OF PARKER ROAD |  | LINE PIPE | PIPE |  | 1968 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | CRUDE OIL | 1 | 10 | 9 | NO | NO | 34 | 0.28 | 52000 | WELDED |  | 619 | 110 | YES | 24 | 628 | 10 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.G. SANDALL | 2187250102 | A LANDOWNER OBSERVED A PATCH OF CRUDE OIL ON THE GROUND AND TELEPHONEDLAKEHEAD. THE LINE WAS SHUTDOWN AND ONCE THE LEAK WAS CONFIRMED, THEEMERGENCY RESPO NSE CREW WAS MOBILIZED TO THE SITE. A BERM WAS BUILTDOWNSTREAM OF THE LINE F OR CONTAINMENT. EXCAVATION ENABLED THE CREW TO LOCATETHE LEAK. NON-DESTRUCTI VE TESTING WAS DONE ON THE JOINT OF PIPE. A PLIDCOSPLIT SLEEVE WAS WELDED ON THE PIPE FOR REPAIR. THE LINE WAS RESTORED FOROPERATION. SOIL SAMPLES HAVE BEEN SENT OUT FOR ANALYSIS TO DETERMINE THEPROPER METHOD OF DISPOSAL.
2017-09-29 08:50 | YES | NO | 19950208 | 1995-12-19 | 18273 | SHELL PIPELINE CORP | YES | 1995-11-14 | 620 | MS | HINDS |  | NO |  | NO | CAPLINE 40-INCH (MILE MARKER 168) |  | LINE PIPE | PIPE |  | 1968 | OTHER | DEFORMATION OF PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 66095.0606 | 133340.434 | CRUDE OIL | 1 | 4 | 0 | NO | NO | 40 | 0.31 | 52000 | WELDED |  | 560 | 476 | YES | 24 | 732 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132
2017-09-29 08:50 | YES | YES | 19950209 | 1995-12-19 | 18273 | SHELL PIPELINE CORP | YES | 1995-12-01 | 1300 | TX | UPTON | MCCAMEY | NO |  | NO | MCCAMEY TANK FARM |  | TANK FARM | PIPE |  | 1936 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 3 | 0 | 3 | 2 | 0 | 2 | 40000 | 29375.5825 | 59262.4151 | NOT GIVEN | 1 | 0 | 0 | YES | YES | 10 | 0 | 0 | WELDED |  | 275 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | UNDER INVESTIGATION | Null | NO DATA |  | Null | Null | J.M. KORPAL | 7132410132 | CONTRACTOR EMPLOYEES WERE IN THE PROCESS OF REPLACING A PAIR OF 10-INCH ANSI300# FLANGES WITH A PAIR OF 10-INCH ANSI 150# FLANGES IN ORDER TO REPLACEVALVE. C206. AN EXPLOSION AND FIRE OCCURRED DURING THIS WORK. THE CAUSE OFTHE INCIDENT IS UNDER INVESTIGATION. SUPPLEMENTAL REPORT 12/26/1995 INDICATESA CHANGE IN INJURIES FROM 3 TO 2, AND A CHANGE IN FATALITIES FROM 2 TO 3. THISSUPPLEMENTAL REPORT DID NOT INDICATE AN UPDATED COMMODITY SPILLED.
2017-09-29 08:50 | YES | NO | 19950210 | 1995-12-27 | 15156 | SINCLAIR PIPELINE CO | NO | 1995-11-22 | 615 | WY | NATRONA |  | NO |  | NO | NATRONA COUNTY, SECTIN 34, TOWNSHIP 34 N,RANGE 80 W. NEAR THE INTERSECTION OF ROBERTSON AND ZERO RD. IN MILLS, WYOMING. |  | TANK FARM | PUMP |  | 1978 | OTHER | SEAL LEAK MOTOR FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7343.8956 | 14815.6038 | CRUDE OIL | 1 | 2 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DON K. NEUWERTH | 3073283549 | SINCLAIR'S PIPELINE CONTROL CENTER EXPERIENCED A SHUTDOWN OF ALL PUMPING EQUIPMENT AT 06:15 AND AT 06:31 RECEIVED A CALL FROM PLATTE PIPELINE STATING THAT THERE WAS A FIRE NEAR SINCLAIR'S CASPER TANKAGE. SINCLAIR OPERATIONS AND MAINTENANCE PERSONNEL ASSISTED THE NATRONA COUNTY FIRE DEPARTMENT BY SHUTING VALVES TO CONTROL THE ESCAPE OF CRUDE OIL AND AT 07:30 THE FIRE DEPARTMENT EXTINGUISHED THE FIRE. THE CONDITION OF THE LOWER BEARING HOUSING OF THE PUMP MOTOR INDICATES THAT THE BEARING FAILED AND THE MOTOR CONTINUED TO ROTATE FOR ASIGNIFICANT LENGTH OF TIME. FROM THIS WE THEORIZE THAT THE BEARING FAILED CAUSING A SEAL LEAK AND THE ESCAPING CRUDE OIL WAS IGNITED BY A SPARI FROM METAL-TO-METAL CONTACT IN THE FAILED BEARING. THE FIRE IS ESTIMATED TO HAVE BURNEDFOR ABOUT 1.5 HOURS CONSUMING 1 BARREL OF CRUDE OIL. ANOTHER 1 BARREL WAS ESTIMATED TO HAVE SPILLED OIL WAS RECOVERED
2017-09-29 08:50 | YES | NO | 19950211 | 1995-12-27 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1995-09-11 | 1200 | WI | CHIPPEWA |  | NO |  | NO | SHELDON STATION, COUNTY ROAD V,1 MILE SOUTH OF THE TOWN OF SHELDON |  | PUMPING STATION | VALVE |  | 1968 | OTHER | LEAKING CHECK VALVE SEAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 55079.2171 | 111117.0284 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. SANDAHL | 2187250102 | APPROXIMATELY 3 BARRELS OF CRUDE OIL WERE RELEASED DUE TO A LEAKING CHECK VALVE ON THE DOWNSTREAM SIDE OF THE STATION'S PRESSURE CONTROL VALVE. FAILURE WAS DUE TO LEAKING CHECK VALVE SEAL. THE 3 BARRELS WERE RECOVERED IN OIL RECLAIMATION AND DISPOSED OF THROUGH INCINERATION. (DNR APPROVED ASPHALT PLANT). THE CHECK VALVE SEALS WERE REPLACED.
2017-09-29 08:50 | YES | NO | 19950212 | 1995-12-27 | 15851 | PRIDE REFINING INC | YES | 1995-11-06 | 1600 | TX | TAYLOR | TYE | NO |  | NO | APPROXIMATELY 2 MILES SOUTH OF TYE, TEXAS ON COUNTY ROAD 310. |  | TANK FARM | TANK |  | 0 | OTHER | TANK BOTTOM FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 500 | 300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON | 9156748231 | AT APPROXIMATELY 8:00 PM WE RECEIVED A CALL FROM ABILENE FIRE DEPARTMENT THATA STRONG CRUDE OIL SMELL WAS COMING FROM THE TYE FACILITY. PERSONNEL WERE DISPATCHED TO CHECK IT OUT. UPON ARRIVAL OUR PERSONNEL DISCOVERED CRUDE OIL WASLEAKING FROM TANK #907. THE TANK WAS THEN ISOLATED AND OIL WAS CONTAINED WITHIN THE FIREWALL. TANK WAS TAKEN OUT OF SERVICE AND THE CONTENTS OF THE TANK WERE REMOVED AND THE OIL WAS PICKED UP. THIS WAS ACCOMPLISHED BY 5:00 PM ON 11/07/95. CLEAN-UP AND TANK REPAIR PLANS ARE BEING DEVELOPED.
2017-09-29 08:50 | YES | NO | 19950213 | 1995-12-27 | 12626 | MOBIL PIPELINE CO - EMPIRE | NO | 1995-11-03 | 1215 | TX | NAVARRO |  | NO |  | NO | APPROX. 2 MI W OF FROST, TX AT MOBIL PIPELINE MI POST 313 LOCATED APPROX. 3/4 MILE SOUTH OF STATE HWY 22 |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 215000 | 157893.7558 | 318535.4813 | NATURAL GAS LIQUID | 2 | 9200 | 0 | NO | NO | 16 | 0.25 | 46000 | WELDED |  | 887 | 500 | YES | 8 | 1111 | 7 | 94 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.G. SCOTT | 2146585914 | A LANDOWNER/TENANT HAD CONTRACTED A DIRT GRADER OPERATOR TO TERRACE HIS COTTON FIELD. THE DIRT GRADER OPERATOR, AT APPROX. 1215HRS. HIT MPLCO'S 16" NGL PIPELINE WITH GRADER BLADE CAUSING A RUPTURE. NO EXPLOSION, FIRE OR INJURIES RESULTED FROM THIS INCIDENT. OPERATIONS CONTROLLER NOTIFIE OF THE LEAK AND IMMEDIATELY SHUT DOWN THE PIPELINE AND NOTIFIED FIELD PERSONNEL. WITHIN 15 MINUTES OF NOTIFICATION, FIELD PERSONNEL WERE ON SITE. MAINLINE BLOCK VALVES WERE CLOSE AND THE LEAK SITE WAS ISOLATED. FIRE DEPARTMENT AND POLICE PERSONNEL WERE ON SITE TO ASSIST WITH AREA MONITORING AND SECCURITY. DUE TO LOCATION OF INCIDENT, AND OTHER FAVORABLE FACTORS, NO PERSONNEL EVACUATIONS WERE NECESSARY. UPON COMPLETION OF A STOPPLE OPERATION, THE ISOLATED SECTION OF PIPELINE WAS DISPLACED WITH NITROGEN AND THE ESCAPING NGL WAS ELIMINATED. PERMANENT REPAIRS WERE COMPLETED AT 1830 HOURS ON NOV 4, 1995 AND THE PIPELINE WAS BACK IN SERVICE AND FULLY OPERATIONAL AT 0400 HRS ON NOV 5, 1995
2017-09-29 08:50 | YES | NO | 19950214 | 1995-12-27 | 10319 | KOCH GATHERING SYSTEMS INC | YES | 1995-12-08 | 1540 | MT | FALLON |  | NO |  | NO | NWSW SEC3 58E 7IN FALLON COUNTY, NH |  | TANK FARM | TANK |  | 1971 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1805 | 1325.5732 | 2674.2165 | CRUDE OIL | 1 | 366 | 365 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | FRANK RAFFAELL | 7015652296 | THE WIND CHILL FACTOR WAS - 40F, AND FROZE THE VAREC GUAGE. THIS GUAGE CONTROLS THE ALARM AND THE START/STOP SWITCH ON THE PUMP. THE PUMP DID NOT START AND THE ALARM DID NOT FUNCTION CAUSING THE TANK TO OVERFILL.
2017-09-29 08:50 | YES | NO | 19960001 | 1996-01-02 | 2552 | COLONIAL PIPELINE CO | YES | 1995-11-24 | 206 | LA | EAST FELICIANA |  | NO |  | NO | SEE ATTACHED MAP |  | TANK FARM | OTHER | OIL CAN PUMP VENT | 1972 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14687.7912 | 29631.2076 | FUEL OIL | 3 | 54 | 45 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | ON NOVEMBER 24, 1995, AT 0915 CST, DURING A ROUTINE YARD CHECK, A COMPANY EMPLOYEE AT BATON ROUGE INJECTION DISCOVERED FUEL OIL LEAKING FROM A BROKEN SIGHT GLASS LOCATED ON A VENT LINE IN THE STATION MANIFOLD. THE TIME OF THE INCIDENT IS LISTED AS 0206 EST ON THE 24TH, THE COMPLETION TIME OF THE LAST OIL BATCH PUMPED OUT OF THE TANK FARM. THE EMPLOYEE WAS ABLE TO STOP THE LEAK BY CLOSING A VALVE ON THE VENT LINE UPSTREAM OF THE SIGHT GLASS. RECOVERY OPERATION BEGAN AT 0945 CST VACUUM PUMPS AND ABSORBENT PADS WERE USED TO CONTAIN ANDRECOVER ALL VISIBLE PRODUCT LOCATED IN THE MANIFOLD AREA. STAINED GRAVEL ANDCONTAMINATED SOIL HAVE BEEN STOCKPILED IN PLASTIC SHEETING AND WILL BE REMEDIATED AT A LATER DATE. AT 1200 CST, WHEN IT WAS DETERMINED THAT THE LEAK PROBABLY MET THE CRITERIA OF A DOT REPORTABLE SPILL, THE NATIONAL RESPONSE CENTERWAS NOTIFIED (REPORT NO. 315167). THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY WAS ALSO NOTIFIED OF THE INCIDENT AT 1720 CST ON NOVEMBER 24TH. AN INVESTIGATION CONTINUES INTO THE CAUSE OF THE INCIDENT. AN AMENDED 7000-1 REPORTWILL BE FILED UPON COMPLETION OF THE INVESTIGATION. SUPPLEMENTAL REPORTSUBMITTED 2/6/1996 STATED THAT AN INVESTIGATION REVEALED THAT THE FOLLOWINGCIRCUMSTANCES CONTRIBUTED TO THE INCIDENT: 1 - NORMAL PRACTICES CALL FOR THE3/4 INCH INLET VALVE ON THIS VENT PIPING BE CLOSED AND THE 3/4 INCH OUTLETVALVE LEFT OPEN DURING OPERATION OF THE CAN PUMP. THESE VALVES WEREINADVERTENTLY LEFT IN THE REVERSE POSITION, IE. THE INLET VALVE WAS OPEN ANDTHE OUTLET VALVE WAS CLOSED. 2 - THE SIGHTGLASS ON THIS DRAIN LINE IS NOTDESIGNED TO SEE THE SYSTEM OPERATING PRESSURE THAT THIS CAN PUMP DISCHARGES.THIS SIGHTGLASS ON THIS OIL VENT LINE AS WELL AS THE SIGHTGLASS ON THE GASVENT PIPING HAS BEEN REMOVED AS A RESULT OF THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 19960002 | 1996-01-16 | 809 | ARCO PIPE LINE CO | YES | 1995-12-12 | 1205 | CA | SAN BERNARDINO |  | NO |  | YES | SECTION 28, TOWNSHIP 8 NORTH, RANGE 19 EAST APPROXIMATELY 15 MILES EAST OF ESSEX, CA |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 80782.8518 | 162971.6416 | CRUDE OIL | 1 | 5 | 5 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1170 | 125 | YES | 12 | 1463 | 10 | 77 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAN T. HISEY | 3104289000 | OUR CONTRACTORS WERE IN THE PROCESS OF PREPARING THE PIPE FOR NEW COATING. WHILE SANDBLASTING THE METAL AT A PITTED AREA, THE BLASTING MEDIA WENT THROUGHTHE PIPE AND 5 BARRELS OF OIL LEAKED OUT. THE PIPELINE WAS NOT RUNNING AT THE TIME.
2017-09-29 08:50 | YES | NO | 19960003 | 1996-01-16 | 12628 | MOBIL PIPELINE CO | YES | 1995-10-12 | 1130 | PA | CARBON | TOWEMESING | NO |  | NO | RELEASE OCCURRED APPROXIMATELY 50 FEET NORTH OF PIPELINE'S INTERSECTION WITH STATION STREET, PLEASE REFER TO ATTACHED MAP |  | LINE PIPE | VALVE |  | 1980 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36719.4781 | 74078.0189 | GASOLINE | 2 | 13 | 13 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM R. DURHAM II | 6092245057 | TWO (2) COMPANY EMPLOYEES WERE INSPECTING, PACKING AND LUBRICATING A MAINLINE VALVE AT MP 62.37 (CARBON VALVE). THE LINE WAS SHUT DOWN BUT UNDER APPROXIMATELY 330 PSI. DURING THE MAINTENANCE ACTIVITY, A 1/2" FITTING OPPOSITE THE PACKING GLAND WAS ERRONEOUSLY REMOVED. THIRTEEN (13) BARRELS OF UNLEADED GASOLINE WERE RELEASED BEFORE THE FITTING WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19960004 | 1996-01-17 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1995-12-10 | 2250 | NY | CAYUGA |  | NO |  | NO |  |  | PUMPING STATION | SCRAPER TRAP |  | 1953 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 44063.3737 | 88893.6227 | FUEL OIL | 3 | 229 | 224 | NO | NO | 16 | 0.5 | 2190 | WELDED |  | 1250 | 1060 | YES | 24 | 1865 | 9 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL C. LARKIN | 6107704507 | WITHIN AUBURN STATION ON DECEMBER 10, 1995, AT 2250 HOURS THE 16" SCRAPER TRAP ON THE INCOMING 14" MAIN LINE PIPELINE SYSTEM FAILED WHILE DELIVERING #2 FUEL OIL INTO WORKING TANK NO. 318. THE FAILURE OCCURRED AT THE BUTT WELD JOINING THE END OF THE SCRAPER TRAP BARREL TO THE "UNIBOLT" SCRAPER TRAP DOOR CLOSURE. THE SCRAPER TRAP BARREL HAS BEEN SENT TO AN OUTSIDE AGENCY FOR FAILURE ANALYSIS EVALUATION. ALL APPLICABLE AGENCIES WERE NOTIFIED AND ALL RELEASED #2 FUEL OIL WAS CONTAINED ON THE AUBURN STATION PROPERTY. ALMOST ALL RELEASED FUEL OIL FLOWED TO THE AUBURN STATION SURFACE WATER COLLECTION POND FACILITAING PROMPT PRODUCT RECOVERY ACTIVITY. RECOVERY AND CLEANUP ACTIVITIES WERE DONE UNDER THE SUPERVISION OF THE SENNETT FIRE DEPARTMENT, CAYUGA COUNTY EMERGENCY SERVICES AND NEW YORK STATE PUBLIC UTILITY COMMISSION.
2017-09-29 08:50 | YES | NO | 19960005 | 1996-01-17 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1995-12-15 | 1330 | NJ | UNION |  | NO |  | NO |  |  | TANK FARM | TANK |  | 1955 | OTHER | TANK ROOF DRAIN SYSTEM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 6609.5061 | 13334.0434 | GASOLINE | 3 | 77 | 75 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL C. LARKIN | 6107704507 | ON DECEMBER 15, 1995, COMPANY MAINTENANCE PERSONNEL WERE DRAINING RAIN WATERFROM THE OPEN TOP FLOATING ROOF OF TANK NO. 101. A GASKET FAILURE WITHIN THETANK. THE ROOF WATER DRAINING ACTIVITY WAS IMMEDIATELY TERMINATED TO MITIGATE THE RELEASE OF GASOLINE PRODUCT. ALL APPLICABLE AGENCIES WERE NOTIFIED AND ALL RELEASED GASOLINE PRODUCT WAS CONTAINED WITHIN THE TANK DIKE. RECOVERY AND CLEANUP ACTIVITIES WERE DONE UNDER THE SUPERVISION OF THE LINDEN FIRE DEPARTMENT, MIDDLESEX COUNTY HAZMAT, AND NEW JERSEY DEP.
2017-09-29 08:50 | YES | NO | 19960006 | 1996-01-17 | 10313 | KOCH PIPELINE INC | YES | 1995-12-21 | 1600 | IA | POLK | ALTOONA | NO |  | NO | SEC 2 T 79N R23W, POLK COUNTY, IOWA |  | LINE PIPE | GIRTH |  | 1981 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 62423.1128 | 125932.6321 | CRUDE OIL | 3 | 21 | 21 | NO | NO | 24 | 0.28 | 60000 | WELDED |  | 978 | 740 | YES | 8 | 1223 | 8 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARC S. DEVARENNES | 5734865488 | RECEIVED REPORT FROM KOCH PIPELINE COMPANY L.P. EMPLOYEE. LINE WAS SHUT DOWN- SECTION ISOLATED - SECITON EXCAVATED. FAILURE DETERMINED TO BE IN HEAT AFFECTED ZONE OF GIRTH WELD. REPAIR CLAMP INSTALLED AND LINE BACK IN SERVICE 12/22/95 AT 1940 HOURS. SOIL HAULED TO APPROVED LAND FILL.
2017-09-29 08:50 | NO | NO | 19960007 | 1996-01-19 | 2170 | CENEX PIPELINE | YES | 1995-12-11 | 1537 | MT | YELLOWSTONE | LAUREL | NO |  | NO | ON CENEX REFINERY PROPERTY, APPROX..5 MI EAST OF STATE HWY 212 SOUTH, AND .5 MI SOUTH OF INTERSTATE 90. |  | LINE PIPE | PIPE |  | 1985 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14687.7912 | 29631.2076 | GASOLINE | 3 | 15 | 0 | NO | NO | 8 | 0.32 | 42000 | WELDED |  | 1440 | 374 | YES | 8 | 1900 | 5 | 85 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | YES | S. MICHEL STAHLY | 4066285209 | ON DECEMBER 11, 1995 AT APPROXIMATELY 3:37 P.M. MOUNTAIN TIME, A CONTRACTOR INSTALLING A FIBER OPTICS COMMUNICATION CABLE ON CENEX REFINERY PROPERTY IN LAUREL, MONTANA HIT AN 8"-DIAMETER PETROLEUM PRODUCTS PIPELINE OWNED AND OPERATED BY CENEX PIPELINE, INC. THE IMPACT OF THE EXCAVATION IMPLEMENT CAUSED THE STEEL PIPE TO RUPTURE, RELEASING UNLEADED GASOLINE TO THE GROUND. THE PRECISEQUANTITY OF GASOLINE RELEASED COULD NOT BE DETERMINED, BUT DID NOT EXCEED 15BARRELS (630 GALLONS). THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (FEDERAL GOVERNMENT), THE MONTANA DEPARTMENT OF ENVIRONMENTAL QUALITY, AND THE YELLOWSTONE COUNTY DISASTER AND EMERGENCY SERVICES. THE LOSS OF PIPELINE PRESSURE RESULTING FROM THE RUPTURE WAS IMMEDIATELY DETECTED AT THE PIPELINE CONTROL CENTER IN LAUREL, MONTANA, AND THE PIPELINE WAS SHUT DOWN IN 40 SECONDS. ALL OF THE RELEASED GASOLINE SOAKED INTO THE GRAVEL SOILS, AND WAS NOTRECOVERABLE IN LIQUID FORM. APPROXIMATELY 300 CUBIC YARDS OF IMPACTED SOIL WAS EXCAVATED FROM THE SITE FOR REMOVAL TO A LANDFARM TREATMENT FACILITY. THE EXCAVATION WAS BACKFILLED WITH SOIL FROM THE REFINERY PROPERTY.
2017-09-29 08:50 | YES | NO | 19960008 | 1996-01-18 | 443 | AMOCO PIPELINE CO | NO | 1995-12-16 | 1010 | IL |  |  | YES | LAT.281'9.1" LONG.93 59'1 | NO |  |  | LINE PIPE | BOLTED FITTING |  | 1979 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 146877.9124 | 296312.0756 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 6.63 | 0.38 | 35000 | FLANGED |  | 2160 | 0 | YES | 8 | 2700 | 0 | 79 | NO DATA | Null | Null | NO DATA |  | OTHER | POSSIBLE ANCHOR JACK-UP | Null | NO DATA |  | Null | Null | HOWARD B. SPALDING | 4099483407 | AT 1010 ON 12/16/95 PERSONNEL ON TEXACO PRODUCTION PLATFORM HI-548 OBSERVED BLOSSOMS AND A SMALL SHEEN ON THE WATER SURFACE NEAR PLATFORM HI-548. AMOCO PIPELINE SHUT THE AFFECTED SYSTEM IN AND DISPATCHED CAL DIVE TO ISOLATE AND INSPECT THE LEAKING PIPELINE. THE PIPELINE WAS INSPECTED FOR DAMAGE AND INSPECTION REVEALED NO DAMAGE TO THE PIPELINE. SOURCE OF LEAK IS ASSUMED TO BE A FLANGE (LAT.28 DEGREES 01' 9.1" LONG. 93 DEGREES 59' 19.3") ON THE CHECK VALVE APPROACHING THE RISER ON HI-548. SINCE THIS SECTION OF LINE IS NOT CURRENTLY ACTIVE THIS 2.13 MILE SECTION OF PIPELINE HAS BEEN DISCONNECTED AND BLINDED OFF AT THE SUBSEA TIE-IN. DURING THE ISOLATION PROCESS A VERY SMALL LEAK WAS DISCOVERED ON A FLANGE DOWNSTREAM OF THE ISOLATED SECTION. THIS LEAK WAS REPAIRED BY REPLACING THE "O" RING IN THE FLANGE (LAT.28 DEGREES 01'7.6" LONG. 93 DEGREES 57'14.5") AND SUBSEQUENTLY INSPECTED DURING STARTUP OF THE SYSTEM WITH NO EVIDENCE OF LEAKING. JUST PRIOR TO THIS EVENT A JACK-UP RIG WAS IN THE VICINITY OF THE PIPELINE AND HIS HAD SEVERAL MARINE VESSELS ANCHORING AROUND IT. IN ADDITION THIS JACK-UP RIG HAD MOVED OFF LOCATION THE NIGHT PRIOR TO THIS EVENT.
2017-09-29 08:50 | YES | NO | 19960009 | 1996-01-22 | 2387 | CITGO PIPELINE CO | YES | 1995-12-19 | 845 | TX | HARDIN | SOUR LAKE | NO |  | NO | 1.5 MILES NORTH OF HWY 105 ON FANNIN STREET INSIDE TEXACO TANK FARM. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3671.9478 | 7407.8019 | CRUDE OIL | 1 | 55 | 55 | NO | NO | 12.75 | 0.25 | 42000 | WELDED |  | 720 | 305 | YES | 8 | 988 | 0 | 90 | EXTERNAL | Null | YES | GALVANIC | COATING DAMAGED | DAMAGE BY OTHERS | COATING DAMAGED IN LEAK | Null | ONE CALL |  | Null | Null | JIM SANDERS | 9184954786 | AT APPROXIMATELY 8:45 A.M. ON THE 19TH OF DECEMBER 1995 CITGO EMPLOYEE RICK DAVIS WAS DRIVING THROUGH TEXACO PIPELINE COMPANY'S TANK FARM WHEN HE SPOTTEDOIL FLOATING ON TOP OF WATER INSIDE A DIKE AREA NEAR OUR 12" PIPELINE. HE CALLED THE CONTROL CENTER IN TULSA TO REPORT A POSSIBLE LEAK. THE CONTROL CENTER REPORTED THAT THE LINE WAS NOT IN OPERATION. HE GAVE INSTRUCTION NOT TO OPERATE THE LINE UNTIL WE COULD INSPECT THE PIPE IN AREA OF DIKE. OIL AND WATERWAS REMOVED WITH A VACUUM TRUCK AND LINE WAS EXPOSED. HOLE CAUSED BY EXTERNAL CORROSION WAS FOUND ON THE TOP 1/4 OF PIPE AT 2:00. COATING IN PIT AREA WASDAMAGED. LINE WAS CLAMPED ON DECEMBER 19TH AND PERMANENTLAY REPAIRED WITH FULL ENCIRCLEMENT SLEEVE ON DECEMBER 28, 1995.
2017-09-29 08:50 | YES | NO | 19960010 | 1996-01-18 | 26127 | CHEVRON PIPELINE CO | NO | 1996-01-09 | 1553 | CA | KINGS | KETTLEMAN CITY | NO |  | NO | APPROX 1 MILE EAST OF INTERSTATE 5 & .5 MILE NORTH OF HWY 145 RELEASE OCCURRED IN FARMLAND, M.P. 28.8 OF KLM PIPELINE SYSTEM. SECTION 31, T18S./R16E |  | LINE PIPE | PIPE |  | 1989 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 180237.8774 | 363612.5997 | CRUDE OIL | 1 | 4987 | 0 | NO | NO | 18 | 0.25 | 52000 | WELDED |  | 1030 | 1000 | YES | 4 | 1285 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | M.H. TEISSERE | 8053923351 | FARMER HIT PIPELINE WHILE USING RIPPER IN HIS FIELD. INCIDENT IS CURRENTLY UNDER INVESTIGATION. CPL WILL UPDATE YOUR OFFICE UPON COMPLETEION OF INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19960011 | 1996-01-18 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1996-01-02 | 843 | CA | LOS ANGELES | CARSON | NO |  | NO | WATSON TERMINAL TANK FARM LOCATED AT 20410S. WILMINGTON BOULEVARD, LONG BEACH, CA 90810 TANK FARM, TANK W-11 |  | TANK FARM | TANK |  | 1971 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 144190.3019 | 290890.0797 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | DURING ROUTINE INSPECTION OF TANK FARM, A LEAK WAS DISCOVERED AT THE BASE OFBREAKOUT TANK W-11. SETTLEMENT AROUND BURIED TANK FILL/DRAIN VALVE PROJECTEDSTRESS CRACK TO BOTTOM PLATE WELD VIA A STEEL BRACE. THE BRACE CONNECTS THE FLOOR PLATE TO THE TANK FILL PIPE. THE TANK WAS TAKEN OUT OF SERVICE, INSPECTED AND IS CURRENTLY BEING REPAIRED.
2017-09-29 08:50 | NO | NO | 19960012 | 1996-01-24 | 30753 | VK-MAIN PASS GATHERING COMPANY,LLC | NO | 1995-12-30 | 1130 | LA | OFFSHORE |  | YES | 29 DER 15.382 88 DEG 29.2 | NO |  |  | LINE PIPE | OTHER | BREAKAWAY SAFETY JOINT | 1995 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CONDENSATE | 1 | 4 | 0 | NO | NO | 10 | 0.5 | 3000 | OTHER |  | 1440 | 800 | YES | 8 | 1800 | 9 | 95 | NO DATA | Null | Null | NO DATA |  | OTHER | NOT YET DETERMINED | Null | OTHER | NOT GIVEN | Null | Null | JOHN LOCANTRO | 7132247400
2017-09-29 08:50 | YES | NO | 19960013 | 1996-01-26 | 809 | ARCO PIPE LINE CO | YES | 1996-01-15 | 940 | OK | CARTER |  | NO |  | NO | 2 MILES S. OF POOLVILLE, OK ON ST HWY. 74 (GRAVEL AND 1.5 MI W. ON COUNTY RD, N.SIDE. SECTION 9 TOWNSHIP 2 S. RANGE 2 W. LATITUDE 34 23' 39",LONGITUDE 97 25'02" |  | PUMPING STATION | BOLTED FITTING |  | 1991 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14419.0302 | 29089.008 | CRUDE OIL | 1 | 60 | 53 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GLENN W. HOFFMEYER | 4052735151 | AT APPROXIMATELY 09:40 AM ON MONDAY JANUARY 15, 1996 A CONNECTING COMPANY PATROL PILOT OBSERVED A LEAK AT ARCO PIPELINE COMPANY'S (APL) POOL STATION IN CARTER COUNTY, OKLAHOMA. THE PILOT SUBSEQUENTLY REPORTED THE OBSERVATION TO APL PERSONNEL AT OUR RINGLING STATION, APPROXIMATELY 20 MILES TO THE SOUTH. APLFIRST RESPONDER PERFORMED A LEAK SITE HAZARD EVALUATION AND DETERMINED THAT A GASKET HAD FAILED IN A BOLTED FLANGE BETWEEN A 12 INCH CHECK VALVE AND A CLOSED VALVE IMMEDIATELY DOWNSTREAM. STEPS WERE TAKEN TO ISOLATE AND CONTAIN THE LEAK WITHIN THE STATION PROPERTY. OF THE APPROXIMATELY 60 BARRELS SPILLED, 53 BARRELS WERE RECOVERED AND RETURNED TO THE SYSTEM. CONTAMINATED SOIL WAS EXCAVATED AND STOCK-PILED FOR FUTURE REMEDIATION. INVESTIGATION OF THE INCIDENT DETERMINED THAT A CLOSED VALVE DOWNSTREAM OF THE CHECK VALVE CREATED AN ISOLATED SECTION CONTAINING CRUDE OIL. SINCE THE SYSTEM WAS NOT INOPERATION AT THE TIME OF THE INCIDENT, IT IS BELIEVED THAT A FLUCTUATION IN TEMPERATURE FROM SINGLE DIGIT TO ABO E 70 DEGREES RESULTED IN EXPANSION OF THE CRUDE OIL SUFFICIENT TO CAUSE THE GASKET FAILURE. STEPS TAKEN TO PREVENT REOCCURENCE OF THIS INCIDENT INCLUDE INSTALLATION OF A RELIEF VALVE BETWEEN THE CHECK AND THE VALVE AND A REVIEW OF EXISTING FACILITIES TO DETERMIN IF OTHER LOCATION CONTAIN PIPING CONFIGURATION POSING SIMILAR RISKS.
2017-09-29 08:50 | YES | NO | 19960014 | 1996-01-30 | 443 | AMOCO PIPELINE CO | YES | 1995-12-25 | 1530 | TX | PALO PINTO |  | NO |  | NO | .5 MILES SOUTH OF GRAFORD, TEXAS ON F.M. HWY 4 |  | LINE PIPE | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 260000 | 190941.2861 | 385205.6983 | CRUDE OIL | 1 | 300 | 290 | YES | NO | 8 | 0.32 | 15950 | NO DATA |  | 512 | 170 | YES | 24 | 641 | 7 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | FRED E. HESSER | 9184913567 | IT IS BELIEVED EXTENDED DROUGHT CONDITITONS ALLOWED THE GROUND TO SHIFT CAUSING A COLLAR JOINT FAILURE IN THE PIPELINE SYSTEM. THE LEAK WAS ISOLATED BY CLOSING THE UPSTREAM AND DOWNSTREAM BLOCK VALVES. WHILE PIPELINE REPLACEMENT REPAIRS WERE BEING MADE IT IS BELIEVED VAPORS TRAPPED IN THE GROUND SURFACE WERE IGNITED. THE FIRE WAS EXTINGUISHED, ALL OBSERVABLE OIL RECOVERED, AND THE AFFECTED AREA IS BEING REMEDIATED. LINE REPLACEMENT REPAIRS WERE COMPLETED.
2017-09-29 08:50 | YES | NO | 19960015 | 1996-01-30 | 443 | AMOCO PIPELINE CO | YES | 1995-12-30 | 1715 | TX | PALO PINTO |  | NO |  | NO | 6 MILES NORTH OF PALO PINTO, TEXAS ON F.M. HWY 4 WEST .5 MILE AT MILE POST 36.37 ON THE RANGER-GRAFORD LINE SEGMENT. |  | LINE PIPE | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 44063.3737 | 88893.6227 | CRUDE OIL | 1 | 100 | 60 | NO | NO | 8 | 0.32 | 15950 | THREADED |  | 512 | 170 | YES | 24 | 641 | 7 | 75 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | FRED E. HESSER | 9184913567 | IT IS BELIEVED EXTENDED DROUGHT CONDITIONS ALLOWED THE GROUND TO SHIFT CAUSING A COLLAR JOINT FAILURE IN THE PIPELINE SYSTEM. THE LINE LEAK WAS ISOLATED BY CLOSING THE UPSTREAM AND DOWNSTREAM BLOCK VALVES. OBSERVABLE OIL WAS RECOVERED WITH VACUUM TRUCKS, LINE REPLACEMENT REPAIRS MADE, AND THE AREA IS BEINGREMEDIATED.
2017-09-29 08:50 | YES | NO | 19960016 | 1996-02-07 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | NO | 1996-01-03 | 400 | TX | UPTON |  | NO |  | NO | FOUR (4) MILES WEST OF MCCAMEY, TEXAS ON U.S. HWY.385 TURN NORTH AT TEXACO LEASE SIGN FOR .1 MILE. STATION IS ON THE LEFT. |  | PUMPING STATION | OTHER | METER ST. RELIEF VALVVE | 1985 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | OTHER | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CARBON DIOXIDE | 3 | 95 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | ICING OF RELIEF VALVE | Null | NO DATA |  | Null | Null | EDWARD A. FANT | 7138537891 | AT APPROXIMATELY 04:45 HOURS ON JANUARY 3, 1996, PERSONNEL IN ENRON'S HOUSTON CONTROL CENTER NOTICED A PRESSURE DROP AT OUR DENVER CITY STATION WHICH IS ON THE NORTH END OF THE SYSTEM. LOCAL PERSONNEL WERE DISPATCHED TO INVESTIGATE. AT APPROXIMATELY 08:15 HOURS THE CONTROL CENTER WAS NOTIFIED BY OUR CUSTOMER'S REPRESENTATIVE THAT A RELIEF VALVE AT OUR MCCAMEY METER STATION, WHICH IS ON THE SOUTH END OF THE SYSTEM, WAS BLOWING CARBON DIOXIDE TO THE ATMOSPHERE. AN ENRON EMPLOYEE ARRIVED AT THE STATION AT 09:00 HOURS AND ISOLATED THE RELIEF VALVE, THEREBY STOPPING THE ESCAPE OF CARBON DIOXIDE. SUBSEQUENT CALCULATION DETERMINED THAT APPROXIMATELY 95 BARRELS OF CARBON DIOXIDE ESCAPED TO THE ATMOSPHERE. THERE WERE NO DEATHS, INJURIES OR PROPERTY DAMAGE ASSOCIATED WITH THIS RELEASE.
2017-09-29 08:50 | NO | NO | 19960017 | 1996-02-07 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1996-01-04 | 1230 | CA | LOS ANGELES | INDUSTRY | NO |  | NO | CORNER NOGALES AVENUE AND VALLEY BOULEVARD, CITY OF INDUSTRY, CALIFORNIA LS 108, 24-INCH BLOCK VALVE |  | LINE PIPE | VALVE |  | 1985 | OTHER | BLOCK VALVE LEAK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 28838.0604 | 58178.0159 | JET FUEL | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | A LEAK FROM A 24" VALVE BONNET WAS DISCOVERED BY A SFPP CONTRACTOR DURING INSTALLATION OF A "PIG" LAUNCHER AND RECEIVER ASSEMBLY. VALVE WAS REPAIRED AND TESTED FOR RETURN TO SERVICE.
2017-09-29 08:50 | NO | NO | 19960018 | 1996-02-02 | 25169 | SOUTH CAROLINA PIPELINE CORP | NO | 1996-01-20 | 1230 | SC | LANCASTER | LANCASTER | NO |  | NO | ON PIPELINE RIGHT-OF-WAY, APPROXIMATELY 300 YEARS SOUTH OF GRACE AVENUE ROAD CROSSING |  | LINE PIPE | PIPE |  | 1978 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 39652.333 | 79994.7719 | L. P. G. | 2 | 1 | 0 | NO | NO | 6.63 | 0.22 | 2777 | WELDED |  | 1440 | 350 | YES | 24 | 2180 | 6 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | JOHN TROY BLALOCK | 8036995811 | ON JANUARY 20, 1996, AT APPROXIMATELY 12:30 P.M., A LEAK ON THE PIPELINE WAS DISCOVERED. IT WAS DETERMINED THAT THE LEAK WAS CAUSED BY DAMAGE INFLICTED BYA MACHINE CLEARING BRUSH ALONG THE RIGHT-OF-WAY.
2017-09-29 08:50 | NO | NO | 19960019 | 1996-02-06 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | NO | 1995-12-31 | 1656 | OK | GARFIELD |  | NO |  | NO | CHAINING STATION 526 + 94 TULSA DELIVERY LINE SW 12, T24N, R6W GARFIELD COUNTY OKLAHOMA |  | LINE PIPE | OTHER | NOT GIVEN | 1972 | OUTSIDE FORCE DAMAGE | CORROSION, EXTERNAL | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 16156.5704 | 32594.3283 | GASOLINE | 2 | 0 | 0 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1440 | 1236 | YES | 24 | 2750 | 7 | 72 | EXTERNAL | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | CONTRACTOR AWARENESS PRG. | NO | NO | DAVID KILIAN | 4053952377 | AN EXTERNAL CORROSION LEAK OCCURRED DUE THE EXCAVATION ACTIVITY OF THE LANDOWNER. PART D COMMENTS: LINE WAS DAMAGED BY AN EXCAVATOR AND AN ASSUMPTION IS MADE THAT A CORROSION CELL DEVELOPED.
2017-09-29 08:50 | YES | NO | 19960020 | 1996-02-16 | 18718 | SUN PIPELINE CO | NO | 1996-01-09 | 1430 | OK | MCCLAIN |  | NO |  | NO | NW SEC 35-6N-3W - MCCLAIN |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2162.8545 | 4363.3512 | CRUDE OIL | 1 | 140 | 135 | NO | NO | 6 | 0.16 | 1120 | WELDED |  | 575 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | PIPE ANALYSIS PENDING | NO DATA |  | Null | NO DATA |  | Null | Null | EDITH F. COEN | 9185866942
2017-09-29 08:50 | YES | NO | 19960021 | 1996-02-20 | 19536 | TOTAL PIPELINE CORP | NO | 1996-01-23 | 1020 | MI | ISABELLA | TOWNSHIP OF LINCOLN | NO |  | NO | N/W .25 OF N/W .25 SECTION 4 T-13-N R4W LINCOLN TWP. ISABELLA CO. |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 32442.8179 | 65450.2679 | CRUDE OIL | 1 | 200 | 160 | NO | NO | 8 | 0.28 | 30000 | WELDED |  | 800 | 415 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | OTHER | STILL UNDER INVESTIGATION | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL D. MARTIN | 5177739978 | A PINHOLE DEVELOPED IN THE PIPE CAUSING CRUDE OIL TO LEAK INTO A PLOWED FIELD. THE 8" LINE WAS LOCATED IN FARMING LAND OUTSIDE OF THE CITY OF MT. PLEASANT, MICHIGAN. A DEFINITIVE CAUSE OF THE CORROSION IS UNKNOWN AT THIS TIME. THESECITON OF PIPE WILL BE REMOVED AND TESTS CONDUCTED ON THAT SECTION. TO DETERMINE CAUSE, EMERGENCY RESPONSE CREWS OF TOTAL PIPELINE CORPORATION RESPONDEDAND RECOVERED ALL FREE PETROLEUM. ADDITIONAL REMEDIATION CONTINUED WITH REMOVAL OF CONTAMINATED EARTH, FOLLOWING APPROVED DISPOSAL PROCEDURES. THIS INCIDENT WAS REPORTED TO MICHIGAN DEPARTMENT OF ENVIRONMENTAL QUALITY, ENVIRONMENTAL RESPONSE DIVIDSION. THEIR FIELD INVESTIGATOR HAS VISITED SITE, AND WE ARE CONTINUING TO WORK WITH THAT AGENCY TOWARD FINAL REMEDIATION.
2017-09-29 08:50 | YES | NO | 19960022 | 1996-02-20 | 15263 | PENNZOIL EXPLORATION & PRODUCTION CO | NO | 1996-01-29 | 955 | LA |  |  | YES | 91 41' 04.2" 28 13' 35.9" | NO | EUGENE ISLAND BLOCK 330 OCS-G 02115, 100 YARDS WEST OF "C" PLATFORM |  | LINE PIPE | BOLTED FITTING |  | 1972 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 100933.2113 | 203623.0558 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 14 | 0 | 52000 | FLANGED |  | 1440 | 1100 | YES | 24 | 1850 |  | 94 | NO DATA | Null | Null | NO DATA |  | OTHER | VIBRATION | Null | NO DATA |  | Null | Null | RICHARD MYERS | 3182694369 | ON JANUARY 29, 1996 IT WAS REPORTED BY KEN MURDOCK TO TORPHY AVANT THAT HE SAW OIL BUBBLES COMING UP 100 YEARS WEST OF "C" PLATFORM. THERE WAS LIGHT SLICK 20' WIDE BY 1 MI. LONG. APPROXIMATELY 1 TO 2 GALS. AT 0955 HRS. FRANCIS BROUSSARD CALL ME (RICHARD MYERS) AND REPORTED THE FINDINGS. AT 1005 I CALLED KEN MURDOCK AND TOLD HIM TO COMMENCE SHUTTING IN ALL OF THE PENZOIL'S PLATFORMSTHAT WERE TIED INTO BONITO PIPELINE. THEN I CALLED ALL OUTSIDE OPERATORS TO SHUT IN. AT 1007 HRS I NOTIFIED MIKE AT SHIP SHOAL 28 (SHELL PIPELINE) THAT WE WERE SHUTTING IN BONITO DUE TO A POSSIBLE LEAK. NOTIFICATION: 1039 HRS - MMS1045HRS NRC, 1052 HRS- MSO 1056 HRS-MMS. A DIVE BOAT (GP4) WAS PICKED UP BY BONITO AND WAS LOADED WITH PROPERT DIVING EQUIPMENT. TIME OF DEPARTURE WAS AT1800 HRS FROM AMILA, LA. ON JANUARY 30, 1996 THE DIVE BOAT GP4 ARRIVED 0600 HRS. AT LOCATION. WHILE AT LOCATION THE GP4 COMMENCE SETTING ANCHORS. IN MEANTIME FRANK TORRES WAS BROUGHT UP TO DATE OF WHAT HAS HAPPEN AND WHAT WAS TO BE EXPECTED. WHAT OCCURRED WAS THE LINE WAS PRESSURED UP WHILE DIVER WAS IN WATER, HE REPORTED SEEING BUBBLES LEAKING FROM THE 2ND AREA OF A 14" BALL VALVE LOCATED 4' FROM THE BASE OF THE 330 "S" RISER ON BONITO PIPELINE. THE LINE WAS SHUT IN AND PRESSURE BLED OFF. JUMPED ANOTHER DIVER AND TIGHTEN UP FLANGES TO 1100 LB. TORQUE. PRESSURED UP THE LINE TO 1440 PSI, LET PRESSURE SETTLE DOWN, HELD AT 1400 PSI. JUMPED DIVER, HE REPORTED NO MORE BUBBLES. A SECOND DIVER JUMP, ALSO INDICATED NO LEAK. PRESSURE WAS BLED OFF AGAIN AND ALL VALVESOPEN. CALLED ALL PLATFORMS AND SAID THEY COULD COME BACK ON LINE. ON JANUARY31, 1996 AT 0600 HRS. DAN JAMES (FIELD FOREMEN) REPORTED HE SPOTTED BUBBLESCOMING UP AGAIN. HE SAID THEY WERE SMALL AND ONLY COMING UP EVERY 30 TO 40 SECONDS. JUMPED DIVER AND HE REPORTED HE COULD NOT SEE ANY BUBBLES COMING UP ANYWHERE AROUND FLANGE. SAID IT COULD BE FROM RESIDUAL THAT MAY BE ON GULF FLOOR OR IN SAND BAGS. REPORTED THIS TO MMS (FRANK TORRES). HE SAID THAT WAS POSSIBLE AND GAVE PERMISSION TO COME BACK ON LINE.
2017-09-29 08:50 | YES | NO | 19960023 | 1996-02-16 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1996-01-12 | 1330 | OK | GARFIELD |  | NO |  | NO | SE/4 SEC. 33, TOWNSHIP 21 NORTH, RANGE 5 WEST FROM PIONEER SCHOOL IN DOUGLAS, OK 1 MILE SOUTH, 3 MILE EAST, 1 MILE SOUTH AND 1/4 WEST |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 720.9515 | 1454.4504 | CRUDE OIL | 1 | 297 | 0 | NO | NO | 8 | 0.16 | 1094 | WELDED |  | 500 | 16 | YES | 24 | 1190 | 5 | 78 | INTERNAL | Null | YES | OTHER | SRB | NO DATA |  | Null | NO DATA |  | Null | Null | EDITH F COEN | 9185866942
2017-09-29 08:50 | YES | NO | 19960024 | 1996-02-16 | 12434 | MID - CONTINENT PIPELINE CO | NO | 1996-01-24 | 1430 | OK | GARFIELD |  | NO |  | NO | NW/4 SEC 2, TOWNSHIP 21 NORTH, RANGE 6 WEST FROM THE CORNER OF MARKET AND 42ND STREET, 4.5 MILES SOUTH OF ENID, OKLAHOMA |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 360.4758 | 727.2252 | CRUDE OIL | 1 | 150 | 0 | NO | NO | 8 | 0.16 | 1094 | WELDED |  | 500 | 0 | YES | 24 | 1190 | 5 | 78 | INTERNAL | Null | YES | OTHER | SRB | NO DATA |  | Null | NO DATA |  | Null | Null | EDITH F. COEN | 9185866942
2017-09-29 08:50 | YES | NO | 19960025 | 1996-02-12 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1996-01-12 | 1545 | TX | HARRIS | BAYTOWN | NO |  | NO | DECKER ROAD AT BAKER ROAD |  | TANK FARM | PIPE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4325.7091 | 8726.7024 | FUEL OIL | 3 | 190 | 187 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON JANUARY 12, 1996, MAINTENANCE PERSONNEL WERE IN THE PROCESS OF MODIFYING PIPING IN A TANK MANIFOLD AT THE BAYTOWN TERMINAL. TO MAKE THE MODIFICATIONS,THE MANIFOLD HAD BEEN DRAINED OF PRODUCT AND TAKEN OUT OF SERVICE. A PORTIONOF THE MANIFOLD WAS RETURNED TO SERVICE PIPING WAS INADVERTANTLY LEFT OPEN. THIS ALLOWED FUEL OIL TO ENTER THE OUT OF SERVICE PIPING AND ESCAPE INTO THE EXCAVATED AREA AROUND THE MANIFOLD. UPON DISCOVERY, OPERATIONS PERSONNEL IMMEDIATELY STOPPED PRODUCT MOVEMENT THROUGH THE MANIFOLD, WHICH IN TURN STOPPED THE RELEASE. 187 BARRELS OF FUEL OIL WAS RECOVERED AND PLACED INTO AN ADJACENT STORAGE TANK. APPROXIMATELY 3 BARRELS OF PRODUCT WERE ABSORBED INTO THE SOIL IN THE EXCAVATED AREA AND TREATMENT OR DISPOSAL OPTIONS ARE CURRENTLY BEINGEVALUATED.
2017-09-29 08:50 | YES | NO | 19960026 | 1996-02-27 | 18386 | BP OIL PIPELINE CO | YES | 1996-02-04 | 1130 | OH | ALLEN | LIMA | NO |  | NO | AT APPROXIMATELY 1101 BUCKEYE ROAD, LIMA OHIO |  | LINE PIPE | PIPE |  | 1968 | OTHER | STRESS CRACK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 720.9515 | 1454.4504 | CRUDE OIL | 1 | 180 | 180 | NO | NO | 2 | 0.15 | 40000 | THREADED |  | 275 | 30 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.A. DEBROCK | 2165862003 | A 2" PIPE FITTING (NIPPLE) THAT WAS ATTACHED TO A 12" MAIN LINE CRUDE PIPELINE AT THE LIMA METER STATION CRACKED AND RELEASED 180 BARRELS OF CRUDE OIL. THE OIL FLOWED APPROXIMATELY 300 FEET ON THE GROUND SURFACE AND ENTERED A STORM SEWER DRAIN. THE OIL TRAVELLED 1600 FEET THROUGH AN 8"/12" STORM SEWER TO AN OUTFALL LOCATION AND INTO A DRAINAGE DITCH AND MOVED 550 FEET DOWNSTREAM INTHE DITCH. ALL FREE OIL WAS PICKED UP BY 02/05/96 AND THE STAINED SOIL WAS REMOVED FOR DISPOSAL. THE 2" FITTING WAS REPLACED WITH AN EXTRA HEAVY FITTING ON 02/04/96.
2017-09-29 08:50 | YES | NO | 19960027 | 1996-03-02 | 15681 | PLATTE PIPE LINE CO | YES | 1996-02-02 | 1100 | MO | CHARITON |  | NO |  | NO | SECTION 8, T53N,R17W,CHARITON COUNTY, MO SALISBURY STATION - 3 MI. WEST ON HWY 24 SALISBURY, MO 65281 |  | PUMPING STATION | PIPE |  | 1952 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 138842 | 100098.3495 | 201938.8022 | CRUDE OIL | 1 | 235 | 220 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER SR | 4194213201 | STATION PERSONNEL NOTICED CRUDE OIL ON THE GROUND IN THE TANK MANIFOLD AREA ON 02/02/96. THE STATION WAS SHUT-IN AND VALVES CLOSED TO ISOLATE THE SOURCE.AN EXCAVATION WAS STARTED IN THE AREA OF THE STAINED GROUND, HOWEVER, SEVERECOLD (-20 DEGREES F) AND GROUND FROST HAMPERED THE RAPID LOCATION OF THE LEAK. THE AMOUNT OF CRUDE RELEASED WAS ESTIMATED AT 5 BARRELS. ON 02/03/96, EXCAVATION WAS CONTINUED AND A TANK LINE IN THE IMMEDIATE AREA OF THE OBSERVED CRUDE OIL WAS EXCAVATED, BUT THERE WAS NO VISIBLE LEAKAGE FOUND.STATION PERSONNEL THEN BEGAN TO PRESSURED UP VARIOUS TANK LINES IN AN ATTEMPT TO LOCATE THE SOURCE OF THE STAIN. IN THE AFTERNOON OF 02/03/96, A LEAK WAS FOUND COMING FROM AN INACTIVE 6" PIPE WHICH WAS ATTACHED TO THE TANK 803 TANK LINE. THE INACTIVE 6" PIPE WAS REMOVED FROM THE TANK LINE, THE TANK LINE REPAIRED, AND THE EXCAVATION WAS BACKFILLED WITH CLEAN MATERIAL. DURING THE PROCESS OF IDENTIFYING THE SOURCE OF THE STAIN, AND IN DRINING DOWN THE TANK LINE FOR REPAIR, AND ADDITIONAL 220-230 BARRELS OF CRUDE OIL WERE RELEASED. 220 BARRELS OF CRUDEOIL WERE RECOVERED IMMEDIATELY FROM THE EXCAVATION USING VACUUM TRUCKS AND RETURNED TO THE TANK. NO CRUDE OIL WAS RELEASED BEYOND THE EXCAVATION AREA, WHICH WAS TOTALLY CONFINED WITHIN THE STATION PROPERTY. ALL OF THE CRUDE OIL CONTAMINATED SOIL WAS REMOVED FROM THE SITE AND PROPERLY DISPOSED. THE NATIONALRESPONSE CENTER WAS NOTIFIED OF THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 19960028 | 1996-02-22 | 19226 | TEXACO PIPELINE INC | YES | 1996-02-20 | 230 | MT | FALLON |  | NO |  | NO | SE CORNER OF NW1/4 OF SEC.5, TWP.9N,RGE.60E GO NORTH OF BAKER, MT ON HWY 7 FOR 14 MI, TURN RIGHT ON OLLIE RD GO 1 MI.,TURN RIGHT ON SEC. LINE REL.SITE 1/2 MILE. |  | LINE PIPE | OTHER | NOT GIVEN | 1981 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 3244.2818 | 6545.0268 | CRUDE OIL | 1 | 85 | 55 | NO | NO | 10 | 0.22 | 2176 | WELDED |  | 1440 | 50 | YES | 8 | 0 | 0 | 81 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GARY QUINN | 4066873304 | FALLON COUNTY ROAD CREW WAS MINING GRAVEL FROM A OPEN PIT AND HIT OUR PIPELINE WITH THE RIPPER TEETH ON A DOZER. THE OPERATOR USED EXISTING EQUIPMENT TO PUSH A DIKE AROUND THE LEAK SITE. THE DIKED ARED IS ABOUT 100' X 100' AND THELEAK CONTAMINATED ONLY ABOUT HALF OF THE INSIDE AREA. THE SYSTEM WAS SHUT DOWN IMMEDIATELY UPON NOTIFICATION AND THE DAMAGED PORTION OF LINE WAS ISOLATEDUSING EXISTING BLOCK VALVES. ABOUT 85 BBLS. OF SWEET CRUDE WAS DISCHARGED WITH 55 BBLS. BEING RECOVERED. CONTAMINATED SOIL BEING REMOVED TO APPROVED BIO-REMEDIATION SITE. LINE WAS MARKED AND EXCAVATOR DID NOT USE ONE-CALL FOR LINELOCATE.
2017-09-29 08:50 | YES | NO | 19960029 | 1996-03-05 | 1044 | WESTTEX 66 PIPELINE CO | YES | 1996-02-05 | 1245 | TX | WALLER |  | NO |  | NO | BROOKSHIRE STATION - BENEDUM-SWEENY LINE - MP 381-36+65 NE/4 OF SE/4 OF SEC. 77, H&TC R.R. A-156 2 MILES EAST OF BROOKSHIRE, TX |  | PUMPING STATION | VALVE |  | 1994 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 720.9515 | 1454.4504 | NATURAL GAS LIQUID | 2 | 15 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS | 9186616267 | THERMAL RELIEF DEVICE ON PUMP DISCHARGE BLOCK VALVE FAILED.
2017-09-29 08:50 | YES | NO | 19960030 | 1996-03-08 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1996-02-06 | 1645 | CA | CONTRA COSTA | RODEO | NO |  | NO | MARSHY AREA OWNED BY WICKLAND OIL COMPANY MP 27 SOUTHERN PACIFIC RAIL ROAD (TRACY LINE) 2/10 MILE EAST FROM UNOCAL REFINERY. |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 720951.5096 | 1454450.3986 | GASOLINE | 3 | 5 | 0 | NO | NO | 8 | 0.19 | 46000 | WELDED |  | 1440 | 757 | YES | 8 | 1800 | 4 | 85 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 2134867720 | A SMALL CORROSION LEAK ON THE BURIED PIPELINE ALLOWED PRODUCT TO MIGRATE UPWARDS INTO A SMALL MARSH AREA AND ADJACENT TO SELBY POND. THE PRODUCT SHEEN THAT FORMED ON TOP OF THE POND WAS NOTICED BY WORKERS AT A N ADJACENT REFINERY.SFPP WAS NOTIFIED, SHUTDOWN AND REPAIRED THE PIPE WITH A SLEEVE.
2017-09-29 08:50 | YES | NO | 19960031 | 1996-03-04 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1996-02-03 | 740 | OH | BUTLER | MIDDLETOWN | NO |  | NO | 3590 YANKEE ROAD, MIDDLETOWN, OHIO |  | TANK FARM | VALVE |  | 0 | OTHER | 1" VALVE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1441.903 | 2908.9008 | L. P. G. | 2 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON FEBRUARY 3, 1996 AT APPROXIMATELY 0740 HOURS, EST, A ONE INCH (1") NEEDLEVALVE, USED FOR SAMPLING THE MOISTURE OF PRODUCT OFF A DEHYDRATION TOWER, FAILED AT TEPPCO'S TODHUNTER TERMINAL. THE FAILURE RESULTED IN THE RELEASE OF PROPANE TO THE ATMOSPHERE WHICH WAS IGNITED BY AN UNKNOWN SOURCE. PERSONNEL ON-SITE IMMEDIATELY INITIATED THE EMERGENCY PLAN. THE SAMPLE VALVE WAS ISOLATEDAND THE FIRE ALLOWED TO BURN UNTIL IT SELF EXTINGUISHED. REPLACEMENT OF THE VALVE AND AN ASSOCIATED PRESSURE GAUGE WAS ACCOMPLISHED, THE PIPE WAS PRESSURE TESTED AND THE UNIT RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19960032 | 1996-03-04 | 13131 | CONOCO INC | YES | 1996-02-08 | 1610 | MO | GREENE |  | NO |  | NO | SE/4, SECTION 18 T30N,R22W GREENE COUNTY, MO |  | LINE PIPE | GIRTH |  | 1930 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 43257.0906 | 87267.0239 | NATURAL GAS LIQUID | 2 | 3000 | 0 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 900 | 685 | YES | 8 | 1133 | 10 | 90 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | VANCE L. WEBB | 4057674845 | ON FEBRUARY 8, 1996, AT 08:12 HRS. CONOCO PIPE LINE'S OIL MOVEMENTS GROUP OBSERVED INDICATIONS OF A POSSIBLE RELEASE ON THE WOOD RIVER NO.1 LINE, IN THE MT. VERNON MISSOURI AREA. THE LINE WAS IMMEDIATELY SHUT DOWN AND MAIN LINE BLOCKVALVES AT MT. VERNON, FAIRGROVE, AND RICHLAND WERE CLOSED TO ISOLATE THE POSSIBLE RELEASE AREA. EMERGENCY RESPONSE PERSONNEL WERE NOTIFIED AND DISPTCHED TO THE AREA. ADDITIONALLY, A PATROL AIRCRAFT WAS DISPATCHED TO FLY THE PIPELINE RIGHT-OF-WAY AND LOOK FOR INDICATIONS OF A RELEASE. BECAUSE OF THE REMOTENESS OF THE RELEASE LOCATIONN IN CONJUNCTION WITH THE PHYSICAL CHARACTERISTICS OF NORMAL BUTANE, (PRODUCT RELEASED) AND LACK OF VISUAL INDICATORS, THE ACTUAL RELEASE SITE WAS VERY DIFFICULT TO ASCERTAIN. THE RELEASE SITE WAS LOCATED AT APPROXIMATELY 16:10 HRS. THE RELEASE APPEARS TO BE THE RESULT OF THE FAILURE OF AN ACETYLENE GIRTH WELD THAT WAS PULLED APART BY THE TREMENDOUS TEMPERATURE VARIATION EXPERIENCED IN THE AREA (FREEZE/THAW). THE DAMAGED SECTION OF LINE WAS REPLACED AND WELD PLACED OVER THE ADJOINING ACETYLENE WELDS.
2017-09-29 08:50 | YES | NO | 19960033 | 1996-03-06 | 15674 | PLANTATION PIPE LINE CO | YES | 1996-02-06 | 815 | GA | HARALSON | BREMEN | NO |  | NO | INCOMING CNF SCRAPER TRAP AREA AT PLANTATION'S BREMEN, GA 30110. NO.A-DOT 62 LEAK SITE-CNF SCRAPER TRAP AREA; BREMEN TANK FARM, BREMEN, GA |  | TANK FARM | OTHER | TUBING FITTING FEEDING | 1986 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5767.6121 | 11635.6032 | DIESEL FUEL | 3 | 85 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC | TRAPPED MOISTURE | NO DATA |  | Null | NO DATA |  | Null | Null | ROY CROOK | 4043645916 | ON THE MORNING OF FEBRUARY 6, 1996, DIESEL FUEL WAS OBSERVED SPRAYING FROM AN AREA NEAR THE CNF INBOUND PIPELINE SCRAPER TRAP WITHIN BREMEN TANK FARM IN BREMEN, GA. AFTER ISOLATING THE AREA, A CORRODED 3/8" CARBON STEEL TUBING FITTING WAS FOUND TO HAVE FAILED. THE TUBING LINE SUPPLIED PRODUCT STREAM TO AN ADJACENT GRAVITOMETER. THE STAINLESS STEEL TUBING UTILIZED CARBON STEEL FITTINGS AND WAS ISULATED TO MINIMIZE THERMAL EFFECTS. THE RELEASED PRODUCT FLOWEDINTO CONCRETE FLUMES AND PIPING LEADING TO THE FACILITY'S CONTAINMENT BASIN WHERE FREE PRODUCT WAS RECOVERED. ALL SIMILAR EQUIPMENT IS IN THE PROCESS OF BEING INSPECTED AND REPAIRED AS NECESSARY.
2017-09-29 08:50 | YES | NO | 19960034 | 1996-03-05 | 15490 | PHILLIPS PIPE LINE CO | YES | 1996-02-05 | 958 | IL | ST CLAIR |  | NO |  | NO | BORGER-E.CHICAGO "GOLD" LINE - MP 690-45+00 SEC.32, T2N,R8W,ST.CLAIR CO., IL 1 MILE SOUTH OF FAIRVIEW HEIGHTS |  | LINE PIPE | LONGITUDINAL WELD |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 144190.3019 | 290890.0797 | DIESEL FUEL | 3 | 461 | 450 | NO | NO | 8.63 | 0.28 | 40000 | WELDED |  | 1100 | 955 | YES | 8 | 1490 | 10 | 90 | EXTERNAL | Null | YES | OTHER | CARBON DIO.INDUCED CORR. | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS | 9186616267 | PIPELINE CONTROLLER OBSERVED PRESSURE FAILURE ALARM AND LOSS OF PRESSURE. THE LINE WAS IMMEDIATELY SHUT DOWN AND BLOCKED. RESPONSE PERSONNEL CONTAINED AND PICKED UP ALL RECOVERABLE DIESEL. CORRODED PIPE JOINT WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19960035 | 1996-03-13 | 7660 | HUNT REFINING CO | NO | 1996-02-09 | 2000 | MS | CLARKE | TOWN OF DESOTO | NO |  | NO | TOWNSHIP 2 N. RANGE 16 E., SECT. 20, APPROXIMATELY 1/2 MILE NORTHEAST OF CLARKE COUNTY ROAD #111. |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 75 | 73 | NO | NO | 8.63 | 0.22 | 42000 | WELDED |  | 1200 | 80 | YES | 24 | 1500 | 0 | 67 | INTERNAL | Null | YES | OTHER | SALT WATER,SPOT PIPELINE | NO DATA |  | Null | NO DATA |  | Null | Null | CAROLL D. PELLEGRIN | 3347716953 | THE SECTION OF PIPELINE THAT DEVELOPED THE LEAK WAS NOT IN OPERATION AT THE TIME OF THE LEAK, HAVING APPROXIMATELY 80 PSI STATIC PRESSURE ON THE LINE. THE LEAK WAS REPORTED TO OUR MELVIN STATION OPERATER AT APPROXIMATELY 2000 ON FEBRUARY 9, 1996. HUNT PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE LEAK AREA.THE LEAK WAS LOCATED WHILE EMERGENCY ACTION WERE BEING TAKEN. THE CRUDE OIL HAD LEAKED INTO A SMALL STREAM, AND BOOMS WERE PUT IN PLACE AHEAD OF THE ESCAPED OIL TO PREVENT FURTHER SPREADING. REQUIRED NOTIFICATIONS WERE MADE AS SOON AS PRACTICAL. THE LEAK WAS DETERMINED BY VISUAL EXAMINATION TO HAVE BEEN CAUSED BY INTERNAL CORROSION. A FULL ENCIRCLEMENT SLEEVE WAS WELDED OVER THE LEAK IN THE PIPE, AND THE PIPE WAS COVERED UP. CLEANUP OPERATIONS CONTINUED UNTIL FEBRUARY 17, UNDER THE SUPERVISION OF MR. ERIC DEAR OF THE MISSISSIPPI DEPARTMENT OF ENVIRONMENTAL QUALITY. AT THIS TIME, THE PIPELINE IS SHUT DOWN, HAVING BEEN PIGGED FREE OF OIL. WE PLAN TO RUN A SMART PIG TO EVALUATE THE CONDITION OF THIS SEGMENT OF PIPELINE. AT THAT TIME, WE WILL MAKE A DETERMINATIONAS TO REPAIR, REPLACE, OR ABANDON THIS PORTION OF THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19960036 | 1996-03-05 | 1044 | WESTTEX 66 PIPELINE CO | YES | 1996-02-07 | 1150 | TX | WALLER |  | NO |  | NO | BROOKSHIRE STATION - BENEDUM -SWEENY LINE-MP 381-36+65 NE/4 OF SE/4OF SEC.77,H&TC RR A-156 2 MILES EAST OF BROOKSHIRE, TX |  | PUMPING STATION | VALVE |  | 1996 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 720.9515 | 1454.4504 | NATURAL GAS LIQUID | 2 | 15 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.R. DUBOIS | 9186616267 | THERMAL RELIEF DEVICE ON DUMP DISCHARGE BLOCK VALVE FAILED TO RESEAT. THERMAL RELIEF SYSTEM REDESIGNED AND REPLACED.
2017-09-29 08:50 | YES | NO | 19960037 | 1996-03-11 | 2731 | CHEVRON PIPELINE CO | YES | 1996-02-05 | 900 | TX | WARD | MONAHANS | NO |  | NO | 3 MILES NORTH OF MONAHANS AT THE CPL TANK FARM. SPILL WAS APPROX. 100 YRDS EAST OF THE TANK FARM FENCE LINE. |  | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12016 | 8662.9533 | 17476.676 | CRUDE OIL | 1 | 370 | 340 | NO | NO | 10.75 | 0.37 | 24000 | WELDED |  | 750 | 524 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.J. JASPER | 7133635422 | THE AIR PATROL PILOT CALLED THE SPILL IN TO THE STATION OPERATOR. THE OPERATOR CALLED THE DISPATCHER TO HAVE THE LINE SHUT DOWN THEN WENT TO INVESTIGATE THE SPILL. THE INCIDENT COMMAND SYSTEM WAS IMPLEMENTED FOR THE RESPONSE. FREEOIL WAS VACUUMED UP AND RETURNED TO THE SYSTEM. THE LINE WAS TEMPORARILY CLAMPED WITH PERMANENT REPAIRS SCHEDULED FOR A LATER DATE.
2017-09-29 08:50 | YES | NO | 19960038 | 1996-03-11 | 2552 | COLONIAL PIPELINE CO | YES | 1996-02-06 | 1300 | TN | HAMILTON | CHATTANOOGA | NO |  | NO | 8" LINE #20 STATION 121+48 |  | LINE PIPE | OTHER | NOT GIVEN | 1962 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3783046 | 2727392.7246 | 5502252.7628 | FUEL OIL | 3 | 1750 | 48 | NO | NO | 8.63 | 0.28 | 42000 | WELDED |  | 1942 | 475 | YES | 24 | 1604 | 10 | 1963 |  | Null | Null |  |  | OTHER | ELECTRICAL DISCHARGE CURR | Null |  |  | Null | Null | J.L. GAMBRELL | 4048412402 | AT APPROXIMATELY 1310 EST ON FEBRUARY 6, 1996, A LANDOWNER ON LOOKOUT MOUNTAIN TENNESSEE, REPORTED TO A COLONIAL PIPELINE COMPANY REPRESENTATIVE THAT A PETROLEUM ODOR AND YELLOW STAINS IN THE SNOW WERE PRESENT NEAR THE COMPANY'S LINE 20, AND 8-INCH OD PIPELINE THAT TRAVERSES THE AREA. A COMPANY EMPLOYEE DISPATCHED TO THE AREA ARRIVED AT THE SCENE AT 1355 EST AND CONFIRMED THE PRODUCT WAS LEAKING AT THE DOWNSTREAM END OF A CASED, OVERHEAD CROSSING OF COLONIAL'S 8-INCH LINE THAT IS ADJACENT TO A SMALL SERVICE ROAD. THE ATLANTA CONTROLCENTER WAS NOTIFIED, AND THE LINE WAS IMMEDIATELY SHUT DOWN. AT 1508 EST THENATIONAL RESPONSE CENTER WAS NOTIFIED, REPORT NO. 324453, AND AT 1520 EST THE TENNESSEE EMERGENCY MANAGEMENT AGENCY WAS INFORMED OF THE LEAK. OTHER AGENCIES NOTIFIED INCLUDE THE CHATTANOOGA STORM WATER DIVISION AND LOCAL FIRE AND POLICE DEPARTMENTS. AFTER EXCAVATION OF THE PIPELINE AT THE END OF THE OVERHEAD SPAN, PRODUCT WAS FOUND TO BE ESCAPING FROM 3 SMALL HOLES PENETRATING THROUGH THE BOTTOM OF BOTH THE CASING PIPE AND THE CARRIER PIPE. THE LINE WAS REPAIRED INITIALLY BY INSTALLING A WELDED, SPLIT-SOLE REPAIR SLEEVE OVER THE HOLES AND RESTARTED AT A REDUCED PRESSURE ON FEBRUARY 7, 1996. THE COMPANY CONTINUED TO MONITOR THE LEAK SITE AND WHEN A SMALL AMOUNT OF PRODUCT WAS DETECTEDESCAPING FROM THE END OF THE CASING ON FEBRUARY 9, 1996, THE LINE WAS AGAIN SHUT DOWN TO SEARCH FOR ADDITIONAL LEAKS. THE ENTIRE 120 FOOT SPAN OF CASING AND CARRIER PIPE WAS REMOVED AND INSPECTED. NO ADDITIONAL LEAKS WERE FOUND AND IT WAS DETERMINED THAT THE PRODUCT PROBABLY WAS FROM THE ORIGINAL RELEASE AND HAD BEEN TRAPPED BY ICE DAMS INSIDE THE CASING. REPAIRS TO THE LINE WERE MADE BY INSTALLING APPROXIMATELY 120 FEET OF 8.625-INCH O.D. X.322-INCH W.T. CARRIER PIPE ENCASED IN 12-INCH O.D. CASING PIPE. COLONIAL AGAIN RESTARTED THELINE ON FEBRUARY 10, 1996, AT A REDUCED PRESSURE. A PRELIMINARY INVESTIGATION INDICATES THAT THE CAUSE OF INCIDENT WAS SOME SORT OF ELECTRICAL DISCHARGE CURRENT. AND INVESTIGATION TO DETERMINE THE SOURCE OF THE ELECTRICAL CHARGE CONTINUES AND A SUPPLEMENTAL REPORT WILL BE FILED AT A LATER DATE. IT IS ESTIMATED THAT APPROXIMATELY 1750 BARRELS OF KEROSINE AND FUEL OIL ESCAPED INTO THE ENVIRONMENT. APPROXIMATELY 44 BARRELS OF THE PRODUCT HAVE BEEN RECOVERED AND RETURNED TO THE SYSTEM. THE REMAINING PRODUCT APPARENTLY HAS SEEPED INTO THE FRACTURED ROCK, AND CAVERNS THAT ARE PREVALENT IN THE MOUNTAIN. TO DATE NOPRODUCT HAS BEEN DETECTED IN ANY OF THE STREAMS ON OR NEAR THE MOUNTAIN. ENVIRONMENTAL MONITORING OF THE CAVERNS AND STREAMS CONTINUE.
2017-09-29 08:50 | YES | NO | 19960039 | 1996-03-11 | 4906 | EXXON PIPELINE CO | YES | 1996-02-07 | 900 | TX |  | KILGORE | NO |  | NO | GREEG COUNTY, TX FROM THE INTERSECTION OF HWY 259 & 31 GO W. ON 31 APPROX. 5 MI. TAKE OILFIELD RD AND GO S. ABOUT 1/4 MI TO PIPELINE RIGHT OF WAY TO LEAK SITE. |  | LINE PIPE | PIPE |  | 1931 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 5046.6606 | 10181.1528 | CRUDE OIL | 1 | 233 | 230 | NO | NO | 8 | 0.32 | 30 | WELDED |  | 695 | 480 | YES | 8 | 982 | 5 | 93 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | YES | BT MAGRUDER | 7136562244 | UPON DISCOVERY OF THE OIL SPILL, EXXON PIPELINE COMPANY'S LONGVIEW AREA OIL SPILL RESPONSE TEAM WAS DISPATCHED TO THE SITE. THE OIL WAS CONTAINED IN A LOW AREA SO THE IMPACTED AREA WAS MINIMAL. THE OIL WAS RECOVERED BY VACUUM TRUCKS. THERE WERE NO OBSERVED IMPACT TO THE ENVIRONMENT OR TO ANY WILDLIFE. THE CAUSE OF THE SPILL WAS DUE TO A FAILED PIPELINE SECTION. THERE WERE NO INJURIES, FIRES, EXPLOSIONS AS A RESULT OF THIS EVENT. NRC REPORT NO. 324623
2017-09-29 08:50 | YES | NO | 19960040 | 1996-03-12 | 30755 | CITGO PRODUCTS PIPELINE COMPANY | YES | 1996-02-17 | 1000 | OK | POTTAWATOMIE |  | NO |  | NO | NORTHEAST QUARTER SEC. 4, TOWNSHIP 8 N, RANGE 3 E. POTAWATOMIE COUNTY, OKLAHOMA 3/4 MILE WEST OF BROOKSVILLE, OK |  | LINE PIPE | PIPE | WELDING FITT, UNAUTH TAP | 1948 | OTHER | UNAUTHORIZED TAP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 57676.1208 | 116356.0319 | GASOLINE | 3 | 120 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 700 | 250 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM SANDERS | 9184954786 | FEBRUARY 17, 1996 AT 10:00 P.M. THE CONTROL CENTER NOTICED AN HOURLY LOSS OF40 BARRELS. AT 11:00 P.M. THE CONTROL CENTER NOTICED 40 ADDITIONAL BARREL LOSS AND SHUT DOWN PIPELINE WITH ABOUT 200 PSI PRESSURE. THE PRESSURE WAS MONITORED AND BY 1:09 A.M. ON FEBRUARY 18TH THE PRESSURE HAD DROPPED TO 6I5 PSI. BY2:10 A.M. FIELD PERSONNEL HAD MANUALLY BLOCKED THE LINE SECTION AND STARTED TO LOOK FOR THE LEAK. THE LEAK WAS LOCATED AT 5:40 A.M. ON FEBRUARY 18TH. NOTIFICATION WAS MADE AND CONTRACT PERSONNEL WERE NOTIFIED. A TEMPORARY REPAIR WAS COMPLETED AT 7:30 A.M. ON FEBRUARY 18TH.
2017-09-29 08:50 | YES | NO | 19960041 | 1996-03-13 | 1046 | PENNZOIL PETROLEUM COMPANY | NO | 1996-02-11 | 700 | MS | LAMAR |  | NO |  | NO | SE 1/4 OF SW 1/4 OF SEC 9,T 1N,R16W OF LAMAR COUNTY, MISSISSIPPI |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1441.903 | 2908.9008 | CRUDE OIL | 1 | 400 | 385 | NO | NO | 14 | 0.38 | 0 | WELDED |  | 650 | 200 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | OTHER | PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | LAMAR CHISOLM | 6017964243 | AN EXTERNAL CORROSION HOLE OCCURRED IN THE 14" PIPELINE. THE RELEASED OIL RAN APPROXIMATELY 400 YARDS DOWN A DRY DRAW IN A GRASSY PASTURE. THIS IS PENZOILS MAIN SALES LINE THAT RUNS BETWEEN BAXTERVILLE AND LUMBERTON,MS. PITS WERE DUG AT VARIOUS LOCATIONS FOR CONTAINMENT. THE OIL WAS PICKED UP BY VACUUM TRUCKS. THE OILY DIRT WAS REMOVED AND THE AREA REMEDIATED.
2017-09-29 08:50 | NO | NO | 19960042 | 1996-03-08 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1996-02-08 | 1040 | AR | PHILLIPS |  | NO |  | NO | 826 OLD HIGHWAY, HELENA, ARKANSAS |  | TANK FARM | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1081.4273 | 2181.6756 | TRANSMIX (PART. REFINED PETRO) | 3 | 2 | 2 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | SEVERE COLD WEATHER | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON FEBRUARY 8, 1996, AT APPROXIMATELY 1040 HOURS, CST, PERSONNEL NOTICED A SHEEN ON A DRAINAGE DITCH RUNNING THROUGH TEPPCO'S HELENA TERMINAL. A CLOSER INSPECTION REVEALED TRANSMIX ESCAPING FROM A 45 DEGREE ELBOW ON A TWO INCH SUMP DISCHARGE LINE WHICH CROSSES THE DITCH. THE ELBOW HAD FROZEN AND SPLIT IN THE THREADED AREA. PERSONNEL IMMEDIATELY INITIATED THE EMERGENCY PLAN. THE PIPE WAS ISOLATED. CONTAINMENT BOOM WAS DEPLOYED ACROSS THE DITCH. ALL PRODUCT WAS RECOVERED FROM THE WATER. THE ELBOW WAS REMOVED, THEN REPLACED AND THE PIPE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19960043 | 1996-03-13 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1996-02-07 | 1530 | IN | GIBSON |  | NO |  | NO | 1.3 MILES SOUTH ON CR 950 OFF SH64, 11.0 MILES EAST OF PRINCETON. INDIANA. |  | PUMPING STATION | VALVE |  | 0 | OTHER | FAILED O-RING ON CLAPPER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 144190.3019 | 290890.0797 | GASOLINE | 3 | 53 | 37 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON FEBRUARY 7, 1996 PERSONNEL AT TEPPCO'S PRINCETON TERMINAL FOUND A LEAK NEAR THE MAINLINE PUMPING UNIT. THE EMERGENCY PLAN WAS IMMEDIATELY INITIATED AND THE PUMP STATION WAS SHUT DOWN. IT WAS DETERMINED THE LEAK ORIGINATED FROM A FAILED O-RING ON THE CLAPPER SHAFT OF THE MAINLINE CHECK VALVE. THERE WAS APPROXIMATELY 53 BARRELS SPILLED. APPROXIMATELY 37 BARRELS WERE RECOVERED. SOIL CONTAMINATED BY THE PRODUCT IS CURRENTLY BEING REMEDIATED IN PLACE.
2017-09-29 08:50 | YES | NO | 19960044 | 1996-03-19 | 3370 | DIAMOND SHAMROCK REFINING & MARKETING CO | YES | 1996-02-17 | 1205 | TX | PARKER |  | NO |  | NO | 1.3 MILES SOUTHWEST OF WHEATLAND,TX G.H. TARPLEY SURVEY, ABSTRACT 1333, PARKER COUNTY,TEXAS |  | LINE PIPE | PIPE |  | 1992 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 50466.6057 | 101811.5279 | L. P. G. | 2 | 6355 | 0 | NO | NO | 8 | 0.25 | 52000 | WELDED |  | 1760 | 700 | YES | 24 | 2200 | 2 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GERALD CHILDERS | 8063783583 | AT APPROXIMATELY 1205 HOURS ON FEBRUARY 17, 1996, A THIRD PARTY CONTRACTOR STRUCK AND RUPTURED OUR 8" SKELLY-BELVIEU PIPELINE. THE LINE WAS IMMEDIATELY SHUT DOWN AND BLOCK VALVES CLOSED IN THE AREA OF THE LEAK. THERE WERE NO INJURIES OR FIRE DURING THE INCIDENT. SEVERAL HOMES WERE EVACUATED AND TRAFFIC ON HWY. 377 WAS REROUTED AS A PRECAUTION. THE DAMAGED SECTION OF PIPE WAS REPLACED WITH PRE-TESTED PIPE AND RETURNED TO SERVICE WITHOUT INCIDENT.
2017-09-29 08:50 | YES | NO | 19960045 | 1996-03-21 | 18718 | SUN PIPELINE CO | NO | 1996-03-03 | 956 | OK | OKLAHOMA | OKLAHOMA | NO |  | NO | NW SECTION 11 - T11N-R1W |  | LINE PIPE | PIPE |  | 1933 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 80 | 75 | NO | NO | 8 | 0.28 | 1818 | WELDED |  | 604 | 150 | YES | 8 | 957 | 12 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | E.F. COEN | 9185866942 | LINE WAS PUNCTURED BY AN EARTH SCRAPER. LINE WAS SHUT DOWN AND A SLEEVE INSTALLED.
2017-09-29 08:50 | YES | NO | 19960046 | 1996-03-18 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1996-02-11 | 836 | CA | KERN |  | NO |  | NO |  |  | PUMPING STATION | SCRAPER TRAP |  | 0 | OTHER | VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 108142.7264 | 218167.5598 | CRUDE OIL | 1 | 2400 | 1380 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. KELLEY | 8053282331 | VALVE BROKE AND CRUDE SPRAYED INTO AIR.
2017-09-29 08:50 | YES | NO | 19960047 | 1996-03-18 | 809 | ARCO PIPE LINE CO | NO | 1996-02-13 | 2000 | CA |  | LONG BEACH | NO |  | NO | PIER D STREET APPROX. 450' WEST OF PICO AVENUE LONG BEACH, CA. |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 50466.6057 | 101811.5279 | CRUDE OIL | 1 | 75 | 54 | NO | NO | 8 | 0.28 | 42000 | WELDED |  | 608 | 72 | YES | 4 | 779 | 7 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAN T. HISEY | 3104289000 | PERSONNEL WORKING FOR TIDELANDS OIL PRODUCTION COMPANY WERE DRIVING DOWN PIER D STREET AND THEY DETECTED A CRUDE OIL ODOR. UPON INVESTIGATION, THEY DISCOVERED A CRUDE OIL SPILL AND INITIATED A SPILL RESPONSE. EXCAVATION OF THE SITE EXPOSED THE PIPELINE AND THE LEAK. REPAIRS WERE MADE BY REPLACING APPROXIMATELY 23 FEET OF PIPELINE. THE PIPELINE WAS RETURNED TO SERVICE. SOIL REMEDIATION AND SITE RESTORATION IS IN PROGRESS. THIS PIPELINE IS OPERATED BY ARCO PIPE LINE COMPANY. POWERINE OIL COMPANY OWNS THE PIPELINE AND IS RESPONSIBLE FOR THE CATHODIC PROTECTION ON THE LINE.
2017-09-29 08:50 | YES | NO | 19960048 | 1996-03-22 | 1046 | PENNZOIL PETROLEUM COMPANY | NO | 1996-02-20 | 800 | MS | LAMAR |  | NO |  | NO | NW 1/4 OF NE 1/4 OF SEC 5, T 1N, R16W OF LAMAR COUNTY, MISSISSIPPI |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 360.4758 | 727.2252 | CRUDE OIL | 1 | 60 | 45 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 650 | 300 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | OTHER | PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | LAMAR CHISOLM | 6017964243 | AN EXTERNAL CORROSION HOLE OCCURRED UNDERGROUND IN THE BUTLER 10" STEEL GATHERLING LINE. THE RELEASED OIL RAN APPROXIMATELY 600 YARDS DOWN LOW DRAW AREA WHICH HAS HEAVY GRASS AND VEGETATION. THIS LINE IS PART OF PENNZOIL'S IN-FIELD PIPELINE SYSTEM. PITS WERE DUG TO CONTAIN OIL. TANK TRUCKS PICKED UP RECOVERABLE OIL. THE OILY DIRT WAS REMOVED AND THE AREA REMEDIATED.
2017-09-29 08:50 | YES | NO | 19960049 | 1996-04-01 | 10313 | KOCH PIPELINE INC | YES | 1996-03-01 | 139 | TX | COLLIN |  | NO |  | NO | NEVADA BOOSTER, 3 MILES NW OF ROYCE CITY, TX |  | PUMPING STATION | OTHER | NIPPLE FAILURE-FITTING | 1995 | OTHER | FAILED FITTING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6700 | 4830.3751 | 9744.8177 | NATURAL GAS LIQUID | 2 | 422 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JERRY ROGERS | 4053952377 | FAILURE OF 3/4" NIPPLE ON BY-PASS LINE AT PUMP STATION.
2017-09-29 08:50 | NO | NO | 19960051 | 1996-03-25 | 2552 | COLONIAL PIPELINE CO | YES | 1996-02-21 | 1354 | GA | CATOOSA |  | NO |  | NO | COLONIAL PIPELINE COMPANY CHATTANOOGA JUNCTION 391 SCRUGGS RD, RINGGOLD, GA 30736 |  | PUMPING STATION | SCRAPER TRAP |  | 1962 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | KEROSENE | 3 | 33 | 14 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.L. GAMBRELL | 4048412402 | AFTER STARTING LINE 20, AN 8-INCH O.D. STUBLINE THAT RUNS FROM ATLANTA, GEORGIA, TO NASHVILLE, TENNESSEE, ON FEBRUARY 21, 1996, THE ATLANTA CONTROL CENTER RECEIVED A HIGH SUMP AND A MECHANICAL GROUP ALARM FROM CHATTANOOGA JUNCTIONAT 1354 EST. A COMPANY EMPLOYEE WAS DISPATCHED TO THE STATION AND FOUND PRODUCT IN THE STATION YARD FROM AN OVERFLOWING SUMP AND FROM AN OPEN SCRAPER TRAP VENT. THE PIPELINE CONTROLLER WAS NOTIFIED AND IMMEDIATELY SHUT DOWN THE LINE. THE TRAP OUTLET VALVE WAS CLOSED, WHICH STOPPED THE RELEASE OF PRODUCT. CLEN-UP CREWS WERE IMMEDIATELY CALLED TO THE STATION AND BEGAN RECOVERY OPERATIONS. IT HAS BEEN DETERMINED THE APPROXIMATELY 33 BARRELS OF KEROSINE WERE RELEASED, ALL OF WHICH, WERE CONTAINED ON COMPANY PROPERTY. TO DATE, APPROXIMATELY 14 BARRELS OF PRODUCT HAVE BEEN RECOVERD AND RETURNED TO THE PIPELINE SYSTEM. THE ENVIRONMENTAL TEAM IS CURRENTLY ASSESSING THE EXTENT OF PROPERTY DAMAGES. THE CAUSE OF THE ACCIDENT HAS BEEN DETERMINED TO BE OPERATOR ERROR. AFTER THE RECEIPT OF A CLEANING PIG AND THE SUBSEQUENT DRAINUP OF THE SCRAPER TRAP, THE SMALL VALVES ON THE TRAP DRAIN LINE AND VENT LINES WERE INADVERTENTLYLEFT OPEN. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER, NO. 327201.
2017-09-29 08:50 | YES | NO | 19960052 | 1996-03-28 | 12127 | MARATHON PIPE LINE CO | YES | 1996-02-29 | 1508 | IL | LAWRENCE | ST. FRANCISVILLE | NO |  | NO | INCIDENT OCCURRED IN A FARM FIELD TWO MILES NORTHWEST OF ST. FRANCISVILLE, IL LAWRENCE COUNTY, DENISON TOWNSHIP, SECTION 18 |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 155000 | 111747.484 | 225439.8118 | NATURAL GAS LIQUID | 2 | 30 | 0 | NO | NO | 4 | 0.16 | 42000 | WELDED |  | 1300 | 700 | YES | 8 | 1731 | 6 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JOSEPH A. FISHER | 4194213201 | AT 15:08 ON FEBRUARY 29, 1996, A LOW PRESSURE ALARM WAS RECEIVED AT MARATHONPIPE LINE COMPANY (MPL) OPERATIONS CENTER LOCATED IN FINDLAY, OH. THE ALARM WAS INITIATED AT MPL'S ST FRANCISVILLE STATION, LOCATED NEAR THE MIDPOINT OF THE PRINCTON-ROBINSON 4" LPG PIPELINE. OPERATIONS CENTER PERSONNEL SHUT DOWN THE PIPELINE'S INITIATING STATION OF PRINCETON, INDIANA AT 15:10. BLOCK VALVES ON THE SYSTEM WERE CLOSED BY OPERATIONS CENTER PERSONNEL; AT PRINCETON STATION (UPSTREAM) AT 15:11, AND AT ST. FRANCISVILLE STATION (UPSTREAM) AT 15:12.FIELD PERSONNEL CLOSED THE LAWRENCEVILLE BLOCK VALVE (DOWN STREAM) AT 15:40.MPL PERSONNEL RESPONDED TO THE AFFECTED AREA AND DISCOVERED THE LINE HAD BEEN STRUCK AND RUPTURED BY A TILE PLOW LAYING PLASTIC DRAINAGE TILE IN A FARM FIELD AT A LOCATION OTHER THEN WHERE THE LINE HAD BEEN MARKED. THE PLOW OPERATOR SHUT DOWN THE PLOW UPON STRIKING THE PIPELINE AND THERE WAS NO FIRE OR EXPLOSION. AS A PRECAUTION, THE AFFECTED AREA SECURED BY BLOCKING THE ROADS LEADING INTO THE AREA AND EVACUATING OCCUPANTS OF FIVE HOMES. MARCH 1, THE TILINGMACHINE WAS PULLED FROM THE PIPELINE AND THE AFFECTED AREA WAS EXCAVATED. A TEMPORARY PIPE CLAMP WAS INSTALLED OVER THE PUNCTURE IN THE PIPE TO HALT THE CONTINUED RELEASE OF BUTANE. MARCH 2-4, THE PIPELINE WAS PURGED. MARCH 5, A TEN FOOT SECTION OF PIPE CONTAINING THE DAMAGED AREA WAS REMOVED AND REPLACED WITH TESTED PIPE. MARCH 6, THE PIPELINE WAS RECOMMISSIONED AND RETURNED TO SERVICE. TO PREVENT ANY CHANCE OF EXPLOSION OR FIRE DURING THE RESPONSE AND REPAIR ACTIVITES, THE AFFECTED AREA WAS MONITORED FOR EXPLOSIVE VAPORS TO PROTECT MPL AND CONTRACTOR PERSONNEL, AND THE PUBLIC. AFTER REPAIRS WERE COMPLETED, THE AFFECTED AREAS OF THE FARM FIELD WERE FLUSHED WITH WATER AND EXCAVATED TO ALLOW ANY RESIDUAL BUTANE TO VAPORIZE AND DISSIPATE.
2017-09-29 08:50 | YES | NO | 19960053 | 1996-03-29 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1996-02-28 | 1100 | CT | NEW HAVEN | NEW HAVEN | NO |  | NO | NEAR LITTLE RIVER, NEW HAVEN, CT |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 950000 | 684903.9341 | 1381727.8787 | FUEL OIL | 3 | 900 | 685 | NO | NO | 12 | 0.22 | 42000 | WELDED |  | 720 | 650 | YES | 24 | 1104 | 9 | 93 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL C. LARKIN | 6107704507 | ON FEBRUARY 28, 1996, AT 1100 HOURS, BUCKEYE PERSONNEL AT NEW HAVEN TERMINALRECEIVED TELEPHONE REPORTS OF A PETROLEUM PRODUCT SHEEN ENTERING THE LITTLE RIVER NEAR ITS CONFLUENCE WITH QUINNIPIAC RIVER. THE PIPELINE WAS SHUTDOWN AND PERSONNEL WERE DISPATCHED IMMEDIATELY. PIPELINE STRIPPING OPERATIONS REVEALED A LOCALIZED REVEALED A LOCALIZED 1/4-INCH DIAMETER CORROSION PIT. A PLIDCOSLEEVE WAS INSTALLED AS A TEMPORARY REPAIR PRIOR TO THE PERMANENT INSTALLATION OF A 6' SECTION OF CERTIFIED, PRE-TESTED PIPE ON 03/01/96. ALL APPLICABLE AGENCIES WERE NOTIFIED AND RECOVERY AND CLEANUP ACTIITIES ARE BEING DONE UNDER THE SUPERVISION OF THE EPA AND CONNECTICUT DEP.
2017-09-29 08:50 | YES | YES | 19960054 | 1996-03-29 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-02-27 | 401 | TX | YOAKUM | NORTH OF PLAINS | NO |  | NO | APPROXIMATELY 2 MILES WEST AND 1.45 MILES NORTH OF THE INTERSECTION OF FM 1780 AND FM2196 IN YOAKUM COUNTY, TEXAS |  | LINE PIPE | PIPE |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 1 | 0 | 1 | 0 | 0 | 0 | 220000 | 158609.3321 | 319979.0877 | L. P. G. | 2 | 4600 | 0 | YES | NO | 10.75 | 0.19 | 52000 | WELDED |  | 1310 | 600 | YES | 24 | 1793 | 3 | 72 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOHNNY L. CAVITT | 9185993795 | PIPELINE WAS STRUCK BY A THIRD PARTY UTILIZING AGRICULTURAL EQUIPMENT FOR"DEEP BREAK" PLOWING. PRODUCT WAS RELEASED AND IGNITED FROM AN UNDETERMINEDSOURCE. EQUIPMENT OPERATOR RECEIVED BURNS WHILE ESCAPING THE SCENE AND LATERDIED. THE DAMAGED LINE SEGEMENT WAS REPLACED WITH NEW PIPE AND RETURNED TOSERVICE. REGIONAL SUPPLEMENT RECEIVED 11/12/1996. ATTACHED TO FILE AT HQ.
2017-09-29 08:50 | YES | NO | 19960055 | 1996-04-01 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | YES | 1996-03-06 | 1230 | OK | GRANT | MEDFORD | NO |  | NO | MEDFORD FACILITY |  | TANK FARM | VALVE |  | 1996 | OTHER | VALVE SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 8651.4181 | 17453.4048 | NATURAL GAS LIQUID | 2 | 320 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JERRY ROGERS | 4053952377 | 10" VALVE STEM/SEAL FAILURE OCCURRED AFTER CHANGING OUT FILTERS AND START UPOF SYSTEM.
2017-09-29 08:50 | YES | NO | 19960056 | 1996-04-01 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-03-01 | 1830 | WY | UINTA |  | NO |  | NO | FROM EVANSTON 22 MILES SOUTH ON COUNTY ROAD 151 |  | LINE PIPE | OTHER | RELIEF VALVE METERING | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 627 | 452.0366 | 911.9404 | NATURAL GAS LIQUID | 2 | 44 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHNNY L. CAVITT | 9185993795 | RELIEF VALVE RELIEVED PREMATURELY. UPON REPORT OF THE INCIDENT, TULSA PIPELINE CONTROL DISPATCHED FIELD PERSONNEL TO INVESTIGATE THE INCIDENT. FIELD PERSONNEL REMOVED THE VALVE AND CHECKED CALIBRATION. THEY REPLACED INTERNAL COMPONENTS, RESET CALIBRATION AND RESTORED VALVE TO NORMAL OPERATION.
2017-09-29 08:50 | NO | NO | 19960057 | 1996-04-08 | 26040 | FOREST OIL CORP | NO | 1995-01-22 | 800 | LA |  |  | YES | LONG 91 515 LAT. 28 17 50 | NO | SHIP SHOAL 277A, OFFSHORE LOUISIANA OCS-G-9627 |  | LINE PIPE | VALVE | HOT TAP VALVE STEM #3 | 1994 | OUTSIDE FORCE DAMAGE | FISHING OPERATIONS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 6 | 0.43 | 36000 | WELDED |  | 1440 | 1440 | YES | 4 | 1440 | 8 | 94 | NO DATA | Null | Null | NO DATA |  | FISHING OPERATIONS |  | Null | NO DATA |  | Null | Null | LARRY E. FONTENOT | 3182640512 | ON JANUARY 22, 1995, THE SHIP SHOAL 277 PIPELINE EXPERIENCED DAMAGE ON (2) HOT TAP VALVES, CAUSING A MINOR LEAK (11.6 GALLONS) THE DAMAGED VALVES WERE REMOVED AND REPLACED WITH BULL PLUGS RAINFORCED WITH (66) ADDITIONAL SANDBAGS. IN ADDITION TO THE BULL PLUGS, 8' X 12" CEMENT PADS WERE INSTALLED OVER THE PLUGS. CEMENT PAD EDGES WERE JETTED INTO THE MUDLINE.
2017-09-29 08:50 | YES | NO | 19960058 | 1996-04-08 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1996-03-07 | 1030 | TX | DUVAL |  | NO |  | NO | 4.5 MI EAST OF FREER, TEXAS ON NORTH SIDE OF S.H. 44 CROOSING |  | LINE PIPE | OTHER | NOT GIVEN | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10814.2726 | 21816.756 | CRUDE OIL | 1 | 436 | 65 | NO | NO | 6.63 | 0.16 | 42000 | WELDED |  | 700 | 0 | YES | 0 | 0 | 0 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | LINE MARKERS & PAINT FENC | NO | NO | W.D. PARTLOW | 7138777370 | LINE WAS STRUCK BY THIRD PARTY TRENCHING CONTRACTOR FOR SOUTHWESTERN BELLTELEPHONE COMPANY. LINE WAS PERMANENTLY MARKED WITH SIGNS AND PAINTED FENCEPOSTS AT ROAD CROSSING WHERE LINE WAS HIT. LINE WAS IDLE AT TIME OF LEAK AND120' OF PIPE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19960059 | 1996-04-08 | 1044 | WESTTEX 66 PIPELINE COMPANY | YES | 1996-03-10 | 2200 | OK | CIMARRON |  | NO |  | NO | POWDER RIVER LINE - HILIGHT TO BORGER-MP 91-29+75 SEC.14,T2N,R6E APPROX.8 MILES SOUTH AND 1 MILE EAST OF BOISE CITY ON HWY.287 |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 48950 | 35290.5764 | 71195.347 | NATURAL GAS LIQUID | 2 | 2700 | 0 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1440 | 552 | YES | 8 | 2085 | 5 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | L.J. SCHMITZ | 9186614814 | FARMER HIT LINE WHILE CHISEL PLOWING FIELD FOR FIRST TIME. THE LINE WAS SHUTDOWN AND BLOCKED. THE SHERIFF WAS NOTIFIED AND BLOCKED HIGHWAY 287.MAINTENANCE PERSONNEL LET LINE BLOW DOWN AND THEN REPLACED THE PIPE.
2017-09-29 08:50 | YES | NO | 19960060 | 1996-04-05 | 2330 | CHEVRON PIPELINE CO | NO | 1996-03-05 | 900 | UT |  | SALT LAKE CITY | NO |  | NO | WARM SPRINGS ROAD, ADJACENT TO INTERSTATE 15 APPROXIMATELY 1040 WEST 1100 NORTH |  | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 720951.5096 | 1454450.3986 | DIESEL FUEL | 1 | 330 | 100 | NO | NO | 4 | 0.24 | 35000 | WELDED |  | 520 | 53 | YES | 24 | 1125 | 8 | 93 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DOUG PELL | 8015397204 | THERE ARE SIGNS OF DAMAGE, POSSIBLY FROM A BACKHOE, WHERE CORROSION OCCURRED. WE ARE UNSURE HOW DAMAGE OCCURRED AND ARE CURRENTLY INVESTIGATING THIS.
2017-09-29 08:50 | YES | NO | 19960061 | 1996-04-09 | 9175 | JAYHAWK PIPELINE CORP | YES | 1996-03-25 | 805 | KS | SEDGWICK |  | NO |  | NO | SW 1/4 SECTION 7-TOWNSHIP 26S- RANGE 1 EAST OF SEDGWICK COUNTY, KS 6358 N. MERIDIAN VALLEY CENTER, KS |  | PUMPING STATION | TANK |  | 1946 | OTHER | ROOF DRAIN PARTED IN TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 26400 | 19033.1199 | 38397.4905 | CRUDE OIL | 1 | 2095 | 1775 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | THE TANK IN QUESTION, LOCATED AT JAYHAWK'S VALLEY CENTER STATION, HAS AN EXTERNAL FLOATING ROOF AND THE DRAIN HOSE PARTED INSIDE THE TANK, WHICH IN TURN LET OIL RUN OUT DRAIN LINE INTO DIKE. ALL OIL WAS CONTAINED INSIDE DIKE. 1,775 BARRELS WERE RECOVERED AND SOIL REMEDIATION WILL BE DONE INSIDE DIKE FOR FINAL CLEAN UP. ALL CRUDE OIL WILL BE REMOVED FROM TANK AND NEW DRAIN HOSE WILLBE INSTALLED.
2017-09-29 08:50 | YES | NO | 19960062 | 1996-04-09 | 9175 | JAYHAWK PIPELINE CORP | YES | 1996-03-25 | 930 | KS | KIOWA |  | NO |  | NO | SW 1/4 SECTION 7- TOWNSHIP 28 SOUTH- RANGE 16 WEST, KIOWA COUNTY, KS 1 1/2 MILE WEST OF HAVILAND, KS |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3604.7575 | 7272.252 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 12.75 | 0.25 | 46000 | WELDED |  | 1250 | 140 | YES | 8 | 1612 | 0 | 58 | INTERNAL | Null | YES | OTHER | NOT GIVEN | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | JAYHAWK PIPELINE WAS NOTIFIED BY LANDOWNER ON MARCH 25, 1996 AT 09:30 AMCONCERNING A PIPELINE LEAK ON HIS LAND. WHEN JAYHAWK'S LINE WAS EXPOSED,THERE WAS A SMALL PINHOLE ON BOTTOM OF PIPE. A FULL ENCIRCLEMENT REPAIR WASMADE TO THE PIPELINE AND SOIL WILL BE REMEDIATED AT LOCATION OF SPILL.CORROSION COUPONS WILL BE INSTALLED ON THIS PIPELINE SYSTEM FOR FURTHERINVESTIGATION.
2017-09-29 08:50 | YES | NO | 19960063 | 1996-04-10 | 22610 | WILLIAMS PIPELINE CO | YES | 1996-03-08 | 440 | KS | WYANDOTTE | KANSAS CITY | NO |  | NO | LOCATED IN THE SE 1/4 OF THE NE 1/4 OF SEC. 34 IN TOWNSHIP 10S, RANGE 25E AT 401 DONOVAN RD IN WYANDOTTE COUNTY, KANSAS. |  | TANK FARM | PUMP |  | 1978 | OTHER | PUMP BEARING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 93723.6962 | 189078.5518 | FUEL OIL | 3 | 10 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883850 | AT 04:00 HOURS ON MARCH 8, 1996, THE LOCAL FIRE DEPARTMENT RESPONDED TO A CALL FROM A PERSON DRIVING BY WPL'S KANSAS CITY, KANSAS TERMINAL. WHEN THE FIREDEPARTMENT ARRIVED IT WAS DISCOVERED THAT A FIRE HAD STARTED AROUND THE 200 HP HORIZONTAL TANK PUMP ON WPL'S TNAK 1506. AT APPROXIMATELY 04:50 HOURS, THEFIRE DEPARTMENT BEGAN EXTINGUISHING THE FIRE WHILE WPL'S OPERATORS CLOSED THE TANK VALVE SUPPLYING SUCTION TO THE PUMP UNIT. AT 05:45 HOURS, THE FIRE WASEXTINGUISHED. AN INVESTIGATION INDICATED THAT 10 BARRELS OF DIESEL FUEL HAD BEEN LOST FROM THE LINE WITH ONE BARREL RECOVERED THROUGH SOIL EXCAVATION. THE INVESTIGATION ALSO INDICATED THAT THE FIRE STARTED AS A RESULT OF A BEARINGFAILURE WHICH CAUSED PRODUCT TO LEAK PAST THE PUMP SEAL INTO THE BEARING HOUSING WHERE THE PRODUCT WAS IGNITED DUE TO THE PRODUCT EXCEEDING ITS AUTO IGNITION TEMPERATURE. THERE WAS MINIMAL SOIL REMEDIATION DUE TO THE FACT THAT THEESCAPED PRODUCT WAS BURNED.
2017-09-29 08:50 | NO | NO | 19960064 | 1996-04-05 | 30781 | OLYMPIC PIPELINE COMPANY | YES | 1996-03-23 | 1430 | WA | COWLITZ | KALAMA | NO |  | NO | PRIVATE FEE OWNED PROPERTY 1/2 MILE EAST I-5 KALAMA, WA T6N 55 R1W |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5407.1363 | 10908.378 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 14 | 0.28 | 52000 | WELDED |  | 1440 | 200 | YES | 24 | 1880 | 10 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES | MUDSLIDE,LANDSLIDE,SUBSID | Null | NO DATA |  | Null | Null | WILLIAM MULKEY | 2062357745 | PROPERTY OWNER NOTIFIED OPL CO. CONTROL CENTER OF DIESEL FUEL PUDDLED ALONG REMOTE SECTION FO R.O.W. IMMEDIATE SHUTDOWN AND INVESTIGATION REVEALED THAT SMALL LEAK RESULTED FROM PIPE MOVEMENT IN AN AREA OF CONSTANT GROUND SHIFT FLOODING, HEAVY RAIN AND SOIL CONDITIONS HAVE CAUSED EROSION & LANDSLIDES ALONG R.O.W. OPL HAS BEEN CONSTANTLY MONITORING CONDITIONS ALONG THIS SEGMENT OF R.O.W BECAUSE OF DAMAGE CAUSED TO RESIDENCES AND PROPERTIES ALONG THE ROUTE.(NATURAL CAUSES). SEEPAGE FROM A STEEP SLOPE RESULTED IN A SLIGHT SHEEN ON SPENCER CREEK , HOWEVER MINIMAL ENVIRONMENTAL IMPACT. BOOMS AND SORBENTS ARE EFFECTIVE IN CLEAN-UP OF WATER. ALL STATE AGENCIES PARTICIPATING IN MONITORING ACTIVITIES AND CLEAN-UP.
2017-09-29 08:50 | YES | NO | 19960065 | 1996-04-30 | 9175 | JAYHAWK PIPELINE CORP | YES | 1996-04-12 | 1115 | KS | MEADE |  | NO |  | NO | SW OF SE1/4 SECTION 26, TOWNSHIP 33 SOUTH, RANGE 30 WEST 9 MILES SOUTH AND 1.5 EAST OF PLAINS, KANSAS. |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 3893.1382 | 7854.0322 | CRUDE OIL | 1 | 83 | 15 | NO | NO | 12.75 | 0.25 | 46000 | WELDED |  | 1250 | 10 | YES | 8 | 1612 | 0 | 58 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | JAYHAWK PIPELINE WAS NOTIFIED BY LANDOWNER ON APRIL 12, 1996 AT 11:15 AM CONCERNING A CRUDE OIL SPILL ON HIS LAND WHERE THE PIPELINE WAS AT. JAYHAWK'S RESPONSE WAS IMMEDIATE AND LINE WAS EXPOSED TO FIND SMALL PINHOLE ON BOTTOM OF PIPE. A FULL ENCIRCLEMENT REPAIR WAS MADE TO THE PIPELINE AND SOIL WILL BE REMEDIATED AT LOCATION OF SPILL.
2017-09-29 08:50 | YES | NO | 19960066 | 1996-04-23 | 2731 | CHEVRON PIPELINE CO | NO | 1996-03-11 | 1655 | LA |  |  | YES | 29DER 32.5'N,90 DER 04'W | NO | MILE POST 44 ON EP PIPELINE |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 216285.4529 | 436335.1196 | L. P. G. | 2 | 6565 | 0 | NO | NO | 8 | 0.22 | 42000 | WELDED |  | 1152 | 740 | YES | 0 | 1885 | 0 | 67 | EXTERNAL | Null | YES | NO DATA |  | DAMAGE BY NATURAL FORCES | TREE ROOT RUBBING COATING | Null | ONE CALL |  | Null | Null | MARK G. BOONE | 5043642020 | VISUAL SIGHTING OF THE LEAK OCCURRED ON MARCH 11TH DURING A SONAT OVERFLIGHT. THE CPL CONTROLLERS TOOK IMMEDIATE ACTION BY BLOCKING IN THE LINE, EVEN THOUGH A PRESSURE DROP WAS NOT OBSERVED. CONFIRJATION THE LEAK LOCATION OCCURREDAT DAYBREAK ON THE 12TH LEAK REPAIR STRATEGICS WERE IMPLEMENTED AND REPAIR COMPLETED. THE CAUSE WAS FOUND TO BE A TREE STUMP UNDER THE PIPE CAUSING STRESS ON THE COATING WHICH CRACKED CAUSING MOISTURE TO GET ON THE SUBSTRATE.
2017-09-29 08:50 | YES | NO | 19960067 | 1996-04-25 | 809 | ARCO PIPE LINE CO | YES | 1996-03-31 | 1030 | TX | PARKER | WEATHERFORD | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1956 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 180237.8774 | 363612.5997 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 18 | 0.28 | 52000 | WELDED |  | 1095 | 615 | YES | 8 | 1373 | 1 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARK LOWE | 7139865029 | CRUDE OIL WAS DETECTED WILLOW CREEK BY PROPERTY OWNER ON MARCH 31, 1996. INFORMATION RELAYED TO ARCO PIPE LINE CO. (APL) BY COUNTY EMERGENCY PLANNER AT APPROXIMATELY 1030 SAME DAY. FIRE DEPARTMENT MADE INITIAL RESPONSE AND DEPLOYED SORBENT BOOMS. PIPELINE WAS SHUT DOWN AND MEASURES WERE TAKEN TO DRAIN LINE. APL ARRIVED AT SITE BY 1130 SAME DAY. CLEANUP CREWS ARRIVED BY 2200 SAME DAY. CLEANUP AND REPAIR ACTIVITIES WERE COMPLETED BY APRIL 11, 1996. THE TEXAS RAILROAD COMMISSION WALKED THE IMPACTED AREA AND CONFIRMED CLEANUP SATISFIED REGULATORY REQUIREMENTS. THE CAUSE OF THE LEAK WAS A CRACK APPROXIMATELY 0.25INCHES LONG IN THE LONGITIUDINAL SEAM OF THE PIPE. THE CAUSE FOR THE CRACK IS NOT KNOWN.
2017-09-29 08:50 | YES | NO | 19960068 | 1996-04-30 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | NO | 1996-03-26 | 345 | KS | MCPHERSON | CONWAY | NO |  | NO | 1/4 MILE NORTH OF HWY 56I, T-19-S,S-23, 24 R5W |  | LINE PIPE | GIRTH |  | 1971 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 62000 | 44698.9936 | 90175.9247 | NATURAL GAS LIQUID | 3 | 1400 | 229 | NO | NO | 8.63 | 0.13 | 42000 | WELDED |  | 720 | 260 | YES | 24 | 1167 | 10 | 86 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHNNY L. CAVITT | 9185993795 | PRODUCT WAS DISCOVERED DURING A ROUTINE CHECK OF THE STATION AREA. EXCAVATION REVEALED A CRACK IN GIRTH WELD. PERMANENT REPAIRS WERE MADE BY INSTALLING 182.56 FEET OF PIPE AND A TRANSITION PIECE.
2017-09-29 08:50 | YES | NO | 19960069 | 1996-05-02 | 737 | ASHLAND PIPELINE CO | NO | 1996-03-28 | 1330 | KY | JEFFERSON | LOUISVILLE | NO |  | NO | NORTH SIDE OF OUTER LOOP .5 MILE EAST OF THIRD STREET ROAD. |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 54071.3632 | 109083.7799 | GASOLINE | 3 | 2 | 2 | NO | NO | 8.63 | 0.25 | 2667 | WELDED |  | 1200 | 900 | YES | 15 | 1530 | 4 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | JAMES O. SIMPSON | 5026832485 | THE ASHLAND CONTROL CENTER, IN ASHLAND KENTUCKY, RECEIVED A PHONE CALL FROM THE JEFFERSON COUNTY FIRE DEPARTMENT AT APPROXIMATELY 1:30 PM CST, MARCH 28, 1996, AND SAID THERE WAS GASOLINE COMING FROM THE GROUND ON THE NORTH SIDE OFOUTERLOOP IN LOUISVILLE, KENTUCKY. THE ASHLAND CONTROL CENTER CALLED THE TRI-STATE DIVISION AND SET UP A CONFERENCE CALL WITH THE THREE PARTIES. THE PIPELINE WAS SHUT DOWN UNTIL WE COULD VERIFY THE LEAK. THE DISTRICT SUPERVISOR FROM LEBANON JUNCTION, KENTUCKY WAS DISPATCHED AND VERIFIED THE LEAK AT APPROXIMATELY 2:15 PM CST. PIPELINE CREWS WERE DISPATCHED FROM LEBANON JUNCTION, KENTUCKY, OWENSBORO, KENTUCKY, AND ALBION, ILLINOIS. HERITAGE REMERDIATION IN LOUISVILLE, KENTUCKY WAS CALLED OUT AND PLACED 8 BOOMS ACROSS POND CREEK TO STOP THE PROGRESS OF A VERY LIGHT SHEEN. THE MAINTENANCE CREW EXCAVATED THE PIPELINE AND DISCOVERED THAT THE PIPE HAD BEEN DAMAGED BY A THIRD PARTY. THE DAMAGE WAS SEVER ENOUGH THAT A PERMANENT REPAIR CLAMP COULD NOT BE USED. A TEMPORARY CLAMP WAS INSTALLED TO STOP THE LEAK UNTIL A STOPPLE CONTRACTOR ARRIVED, PIPELINE DRAINED AND REPAIRS MADE. THE DAMAGED SECTION OF PIPE WAS CUT OUT AND REPLACED BY 14 FEED OF PRE-TESTED PIPE. THE PIPELINE WAS PLACED BACK INTO SERVICE ON SATURDAY, MARCH 30, 1996 AT APPROXIMATELY 4:00 AM CST. THE INITIAL CLEANUP EFFORT HAS BEEN COMPLETED AND CONTAMINATED DIRT HAS BEEN REMOVED FOR HBIO-REMEDIATION AT WASTE MANAGEMENT'S OUTER LOOP LANDFILL. REMEDIATION EFFORTS WILL CONTINUE UNTIL SUCH TIME SOIL ANALYSIS IS SATISFACTORY WITH THE KENTUCKY DIVISION OF WASTE MANAGEMENT.
2017-09-29 08:50 | YES | NO | 19960070 | 1996-05-06 | 443 | AMOCO PIPELINE CO | NO | 1996-04-07 | 930 | WY | NATRONA |  | NO |  | NO | T33N-R79W-S6 SE 1/4 |  | PUMPING STATION | OTHER | PUMP STATION SUMP PUMP | 1988 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 15860.9332 | 31997.9088 | CRUDE OIL | 1 | 1565 | 1000 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. PETERSON | 3038305067 | ON APRIL 7 AN EMPLOYEE BECAME AWARE OF A CRUDE OIL OUTAGE WITHIN THE STATIONGROUNDS. RESPONSE AND CONTAINMENT ACTIVITIES WERE INITIATED. INVESTIGATION LED TO THE CAUSE OF A MALFUNCTION THE SUMP TANK LEVEL CONTROL WHICH RESULTED IN THE OVERFLOW OF THE SUMP TANK. THE NRC WAS NOTIFIED AND REPORT #335147 WAS ISSUED. THE WYOMING DBQ WAS NOTIFIED AND REPORTS #96-04-07-1034 WERE ISSUED.
2017-09-29 08:50 | YES | NO | 19960071 | 1996-05-06 | 22610 | WILLIAMS PIPELINE CO | YES | 1996-04-04 | 1110 | OK | OSAGE |  | NO |  | NO | NE 1/4 OF SECTION 4, TOWNSHIP 22 N, RANGE 11E IN OSAGE COUNTY OKLAHOMA. |  | LINE PIPE | PIPE |  | 1931 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | CRUDE OIL | 1 | 561 | 484 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 260 | 343 | YES | 8 | 1271 |  | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | STEVEN S. BALL | 9185883850 | ON APRIL 4, 1996 AT APPROXIMATELY 11:05 HOURS, THE OPERATIONS CONTROL DEPARTMENT RECEIVED A LOSS OF PRESSURE ALARM ON THE BARNSDALL TO TULSA LINE, WHICH WAS IDLE AT THE TIMNE. WHILE TRYING TO VERIFY THE ALARM, A LANDOWNER (RICK STEWARD) CONTACTED THE OPERATIONS CONTROL DEPARTMENT AT 11:10 HOURS TO REPORT THAT A PIPELINE HAD BEEN STRUCK BY EXCAVATION EQUIPMENT AND THAT THE LINE WAS LEAKING CRUDE OIL. THE OPERATIONS CONTROL DEPARTMENT IMMEDIATELY CLOSED THE MOTOR OPERATED VALVES AT MP 16 AND MP 14 IN AN ATTEMPT TO ISOLATE THE LEAK. ALSO, AN ATTEMPT WAS MADE TO OPEN THE LINE AT BARNSDALL TO TRY AND DRAIN AS MUCH PRODUCT AS POSSIBLE FROM THE LEAK INTO TANKAGE AT BARNSDALL. OPERATIONS CONTROL THEN CONTACTED THE SOUTHERN REGION OFFICE AT APPROXIMATELY 11:20 HOURS TO REPORT THE INCIDENT, PROVIDING THE GENERAL LOCATION OF THE LEAK AND THE TELEPHONE NUMBER FOR MR. STEWARD. THE SOUTHERN REGION IMMEDIATELY CONTACTED THE TULSA AREA MAINTENANCE CREW AND INFORMED THEM OF THE SITUATION AND INSTRUCTEDTHEM TO TRAVEL TO THE LEAK SITE TO RESPOND TO THE LEAK NOTIFICATION. UPON ARRIVAL AT THE SITE, AT APPROXIMATELY 12:40 HOURS, WPL PERSONNEL BEGAN SECURINGTHE LOCATION AND PREVENTING THE SPILLED MATERIAL FROM FLOWING AWAY FROM THE LEAK SITE. CLEAN-UP EQUIPMENT ARRIVED AT THE SITE AND THE FREE CRUDE OIL WAS RECOVERED. THE PIPELINE WAS REPARIRED BY REPLACING THE DAMAED SECTION OF PIPETHE REPAIRS WERE COMPLETED AT 01:30 HOURS ON APRIL 5, 1996. CLEANUP OPERATIONS ARE CONTINUING WITH WPL ENVIRONMENTAL PERSONNEL WORKING WITH OKLAHOMA ENVIRONMENTAL OFFICIALS TO ADDRESS ANY FUTURE ENVIRONMENTAL ISSUES.
2017-09-29 08:50 | YES | NO | 19960072 | 1996-05-17 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1996-04-16 | 1730 | AR | WHITE |  | NO |  | NO | 194 TANK FARM ROAD, GARNER, ARKANSAS |  | PUMPING STATION | OTHER | OVER PRESSURE RELIEF VALV | 0 | OTHER | OPERATION RELIEF VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 6488.5636 | 13090.0536 | FUEL OIL | 3 | 190 | 178 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | ON APRIL 16, 1996, AT APPROXIMATELY 1730 HOURS, CST, PERSONNEL AT TEPPCO'S MCRAE TERMINAL DETERMINED THE OVER PRESSURE SAFETY RELIEF VALVE ON THE DISCHARGE OF A 700 H.P. PUMP HAD RELEASED FUEL OIL TO THE FLARE CONTAINMENT AREA. THE PUMP WAS IMMEDIATELY SHUTDOWN AND THE EMERGENCY PLAN WAS INITIATED. THERE WERE APPROXIMATELY 190 BARRELS SPILLED WITH APPROXIMATELY 178 BARRELS RECOVERED. ALL RELEASED PRODUCT WAS CONTAINED IN THE CONTAINMENT AREA. SOIL CONTAMINATED BY THE PRODUCT IS CURRENTLY BEING REMEDIATED IN PLACE.
2017-09-29 08:50 | YES | NO | 19960073 | 1996-05-14 | 2731 | CHEVRON PIPELINE CO | YES | 1996-04-15 | 950 | TX | TAYLOR | ABILENE | NO |  | NO | (MP 8.82 NEAR BUFFALO GAP) |  | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10814.2726 | 21816.756 | L. P. G. | 2 | 370 | 0 | NO | NO | 2.88 | 0.13 | 42000 | WELDED |  | 1044 | 550 | YES | 0 | 1800 | 0 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BILL JASPER | 7133635422 | A CONTRACTOR HIT THE LINE WITH A DOZIER WHILE EXCAVATING. THE LINE WAS MARKED WITH VISIBLE SIGNS ON EITHER SIDE OF THE EXCAVATION.
2017-09-29 08:50 | NO | NO | 19960074 | 1996-05-20 | 2325 | CHEVRON USA INC | NO | 1996-04-14 | 1305 | LA |  |  | YES | LAT 29 00 25 LONG 90 09 3 | Null |  |  | LINE PIPE | PIPE |  | 1996 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2.8838 | 5.8178 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 8 | 0.5 | 35000 | NO DATA |  | 696 | 300 | YES | 2 | 870 | 9 | 92 | INTERNAL | Null | YES | OTHER | CHEMICAL (PRODUCED WATER) | NO DATA |  | Null | NO DATA |  | Null | Null | JEFFREY J. SMITH | 5045927952 | PIPELINE FAILED DUE TO INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19960075 | 1996-05-13 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1996-04-15 | 900 | MN | ST LOUIS |  | NO |  | NO | DOWNSTREAM OF FLOODWOOD STATION, M.P. 1044.49 |  | LINE PIPE | PIPE |  | 1954 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 72095.151 | 145445.0399 | CRUDE OIL | 1 | 15 | 12 | NO | NO | 26 | 0.28 | 52000 | NO DATA |  | 774 | 535 | YES | 24 | 968 |  | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. SANDAHL | 2187250102 | ON APRIL 15, 1996, DURING A ROUTINE PIPELINE PATROL, LAKEHEAD'S PATROL PILOTDISCOVERED A SMALL CRUDE OIL LEAK NEAR M.P. 1044.49 (300 YARDS DOWNSTREAM OFFLOODWOOD STATION) AT APPROXIMATELY 09:00 MST. LINE 2 (26") WAS SHUT DOWN AT09:10 MST. THE LEAK OCCURRED IN A SWAMPY, LOW LYING AREA WHICH PREVENTED THE15 BBLS. OF OSA (SYNTHETIC) CRUDE OIL FROM MIGRATING AND LIMITING THE AREA IMPACTED TO APPROXIMATELY 80 FT. BY 200 FT. ALONG THE RIGHT-OF-WAY. THE LINE WAS EXCAVATED AND THE NATURE OF THE LEAK WAS DETERMINED TO BE CAUSED BY TWO SMALL CRACKS IN THE SIDE SEAM OF THE PIPE. MAINLINE PRESSURE WAS BLED OFF AND APLIDCO SPLIT SLEEVE REPAIR WAS INSTALLED WITH ENDS WELDED ON 04/18/96.
2017-09-29 08:50 | YES | NO | 19960076 | 1996-05-15 | 4805 | EXPLORER PIPELINE CO | YES | 1996-04-16 | 1505 | MO | ST CHARLES | WELDON | NO |  | NO | ADJACENT TO HIGHWAY 94 2 MILES SOUTH OF INTERSECTION OF HIGHWAY 94 AND HIGHWAY 40. |  | LINE PIPE | PIPE |  | 1971 | OTHER | LEAK, SPHERE CUT PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 165 | 164 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RODNEY E. SANDS | 9184935106 | AT 1505 HOURS APRIL 16, 1996 165 BARRELS OF #2 FUEL OIL WAS RELEASED INTO A DITCH THAT HAD BEEN EXCAVATED FOR RELOCATION OF 268 FEET OF 24" PIPELINE AT MILEPOST 360 NEAR WELDON SPRINGS, MISSOURI. EVACUATION OF FUEL OIL FROM THE SECTION OF 24" PIPE TO BE REMOVED WAS ACCOMPLISHED BY MOVING 24" SPHERES TO THEREPAIR SITE THROUGHT THE PIPELINE SYSTEM, DISPLACIANG PRODUCT FROM THE LINE SECTION TO BE REMOVED BY INJECTING NITROGEN BETWEEN THE SPHERES LOCATED AT THE SITE AND PUSHING THE PRODUCT DISPLACED BY NITROGEN INTO TANKS AT EXPLORER'SWOOD RIVER TANK FARM. DURING THE EVACUATION PROCEDURE FUEL OIL LEAKED AROUNDONE OF THE SEALING SPHERES INTO THE SECTION OF PIPE TO BE REPLACED. WHEN CUTTING OF THE 24" PIPE BEGAN, FUEL OIL ESCAPED INTO THE EXCAVATED TRENCH. EARTHEN CONTAINMENT DAMS WHERE IMMEDIATELY CONSTRUCTED CONFINING THE RELEASED FUELTO A 10'X30' AREA IN AT THE EXCAVATED CONSTRUCTION SITE. VACUUM TRUCKS REMOVED THE FUEL FROM THIS AREA, CONTAMINATED DIRT WAS REMOVED AND PLACED IN LINEDCONTAINMENT BOXES FOR DISPOSAL. APPROPRIATE REGULATORY AGENCIES WERE NOTIFIED, AND WORK PROCEEDED TO TIE-IN THE NEW SECTION OF PIPELINE. WORK WAS COMPLETED, THE PIPELINE REFILLED AND PLACED BACK INTO OPERATION BY 0630 HOURS APRIL 17, 1996.
2017-09-29 08:50 | YES | NO | 19960077 | 1996-05-24 | 13162 | NAVAJO REFINING CO | YES | 1996-05-09 | 1255 | TX | EL PASO |  | NO |  | NO | FROM EL PASO, TEXAS HWY 62/80 E.18 MI, TURN N. ON HUECO TANKS ST. PK RD, GO 8 MILES TO THE PARK. THE SPILL IS LOCATED IN THE NORTHWEST CORNER OF THE PARK. |  | LINE PIPE | PIPE |  | 1959 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 108142.7264 | 218167.5598 | GASOLINE | 3 | 304 | 20 | NO | NO | 6.63 | 0.16 | 1978 | WELDED |  | 1100 | 152 | YES | 7 | 598 | 4 | 96 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | CONTRACTOR PUBLIC AWARENE | NO | NO | J. TOWNSEND | 5057483311 | 12:55 P.M. THE ARTESIA OPERATOR NOTICED A PRESSURE AND RATE DROP ON THE 6" EL PASO PRODUCTS LINE AND CALLED EL PASO. 12:59 P.M. THE ARTESIA OPERATOR SUSPECTED A PROBLEM AND SHUT THE LINE DOWN, BLOCKED IN MP128. 13:05 P.M. EL PASO TERMINAL SUPERINTENDENT CALLED AND SAID A THIRD PARTY HAD DUG INOT OUR LINE INSIDE HUECO TANKS STATE PARK. NAVAJO EMPLOYEES AND EQUIPMENT AS WELL AS COANTRACTOR EMPLOYEES AND EQUIPMENT WERE DISPATCHED TO REPAIR THE PIPELINE AND CLEAN THE SPILL SITE AREA. PIPELINE WAS REPAIRED AND OPERATIONS RESUMED AT 9:00 P.M. ENVIRONMENTAL STUDY AND CLEAN UP ARE IN PROGRESS. 2:15 05/09/96 TELEPHONIC NOTICE. NATIONAL RESPONSE CENTER- MR. CHECKAN REPORT #340565.
2017-09-29 08:50 | YES | NO | 19960078 | 1996-05-28 | 443 | AMOCO PIPELINE CO | YES | 1996-05-03 | 830 | TX | SCURRY | SNYDER | NO |  | NO | CITY OF SNYDER TEXAS, 100 YARDS EAST OF THE INTERSECTION OF KS & Y DRIVE AND 23RD ST. |  | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 25233.3028 | 50905.764 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 8 | 0.03 | 42000 | WELDED |  | 539 | 210 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | MICROBIOLOGICAL | NO DATA |  | Null | NO DATA |  | Null | Null | R.A. WILSON | 9155706356 | THIS LINE WAS BEING FILLED TO RUN OIL EAST TO THE AMOCO PIPELINE COGDELL JUNCTION. THE LINE PRESSURE WAS BEING MONITORED BY THE AMOCO PIPELINE CONTROL CENTER IN TULSA OKLAHOMA. THE CONTROL CENTER NOTICED A DROP IN PRESSURE, SHUT OFF THE PUMP, AND CALLED THE LOCAL SNYDER OPERATIONS PERSONNEL. SNYDER PERSONNEL WENT OUT, LOCATED THE LEAK, AND INITIATED THE APL EMERGENCY RESPONSE PLAN.AFTER THE AREA WAS SECURED, THE LINE WAS EXCAVATED, THE SECTION CONTAINING THE CORROSION WAS REMOVED AND REPLACE.
2017-09-29 08:50 | YES | NO | 19960079 | 1996-05-29 | 26149 | ALYESKA PIPELINE SERVICE CO | YES | 1996-04-20 | 1700 | AK |  | GLENNALLEN | NO |  | YES | NEAR TRANS-ALASKA PIPELINE MILE 593, RICHARDSON HIGHWAY MILE 212 |  | LINE PIPE | VALVE |  | 1976 | OTHER | INADEQUATE DESIGN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 0 | 0 | YES | NO | 0.5 | 0 | 35000 | THREADED |  | 1200 | 650 | YES | 24 | 1127 | 0 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN S. DAYTON | 9072781611 | EVIDENCE OF CRUDE OIL WAS FOUND SATURDAY APRIL 20, 1996 AT THE BOTTOM OF AN INSTRUMENT ACCESS VAULT APPROXIMATELY 60 FEET NORTH OF CHECK VALVE 92. THE VAULT WAS APPROXIMATELY TWENTY FEED DEEP. THE OIL WAS APPROXIMATELY 18" DEEP INTHE 36" DIAMETER VAULT. THE PIPELINE PRESSURE WAS REDUCED FROM APPROXIMATELY650 PSI TO APPROXIMATELY 325 PSI BY REDUCING THROUGHOUT AND ADJUSTING PUMP STATION SUCTION/DISCHARGE PRESSURES. THE SECOND BYPASS VALVE ON CHECK VALVE 92WAS CLOSED IN CASE THE LEAK WAS BETWEEN THE TWO SERIES VALVES. EXCAVATION EQUIPMENT WAS BROUGHT IN AND REVEALED THAT A 1/2" SCREWED PLUG LOCATED ON THE 6" BYPASS PIPING WAS LOOSE AND RESPONSIBLE FOR THE OIL LEAKAGE. A NEW PIPE PLUG WAS SCREWED INTO THE THREAD-O-LET AND THE BYPASS PIPING WAS PRESSURIZED. PIPELINE PRESSURE RESTRICTIONS WERE REMOVED AT THIS POINT AND THE BYPASS PIPINGWAS CLEANED FOR INSPECTION. EXAMINATION REVEALED FIVE RADIAL CRACKS IN THE THREAD-O-LET THAT THE PIPE PLUG WAS SCREWED INTO. THE BYPASS VALVE WAS CLOSED AND THE ENTIRE FLANGED BYPASS SPOOL WAS REPLACED. EXCAVATION CONTINUES TO REMOVE THE CONTAMINATED SOIL FROM THE PIPE DITCH. THE DITCH WAS ORIGINALLY CUT INTO SOLID BEDROCK IN THE AREA OF THE LEAK TO A DEPTH OF APPROXIMATELY 25 FEET. EXCAVATION IS VERY SLOW DUE TO THE DEPTH OF THE HOLE, CRUDE OIL VAPOR AND THE NEED TO HAD EXCAVATE AROUND THE OPERATING PIPELINE. DURING EXCAVATION ACTIVITIES ON APRIL 27, 1996, A BACKHOE SCRAPED AGAINST THE BEDROCK AND AUSED A SPARK TO IGNITE THE CR5UDE VAPOR IN THE DITCH. THE OPERATOR IMMEDIATELY EXTINGUISHED THE BURNING SOIL BY SMOTHERING THE FIRE WITH A BUCKET FULL OF EXCAVATED MATERIAL. THERE WERE NO INJURIES AND NO DAMAGE TO THE PIPELINE OR EXCAVATION EQUIPMENT. AS OF THIS DATE, APPROXIMATELY 250 FEET OF MAIN LINE PIPE HAS BEEN EXCAVATED AND BACKFILLED. A TOTAL OF 8,442 GALLONS OF OIL AND WATER HAS BEEN RECOVERED (2,200 GALLONS CRUDE OIL). APPROXIMATELY 3,200 CUBIC YARDSO F CONTAMINATED SOIL HAS BEEN EXCAVATED. APPROXIMATELY 1,500 CUBIC YARDS HAS BEENCHARACTERIZED AS HEAVILY CONTAMINATED WITH REMAINDER BEING LIGHTLY CONTAMINATED. THE SOUTHERN EXTREMITY OF CONTAMINATED SOILS WAS FOUND ON MAY 14TH. HOWEVER, EXCAVATION IS NOT COMPLETE SINCE THE NORTHERN EXTREMITY OF THE CONTAMINATED SOIL HAS NOT BEEN DETERMINED. A TEST HOLE TO EXPOSE THE PIPE 200 FEET NORTH (DOWNHILL) FROM THE VALVE SHOWED NO EVIDENCE OF CRUDE OIL OR BENZENE VAPORS. THIS WOULD INDICATE THAT EXCAVATION IS MORE THAN 50% COMPLETE. THE PIPE DITCH IS IN SOLID BEDROCK AND IS QUITE IMPENETRABLE. NO EVIDENCE HAS BEEN FOUNDTHAT INDICATES THE CRUDE OIL IS MIGRATING OUT OF THE PIPE TRENCH. A SUPPLEMENTAL ACCIDENT REPORT WILL BE FILED WHEN FINAL SPILL ESTIMATES ARE COMPLETE. THIS ACCIDENT WAS REPORTED BY TELEPHONE ON APRIL 20, 1996. IT WAS EXPECTED THAT THE SPILL VOLUME AND REPAIRS WOULD EXCEED THE REPORTING LIMIT. THE SMALL FIRE ON APRIL 27TH WAS REPORTED TO THE LOCAL DEPARTMENT OF TRANSPORTATION REPRESENTATIVE ONLY. THE CAUSE OF THE SPILL APPEARS TO BE CAUSED BY THE INADEQUATEDESIGN AND INSTALLATION OF A VALVE ACTUATOR VAULT IN 1982 THAT WAS BEARING ON THE 1/2" THREADED PIPE PLUG. THE VAULT CAUSED THE THREAD-O-LET TO CRACK ANDLEAK. THERE ARE 40 BELOW GRADE MAINLINE CHECK VALVES IN THE SYSTEM. ALL HAVEBEEN VISUALLY INSPECTED AS MUCH AS POSSIBLE WITHOUT EXCAVATION AND NO ADDITIONAL PROBLEMS HAVE BEEN IDENTIFIED.
2017-09-29 08:50 | YES | NO | 19960080 | 1996-05-29 | 2552 | COLONIAL PIPELINE CO | YES | 1996-04-23 | 1810 | SC | CHEROKEE |  | NO |  | NO | LINE #1, STATION 5305 +15 |  | LINE PIPE | OTHER | NOT GIVEN | 1978 | OTHER | NOT GIVEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 324428.1793 | 654502.6794 | GASOLINE | 3 | 33 | 33 | NO | NO | 40 | 0.31 | 0 | WELDED |  | 936 | 0 | YES | 4 | 0 | 10 | 1978 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J.L. GAMBRELL | 4048412402 | AT 1810 EST ON APRIL 23, 1996, THE ATLANTA CONTROL CENTER RECEIVED A CALL FROM A LANDOWNER NEAR BLACKSBURG, SC REPORTING PRODUCT IN A SMALL STREAM NEAR COLONIAL'S TWO PIPELINES THAT TRAVERSE THIS AREA. THE TWO PIPELINES, A 36-INCHDISTILLATE LINE AND A 40-INCH GASOLINE LINE WERE IMMEDIATELY SHUT DOWN AND PERSONNEL WERE DISPATCHED TO THE AREA TO INVESTIGATE. A COMPANY REPRESENTATIVEARRIVED AT THE SITE AND NOTED A SMALL AMOUNT OF GASOLINE IN THE CREEK. EMERGENCY RESPONSE PERSONNEL AND RESPONSE AND REPAIR CONTRACTORS WERE DISPATCHED IMMEDIATELY TO THE SCENE TO BEGIN CONTAINMENT AND RECOVERY OPERATIONS. THE 40-INCH GASOLINE LINE WAS EXPOSED AND THE SOURCE OF THE LEAK WAS FOUND TO BE A SMALL CRACK LOCATED AT THE JUNCTION OF TWO OVERLAPPING DENTS ON THE BOTTOM OF THE PIPE. THE LINE WAS REPAIRED BY INSTALLING A REPAIR CLAMP OVER THE DENTS AND CRACK. AS OF 4/21/96, APPROXIMATELY 33 BARRELS OF GASOLINE HAD BEEN RECOVERED. THE ENVIRONMENTAL TEAM. IS CONTINUING RECOVERY ACTIVITIES. THE INVESTIGATION AND CLEAN-UP CONTINUES INTO THE INCIDENT. AN AMENDED REPORT ALL BE FILEDAT A LATER DATE TO PROVIDE THE AMOUNT OF PRODUCT SPILLED, THE PRESSURE OF THE LINE AT THE INCIDENT OCCURRED, AND THE HYDROSTATIC PRESSURE AT THE SPILL SITE.
2017-09-29 08:50 | YES | NO | 19960081 | 1996-06-04 | 4805 | EXPLORER PIPELINE CO | YES | 1996-05-06 | 1500 | OK | TULSA | GLENPOOL | NO |  | NO | EXPLORER PIPELINE COMPANY'S GLENPOOL TANKFARM AT INTERSECTION OF HIGHWAY 75 AND 126TH STREET, GLENPOOL OK. |  | TANK FARM | TANK |  | 1986 | OTHER | ICE DAMAGED ROOF WATER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1441.903 | 2908.9008 | GASOLINE | 2 | 202 | 202 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RODNEY E. SANDS | 9184935100 | ON MAY 6, 1996 AT 1530 HOURS A CONTRACT MAINTENANCE INSPECTOR DISCOVERED GASOLINE ESCAPING FROM THE ROOF DRAIN OF OPEN FLOATING ROOF TANK 334. THE ROOF DRAIN ON EMPTY TANK 334 HAD BEEN OPENED EARLIER THAT MORNING TO DRAIN THE PREVIOUS NIGHTS RAINWATER FROM THE ROOF. THERE WAS NO WATER FLOW FROM THE ROOF DRAIN WHEN IT WAS OPENED, WHICH IS NOT USUSAL WHEN THE TANK IS EMPTY AND THE ROOF IS STANDING ON LEGS, SO THE DRAIN WAS LEFT OPEN TO DRAIN WHEN THE TANK ROOF BEGAN FLOATING. AT 1241 HOURS THE GLENPOOL TERMINAL OPERATOR SWITCHED THE 28" MAINLINE INTO THE TANK 334. UNLEADED GASOLINE BEGAN LEAKING FROM THE DRAINLINE SOMETIME PRIOR TO DISCOVERY AT 1530 HOURS THE SAME DAY. UPON DISCOVERY OF GASOLINE LEAKING FROM THE ROOF DRAIN LINE, THE ROOF DRAIN VALVE WAS CLOSEDAND VACUUM TRUCKS WERE IMMEDIATELY DISPATCHED TO THE SITE. THE SPILLED GASOLINE WAS FLOATING ON STANDING RAINWATER AND WAS TOTALLY CONTAINED WITHIN THE TANK DIKE AREA. THE SPILLED GASOLINE WAS RECOVERED WITH VACUUM TRUCKS BY 2100 HOURS ON MAY 6, 1996. THANK 334 WAS REMOVED FROM SERVICE AND CLEANED. IT WAS DETERMINED THE ROOF DRAIN PIPE ADJACENT TO THE BOTTOM OF THE FLOATING ROOF WAS SPLIT, ALLOWING GASOLINE TO FLOW FROM THE TANK INTO THE WATER DRAIN LINE.
2017-09-29 08:50 | YES | NO | 19960082 | 1996-06-03 | 809 | ARCO PIPE LINE CO | YES | 1996-05-20 | 1800 | OK | PONTOTOC |  | NO |  | NO | FROM THE TOWN OF OAKMAN, OKLAHOMA, ONE MILE EAST AND 0.2 MILES S. IN SECTION 7, TOWNSHIP 4N,RANGE 7ESE QUARTER. LATTITUDE N34 49' 35.2, LONGITUDE W96 36' 06.7 |  | PUMPING STATION | OTHER | CONNECT TO 30"X1" THREAD | 1985 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 780000 | 562342.1775 | 1134471.3109 | CRUDE OIL | 1 | 5080 | 4845 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | GLENN W. HOFFMEYER | 4052735151 | AT APPROXIMATELY 18:00 ON MAY 20, 1996, A LEAK WAS DISCOVERED AND EXCAVATIONAT THE SITE REVEALED THAT THE SOURCE OF THE RELEASE WAS A 1-INCH THREAD-O-LETT AT THE 6-O'CLOCK POSITION ON A BURIED PORTION OF THE 30-INCH MAIN LINE, APPROXIMATELY 30 FEET NORTH OF THE STATION BLOCK VALVE. THE LEAK OCCURRED IMMEDIATELY FOLLOWING THE COMMISSIONING OF THE 30" SEAWAY PIPELINE, WHICH EXTENDSFROM FREEPORT, TEXAS TO CUSHING, OKLAHOMA. THE 1-INCH THREAD-O-LETT WAS DETERMINED TO BE A SAMPLE CONNECTION WHICH HAD APPRARENTLY BEEN DAMAGED DURINGCONSTRUCTION ACTIVITY ASSOCIATED WITH THE CONVERSION OF THE SEAWAY 30" FROMGAS TO LIQUID SERVICE. IMMEDIATELY AFTER NOTIFICATION OF THE RELEASE, THE LINE WAS SHUT DOWN AND EMERGENCY RESPONSE AND CLEANUP PERSONNEL WENT TO THE SITETO UNDERTAKE CONTAINMENT, CLEANUP AND REPAIR ACTIVITIES. ALTHOUGH NO WATER WASYS WERE AFFECTED, THE AREA AFFECTED BY THE RELEASE INCLUDED APPROXIMATELY3/4 MILE OF A DRY CREEK, LOCATED ON PRIVATE PROPERTY TO THE SOUTH OF THESEAWAY FACILITY. METERED VOLUMES INDICATE A TOTAL RELEASE VOLUME OFAPPROXIMATELY 5,080 BARRELS OF CRUDE, INCLUDING THE VOLUME OF OIL REMOVED TOMAKE REPAIRS ON THE PIPELINE. APPROXIMATELY 5,100 BARRELS OF LIQUID HAS BEENRECOVERED FROM THE RELEASE SITE AND TRANSPORTED TO OUR PANOVA STATION FORRE-INJECTION INTO THE SYSTEM. LIQUID RECOVERED CONTAINS AN ESTIMATED 5% WATERUSED IN FLUSHING OPERATIONS DURING WASHING OF THE DRY CREEK, MAKING THEESTIMATED VOLUME OF CRUDE OIL RECOVERED 4,845 BARRELS.
2017-09-29 08:50 | YES | NO | 19960083 | 1996-06-04 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1996-05-15 | 800 | MN |  | VIKING | NO |  | NO | VIKING STATION - M.P. 847.91 |  | PUMPING STATION | BOLTED FITTING | FLANGE | 1973 | OTHER | HEADER PIPING FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 28838.0604 | 58178.0159 | CRUDE OIL | 1 | 50 | 5 | NO | NO | 34 | 0 | 0 | FLANGED |  | 960 | 600 | YES | 24 | 1400 | 7 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.C. SANDAHL | 2187250102 | LEAKHEAD FIELD PERSONNEL DISCOVERED OIL ON TOP OF THE GROUND ADJACENT TO THEVIKING LINE 3 PUMPHOUSE BUILDING ON MAY 15. EXCAVATION CONFIRMED OIL SATURATED SOIL NEAR THE UNIT 3.3 FLANGE AT 1100 MST. THE FEDERAL EMERGENCY RESPONSE CENTER WAS CONTACTED AT 1145 MST ON MAY 15. THE MINNESOTA DUTY OFFICER WAS CONTACTED AT 1155 MST ON MAY 15. UNIT 3.3 WAS SHUTDOWN AND ISOLATED AT 1147 MST. UNIT 3.3 SUCTION VALVE FLANG (UNIT SIDE) WAS EXPOSED AT 1400 MST AND NO LEAKAGE WAS APPARENT AND INVESTIGATION ON THE OTHER SIDE OF THE VALVE COMMENCED.AT 1700 MST THE LEAK WAS CONFIRMED TO BE FROM THE FLANGE CONNECTION OF THE HEADER SIDE OF UNIT 3.3 SUCTION VALVE. LAKEHEAD WAS LATER CONTACTED BY THE MINNESOTA OFFICE OF PIPELIFNE SAFETY (MNOPS) AND THE MINNESOTA POLLUTION CONTROLAGENCY (MPCA). REPRESENTATIVES FROM BOTH THE MNOPS AND MPCA WERE ON SITY ON MAY 16. THE GASKET WAS REPLACED REQUIRING A STATION DRAIN-UP AND THE STATION PLACED BACK ON LINE AT O414 MST ON MAY 16.
2017-09-29 08:50 | YES | NO | 19960084 | 1996-06-04 | 19226 | TEXACO PIPELINE INC | NO | 1996-05-10 | 2130 | TX |  | PORT ARTHUR | NO |  | NO | 1825 H.O. MILLS AND WEST PORT ARTHUR ROAD PORT ARTHUR, TEXAS |  | TANK FARM | TANK |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 3965.2333 | 7999.4772 | JET FUEL | 3 | 176 | 175 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. LEDNICKY | 7134323401 | TEXACO PIPELINE INC. PORT ARTHUR PORDUCTS STATION OPERATOR MADEN IMPROPER VALVE ALIGNMENT CAUSING PRESSURE INCREASE ON DELIVERY MAINFORLD TO COLONIAL PIPELINE COMPANY. PRESSURE REACHED LEVEL SUFFICIENT TO ACTIVATE RELIEF VALVES RELIEVING PRODUCT INTO MAINFOLD SURGE TANK. THE OPERATOR WAS UNABLE TO SHUT DOWN THE PRODUCT STREAM BEFOR THE SURGE TANK BECAME FULL AND DID OVERLFOW. ALL SPILLED PRODUCT WAS CONATAINE WITH THE TANK FARM LEVEE.
2017-09-29 08:50 | YES | NO | 19960085 | 1996-06-04 | 1036 | BADGER PIPELINE CO | YES | 1996-05-05 | 700 | IL | WINNEBAGO | ROCKFORD | NO |  | NO | 7245 CUNNINGHAM ROAD ROCKFORD, IL 61102 |  | PUMPING STATION | TANK |  | 1954 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 12500 | 9011.8939 | 18180.63 | GASOLINE | 1 | 180 | 180 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAY ANDREWS | 8474390270 | ON MAY 5, 1996 THE BADGER PIPELINE CONTROL CENTER RECEIVED A VAPOR DTECTION ALARM FROM THE BADGER ROCKFORD STATION. UPON RECEIPT OF THE ALARM THE CONTROLLER SHUT DOWN THE PIPELINE AND NOTIFIED A BADGER FIELD TECHNICIAN. THE BADGERPIPE LINE TECHNICIAN RESPONDED TO THE ALARM. UPON ARRIVAL AT THE STATION THEEMPLOYEE OBSERVED THAT A TANK AT A N ADJACENT OIL TERMINAL UPON WHICH BADGERHAD BEEN DELIVERING WAS OVER FLOWING. THE EMPLOYEE CALLED THE CONTROL CENTERAND TOLD THEM OF THE OVERFILL AND PUSHED BUTTONS AT THE STATION TO CLOSE THEPIPELINE MANIFOLD VALVE TO THE OIL TERMINAL. THE TECHNICIAN ALSO INADVERTENTYLY AND WITHOUT THIS DNOWLEDGE PUSHED A BUTTON WHICH SWITCHED THE DIVERTER VALVE FROM THE MANIFOLD INTO THE STATION INTERFACE TANK. UPON START UP ON MAY 6, 1996 THE BADGER CONTROLLER FAILED TO NOTICE THAT THE DIVERTER VALVE HAD BEEN SWITCHED. WHEN THE LIN STARTED INSTEAD OF MAKINGT A DELIVERY INTO THE OIL TERMINAL THE PRODUCT WAS DIVERTED INTO THE 1500 BARREL INTERFACE TANK. THE PRIMARY TANK ALARM FAILED AND APPROXIMATELY 6500 GALLONS OF NOLEAD GASOLINE WAS SPILLED INTO THE TANK DIKE BEFORE THE CONTROLLER REALIZED THE DIVETER VALVE WAS IN THE WRONG POSITION. ALL OF THE PRODUCT WAS CONTAINED WITHIN VALVE WAS IN THE WRONG PISITION. ALL OF THE PRODUCT WAS CONTAINED WITHIN THE TANK DIKE AND WAS SAFELY REMOVED WITHIN THE NEXT 8 HOURS.
2017-09-29 08:50 | YES | NO | 19960086 | 1996-06-05 | 1044 | WESTTEX 66 PIPELINE COMPANY | YES | 1996-05-08 | 1956 | TX | FORT BEND |  | NO |  | NO | BENEDUM-SWEENY LINE-ROSENBERG PUMP STATION APPROXIMATELY 7 MI. S. OF ROSENBERG,TX, OR 4 MI. NE OF NEEDVILLE, TX. THE PUMP STATION IS ON THE S. SIDE OF FM 361, |  | PUMPING STATION | PUMP | PUMP SEAL | 1995 | OTHER | PUMP SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2600 | 1874.4739 | 3781.571 | NATURAL GAS LIQUID | 2 | 6 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J. SCHMITZ | 9186614814 | THE FIRE DEPARTMENT RELAYED A CITIZEN'S REPORT OF ODOR AND A CLOUD AT THE PUMP STATION. THE LINE WAS SHUT DOWN. THE FIRE DEPARTMENT MONITORED THE SITE AND CONTROLLED ACCESS UNTIL COMPANY EMPLOYEES ARRIVED. THE SEAL WAS REPLACED AND SHUTDOWN ALARMS WERE RE-ADJUSTED. APPROX. 1200 FEET NW OF THE INTERSECTION OF FM 361 AND FM 2977
2017-09-29 08:50 | YES | NO | 19960087 | 1996-06-17 | 30871 | MID-VALLEY PIPELINE COMPANY | YES | 1996-05-10 | 256 | OH | WOOD | CYGNET | NO |  | NO | 1.5 MILES SOUTH OF CYGNET, OH ON ROCK RIDGE ROAD, AT MID-VALLEY'S CYGNET PUMP STATION/TANK FARM. |  | LINE PIPE | PIPE |  | 1983 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 72095.151 | 145445.0399 | CRUDE OIL | 1 | 100 | 93 | NO | NO | 0.5 | 0.14 | 35000 | THREADED |  | 788 | 550 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.L. COOK | 6063714469 | AT 0130 A HEAVY RAIN AND LIGHTNING STORM IN THE AREA DISRUPTED SATELLITECOMMUNICATION WITH MVPL CONTROL CENTER AND SHUTDOWN CYGNET PUMPS. DUE TOCYGNET PUMPS BEING DOWN PRESSURE ROSE TO THE RELIEF POINT AND PART OF THESTREAM BEGAN RELIEVING INTO CYGNET TANKAGE. A 1/2" NIPPLE APPENDAGE NEXT TOTHE RELIEF VALVE FAILED AND RELEASED CRUDE FOR 30 MINUTES UNTIL LINE WASSHUTDOWN.
2017-09-29 08:50 | YES | NO | 19960088 | 1996-06-12 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1996-05-07 | 705 | CA | ORANGE | ORANGE | NO |  | NO | ORANGE TERMINAL LOCATED AT 1350 N. MAIN STREET, ORANGE, CALIFORNIA 92667 TANK FARM, SANTA ANA RIVER BED AND BIKE TRAIL. |  | TANK FARM | TANK |  | 1962 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 144190.3019 | 290890.0797 | GASOLINE | 3 | 235 | 205 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 7145604720 | MALFUNCTION IN RELIEF VALVE RESULTED IN ABOVEGROUND STORAGE TANK OVERFLOW. TANK IS LOCATED IN AREA OF SECONDARY CONTAINMENT. RELEASE DID NOT AFFECT SURFACE WATERS AND WAS CONTAINED BY USING SAND BAGS AND CLEANED UP BY VACUUM TRUCKS
2017-09-29 08:50 | YES | NO | 19960089 | 1996-06-11 | 30869 | WAMSUTTER PIPELINE, INC. | NO | 1996-05-12 | 1100 | WY | SWEETWATER |  | NO |  | YES | SECT.24 T19N R98W - 1.5 MILES NORTHEAST OF CIG PLANT - SOUTH OF PP & L SUBSTATION. |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 5046.6606 | 10181.1528 | CRUDE OIL | 1 | 200 | 60 | NO | NO | 6.63 | 0.19 | 35000 | WELDED |  | 1011 | 400 | YES | 0 | 1573 |  |  | INTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES W. MUSGROVE | 3073526009 | THE LEAK WAS FOUND 11:00 AM ON MAY 12, 1996 BY JIM BALL OVERLAND TRAIL/WAMSUTTER OPERATOR. THE LEAK WAS QUICKLY ISOLATED, EMERGENCY CREW DISPATCHED. AN ESTIMATED 200 BARRELS WAS SPILLED BASED ON THE STAINED AREA. SIXTY BARRELS OF CRUDE WAS VACUUMED UP AND STORED IN A TANK FOR REDELIVERY. SPILL WAS CONFINEDTO THE R.O.W. IN A REMOTE AREA WITH NO THREAT TO THE PUBLIC OR WATER WAY. THE LEAK WAS CAUSED BY INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19960090 | 1996-06-18 | 1845 | BUCKEYE PIPELINE CO LP | NO | 1996-05-16 | 712 | FL | BROWARD |  | NO |  | NO |  |  | PUMPING STATION | VALVE |  | 1959 | OTHER | BONNET GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 21628.5453 | 43633.512 | JET FUEL | 3 | 130 | 99 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL C. LARKIN | 6107704507 | AT 0712 ON MAY 16, 1996, THE RECEIPT CONTROLLER AT PORT EVERGLADES PUMP STATION RECEIVED A CALL FROM TEXACO REPORTING A SMELL OF PRODUCT IN THE VICINITY OF EVERGLADES 10" LOW PRESSURE RECEIPT LINE. AT 0714 EVERGLADES RECEIPT LINEFROM COASTAL WAS SHUT DOWN AND PERSONNEL WERE IMMEDIATELY DISPATCHED TO INVESTIGATE. PRODUCT WAS DISCOVERED IN A DITCH AND IN A VALVE PIT. THE SOURCE OF THE RELEASE WAS DETERMINED TO BE A VALVE BONNET GASKET. REPAIRS WERE COMPLETEDAT 1625 ON MAY 26, 1996. ALL APPLICABLE AGENCIES WERE NOTIFIED AND RECOVERYAND CLEANUP ACTIVITIES HAVE BEEN COMPLETED. THE COAST GUARD, BROWARD COUNTY EMERGENCY MANAGEMENT, PORT EVERGLADES FIRE DEPARTMENT, AND THE DEPARTMENT OF NATURAL RESOURCE PROTECTION OF BROWARD COUNTY WERE ALL ON SITE.
2017-09-29 08:50 | YES | NO | 19960091 | 1996-06-20 | 2552 | COLONIAL PIPELINE CO | YES | 1996-05-17 | 1630 | NC | GUILFORD | GREENSBORO | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 72095.151 | 145445.0399 | GASOLINE | 3 | 1 | 1 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1252 | 1075 | YES | 24 | 1566 | 0 | 63 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | J.A. COX | 4048412296 | ON MAY 17, 1996, AT 1530 HOURS COLONIAL PIPELINE COMPANY WAS NOTIFIED OF A SHEEN OF PRODUCT ON A CREEK OFF INDIAN HILLS LANE. ALL THREE SELMA STUBLINES WERE SHUT DOWN AT 1534 HOURS. THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 1624HOURS (REPORT NUMBER 342514). THE SOURCE OF THE LEAK WAS DISCOVERED TO BE ANON LINE 23 AT 2242 HOURS. TWO DENTS WERE FOUND ON THE PIPELINE AT THE 12:00 AND 1:00 O'CLOCK POSITIONS. THE LEAK RESULTED FROM A CRACK LOCATED BETWEEN THEDENTS. AN 18-INCH SLEEVE WAS INSTALLED, AND THE PIPELINE WAS RESTARTED AT 0706 HOURS ON MAY 18, 1996.THE FINAL CLEAN-UP WAS COMPLETED ON MAY 24, 1996.
2017-09-29 08:50 | YES | NO | 19960092 | 1996-06-21 | 12127 | MARATHON PIPE LINE CO | YES | 1996-05-23 | 2200 | LA | ST JAMES | GRAMMERCY | NO |  | NO | SECTION 73, T11S, R5E, 347 FEET SOUTH OF THE CENTER LINE OF HIGHWAY 61 SOUTHBOUND LANE. |  | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6984000 | 5035125.3431 | 10157881.5841 | GASOLINE | 3 | 11308 | 781 | NO | NO | 20 | 0.31 | 65000 | WELDED |  | 1440 | 1094 | YES | 24 | 1926 | 2 | 1977 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | JOSEPH A. FISHER | 4194213201 | THE PRECISE TIME AND DURATION OF THE RELEASE ARE UNKNOWN AT THIS TIME. THE RELEASE APPEARS TO HAVE BEGUN SOMETIME AFTER 2200 HOURS (CDT) ON MAY 23, 1996.THE RELEASE OCCURRED IN A TIDALLY AFFECTED SWAMP, SITUATED BETWEEN U.S. HIGHWAY 61 (AIRLINE HIGHWAY) AND THE KANSAS CITY SOUTHERN RAILROAD, AND PRODUCT MIGRATED INTO THE BLIND RIVER. THE PUMPS AT GARYVILLE STATION WERE SHUT DOWN AND LOCAL MPL PERSONNEL WERE DISPATCHED TO THE AREA TO INVESTIGATE THE SITUATION. AFTER THE RELEASE LOCATION WAS DISCOVERED, THE BLOCK VALVES ON EITHER SIDEOF THE RELEASE SITE WERE CLOSED. DURING THE REPONSE, A PORTION OF AIRLINE HIGHWAY AND THE RAILROAD WERE CLOSED TO TRAFFIC. THE NATIONAL RESPONSE CENTER AND THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY WERE PROMPTLY NOTIFIED OF THE INCIDENT. AN INCIDENT COMMAND CENTER WAS SET UP WITHIN HOURS AND A RESPONSE TEAM CONSISTING OF MARATHON PERSONNEL AND SEVERAL RESPONSE CONTRACTORS WERE BROUGHT IN TO EFFECT THE RESPONSE. APPROXIMATELY 3600 FEET OF BOOM WAS PLACED AT STRATEGIC LOCATIONS IN THE BLIND RIVER AND ITS TRIBUTARIES TO CONTAINTHE RELEASE. THE RESPONSE AREA WAS ROUTINELY MONITORED FOR FLAMMABLE ATMOSPHERE, BENZENE AND CARBON DIOXIDE TO ENSURE SAFETY OF PERSONNEL AND PUBLIC. SOME MONITORING WAS ALSO DONE FOR TOTAL PETROLEUM HYDROCARBONS AND TOTAL VOC. WEBELIEVE THAT NO MEMBER OF THE PUBLIC WAS THROUGHOUT THE INCIDENT TO MONITORVITAL SIGNS OF THE PERSONNEL WORKING IN THE AFFECTED AREA. THE PRINCIPLE AFFECTED AREA WAS BERMED OFF TO FURTHER PREVENT POTENTIAL OFFSITE MIGRATION OF RESIDUAL HYDROCARBONS. DURING THE INITIAL RESPONSE, MARATHON WORKED CLOSELY WITH STATE AND FEDERAL AGENCIES TO ASSESS POTENTIAL IMPACTS TO WATER AND WILDLIFE, AND WE CONTINUE THESE SITE ASSESSMENTS TO DEVELOP LONG-TERM REMEDIATION PLANS. THE FAILED SECTION OF PIPE WAS REPLACED WITH A 24-FOOT SECTION OF COMPARABLE PRETESTED PIPE. FURTHER INSPECTION OF THE LINE DISCOVERED AN ADDITIONALLOCATION WITH SURFACE DAMAGE. THE PIPE AT THIS SECOND LOCATION WAS REPLACED WITH AN 18-FOOT SECTION OF COMPARABLE PRETESTED PIPE. PLANS ARE BEING FORMULATED TO CONDUCT AN INTERNAL INSPECTION OF THE PIPELINE WITH AN INLINE INSPECTION TOOL (SMART PIG). THE LINE HAS BEEN RETURNED TO OPERATION AND, AS A PRECAUTION, THE SYSTEM IS BEING OPERATED AT A REDUCED MAXIMUM PRESSURE OF 875 PSIG UNTIL THE ANALYSIS OF THE LINE CONDITION CAN BE COMPLETED. AS OF THIS WRITING (8-20-01) ALL DAMAGE CLAIMS HAVE BEEN SETTLED AND THE PIPELINE RETURNED TO FULL OPERATING SERVICE.
2017-09-29 08:50 | YES | NO | 19960093 | 1996-06-21 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | YES | 1996-05-18 | 1330 | TX | LIBERTY | CLEVELAND | NO |  | NO | 3-4 MILES WEST OF CLEVELAND, TX OFF HWY 105 AND CLOSE TO RAILROAD RIGHT-OF-WAY. |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5407.1363 | 10908.378 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 10 | 0.37 | 30000 | WELDED |  | 750 | 100 | YES | 12 | 1006 | 12 | 80 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | JERRY ROGERS | 4053952377 | THIRD PARTY OPERATOR STRUCK PIPELINE WITH DOZER EQUIPMENT, PUNCTURING PIPELINE AND ALLOWING PRODUCT AND NITROGEN TO BE RELEASED.
2017-09-29 08:50 | YES | NO | 19960094 | 1996-06-21 | 18718 | SUN PIPELINE CO | NO | 1996-06-04 | 1130 | OK | MCCLAIN |  | NO |  | NO | SW11-5N-3W MCLAIN COUNTY, OK |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 720.9515 | 1454.4504 | CRUDE OIL | 1 | 50 | 40 | NO | NO | 6.63 | 0.16 | 904 | NO DATA |  | 651 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | E.F. COEN | 9185866942 | J. CURRY, CONTRACT AIR PATROL SPOTTED LEAK. R. NEWELL, A. PONDS, SPL EMPLOYEES, D. GAMBLE AND R. JARMAN. RINEHART CONTRACT EMPLOYEES DUG OUT LINE AND INSTALLED A TEMPORARY CLAMP. OIL WAS PICKED UP BY FEMCO TANK SERVICE AND HAULED TO MAYSVILLE STATION.
2017-09-29 08:50 | NO | NO | 19960095 | 1996-06-26 | 19223 | SUN PIPE LINE COMPANY | YES | 1996-05-23 | 1835 | PA | LYCOMING | WILLIAMSPORT | NO |  | NO | SUSQUEHANNA RIVER, WEST BRANCH |  | LINE PIPE | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 1 | 0 | NO | NO | 8 | 0.32 | 2610 | WELDED |  | 1300 | 1200 | NO | 0 | 0 |  |  | NO DATA | Null | YES | NO DATA |  | OTHER | NOT GIVEN | Null | ONE CALL |  | Null | Null | ALAN D. GILLIE | 2159773344 | THE POST-LEAK INTERNAL INSPECTION USING AN ENDURO GEOMETRY PIG, INDICATES THA THER WERE TOW ANOMALIES CLASSIFIED AS "SHARP" IN THE IMMEDIATE VICINITY OF THE LEAK. THESE "SHARP" INDICATIONS PROHIBITED PASSAGE OF AN ATLAS WIRELINE MAGNETIC FLUX INSPECTION TOOL. IT WAS IMPRACTICAL TO EXPOSE THE LINE TO CONDUCT AN EXTERNAL INSPECTION DUE TO THE SUSQUEHANNA RIVER AND ITS CONDITIONS. BASED UPON THE ABOVE, WE COULD NOT DETERMINE A SPECIFIC CAUSE OF THE LEAK. WE REPLACED TH ENTIRE CROSSING PER OUR CORRESPONDENCE WITH OPS.
2017-09-29 08:50 | NO | NO | 19960096 | 1996-06-27 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1996-05-28 | 1630 | TX | NAVARRO |  | NO |  | NO | RICHLAND CHAMBERS LAKE, NAVARRO COUNTY, TEXAS, APPROX. 6 MILES EAST OF CORSICANA |  | LINE PIPE | OTHER | NOT GIVEN | 1986 | OTHER | NOT GIVEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT | 2146585914 | AT APPROXIMATELY 1630 HRS. ON MAY 28, 1996, COMPANY PATROL PILOT REPORTED A SMALL SHEEN AT MILE POST 11 RICHLAND CHAMBERS RESERVOIR. MOBIL PIPE LINE COMPANY HAS A 2" CRUDE OIL PIPELINE CROSSING RICHLAND CHAMBERS. THE PATROL PILOT REPORTED THE SHEEN TO MPL CO. OPERATIONS CONTROL CENTER IN DALLAS AND THE LINE WAS IMMEDIATELY SHUT DOWN AND ISOLATED. CREWS FROM CORSICANA, TEXAS WERE DISPATCHED TO THE AREA TO INVESTIGATE SITUATION. NO PRESSURE DROP HAD BEEN NOTICED BY DALLAS SO TO ENSURE THE INTEGRITY OF THE PIPELINE THE OIL IN THE ISOLATED SECTION WAS DISPLACED WITH NITROGEN AND A 6 HOUR PLRESSURE TEST WAS CONDUCTED. THE TEST HELD A CONSTANT 525 PSI. AND THEREFORE IT WAS DETERMINED THAT NO LEAK HAD OCCURRED. THE LINE WAS PUT BACK IN SERVICE AT APPROX. 1100 HRS. ON MAY 30, 1996. ALL REQUIRED GOVERNMENTAL AGENCIES WERE NOTIFIED. THE SHEEN THAT WAS REPORTED BY THE PATROL PILOT COULD HAVE POSSIBLY BEEN FROM OLD ABANDONED WELLS IN THE VICINITY PRIOR TO THE CONSTRUCTION OF THE RESERVOIR.
2017-09-29 08:50 | YES | NO | 19960097 | 1996-06-28 | 22610 | WILLIAMS PIPELINE CO | YES | 1996-05-21 | 930 | OK | OSAGE |  | NO |  | NO | SOUTHWEST 1/4 OF THE NORTHEAST 1/4 OF SECTION 25, TOWNSHIP 25N RANGE 6E IN OSAGE COUNTY, OKLAHOMA. |  | LINE PIPE | PIPE |  | 1947 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 0 | 0 | YES | NO | 8 | 0.2 | 35000 | WELDED |  | 900 | 500 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S. BALL | 9185883454 | ON MAY 21, 1996, THE WPL MAINTENANCE CREW WAS PERFORMING ROUTINE MAINTENANCEON THE PONCA CITY OF BARNSDALL #1-8" LINE BY REMOVING A CASING FROM THE PIPELINE WHERE IT CROSSED AND ABANDONED RAILROAD. WHILE PERFORMING THE CASING REMOVAL PROCEDURES, THE CARRIER PIPE WAS ACCIDENTALLY CUT RELEASING PRODUCT, WHICH IGNITED CREATING A SMALL CONTROLLABLE FIRE.A THE FIRE WAS IMMEDIATELY EXTINGUISHED, THE OPENING WAS CLAMPED OFF AND THE LINE WAS REPAIRED USING A PATCH. SINCE SUCH A SMALL RELEASE WAS EXPERIENCED, LESS THEN 5 GALLONS, NO EXTENSIVE ENVIRONMENTAL CLEAN-UP OPERATIONS WERE REQUIRED.
2017-09-29 08:50 | YES | NO | 19960098 | 1996-06-25 | 9175 | JAYHAWK PIPELINE CORP | YES | 1996-06-12 | 1430 | KS | MCPHERSON |  | NO |  | NO | SW 1/4 SECTION 11, TOWNSHIP 21 SOUTH RANGE 5 WEST, MCPHERSON COUNTY 4 MILES WEST OF INMAN KANSAS |  | LINE PIPE | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4325.7091 | 8726.7024 | CRUDE OIL | 1 | 75 | 0 | NO | NO | 8.63 | 0.28 | 35000 | WELDED |  | 500 | 200 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | LANDOWNER REPORTED TO JAYHAWK CONCERNING CRUDE OIL SPILL IN HIS WHEAT FIELD.JAYHAWK RESPONDED AND CONTAINED LEAK. A FULL ENCIRLEMENT WAS USED FOR REPAIRAND SOIL WILL BE REMEDIATED ON SITE.
2017-09-29 08:50 | YES | NO | 19960099 | 1996-06-24 | 2271 | CHASE TRANSPORTATION CO | YES | 1996-05-24 | 2025 | KS | RENO |  | NO |  | NO | FROM PRETTY PRAIRIE, KANSAS, 3 MILES NORTH AND 1 MILE WEST ON S.E. CORNER OF INTERSECTION. LEGAL DESCRIPTION- NW NW 1/4 SECTION 1 26S 7W RENO COUNTY, KS |  | PUMPING STATION | PUMP |  | 0 | OTHER | FAILED TUBING CONNECTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 90118.9387 | 181806.2998 | GASOLINE | 2 | 52 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LARRY ANGELL | 3168285634 | AT CHASE'S PRETTY PRAIRIE PUMP STATION ON PUMP #3 THE PUMP SEAL COOLING LINE 1/2" STAINLESS STEEL TUBING COUPLING CONNECTION FAILED (CAME OFF) CAUSING PRODUCT TO BE RELEASED.
2017-09-29 08:50 | YES | NO | 19960100 | 1996-06-24 | 30781 | OLYMPIC PIPELINE COMPANY | YES | 1996-06-17 | 1110 | WA | SNOHOMISH | EVERETT | NO |  | NO | 2.5 MILES EAST OF I-5 ON HWY 2 ON SOUTH DIKE OF NORTH EBBY SLOUGH CROSSING. EAST END OF EBBY ISLAND. PIPELINE M.P. 74.2 S23 T29N R5E |  | LINE PIPE | OTHER | NOT GIVEN | 1973 | FAILED PIPE | BUCKLE IN PIPE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7209.5151 | 14544.504 | GASOLINE | 2 | 25 | 5 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 920 | 547 | YES | 24 | 1145 | 8 | 73 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM MULKEY | 2062357745 | CONTRACTOR REPORTED PRODUCT SHEEN ON DRAINAGE DITCH AT EAST END OF EBBEY ISLAND. LINE(S) IMMEDIATELY SHUT DOWN & HELICOPTER DISPATCHED TO AREA. SHEEN ON WATER WAS IDENTIFIED NEAR 20" LINE CROSSING. EXCAVATED AREA ON SOUTH SIDE OF RETENTION DIKE REVEALED A BUCKLE IN PIPE AT 3-R BEND. CLEANUP WAS ACCOMPLISHED BY SORBENTS, SKIMMER AND SOIL REMOVAL. DOWNTIME ON 20" LINE ESTIMATED AT +100 HOURS PROPERTY DAMAGE ESTIMATED AT + 10,000 OPS NOTIFICATION 11:35 06/17/1996 INCIDENT NO 347536-RUTHEFORD.
2017-09-29 08:50 | YES | NO | 19960101 | 1996-07-01 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1996-05-30 | 1645 | LA | CADDO | SHREVEPORT | NO |  | NO | APPROXIMATELY 0.4 MI SOUTH FROM INTERSECTION OF VALLEY VIEW DRIVE AND MANSFIELD ROAD |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 10093.3211 | 20362.3056 | NATURAL GAS LIQUID | 3 | 65 | 21 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 330 | 90 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | W.J. HOFF | 7137593710 | AT APPROXIMATELY 1645 HOURS CDT, MAY 30, 1996, WHILE STRIPPING COVER OFF AN ABANDONED TEPPCO LINE, THE TRACKHOE'S BUCKET STRUCK AND PUNCTURED THE ADJACENT 8" LINE P-29. THE TEPPCO EMERGENCY PLAN WAS IMMEDATELY INITIATED, THE LINE WAS ISOLATED AND ALL REQUIRED NOTIFICATIONS WERE MADE. REMOVAL OF THE LEAKINGSECTION OF PIPE AND INSTALLATION OF NEW PIPE WAS COMPLETED MAY 31, 1996. DISPOSAL OF THE CONTAMINATED SOIL WAS COMPLETED UNDER THE GUIDANCE FURNISHED THROUGH THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY.
2017-09-29 08:50 | YES | NO | 19960102 | 1996-07-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-06-09 | 1850 | TX | GAINES |  | NO |  | NO | T-17-S R-39-E SECTION 5, PUBLIC SCHOOL BLOCK A-9 20 MILES WEST OF SEMINOLE, TX ON HIGHWAY 62/180, THEN 4-1/2 MILES NORTH. |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25080 | 18081.4639 | 36477.616 | NATURAL GAS LIQUID | 2 | 2078 | 0 | NO | NO | 6.63 | 0.16 | 42000 | WELDED |  | 1421 | 723 | YES | 27 | 1777 | 3 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOHNNY L. CAVITT | 9185993795 | A THIRD PARTY (FARMER) STRUCK AND PUNCTURED A SIX INCH PIPELINE CAUSING PRODUCT TO BE RELEASED. THE PIPE WAS EXCAVATED, REPAIRED AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19960103 | 1996-07-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | NO | 1996-06-06 | 1135 | KS | CHAUTAUQUA |  | NO |  | NO | 3 MILES NORTH OF SEDAN, KANSAS T-33-S R-11-E SEC 14 |  | LINE PIPE | PIPE |  | 1981 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10539 | 7598.108 | 15328.4528 | GASOLINE | 3 | 50 | 29 | NO | NO | 6.63 | 0.13 | 60000 | WELDED |  | 1630 | 0 | YES | 24 | 2246 | 8 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | JOHNNY L. CAVITT | 9185993795 | CONTRACTOR WAS PULLING ROCK TOWARDS LINE WHEN BUCKET TEETH SLIPPED OFF ROCKAND GOUGED THE PIPELINE CAUSING RELEASE OF PRODUCT. A SLEEVE WAS WELDED INTOPLACE AND THE LINE WAS RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19960104 | 1996-07-09 | 9175 | JAYHAWK PIPELINE CORP | YES | 1996-06-23 | 817 | KS | HASKELL |  | NO |  | NO | SW 1/4 SECTION 9, TOWNSHIP 27 SOUTH, RANGE 34 WEST, HASKELL COUNTY, KS 22 MILES NORTH OF SATANTA, KS. |  | LINE PIPE | PIPE |  | 1958 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4325.7091 | 8726.7024 | CRUDE OIL | 1 | 500 | 470 | NO | NO | 6.65 | 0.19 | 35000 | WELDED |  | 1250 | 1060 | YES | 8 | 1615 | 0 | 58 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | PIPE BROKE NEAR PREVIOUS WELD. PIPELINE WAS SHUT DOWN AND JAYHAWK RESPONDED WITHIN 2 HOURS OF NOTIFICATION. RECOVERED THE OIL. REPLACED 404 FT. OF TESTEDPIPE AND SOIL WILL BE REMEDIATED AT LOCATION.
2017-09-29 08:50 | NO | NO | 19960105 | 1996-07-09 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-06-11 | 1445 | WI | ROCK |  | NO |  | NO | R-12-E T-3-N SEC 18 11 MILES WEST OF JANESVILLE, WISCONSIN ON HWY 14 |  | TANK FARM | OTHER | NIPPLE ON PIPING | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 68.4904 | 138.1728 | L. P. G. | 3 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | SID RUETER | 9185811538 | WHILE REMOVING ABOVE GROUND PIPE AND FITTINGS FOR MAINTENANCE, A ONE-INCH NIPPLE CRACKED, RELEASING PRODUCT TO THE ATMOSPHERE. NIPPLE WAS REPLACED AND LINE WAS RESTORED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19960106 | 1996-07-10 | 12127 | MARATHON PIPE LINE CO | YES | 1996-06-10 | 1530 | IN | HENDRICKS |  | NO |  | NO | SW 1/4 SECT. 18, T17N,R2E BROWN TWP. HENDRICKS COUNTY, IN IN FARM FIELD NORTH OF COUNTY RD. 1000N |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 86514.1812 | 174534.0478 | GASOLINE | 3 | 10 | 2 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 1000 | 375 | YES | 8 | 1270 | 10 | 91 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH A. FISHER | 4194213201 | AT APPROXIMATELY 15:30 ON JUNE 10, 1996 MARATHON PIPELINE COMPANY'S (MPL'S)OPERATIONS CENTER LOCATED FINDLAY, OH WAS NOTIFIED BY A PROPERTY OWNER THAT THERE APPEARED TO BE A SMALL QUANTITY OF HYDROCARBON FLOATING ON STANDING WATERIN A FARM FIELD FOUR MILES NORTHEAST OF BROWNSBURG, IN. MPL'S #2-10" PRODUCTS LINE AND MARTINSVILLE TO INDIANAPOLIS 8" PRODUCTS LINE WHICH ARE KNOWN TO TRAVERSE THE AREA IN QUESTION, WERE SHUT DOWN AND MPL PERSONNEL RESPONDED TO THE SITE. UPON SITE INVESTIGATION, IT WAS DETERMINED THAT THE MARTINSVILLE TO INDIANAPOLIS LINE WAS NOT INVOVED, BUT THE #2-10" WAS DIRECTLY UNDER THE AREAOF FREE PRODUCT. THE PIPE LINE WAS EXCAVATED AND A PINHOLE CAUSED BY EXTERNAL CORROSION WAS DISCOVERED. FREE PRODUCT WAS RECOVERED WITH A VACUUM TRUCK AND MOST OF THE AFFECTED SOIL WAS EXCAVATED AND STOCKPILED ON PLASTIC. THE AFFECTED AREA OF PIPE WAS TEMPORARILY CLAMPED UNTIL FUEL OIL COULD BE MOVED THROUGH THE PIPELINE TO THE RELEASE LOCATION. A 26 FOOT SECTION OF PIPE WAS REMOVED AND REPLACED WITH HYDROSTATICALLY TESTED PIPE ON JUNE 13, 1996. THE PIPE LINE WAS RETURNED TO NORMAL OPERATIONS AT 17:00 JUNE 13, 1996. MPL IS WORKING WITH THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT TO REMOVE THE AFFECTEDSOIL AND REMEDIATE THE SITE.
2017-09-29 08:50 | YES | NO | 19960107 | 1996-07-16 | 1044 | WESTTEX 66 PIPELINE COMPANY | NO | 1996-06-21 | 1326 | TX | HUTCHINSON |  | NO |  | NO | DUMAS/SNEED SYSTEM-LINE G-203-MP7 38 +60 SEC.79, BLOCK 46, H &TCRR SURVEY 2 MILES EAST OF SANFORD, TX |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 14068 | 10142.3458 | 20461.2082 | NATURAL GAS LIQUID | 1 | 720 | 1 | NO | NO | 8.63 | 0.16 | 30000 | WELDED |  | 490 | 190 | YES | 8 | 900 | 9 | 95 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.J SCHMITZ | 9186614814 | PIPELINE CONTROLLER OBSERVED A DISCREPANCY. MEASUREMENT TECHNICIAN VERIFIED AND THE LINE WAS IMMEDIATELY BLOCKED IN. PIPE SECTION WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19960108 | 1996-07-15 | 30888 | SUN PIPE LINE COMPANY | NO | 1996-06-20 | 1430 | AR | FAULKNER |  | NO |  | NO | CONWAY TERMINAL |  | TANK FARM | PUMP | SUMP SYSTEM AND SLOP TANK | 0 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 216.2855 | 436.3351 | TURBINE FUEL | 1 | 50 | 49 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | HEAVY RAINFALL | Null | NO DATA |  | Null | Null | E.F. COEN | 9185866942 | SUMP SYSTEM WAS OVERLOADED DUE TO HEAVY RAINFALL. THIS CAUSED WATER TO BE PUMPED INTO THE "SLOP" TANK WHICH FLOATED PRODUCT OVER THE TOP INTO TANK DIKE.
2017-09-29 08:50 | YES | NO | 19960109 | 1996-07-12 | 30755 | CITGO PIPELINE COMPANY | YES | 1996-06-26 | 1915 | TX | ORANGE | VIDOR | NO |  | NO | EAST OF BEAUMONT WATER CANAL ON AN OVERHEAD CROSSING OF THAT CANAL. |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 252333.0284 | 509057.6395 | CRUDE OIL | 1 | 200 | 0 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 1000 | 15 | YES | 64 | 800 | 0 | 54 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. MOSELEY | 4092873594 | THERE WAS A LEAK CAUSED BY CORROSION NEAR THE END OF CASED CROSSING, EAST OFTHE BEAUMONT WATER CANAL. IT WAS REPORTED BY ATV RIDERS WHO RIDE THROUGH THEAREA DAILY. THE VIDOR FIRE DEPT. WAS CALLED OUT AND IN TURN CALLED US. THE LINE WAS DOWN AT THE TIME THE LEAK WAS DISCOVERED.
2017-09-29 08:50 | YES | NO | 19960111 | 1996-07-19 | 15851 | PRIDE REFINING INC | NO | 1996-06-19 | 1430 | TX | PARKER |  | NO |  | NO | APPROXIMATELY 2 MILES SOUTH OF BROCK, TEXAS ON FM ROAD 1189 1/2 MILE WEST. |  | LINE PIPE | PIPE |  | 1920 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 3 | 150 | 0 | NO | NO | 6.63 | 0.25 | 400 | THREADED |  | 351 | 120 | YES | 8 | 439 | 0 | 85 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS | PLOW | Null | OTHER | COMPANY LANDOWNER PROG. | NO | NO | JOHN T. MACON | 9156748231 | ON JUNE 19, 1996 AT APPROXIMATELY 2:20PM WE RECEIVED A CALL AT OUR ALEDO TERMINAL THAT OUR PIPELINE HAD BEEN STRUCK WHILE A FARMER WAS PLOWING HIS FIELD NEAR BROCK, TEXAS. OUR STATION OPERATOR THEN CALLED OUR PIPELINE CONTROL IN ABILENE TO SHUT DOWN THE PIPELINE. OUR STATION OPERATOR THEN WENT TO INVESTIGATE AND ACCESS THE SITUATION AT THE LEAK SITE. UPON ARRIVAL OF OUR MAINTENANCECREW A TEMPORARY CLAMP WAS PLACED ON THE LINE, AND THE CLEAN-UP PROCESS BEGAN. APPROXIMATELY 250' OF 6" PIPE WAS REPLACED ON 06/24/96. CLEAN-UP PROCEDURES ARE BEING DEVELOPED WITH THE TNRCC.
2017-09-29 08:50 | YES | NO | 19960112 | 1996-07-11 | 12625 | MOBIL OIL EXPLORATION & PRODUCTION SE INC | NO | 1996-06-10 | 1100 | TX | CALLAHAN | CLYDE | NO |  | NO | MOBIL PIPE LINE COMPANY MILE POST NUMBER 155, 5 MILES SOUTH OF CLYDE, TX ON HWY. 604, TURN EAST ON FM 3217 AND GO 2.5 MILES. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30365 | 21891.6926 | 44164.3864 | NATURAL GAS LIQUID | 2 | 1021 | 0 | NO | NO | 8.63 | 0.2 | 42000 | WELDED |  | 723 | 550 | YES | 25 | 904 | 6 | 71 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR | CONTRACTOR'S BACKHOE | Null | OTHER | CO.PROGRAM | Null | YES | D.G. SCOTT | 2146585914 | OPERATORS CONTRACTOR WAS DIGGING A BELL HOLE WITH A BACKHOE IN PREPARATION TOHYDRO-TEST A 12" PIPELINE WITHIN SAME RIGHT-OF-WAY OF SUBJECT 8" NGL LINE WHEN HIS BACKHOE ACCIDENTLY HIT THE 8" NGL PIPELINE WHICH WAS APPROX. 6' AWAY.THE LINE HAD BEEN PREVIOUSLY IDENTIFIED AND MARKED AND OPERATORS REPRESENTATIVE WAS ON SITE AT TIME OF ACCIDENT. OPERATORS DALLAS BASED PIPELINE OPERATIONS CONTROL CENTER WAS IMMEDIATELY NOTIFIED AND THE LINE WAS SHUT DOWN AND ISOLATED. MAINTENANCE CREWS WERE DISPATCHED TO THE SITE TO INITIATE REPAIR AND CLEANUP OPERATIONS. PERMANENT REPAIRS WERE MADE BY REPLACING DAMAGED SECTION OF PIPE WITH TESTED X-42 .322 WALL PIPE. ALL REQUIRED NOTIFICATIONS WERE MADEIN ACCORDANCE WITH DOT REGULATIONS.NORMAL OPERATIONS RESUMED JUNE 11, 1996.
2017-09-29 08:50 | YES | NO | 19960113 | 1996-07-22 | 7660 | HUNT REFINING CO | YES | 1996-06-24 | 1200 | AL | SUMTER | BELLAMY | NO |  | NO | TOWNSHIP 17 N., RANGE 1 WEST SECTION 17, N.E. 1/4 OF NORTHEAST 1/4. APPROX,3/4 MILES S. OF HIGHWAY #80, AND APPROX. 1/4 MI. SOUTH OF THE SUCARNOOCHEE RIVER. |  | LINE PIPE | PIPE |  | 1973 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 110 | 108 | NO | NO | 12.75 | 0.22 | 52000 | WELDED |  | 900 | 100 | YES | 24 | 1600 | 11 | 73 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CAROLL D. PELLEGRIN | 3347716953 | LEAK WAS REPORTED TO MELVIN STATION BY OUR AERIAL PATROL AT APPROXIMATELY 12:00 NOON ON MONDAY, JUNE 24. THE PIPELINE WAS IMMEDIATELY SHUT DOWN, AND PERSONNEL WERE DISPATCHED TOWARD THE LEAK SITE. THE LEAK OCCURRED ON A 150 FOOT WIDE JOINT RIGHT OF WAY HELD BY HUNT AND ALABAMA POWER. AFTER INITIAL ASSESMENT, EQUIPMENT AND CLEANUP CREWS WERE DIRECTED TO THE LOCATION. CALLS TO THE NATIONAL RESPONSE CENTER AND OTHER REGULATORY AGENCIES WERE ACCOUMPLISHED BY 3:45 P.M. CLEANUP EQUIPMENT AND CREWS WERE ON SITE AND IN THE PROCESS OF RECOVERY OF CRUDE OIL BY 4:30 P.M. THE LEAK LOCATION ON THE PIPELINE WAS EXPOSED ATAPPROXIMATELY 10:30 P.M., AND LEAK WAS DETERMINED TO HAVE BEEN CAUSED BY EXTERNAL CORROSION. A FULL ENCIRCLEMENT SLEEVE WAS WELDED OVER THE LEAK SPOT. THEEXTERNAL COATING OF THE PIPE WAS VISUALLY INSPECTED ON ALL EXPOSED PIPE, WITH NO DEFECTS DETECTED. THE PIPELINE WAS RETURNED INTO SERVICE AT APPROXIMATELY 3:30 A.M. ON TUESDAY, JUNE 25. CATHODIC PROTECTION READING AT LOCATION OF LEAK 1.329 MV.
2017-09-29 08:50 | NO | NO | 19960114 | 1996-07-22 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-06-24 | 1230 | IA | HUMBOLDT |  | NO |  | NO | 1/4 MILE FROM VALVE SITE AT AM 110 OR MP 109.9 T-92-N R-29-W SEC.5 |  | LINE PIPE | GIRTH |  | 1969 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 9317 | 6717.1052 | 13551.1144 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 6 | 0.16 | 46000 | WELDED |  | 1440 | 150 | YES | 24 | 2035 | 5 | 69 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SID RUETER | 9185993795 | LANDOWNER REPORTED A DEAD SPOT OF VEGETATION. INVESTIGATION FOUND A PINHOLE LEAK IN GIRTH WELD. A SLEEVE WAS INSTALLED AS A PERMANENT REPAIR.
2017-09-29 08:50 | YES | NO | 19960115 | 1996-07-22 | 13131 | CONOCO INC | YES | 1996-06-09 | 200 | IL | MADISON | HARTFORD | NO |  | NO | SW/4 SECTION 10 T4N,R9W MADISON COUNTY, ILLNOIS |  | TANK FARM | TANK |  | 1954 | INCORRECT OPERATION BY OPERATOR PERSONNEL | MALFUNCTION OF CONTROL | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7209.5151 | 14544.504 | TRANSMIX (PART. REFINED PETRO) | 1 | 126 | 75 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | VANCE L. WEBB | 4057674845 | ON JUNE 9, 1996, AT 02:00 HRS CONOCO PIPE LINE'S (CPL) WOOD RIVER FACILITY EXPERIENCED A TANK OVERFILL WHILE RECEIVING TRANSMIX FROM A THIRD PARTY PIPELINE INTO TANK 406. THE OVERFILL WAS DETECTED UPON COMPLETION OF THE RECEIPT. TOTAL VOLUME OF THE OVERFILL WAS 126 BBLS. THE INCIDENT HAS BEEN FOUND TO BE THE RESULT OF MULTIPLE FACTORS. THE FIRST OF WHICH IS HUMAN ERROR. CPL HAS IN PLACE MULTIPLE PROCEDURES, THAT HAD THEY BEEN FOLLOWED BY THE CPL OPERATOR ONDUTY, WOULD HAVE PREVENTED THIS RELEASE. THESE PROCEDURES WERE IMMEDIATELY REVIEWED WITH ALL OF THE OPERATORS AT THE WOOD RIVER FACILITY. THE OPERATOR ONDUTY AT THE TIME OF THE OVERFILL WAS REPRIMANDED. THE SECOND HUMAN FACTOR CONTRIBUTING TO THE OVERFILL OF THE TANK WAS THE EXCEEDING OF THE WRITTEN DELIVERY ORDERS BY THE THIRD PARTY PIPELINE OPERATOR. THE THIRD FACTOR CONTRIBUTING TO THE TANK OVERFILL IS A MECHANICAL ONE. THE HIGH LEVEL ALARM SYSTEM THAT SHOULD HAVE TRIGGERED, BOTH AUDIBLE AND VISUAL ALARMS, AT BOTH THE FACILITY AND AT CPL'S OIL MOVEMENTS GROUP CONTROL ROOM IN HOUSTON, DID NOT FUNCTION. UPON A THOROUGH EXAMINATION OF THE EQUIPMENT, BOTH ELECTRICAL ANFD MECHANICAL, NO PROBLEMS COULD BE FOUND. THE EQUIPMENT WAS TESTED MULTIPLE TIMES BY PHYSICALLY RAISING THE PRODUCT LEVEL IN THE EXTERIOR STAND PIPE OF THE TANK WITH A PRESSURE PUMP. THE EQUIPMENT FUNCTIONED CORRECTLY AND THE ALARMS WERE RECEIVED AT BOTH LOCATIONS IN ALL OF THE TEST. ADDITIONALLY, QUARTERLY MAINTENANCE RECORDS INDICATE THAT THE EQUIPMENT WAS ALSO FUNCTIONING CORRECTLY DURING THE PREVIOUS TEST CONDUCTED IN THE FIRST QUARTER. IT WAS CONCLUDED THAT BECAUSE THE TANK IS IN TRANSMIX SERVICE, DEBRIS FROM THE OFF-SPEC PRODUCT MUST HAVE BECOME LODGED IN THE STAND PIPE ORIFICE AND PIPING, AT THE POINT WHERE THE STAND PIPE IS CONNECTED TO THE TANK, SUCH THE TANK HEAD ALONE WAS NOT SUFFICIENT TO DISLODGE THE DEBRIS AND TRIGGER THE ALARM. PIPING MODIFICATIONS WERE MADE TO THE STAND PIPE TO PREVENT A SIMILAR OCCURRENCE.
2017-09-29 08:50 | YES | NO | 19960116 | 1996-07-29 | 2552 | COLONIAL PIPELINE CO | YES | 1996-06-26 | 2354 | SC | GREENVILLE | SIMPSONVILLE | NO |  | NO | NEAR GREENVILLE, S.C., IN THE REEDY RIVER |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 26899360 | 19393134.1995 | 39123784.8752 | DIESEL FUEL | 3 | 22800 | 21472 | NO | NO | 36 | 0.28 | 52000 | WELDED |  | 374 | 399 | YES | 24 | 803 | 0 | 1963 | EXTERNAL | Null | YES | OTHER | GENERAL CORR. PITTING COR |  |  | Null |  |  | Null | Null | J.A. COX | 4048412296 | AFTER RUNNING AN INTERNAL INSPECTION TOOL TO IDENTIFY CORROSION AND MECHANICAL DAMAGE IN COLONIAL PIPELINE COMPANY'S 36-INCH DIAMETER PIPELINE (LINE 2) INMARCH OF 1996, THE PIGGING FIRM AND COLONIAL PERSONNEL SCANNED THE DATA ANDDISCOVERED A LOCATION WHICH APPEARED TO HAVE EXTENSIVE CORROSION. THE LOCATIONWAS INVESTIGATED ON APRIL 4, 1996, AND FOUND TO BE IN THE REEDY RIVER. THEPIPELINE PRESSURE WAS REDUCED, AND A SAFTEY-RELATED CONDITION REPORT NO 1-96,WAS FILED WITH THE OFFICE OF PIPELINE SAFETY. A PROJECT TO PERMANENTLY REPLACETHE RIVER CROSSING WAS IMMEDIATELY INITIATED AND SCHEDULED. AN APRIL ATTEMPTTO TEMPORARILY REPAIR THE LOCATION UNTIL THE PERMANENT REPAIR SCHEDULED FORJULY COULD BEGIN WAS INITIATED, BUT LATER ABANDONED DUE TO POTENNTIAL UNSAFEWORKING CONDITIONS AT THE SITE. DURING THE CLOSE OUT OF A DELIVERY AT ATLANTAJUNCTION AND A SUBSEQUENT RATE INCREASE TO LINE 2 NORTH OF ATLANTA, THECONTROLLER EXPERIENCED A FAILURE WHICH PREVENTED GASTONIA STATION FROMSTARTING. A SUBSEQUENT PRESSURE INCREASE CAUSED SIMPSONVILLE STATION TOSHUTDOWN. THE PRESSURE SURGE FROM SIMPSONVILLE STATION SHUTTING DOWN CAUSEDTHE CORRODED SECTION OF PIPE IN THE REEDY RIVER TO RUPTURE. THE CONTROLLERSHUT THE PIPELINE DOWN AND DISPATCHED PERSONNEL TO INVESTIGATE SIMPSONVILLESTATION AND THE REEDY RIVER. PERSONNEL AT THE REEDY RIVER REPORTED DIESEL FUELON THE RIVER AT 0215 EDT ON JUNE 27, 1996. THE NATIONAL RESPONSE CENTER WASNOTIFIED AT 0235 EDT ON JUNE 27, 1996. A SUBSEQUENT DETAILED REVIEW OF SCADADATA INDICATED THE LEAK ACTUALLY OCCURRED AT 2354 EDT ON JUNE 26, 1996. THEFAILED SECTION WAS REPLACED BY A TEMPORARY REPAIR ON JUNE 29, 1996, AND APERMANENT PIPELINE RIVER CROSSING IS CURRENTLY UNDER CONSTRUCTION.
2017-09-29 08:50 | YES | YES | 19960117 | 1996-07-31 | 12127 | MARATHON PIPE LINE CO | YES | 1996-07-01 | 624 | IL | PUTNAM | GREENCASTLE | NO |  | NO | PUTNAM COUNTY AIRPORT, ONE MILE EAST OF THE CITY OF GREENCASTLE. |  | LINE PIPE | PIPE |  | 1945 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 230000 | 165818.8472 | 334523.5917 | DIESEL FUEL | 3 | 725 | 698 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1440 | 870 | YES | 8 | 1938 | 9 | 89 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOSEPH FISHER | 4194213201 | AT 0624 CDT ON JULY 1, 1996, MARATHON PIPE LINE COMPANY'S (MPL'S) OPERATION CENTER, LOCATED IN FINDLAY, OH, NOTED A CHANGE IN INCOMING PRESSURE ON THE RIO 8" PRODUCTS PIPELINE AT MPL'S CLERMONT, IN STATION. BETWEEN 0624 CDT AND 0626 CDT MORE INDICATIONS OF PRESSURE/FLOW IRREGULARITIES WERE RECEIVED. AT APPROX 0627 CDT A CALL WAS RECEIVED FROM A REP OF MILESTONE CONTRACTORS, L.P. STATING THAT THEY HAD STRUCK A MPL PIPELINE AT THE PUTNAM COUNTY AIRPORT AT GREENCASTLE, IN. AT 0629 CDT THE RIO 8" PIPELINE WAS SHUT DOWN. MPL EMERGENCY PERSONNEL AND CONTRACTORS RESPONDED TO THE SCENE AND FOUND THAT THE PIPELINE HAD BEEN STRUCK BY A MILESTONE BULLDOZER EXCAVATING FOR THE EXPANSION OF A PAVED AREA. THE PRODUCT IN THE PIPELINE WAS LOW SULFUR DIESEL FUEL. ONE OF THE MILESTONE EQUIPMENT OPERATORS AND A MILESTONE LABORER WERE SPRAYED WITH DIESEL AND THE EQUIPMENT OPERATOR WAS TREATED AT A LOCAL HOSPITAL. UPON HITTING THE PIPELINE, MILESTONE IMMEDIATELY BEGAN CONSTRUCTING AN EARTHEN DAM TO CONTAIN THE ESCAPING PRODUCT. WHEN MPL RESPONDERS AND CONTRACTORS ARRIVED, THEY REMOVED THE MILESTONE PERSONNEL TO A SAFE AREA AND CONTAINED THE PRODUCT. THE AIRPORT WAS TEMPORARILY SHUT DOWN. IT WAS REOPENED ON JUNE 2, 1996. A 10 FOOT SECTION OF PIPE, CONTAINING THE DAMAGED AREA, WAS REMOVED AND REPLACED WITH NEW,HYDROSTATICALLY TESTED PIPE. THE PIPELINE WAS STARTED BACK UP ON JULY 2, 1996 AT 1543 CDT, AND RETURNED TO REGULAR OPERATION. MUCH OF THE OIL-CONTAMINATED SOIL HAS BEEN EXCAVATED AND IS STOCKPILED AWAITING DISPOSAL. MPL CONTINUES TO WORK WITH THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT TO REMEDIATE THE OIL CONTAMINATION AT THE SITE.
2017-09-29 08:50 | YES | NO | 19960118 | 1996-08-01 | 1004 | KOCH HYDROCARBON COMPANY | NO | 1996-06-28 | 1300 | OK | GARFIELD |  | NO |  | NO | SEC. 17, R 3W, T 21N GARFIELD COUNTY OK |  | TANK FARM | VALVE |  | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 4311 | 3108.022 | 6270.1357 | NATURAL GAS LIQUID | 2 | 9 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | JERRY ROGERS | 4053952377 | CONTRACTOR WAS DIGGING OUT A VALVE AND HIT AN EXTENDED GREASE FITTING CAUSING A RELEASE OF NATURAL GAS LIQUIDS.
2017-09-29 08:50 | YES | NO | 19960119 | 1996-07-30 | 2731 | CHEVRON PIPELINE CO | YES | 1996-06-27 | 1810 | TX | WINKLER | WINK | NO |  | NO | 2 MILES NORTH OF WINK TX |  | TANK FARM | TANK |  | 1928 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 215000 | 155004.5746 | 312706.8357 | CRUDE OIL | 1 | 100 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | WJ JASPER | 7133635422 | AT APPROX 610PM ON 6/27/96, LIGHTNING STRUCK TANK 1648, AN 80,000 BBL CONE ROOF TANK WITH APPROX 10,000 BBLS OF CRUDE OIL IN IT. THE ROOF OF THE TANK COMPLETELY SEVERED FROM THE SHELL AND THE CONTENTS OF THE TANK IGNITED. THERE WAS A FROTH-OVER APPROX 5 HRS. INTO THE FIRE WHICH ALLOWED 100 BBLS TO SPILL INTO THE TANK BERM. THE FIRE WAS ALLOWED TO BURN AND DECLARED OUT AT 6:00AM ON6/28/96.
2017-09-29 08:50 | NO | NO | 19960120 | 1996-08-05 | 19223 | SUN PIPE LINE COMPANY | YES | 1996-07-04 | 2000 | PA | LUZERNE | SHICKSHINNY | NO |  | NO | THIS LEAK OCCURRED APPROX 0.5 MILES NORTH OF SHICKSHINNY, PA JUST WEST OF ROUTE 239. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 46861.8481 | 94539.2759 | DIESEL FUEL | 1 | 49 | 2 | NO | NO | 6 | 0.28 | 2540 | WELDED |  | 1200 | 479 | YES | 24 | 1800 | 10 | 65 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | KEVIN FULMER | 6106703237 | AN APPROX 1/8" PIN HOLE LEAK DEVELOPED, DUE TO CORROSION, AT CREEK CROSSING APPROX 0.5 MILES NORTH OF SHICKSHINNY, PA. CLEANUP CREWS DEPLOYED BOOMS IN THE CREEK AND A TEMPORARY CLAMP WAS INSTALLED. PERMANENT REPAIR INVOLVED REPLACEMENT OF APPROX 120 FEET OF PIPE. NO SIGNIFICANT ENVIRONMENTAL DAMAGE OCCURED.
2017-09-29 08:50 | YES | NO | 19960121 | 1996-08-13 | 2731 | CHEVRON PIPELINE CO | NO | 1996-08-01 | 1400 | LA |  | BURAS | NO |  | Null |  |  | TANK FARM | VALVE | TANK | 0 | OTHER | UNKNOWN/UNDER INVESTIGATI | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14419.0302 | 29089.008 | CRUDE OIL | 1 | 2500 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALPHONSE MILLER | 5045927715 | WHILE MAKING HIS ROUNDS THE TERMINAL OPERATOR OBSERVED A RELEASE OF CRUDE OIL IN THE TANK BERM AREA AROUND TANK 2049 AT THE OSTRICA PORTION OF EMPIRE TERMINAL. THE OPERATOR IMMEDIATELY LOCATED THE SOURCE WHICH WAS AN OPEN NOZZEL VALVE ON THE TANK, THE VALVE WAS CLOSED AND THE AREA SECURED.
2017-09-29 08:50 | YES | NO | 19960122 | 1996-08-13 | 443 | AMOCO PIPELINE CO | YES | 1996-07-12 | 1430 | TX | CHILDRESS |  | NO |  | NO | FROM CHILDRESS TX, TAKE HWY 62/83 S. 2 MILES TO JCT. OF FM2042. TURN RIGHT, WEST, ON FM2042 AND CONTINUE APPROX 5 MILES TO THE STATION LOCATED ON THE RIGHT. |  | PUMPING STATION | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10814.2726 | 21816.756 | CRUDE OIL | 1 | 130 | 129 | NO | NO | 12 | 0 | 0 | OTHER |  | 836 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | TOM BROZOVICH | 8068977013 | PIPE THAT LEAKED WAS A DEAD LEG ON A MANIFOLD LOCATED WITHIN THE STATION GROUNDS.
2017-09-29 08:50 | YES | NO | 19960123 | 1996-08-15 | 14194 | OILTANKING OF TEXAS PIPELINE CO | NO | 1996-07-09 | 0 | TX | HARRIS | GALENA PARK | NO |  | NO | 2151 FEDERAL ROAD, 1.400 FEET EAST AT CASED RAILROAD CROSSING |  | LINE PIPE | PIPE |  | 1978 | FAILED PIPE | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 50466.6057 | 101811.5279 | CRUDE OIL | 1 | 6 | 0 | NO | NO | 24 | 0.28 | 824 | OTHER |  | 275 | 10 | YES | 24 | 740 | 1 | 78 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | GIL CHARTIER | 7134577900 | ON ROUTINE RIGHT-OF-WAY INSPECTION, DISCOLORED GROUND WAS NOTED AT CASING VENT. IN A 10' X 12' AREA, A LINE PIPE HAD FAILED IN CASING AND OIL HAD LEAKED OUT OF CASING VENT RISER JUST BELOW GRADE. LINE HAS BEEN STATIC FOR AT LEAST SIX YEARS. MOST OF CONTAMINATION IS BELOW GRADE. LINE PIPE IS BEING PARTIALLYREMOVED WITH THE REMAINDER FILLED WITH CONCRETE AND CASING FILLED WITH CONCRETE.
2017-09-29 08:50 | YES | NO | 19960124 | 1996-08-30 | 25146 | LYONDELL PETROCHEMICAL CO | NO | 1996-07-27 | 1500 | TX | HARRIS | CHANNELVIEW | NO |  | NO | THE ACCIDENT OCCURRED AT AN ARCO PIPE LINE COMPANY METER STATION LOCATED WITHIN THE LYONDELL PETROCHEMICAL FACILITY LOCATED AT 8280 SHELDON ROAD IN CHANNELVIEW |  | LINE PIPE | BOLTED FITTING |  | 1996 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000000 | 6488563.5865 | 13090053.5878 | BUTANE | 2 | 2305 | 0 | YES | YES | 12 | 0.5 | 0 | FLANGED |  | 2000 | 1730 | YES | 4 | 3380 | 10 | 95 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARK LOWE | 7139865029 | AT APPROX 1500 ON 7/27/96, THE ARCO PIPE LINE COMPANY OPERATIONS CONTROL CENTER WAS NOTIFIED OF AN ETHYLENE RELEASE BY LYONDELL PETROCHEMICAL COMPANY PERSONNEL. ETHYLENE WAS BEING RELEASED FROM A 12 INCH FLANGE CONNECTION WITHIN ARCO PIPE LINE COMPANY'S METER STATION INSIDE THE LYONDELL FACILITY. AT APPROX1545, THE VAPOR CLOUD IGNITED; FIRE AND RUPTURES FOLLOWED. AT 1700, THE FIREBEGAN TO SUBSIDE AND BURNED ITSELF OUT OVER THE NEXT SEVERAL HOURS. AS OF THEDATE OF THE REPORT THE INCIDENT INVESTIGATION IS ONGOING. A SPECIFIC CAUSE FOR THE INCIDENT HAS NOT BEEN DETERMINED. AS ADDITIONAL INFORMATION BECOMES AVAILABLE, SUPPLEMENTS TO THIS REPORT WILL BE SUBMITTED. SUPPLEMENTAL REPORTRECEIVED 4/28/97 INDICATES THAT THE MOST LIKELY CAUSE OF THE ETHYLENE LEAK WASA GASKET DAMAGED DURING INSTALLATION. THE OTHER PIPELINES AT THE METERSTATION FAILED AS A RESULT OF THE SUBSEQUENT FIRE AND EXPLOSION. THIS IS ANUPDATE TO THE ACCIDENT NOTIFICATION REPORT SUBMITTED ON 8/22/1996. BBLSSPILLED INCREASED FROM 2288 TO 2305
2017-09-29 08:50 | YES | NO | 19960125 | 1996-08-23 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | NO | 1996-04-29 | 1300 | TX | MEDINA | CASTORVILLE | NO |  | NO | 3 MILES SOUTH OF CASTORVILLE, TX OFF FM 1343. |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 72095.151 | 145445.0399 | CRUDE OIL | 1 | 2200 | 0 | NO | NO | 12 | 0.38 | 30000 | THREADED |  | 777 | 500 | YES | 8 | 971 |  | 91 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | MAX KOSTER | 4053952377 | SUPPLEMENTAL RECEIVED 10/17/1996 INDICATES CHANGE IN PROPERTY DAMAGE FROM $0TO $100,000.
2017-09-29 08:50 | YES | NO | 19960126 | 1996-08-27 | 19223 | SUN PIPE LINE COMPANY | YES | 1996-07-26 | 1935 | MI | ST. CLAIR |  | NO |  | NO | 429 WEST OF PALMS ROAD, 1320 NORTH OF FRITH ROAD SECTION 2, COLUMBUS TOWNSHIP (400 NORTH OF PALMS RD. |  | LINE PIPE | GIRTH |  | 1950 | FAILED WELD | UNDER INVESTIGATION | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | BUTANE | 2 | 8 | 0 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1200 | 810 | YES | 24 | 1500 | 10 | 58 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHRISTINE MAZZARA | 3132928850 | AT 7:35 PM ON JULY 26, 1996 SUN PIPE LINE COMPANY WAS NOTIFIED, VIA TELEPHONE, BY A COLUMBUS TOWNSHIP RESIDENT OF A NATURAL GAS TYPE ODOR IN THE AREA. THE LPG SYSTEM TRAVERSING THE AREA WAS SHUT DOWN AT 7:40PM. A COMPANY INVESTIGATOR WAS ON SITE AT 9PM AND QUICKLY LOCATED LEAK SITE. INSPECTION AND REPAIR PROCEDURES FOLLOWED. INSPECTION REVEALED A FAILURE IN THE GIRTH WELD METAL AT6:00 POSITION, LINE PIPE WAS IN GOOD CONDITION.
2017-09-29 08:50 | YES | NO | 19960127 | 1996-08-27 | 4906 | EXXON PIPELINE CO | YES | 1996-07-26 | 500 |  |  |  | YES | X=2544826.85 Y=166,628.86 | NO | OFFSHORE LOUISIANA |  | LINE PIPE | WELDING FITTING |  | 1986 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 330000 | 237913.9982 | 479968.6316 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 8 | 0.5 | 35 | WELDED |  | 1440 | 180 | YES | 24 | 2156 | 9 | 86 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | BT MAGRUDER | 7136562190 | AN OIL SHEEN WAS SPOTTED BY A 3RD PARTY DURING AN OVERFLIGHT NEAR IT'S PIPELINE THAT TIES INTO EPC'S PIPELINE. DIVERS AND AN EPC'S COMPANY REPRESENTATIVEWERE SENT TO INVESTIGATE. UPON COMPLETION OF THE INVESTIGATION, THE SOURCE OF THE SHEEN (APPROX. 38 GALLONS) WAS DETERMINED TO BE EPC'S 8 INCH PIPELINE. THE SHEEN DISSIPATED. REPAIR PERSONNEL AND EQUIPMENT WERE DISPATCHED TO THE SIT AND REPAIRED THE PIPELINE SEGMENT THAT LEAKED. REPAIRS WERE COMPLETED AND THE LINE WAS PLACED BACK IN SERVICE ON 7/31/96. NRC REPORT NO. 353471.
2017-09-29 08:50 | YES | NO | 19960128 | 1996-08-27 | 570 | ARCO WESTERN GAS PIPE LINE CO | NO | 1996-07-29 | 612 | CA |  | LONG BEACH | NO |  | NO | SPRING STREET, AT CENTERLINE OF GREENBRIER, TO EAST OF SPRING STREET/CLARK AVENUE INTERSECTION |  | LINE PIPE | LONGITUDINAL WELD |  | 1928 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 1113000 | 802419.0302 | 1618803.2937 | CRUDE OIL | 1 | 250 | 246 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 600 | 0 | YES | 4 | 870 | 4 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAN HISEY | 5624289000 | PIPELINE WAS NOT PUMPING AT THE TIME THE RELEASE WAS DISCOVERED. RELEASE WASREPORTED TO ARCO PIPE LINE COMPANY (APL) CONTROL CENTER AND APL SENT OUT ACREW TO INVESTIGATE. EXCAVATION REVEALED THAT THE LINE SPLIT TO DUE TOINTERNAL PRESSURE. THE PIPE WILL BE SENT FOR METALLURGICAL ANALYSIS TODETERMINE WHY IT FAILED ALONG THE LONGITUDINAL SEAM. SUPPLEMENTAL RECEIVED3/10/1997 INDICATES A CHANGE IN PROPERTY DAMAGE FROM 900,000 TO 1,113,000 ANDA CHANGE IN THE LOSS OF BARRELS FROM 230 TO 250 AND A CHANGE IN THE BBLSRECOVERED FROM 170 TO 246. COMMENTS CHANGES INCLUDE THAT THE EXCAVATIONREVEALED THAT THE LINE SPLIT ALONG THE LONGITUDINAL WELD DUE TO INTERNALPRESSURE. METALLURGICAL ANALYSIS REVEALED THAT THE WELD WAS OF POOR QUALITYAND CONTAINED INTERGRANULAR CRACKS. IT IS BELIEVED THAT A CONTRIBUTING FACTORWAS THE THERMAL EXPANSION OF THE CRUDE OIL DUE TO INCREASED SOIL TEMPERATUREDURING THE SUMMER, ON A BLOCKED IN-LINE.
2017-09-29 08:50 | YES | NO | 19960129 | 1996-09-13 | 25146 | LYONDELL PETROCHEMICAL CO | NO | 1996-07-31 | 1425 | TX | HARRIS |  | NO |  | NO | THE CHANNELVIEW FACILITY IS LOCATED APPROX 6 MILES NORTH OF INTERSTATE HWY 10 ON SHELDON RD, WEST OF THE SAN JACINTO RIVER. |  | LINE PIPE | PIPE | SEE ACCOUNT OF ACCIDENT | 0 | OTHER | MAINTENANCE ACTIVITY | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | L. P. G. | 2 | 4 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BRAD YAW | 7134528114 | ON JULY 31, 1996, AT 2:25 PM, A FIRE OCCURRED AT THE CHANNELVIEW EAST PLANT #3 PIPE LINE PIG TRAP, WHEN CAT BB'S (MIXED BUTYLENES FROM THE LCRC FCC UNIT)OVER PRESSURED AND RUPTURED A FIRE HOSE. THE INCIDENT TOOK PLACE AS OPERATORS WERE WAITING FOR THE #3 PIPE LINE TO BE DEPRESSURED, IN PREPARATION FOR CLEARING AND MODIFICATIONS. A FIRE HOSE WAS HOOKED UP TO THE #3 PIPE LINE PIG TRAP LOW POINT BLEED VALVE TO PREPARE FOR HYDROCARBON DISPLACEMENT WITH WATER TOWARD THE LCRC REFINERY. EAST PLANT TANK FARM PERSONNEL, CONCERNED ABOUT THE OPERABILITY OF THE LOW POINT BLEED, DECIDED TO EXERCISE THE VALVE, OR MOVE IT WITHOUT ACTUALLY OPENING IT. WHEN THEY CONNECTED A VALVE WRENCH TO THE VALVE HANDLE AND TAPPED ON THE VALVE WRENCH WITH A PIPE WRENCH, THE VALVE MOVED ENOUGH TO OPEN. THIS CAUSED THE 300 PSIG CAT BB'S TO ENTER THE FIRE HOSE, RESULTING IN A RUPTURE. THE CAT BB VAPORS CAUGHT FIRE IMMEDIATELY (PROBABLY FROM STATIC ELECTRICITY) CAUSING THE OPERATIONS GROUP TO VACATE THE AREA, WITH NO TIME TO REVERSE THE VALVE WRENCH AND TAP THE VALVE CLOSED. NO PERSONNEL WERE INJURED, BUT THERE WAS DAMAGE TO A SMALL BUILDING, OVERHEAD POWER LINES, LOCAL INSTRUMENTS AND A JUMPER LINE. THE ALL-CLEAR WAS SOUNDED AT 3:15PM.
2017-09-29 08:50 | YES | NO | 19960130 | 1996-08-30 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | NO | 1996-07-31 | 1630 | OK | STEPHENS |  | NO |  | NO | SW/4 NW/4 SECTION 17, T.2 N. - R. 5 W. |  | LINE PIPE | WELDING FITTING |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 139000 | 100212.2598 | 202168.6054 | CRUDE OIL | 1 | 205 | 180 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | WALTER LONG | 4052557151 | RELEASE RESULTED FROM GALVANIC CORROSION WITHIN WELD AREA WHERE WELD FLANGECONNECTED TO PIPELINE. SUPPLEMENTAL REPORT RECEIVED 10/2/1996 REVISES REPORTSUBMITTED ON 8/29/1996 CHANGING CORROSION FROM EXTERNAL TO INTERNAL.
2017-09-29 08:50 | YES | YES | 19960131 | 1996-09-10 | 26125 | CALNEV PIPELINE CO | YES | 1996-07-29 | 1138 | NV | CLARK |  | NO |  | NO | NORTHWEST CORNER OF POLARIS AVENUE AND HACIENDA STREET, IN LAS VEGAS NEVADA. (SEE ATTACHED DIAGRAMS). |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 3 | 0 | 3 | 400000 | 288380.6038 | 581780.1595 | JET FUEL | 1 | 300 | 0 | NO | NO | 6 | 0.19 | 2000 | WELDED |  | 1440 | 450 | YES | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BRIAN MCGUIRE | 9093879509 | AT 1120(MILITARY TIME) ON JULY 29, 1996, JUST PRIOR TO THE PIPELINE RUPTURE,BOTH THE 8" MAINLINE AND THE 6" LATERAL CONTAINED JET A. THE 6" LATERAL WAS OPERATING BETWEEN 200 AND 400 PSI, AND FUEL WAS ENTERING INTO THE WEST TANKAGEOF THE MCCARRAN AIRPORT AT A RATE OF ABOUT 1170 BARRELS PER HOUR. THE PIPELINE IS MONITORED BY A DISPATCHER FROM THE CONTROL DESK, LOCATED AT THE COLTON,CA. TERMINAL. FROM THIS LOCATION THE DISPATCHER CAN MONITOR THE PIPELINE RATE, OPERATING PRESSURES, AND THE STATUS OF MAINLINE PUMPS AND VALVES. AT APPROX 1125 THE COLTON TERMINAL DISPATCHER, PAUL WILSON, LOST THE COMMUNICATIONS LINK WITH THE MCCARRAN WEST STATION. THE COMMUNICATIONS LINK IS A MICROWAVE NETWORK WHICH ALLOWS CALNEV TO CONTINUOUSLY MONITOR THE PIPELINE STATUS. ALTHOUGH THE COMMUNICATIONS HAD FAILED, PRODUCT CONTINUED TO PUMP INTO THE MCCARRANWEST TANKAGE. AT 1131 THE CONTROL VALVE THAT ALLOWS PRODUCT INTO THE MCCARRAN WEST AIRPORT CLOSED. THIS VALVE IS PROGRAMMED TO CLOSE AUTOMATICALLY IF COMMUNICATIONS ARE NOT RESTORED WITHIN FIVE MINUTES. AT THIS TIME THE DISPATCHERWAS IN THE PROCESS OF BRINGING THE VALLEY WELLS PUMPS ON LINE, THE LINE SECTION NEAR THE STATION WAS SLACK, WITH ALMOST NO PRESSURE. WHEN THE MCCARRAN VALVE CLOSED IT DID NOT RESULT IN AN IMMEDIATE INCREASE IN PRESSURE APPARENT TOTHE DISPATCHER, AND THE PRESSURES APPEARED TO FLUCTUATE. HOWEVER, THE PIPELINE PRESSURES AT BRACKEN PEAKED AT 970 PSI. AT 1139 THE CALNEV MAINTENANCE MAN, PAT MASSEY, WAS ON THE OTHER SIDE OF THE I-15 FREEWAY IN THE PARKING LOT OFTHE HACIENDA HOTEL. PAT SAW, "A GEYSER", BUT WAS NOT SURE IF IT WAS CALNEV PIPELINE PRODUCT, OR POSSIBLY A WATER LINE. HE TRAVELED TO THE BRACKEN JUCTIONINTERSECTION AND DETERMINED THAT PRODUCT WAS FLOWING FROM THE PIPELINE. PATIMMEDIATELY CALLED THE COLTON TERMINAL VIA A CELLULAR PHONE. PAT THEN CONTACTED KEN SEALE, LAS VEGAS TERMINAL MANAGER, AND INFORMED HIM OF THE INCIDENT. CALNEV DID NOT HAVE ANY CONSTRUCTION ACTIVITIES ONGOING IN THIS AREA, AND PATDID NOT SEE ANY OTHER CONSTRUCTION EQUIPMENT IN THE AREA. AT APPROX 1143 THECOLTON PIPELINE SUPERINTENDENT, JEFF PARRISH, RECEIVED A PHONE CALL FROM CALNEV MAINTENANCE MAN, PAT MASSEY, WHO INFORMED JEFF THAT THERE WAS A PIPELINE RUPTURE, AND PRODUCT WAS SPRAYING OUT OT THE LINE. AT 1145 THE COLTON DISPATCHER SHUT DOWN THE MAINLINE PUMP STATIONS, CLOSED THE MOTOR OPERATED VALVE (MOV) AT THE BRACKEN JUNCTION, AND OPENED THE MCCARRAN WEST VALVE.
2017-09-29 08:50 | YES | NO | 19960132 | 1996-09-04 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1996-08-01 | 1400 | TX | LOVING |  | NO |  | NO | SECTION 3, BLOCK 54, TOWNSHIP 1 |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 21628.5453 | 43633.512 | CARBON DIOXIDE | 3 | 4000 | 0 | NO | NO | 6 | 0.19 | 72000 | WELDED |  | 2300 | 1800 | YES | 8 | 3000 | 2 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | EDWARD FANT | 7138537891 | ON AUGUST 1, 1996 AT APPROX 1400HRS, ENRON LIQUIDS PIPELINE COMPANY'S (ELPC)CONTROL CENTER IN HOUSTON, TX WAS NOTIFIED BY DON HARVEY OF MERIDIAN OIL COMPANY THAT ELPC'S CENTER BASIN PIPELINE WAS STRUCK BY A BACKHOE AND CARBON DIOXIDE WAS LEAKING TO THE ATMOSPHERE. ELPC'S EMERGENCY RESPONSE WAS INITIATED AND PERSONNEL WERE DISPATCHED TO VALVES ON EITHER SIDE OF THE SITE TO ISOLATE THE SEGMENT. THE SEGMENT WAS ISOLATED AT APPROX 18:15 HRS. THE SEGMENT WAS BLOWN DOWN TO ATMOSPHERE THROUGH BLOWDOWNS AT ADJACENT METERING STATIONS. APPROX 4,000 BBLS (10 MMCF) OF CARBON DIOXIDE WAS RELEASED TO THE ATMOSPHERE. THERE WERE NO DEATHS OR INJURIES AND DAMAGE WAS LESS THAN $50,000. ELPC PERSONNEL DID NOT KNOW THAT EXCAVATION WORK WAS BEING DONE NEAR THE PIPELINE. WE HAD NOT BEEN NOTIFIED BY THE ONE CALL SYSTEM NOR THE CONSTRUCTION COMPANY. THE OPERATOR OF THE BACKHOE, BRENT CARGAL OF HOLLMAN CONSTRUCTION COMPANY, STATED THAT HE HAD NOT NOTIFIED THE ONE CALL SYSTEM.
2017-09-29 08:50 | YES | NO | 19960133 | 1996-09-04 | 4472 | ENRON LIQUIDS PIPELINE CO (HYDROCARBON TRANS INC) | YES | 1996-08-04 | 1400 | TX | LOVING |  | NO |  | NO | SECTION 3, BLOCK 54, TOWNSHIP 1 |  | LINE PIPE | WELDING FITTING | EL MAR MTR STAT 1 IN PIPE | 1994 | OTHER | A 1" PIPE NIPPLE BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2162.8545 | 4363.3512 | CARBON DIOXIDE | 2 | 404 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD FANT | 7138537891 | AT APPROX 1200HRS ON AUGUST 4, 1996. ENRON LIQUIDS PIPELINE COMPANY'S (ELPC)CONTROL CENTER IN HOUSTON, TX RECEIVED A POWER FAILURE AND A HIGH FLOW RATE ALARM FROM THE EL MAR METER STATION. ELPC'S EMERGENCY RESPONSE WAS INITIATED AND PERSONNEL WERE DISPATCHED TO THE METER STATION. PERSONNEL DISCOVERED A ONE INCH NIPPLE LYING ON THE GROUND AND CARBON DIOXIDE BEING RELEASED TO THE ATMOSPHERE. THE STATION WAS ISOLATED BY MANUALLY SHUTTING OFF THE INLET AND OUTLET STATION VALVES. APPROX 404 BARRELS (1 MMCF) OF CARBON DIOXIDE WAS RELEASED. SUBSEQUENT INVESTIGATION DISCLOSED THAT THE NIPPLE HAD BROKEN OFF INSIDE THE THREAD-O-LET. THE SURGE PROTECTION FOR THE A/C POWER HAD BEEN BLOWN. THEREWAS A REPORT THAT LIGHTNING WAS IN THE AREA. THERE WERE NO DEATHS OR INJURIES AND DAMAGE WAS LESS THAN $50,000.
2017-09-29 08:50 | YES | NO | 19960134 | 1996-09-04 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1996-08-01 | 1350 | PA | DELAWARE | BETHEL | NO |  | NO | SEE ATTACHED DRAWING NUMBER 11744-A |  | TANK FARM | PIPE |  | 1958 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 25233.3028 | 50905.764 | GASOLINE | 3 | 890 | 786 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL LARKIN | 6107704507 | ON AUGUST 1, 1996, MAINTENANCE ACTIVITIES WERE BEING CONDUCTED ON TANK 12 ATLAUREL PIPE LINE COMPANY'S BOOTH STATION. AT 1350 HRS, THE INACTIVE AND ISOLATED TANK LINE TO TANK 12 RUPTURED, RESULTING IN THE RELEASE OF 890 BARRELS OF GASOLINE. A ONE-INCH VALVE ON THE RELIEF LINE SYSTEM LOCATED AT THE TANK 12SHELL GATE VALVE WAS PARTIALLY CLOSED ALLOWING THE ABOVE GROUND TANK LINE TOBUILD UP PRESSURE UNTIL FAILURE OCCURRED. ALL APPLICABLE AGENCIES WERE NOTIFIED AND ALL RELEASED PRODUCT WAS CONTAINED ON THE BOOTH STATION PROPERTY. RECOVERY AND CLEANUP ACTIVITIES WERE CONDUCTED UNDER THE SUPERVISION OF THE LOCAL FIRE DEPARTMENT AND DELAWARE COUNTY EMERGENCY MANAGEMENT AGENCY.
2017-09-29 08:50 | YES | NO | 19960135 | 1996-09-16 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 1996-07-17 | 1557 | PA | DELAWARE | MIDDLETOWN | NO |  | NO | W/IN 14 IN LINE WHICH RUNS PARALLEL TO RTE 452 & APPROX 1 MILE SOUTH OF RTE 1. LINE IS LOCATED ON RIM OF RD. CLOSEST DRVWAY IS 123 PENNEL RD. |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 126166.5142 | 254528.8198 | GASOLINE | 1 | 15 | 15 | NO | NO | 14 | 0.25 | 52000 | NO DATA |  | 1200 | 1000 | YES | 49 | 1500 |  | 56 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | ALAN BRETZ | 2159376241 | THE CHAIN OF EVENTS BEGAN WITH THE COMPLAINT OF ODORS BY THE (123 PENNEL RD.) RESIDENT TO THEIR LOCAL MUNICIPALITY. THE LOCAL MUNICIPALITY INVESTIGATED AND CONTACTED SUN PIPE LINE COMPANY (SPL). THE LINE SECTION WAS INVESTIGATED AND EXCAVATED. AFTER EXCAVATING, THE RELEASE WAS VERIFIED BY SPL. A 1500PSI CLAMP WAS PLACED ON THE DAMAGED SECTION AND FREE PRODUCT REMOVAL BEGAN. APPROX TWO WEEKS LATER SPL RE-EXCAVATED THE SITE AND CUT THE DAMAGED SECTION OUT, REPLACING IT WITH NEW PIPE AND COATING. THE SECTION REMOVED WAS SENT OUT FOR METAULLURGICAL ANALYSIS. IT IS BELIEVED THAT THE PIPE AND INSULATION WERE DAMAGED YEARS AGO WHEN A SEWER LATERAL WAS INSTALLED AT THE (123 PENNEL RD.) RESIDENCE. THE DAMAGED PIPE SECTION SHOWED DAMAGE ONLY IN THE AREA OF THE LATERAL.THIS WORK WAS PART OF A BORO PROJECT TYING IN LATERALS TO ALL THE HOMES ON THE STREET. THE LATERALS WERE INSTALLED AROUND 1969-70. SPL BECAME A MEMBER OFTHE "ONE-CALL" SYSTEM IN THE LATE 80'S.
2017-09-29 08:50 | YES | NO | 19960136 | 1996-10-02 | 15674 | PLANTATION PIPE LINE CO | YES | 1996-09-06 | 1145 | VA | CHESTERFIELD | RICHMOND | NO |  | NO | A-DOT63-0 |  | LINE PIPE | PIPE |  | 1964 | OTHER | INTERNAL MILL DEFECT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 50466.6057 | 101811.5279 | GASOLINE | 3 | 12 | 7 | NO | NO | 12 | 0.2 | 52000 | WELDED |  | 1094 | 788 | YES | 20 | 1415 | 8 | 64 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JERRY MILHORN | 4043645948 | PLANTATION WAS NOTIFIED OF POSSIBLE RELEASE BY PROPERTY OWNER WHO SMELLED GASOLINE. PLANTATION INVESTIGATED AND DISCOVERED AN APPARENT MILL DEFECT. THE MILL DEFECT WAS LOCATED AT AN APPROX STATION NUMBER OF 205+88 IN THE 7 O'CLOCKPOSITION. A FULL ENCIRCLEMENT SLEEVE WAS PLACED OVER THE DEFECT. PLANTATION WILL REMOVE THE FAILED SECTION OF PIPE AND TEST IT FOR CAUSE OF FAILURE.
2017-09-29 08:50 | YES | NO | 19960137 | 1996-09-23 | 443 | AMOCO PIPELINE CO | YES | 1996-08-27 | 1345 | ND | MOUNTRAIL |  | NO |  | NO | M.P 35.7, SENE SECTION 7, TOWNSHIP 157N, RANGE 94W |  | LINE PIPE | PIPE |  | 1954 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 680 | 650 | NO | NO | 8 | 0.19 | 42000 | WELDED |  | 1074 | 150 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RE PETERSON | 3038305067 | THE AMOCO AERIAL PATROL PILOT REPORTED AN OUTAGE OF CRUDE OIL DURING ROUTINEPATROL ON 8/27/96 AT 1345 HOURS. INSPECTION OF THE PIPE REVEALED AN OLD TRANSITE LINE LAYING ACROSS THE AMOCO LINE CAUSED EXTERNAL CORROSION RESULTING INDEVELOPMENT OF A SMALL HOLE IN THE LINE.
2017-09-29 08:50 | NO | NO | 19960138 | 1996-09-17 | 11237 | T E PRODUCTS PIPELINE COMPANY, L P | YES | 1996-08-16 | 1100 | LA | WEBSTER |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1926 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2523.3303 | 5090.5764 | DIESEL FUEL | 3 | 1 | 1 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 660 | 200 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | O H CUNNINGHAM | 7137593615 | AT APPROX 1100HRS, CDT, ON AUGUST 15, 1996, A TEPPCO SURVEY CREW WORKING ON THE RIGHT-OF-WAY DISCOVERED PRODUCT SHEEN ON A DRAINAGE DITCH CROSSING. THE SURVEY CREW NOTIFIED OPERATING PERSONNEL. AT THAT TIME, THE EMERGENCY PLAN WASINITIATED, THE PIPELINE SYSTEM WAS SHUT DOWN, AND THE SECTION CONTAINING THELEAK WAS ISOLATED. A PLIDCO LEAK CLAMP WAS PLACED ONTO THE SYSTEM. CLEAN-UP CONSISTED OF REMOVAL OF THE SHEEN FROM THE STANDING WATER IN THE DITCH.
2017-09-29 08:50 | YES | YES | 19960139 | 1996-09-25 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | YES | 1996-08-24 | 1539 | TX | KAUFMAN | LIVELY | NO |  | NO | RURAL COMMUNITY DEVELOPMENT IN LIVELY, TX. AREA |  | LINE PIPE | PIPE |  | 1981 | OTHER | UNKNOWN AT THIS TIME | ALL OTHER CAUSES | MISCELLANEOUS | 2 | 0 | 2 | 0 | 0 | 0 | 217658 | 156920.8637 | 316572.7649 | BUTANE | 2 | 5518 | 0 | YES | YES | 8 | 0.19 | 46000 | WELDED |  | 1440 | 1273 | YES | 8 | 1855 | 7 | 95 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA | UNDER INVESTIGATION | Null | Null | JERRY ROGERS | 4053952377 | RELEASE OF PRODUCT AND IGNITION. CURRENTLY UNDER INVESTIGATION BY KOCH, NTSB& DOT.
2017-09-29 08:50 | NO | NO | 19960140 | 1996-09-26 | 26304 | UNOCAL PIPELINE CO - WESTERN REGION | NO | 1996-08-31 | 1030 | LA |  |  | NO | SEE COMMENTS | Null | PIPELINE - SOUTH TIMBALIER BLOCK 196 "A" TO SHIP SHOAL 208 "F" |  | LINE PIPE | VALVE | CHECK VALVE ON PIG DRIP | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2 | 0 | NO | NO | 6 | 0 | 0 | NO DATA |  | 1440 | 1440 | NO | 0 | 0 |  |  | EXTERNAL | Null | Null | OTHER | FSV CORRODED | NO DATA |  | Null | NO DATA |  | Null | Null | PAM TULLOS | 7138766229 | RICK THOMAS (UNOCAL) WAS TRYING TO BLEED PSI OFF PIPELINE AT SHIP SHOAL BLOCK208 "F" WHEN THE FSV ON THE SKID DRAIN DID NOT HOLD AND SENT FLUID BACK INTOTHE SKID AND OVER FLOWED THE SKID. THE BLEED LINE WAS THEN SHUT OFF AND THECORRODED FSV WAS REPLACED ON 9/9/96, AND THEN TESTED FOR 1 MIN. - BLED PIG RECEIVER, FSV HEAD. OFFSHORE COORDINATES: 28DEG, 31' 38"N (LAT) 90DEG 55' 24"W(LONG).
2017-09-29 08:50 | YES | YES | 19960141 | 1996-09-26 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-08-29 | 1426 | IA | MONONA |  | NO |  | NO | 4 1/2- MILES SO WEST OF MAPLETON, IA ON HWY 175, THEN 2.5 MILES WEST. SEC 31 T-84-N R-43-W |  | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 63929 | 46089.7091 | 92981.5595 | L. P. G. | 2 | 2700 | 0 | NO | NO | 7 | 0.16 | 46000 | WELDED |  | 1440 | 310 | YES | 24 | 2119 |  | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | PIPELINE MARKERS | NO | NO | JOHNNY CAVITT | 9185993795 | PRIVATE LAND OWNER WAS GRADING A FIELD ROAD AND STRUCK THE PIPELINE CAUSING A RUPTURE.
2017-09-29 08:50 | YES | NO | 19960142 | 1996-09-27 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1996-08-24 | 1431 | MN | DONALDSON |  | NO |  | NO | DONALDSON STATION |  | LINE PIPE | PIPE |  | 1973 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 360475.7548 | 727225.1993 | CRUDE OIL | 1 | 5000 | 4252 | NO | NO | 48 | 0.41 | 880 | WELDED |  | 622 | 569 | YES | 24 | 793 | 10 | 73 | EXTERNAL | Null | YES | OTHER | METAL LOSS DUE TO DISBOND | NO DATA |  | Null | NO DATA |  | Null | Null | RC SANDAHL | 2187250102 | AT APPROX 14:31 MST ON AUGUST 24, 1996, A LEAK OCCURRED ON 48" LOOP SECTION OF LINE 3 AT DONALDSON STATION. ABNORMAL OPERATING PRESSURES WERE OBSERVED BYTHE EDMONTON CONTROL CENTER AND LINE 3 WAS IMMEDIATELY SHUT DOWN. THE LEAK WAS CONTAINED ON DONALDSON PROPERTY. THE 48" LOOP WAS ISOLATED AND LINE 3 WAS PUT BACK INTO SERVICE WITH THE LOOP BYPASSED AT 7:16 MST ON AUGUST 25. THE 48" LOOP WAS PUT BACK IN SERVICE AT 20:30 MST ON AUGUST 30. THE MINNESOTA STAT DUTY OFFICER AND NATIONAL RESPONSE CENTER WERE NOTIFIED. THE FAILURE APPEARS TO HAVE RESULTED FROM EXTERNAL CORROSION ON A SECTION OF HAND WRAPPED PIPING BETWEEN TWO FITTINGS. THE PIPE WAS DISBONDED WHICH SHIELDED CATHODIC PROTECTION.
2017-09-29 08:50 | YES | NO | 19960143 | 1996-09-26 | 18156 | SEADRIFT PIPELINE CORP | NO | 1996-08-31 | 1815 | TX | KENEDY |  | NO |  | NO | KENEDY RANCH,1 MILE WEST OF HWY 77, 5 MILES NORTH OF ARMSTRONG. GATE IS CALLED THE TURCOTTE GATE. LEAK LOCATED AT STAT 4520+72 OF OUR ELLA-BROWNSVILLE PIPELINE. |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 73956 | 53318.6898 | 107565.3337 | L. P. G. | 2 | 120 | 0 | NO | NO | 6 | 0.25 | 42000 | WELDED |  | 1902 | 310 | NO | 8 | 2938 | 9 | 93 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN WALTHALL | 5125533163 | A CORROSION PINHOLE WITH A CALCULATED DIAMETER OF LESS THAN 0.03" IS THOUGHTTO HAVE BEGUN AROUND JULY 23, 1996, AND AND DETECTED ON AUGUST 31, 1996. THEPIPELINE IS A BATCH OPERATION MAKING DETECTION OF A LEAK THIS SMALL (21 LBS/HR) IMPOSSIBLE DURING FLOWING CONDITIONS. THE LEAK WAS DETECTED DURING AN EXTENDED NO-FLOW PERIOD.
2017-09-29 08:50 | YES | NO | 19960144 | 1996-09-23 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1996-08-28 | 1215 | CA | KERN |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3604.7575 | 7272.252 | CRUDE OIL | 3 | 1380 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RE KELLEY | 8053282331 | FARMER RIPPING FIELD AND HIT PIPELINE WITH RIPPER.
2017-09-29 08:50 | YES | NO | 19960145 | 1996-09-30 | 9175 | JAYHAWK PIPELINE CORP | YES | 1996-09-06 | 1230 | KS | RENO |  | NO |  | NO | NW 1/4 SECT 13, TOWNSHIP 23 SO, RANGE 4 WEST OF RENO CO. KANSAS 2 MILES NORTH AND 2 MILES WEST OF BURRTON, KS |  | LINE PIPE | PIPE |  | 1930 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 3748.9478 | 7563.1421 | CRUDE OIL | 1 | 100 | 15 | NO | NO | 3.5 | 0.19 | 25000 | THREADED |  | 100 | 20 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN WILKERSON | 3162419270 | THIS GATHERING LINE DELIVERS OIL INTO JAYHAWK'S BURRTON STATION. JAYHAWK'S AIR PATROL SPOTTED THE SPILL. JAYHAWK PERSONNEL RESPONDED IMMEDIATELY AND SHUTDOWN THE SYSTEM. WITH THE AREA SANDY, THE OIL SATURATED THE SOIL AND JAYHAWKRECOVERED ALL THAT WAS POSSIBLE. JAYHAWK WILL REMEDIATE THE SOIL ON SITE, UNTIL KANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT GIVES THE SITE A CLEAN BILL OF HEALTH.
2017-09-29 08:50 | NO | NO | 19960146 | 1996-10-22 | 19223 | SUN PIPELINE CO | YES | 1996-09-23 | 1105 | MI | ST. CLAIR |  | NO |  | NO | 29' WEST OF THE CENTER LINE OF MAYERS RD, 1320' NORTH OF FRITH RD, SEC 1, COLUMBUS TOWNSHIP. IN FRONT YARD OF 380 MAYERS RD. |  | LINE PIPE | GIRTH |  | 1950 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | BUTANE | 2 | 2 | 0 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 1200 | 810 | YES | 24 | 1500 | 10 | 58 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHRISTINE MAZZARA | 3132928850 | AT 1105AM SUN PIPELINE CO. CONTROL CENTER WAS NOTIFIED BY A PROPERTY OWNER,RICHARD PIETROSKI THAT A WHITE, LIQUID WAS BUBBLING OUT OF THE GROUND OVER THEPIPELINE INTO A DRAINAGE DITCH. INVESTIGATION REVEALED A LEAK, INSPECTIONREVEALED A FLAW IN THE WELD METAL.
2017-09-29 08:50 | YES | NO | 19960147 | 1996-10-18 | 2552 | COLONIAL PIPELINE CO | YES | 1996-06-30 | 2156 | GA | BIBB | MACON | NO |  | NO | COLONIAL'S SOUTH MACON DELIVERY. 519 FORSYTH ROAD, MACON, GA. 31210 |  | NO DATA | BOLTED FITTING | PROVER LOOP FLANGE | 1963 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 72095.151 | 145445.0399 | DIESEL FUEL | 3 | 5 | 4 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JA COX | 4048412296 | ON JUNE 30, 1996, AT 21:56EST, THE COLONIAL PIPELINE OPERATOR SWITCHED THE DELIVERY FROM ONE SHIPPER TO ANOTHER. AFTER THE SWITCH A HIGH MANIFOLD PRESSURE WAS ALARM WAS RECEIVED AND THE TAKE-OFF VALVE CLOSED. THE CONTROLLER WAS NOTIFIED AND THE OPERATOR CALLED THE SHIPPER. THE SHIPPER HAD FAILED TO OPEN HIS DELIVERY VALVE. AFTER THE DELIVERY VALVE WAS OPEN THE WAS RESUMED AT 22:04EST. WHEN THE OPERATOR CHECKED THE STATION HE DISCOVERED THAT PRODUCT WAS SPRAYING FROM THE PROVER LOOP. HE IMMEDIATELY CALLED THE CONTROLLER AND CLOSED OUT THE DELIVERY. THE OPERATOR ISOLATED THE PROVER AND THE DELIVERY WAS RESUMEDAT 22:24EST. A RESPONSE CREW WAS DISPATCHED TO SOUTH MACON DELIVERY AT 23:10EST. COLONIAL PERSONNEL BEGAN DIGGING RECOVERY PITS TO COLLECT PRODUCT WHICH WAS PUMPED TO THE SUMP. ON JULY 1, 1996, TEST HOLES WERE DRILLED TO DETERMINETHE EXTENT OF THE CONTAMINATION AND THE MAINTENANCE CREW BEGAN REMOVING THE CONTAMINATED SOIL FOR DISPOSAL. A FLANGE WAS REMOVED FROM THE BI-DIRECTIONAL PROVER AT 09:20. THERE WAS A ONE INCH SECTION OF GASKET MATERIAL TORN LOOSE. A NEW GASKET WAS PUT INTO SERVICE AND PROVER FLANGE BOLTED BACK INTO PLACE. THE GEORGIA EMERGENCY RESPONSE AGENCY WAS NOTIFIED ON JULY 3, 1996 BY JEFF RICHARDS AT 15:35 - REPORT #070396-07. THE GEORGIA GEOLOGIC SURVEY - ROGER CARTER - WAS NOTIFIED ON JULY 3, 1996 EDT BY JEFF RICHARDS. ON JULY 30, 1996, AT 13:10 EST THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC REPORT NO. 354026) BECAUSE THE COSTS HAD EXCEEDED THE $50,000 LIMIT. AT THIS TIME THE CLEAN-UP IS COMPLETE AND COLONIAL IS AWAITING FINAL APPROVAL FROM THE GEORGIA DEPT. OF NATURAL RESOURCES.
2017-09-29 08:50 | YES | YES | 19960149 | 1996-10-21 | 13131 | CONOCO INC | NO | 1996-09-08 | 1900 | TX |  |  | NO | SEE COMMENTS | NO | WD 96 R + 10 ELEVATION |  | LINE PIPE | PIPE |  | 1968 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | NOT GIVEN | 1 | 0 | 0 | YES | NO | 10 | 0.5 | 24000 | FLANGED |  | 1440 | 0 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | TAMMY YORK | 3182693444 | WE WERE DISMANTLING A PIPELINE RISER SECTION AT THE +10' ELEVATION AND INSTALLING A NEW RISER SECTION. THE PIPELINE, RISER, AND PIG TRAPS HAD BEEN FLUSHED WITH +3 VOLUMES OF WATER AND TWO PIGS HAD BEEN RUN. THE PIPELINE WAS ISOLATED ABOVE THE PIG TRAPS ON BOTH ENDS BY REMOVING SECTIONS OF PIPE AND INSTALLING BLIND FLANGES. THE SDV'S PNEUMATIC SIGNAL LINE WAS REMOVED AND THE VALVE WAS CLOSED. THE RISER WAS DISCONNECTED FROM THE BOTTOM OF THE SHUTDOWN VALVE AT THE +15' ELEVATION AND SET 1 PIPE DIAMETER OFF TO THE SIDE OF THE SDV. THE RISER WAS FULL OF WATER WHEN THE BOTTOM FLANGE OF THE SDV WAS DISCONNECTED. NO HYDROCARBONS WERE PRESENT. A DIVER HOT CUT THE RISER AT THE -15' ELEVATION.AFTER THE DIVER RETURNED TO THE SURFACE AND WAS BACK ON THE BOAT, THE OPEN END OF THE RISER WAS CHECKED FOR GAS WITH A GAS DETECTOR. NO GAS WAS DETECTED.A CONTRACTOR WAS IN THE PROCESS OF HOT CUTTING THE STUDS AND NUTS OFF THE TOP FLANGE OF THE SDV TO FACILITATE IN REMOVAL OF THE VALVE. HOT SLAG, SPARKS, AND MOLTEN METAL FROM HIS CUTTING OPERATION FELL INTO THE OPEN END OF THE RISER POSITIONED BELOW AND TO THE SIDE OF THE HOT WORK AREA. RESIDUAL HYDROCARBONS INSIDE OF THIS RIGER IGNITED AND FLASHED. THE CONTRACTORS LEFT FOREARM RECEIVED A SECOND DEGREE BURN. HE WAS TREATED AND RELEASED TO FULL DUTY. OFFSHORE COORS: LAT 28DEG53'56.96" LONG 89DEG50'13.17"
2017-09-29 08:50 | YES | NO | 19960150 | 1996-10-17 | 2814 | FINA PIPE LINE CO | NO | 1996-09-02 | 1210 | TX | HOWARD |  | NO |  | NO | T&P RR CO. SURVEY, BLK.32, T-1-S, SECTION 2 4.9 MI. EAST OF THE CENTER OF BIG SPRING, TX, 0.57 MI. SOUTH OF MIDWAY RD. & 1.0 MI. SOUTH OF I-H20. |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 27500 | 19826.1665 | 39997.386 | CRUDE OIL | 1 | 150 | 120 | NO | NO | 8 | 0 | 0 | WELDED |  | 0 | 0 | NO | 0 | 0 |  |  | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED | 9152639256 | LANDOWNER/RESIDENT (DAVID HIGGINS) CALLED FINA'S BIG SPRING REFINERY (BSR) @12:10PM, MONDAY, SEPT 2ND(LABOR DAY), TO REPORT THAT HIS DOG CAME HOME COVERED IN OIL. HE CHECKED HIS CREEK BOTTOM LAND PROPERY AND DISCOVERED THAT BEALSCREEK WAS COVERED WITH OIL. THE BSR SHIFT FOREMAN CONTACTED THE PIPELINE'S CONTROL CENTER TO REPORT A LIKELY LEAK. THE CONTROL CENTER WAS NOTIFIED AT 12:20PM, AND IMMEDIATELY DISPATCHED FIELD PERSONNEL TO LOCATED SOURCE OF A LEAK.THE SOURCE OF THE LEAK WAS DISCOVERED AT 12:40PM. AT 1:45PM FARTHEST EXTENT OF CONTAMINATION ON CREEK WAS FOUND. AT 2:05PM, CLAMP WAS INSTALLED ON PIPE TO PREVENT FURTHER LEAKAGE. AT 2:50PM, BOOMS HAD BEEN PLACED AT A POINT IN THECREEK AT THE LEADING EDGE OF THE SPILL, APPROX. 3.25 MI. DOWNSTREAM FROM THELEAK SITE. BY WEDNESDAY, SEPT. 4TH , 120 BBLS OF OIL HAD BEEN RECOVERED. THIS WAS THE TOTAL THAT WAS RECOVERABLE. SUBSEQUENT TO THAT DATE, "POLISHING" OFMINOR SHEENS AND "POCKETS" OF OIL WAS DONE. ON THURS, SEPT 12TH, ALL BOOMS WERE PULLED AND RESPONSE ACTIVITIES WERE COMPLETED. AGENCIES (RRC&TNRCC) AUTHORIZED THIS CLOSE-OUT. COATING WAS "FIELD-WRAP" ONLY; NOT IN GOOD SHAPE. PIPELINE WS "STATIC". MINIMAL - PIPELINE WAS "STATIC"-ELEVATION HEAD PRESSURE, ONLY
2017-09-29 08:50 | YES | NO | 19960151 | 1996-10-11 | 19226 | TEXACO PIPELINE INC | YES | 1996-09-14 | 1115 | KS | BUTLER | EL DORADO | NO |  | NO | 28S-4E, NORTHWEST QUARTER OF SECTION 34 |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | CRUDE OIL | 1 | 600 | 350 | NO | NO | 20 | 0.25 | 1500 | WELDED |  | 1080 | 70 | YES | 24 | 1350 | 0 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JE ZANG | 3163214645 | OUTSIDE EXCAVATION COMPANY DUG INTO CRUDE OIL PIPELINE WHILE EXCAVATING FOR UNRELATED SEWER LAGOON.
2017-09-29 08:50 | NO | NO | 19960152 | 1996-10-08 | 19226 | TEXACO PIPELINE INC | NO | 1996-09-18 | 1130 | OK | CREEK | TULSA | NO |  | NO | NE 1/4 OF SECTION 6, T-18N, R-12E; 7000 BLOCK OF SOUTH 69TH WEST AVENUE IN TULSA, OK |  | LINE PIPE | PIPE |  | 1949 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 793.0467 | 1599.8954 | CRUDE OIL | 3 | 5 | 4 | NO | NO | 10.75 | 0.31 | 36000 | WELDED |  | 790 | 100 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | BOYD URATL | 9182253469 | PIPELINE OVERHEAD CROSSING WAS SHOT WITH A HIGH POWERED RIFLE. WITNESS SAW INDIVIDUAL FIRING RIFLE INTO CREEK AND SUBSEQUENTLY HITTING PIPELINE. INDIVIDUAL THEN FLED SCENE AFTER NOTICING OIL SPRAYING FROM LINE. WITNESS CALLED TEXACO AND REPORTED INCIDENT. LINE WAS IMMEDIATELY SHUT DOWN AND REPAIR/CLEANUP CREWS DISPATCHED TO SITE. BULLET DID NOT FULLY PENETRATE PIPELINE. CAUSE OF ACCIDENT: VANDALISM; OVERHEAD CROSSING WAS SHOT WITH A HIGH POWERED RIFLE.
2017-09-29 08:50 | NO | NO | 19960153 | 1996-10-08 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1996-09-19 | 102 | AR | IZARD |  | NO |  | NO | SEC.33 T17NR7W IZARD, CO. AR. |  | LINE PIPE | VALVE |  | 1969 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | OTHER | VANDALISM | Null | NO DATA |  | Null | Null | MARC DEVARENNES | 5734865488 | VANDALS BROKE INTO A BURIED CAN CONTAINING A 3 INCH VALVE WITH AN ASSOCIATED1/2 INCH VALVE ON THE UPSTREAM SIDE OF MAINLINE BLOCK VALVE #3-39. THE 1/2 INCH VALVE WAS LEFT 1/4 OPEN.
2017-09-29 08:50 | YES | NO | 19960154 | 1996-10-10 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-09-05 | 1246 | IA | VAN BUREN |  | NO |  | NO | 2 MILES WEST OF CANTRIL, IOWA ON HIGHWAY 2 T-68-N R-11-W SEC 35 |  | TANK FARM | VALVE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 144.1903 | 290.8901 | L. P. G. | 2 | 13 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | JOHNNY CAVITT | 9185993795 | MECHANICAL DAMAGE TO RELIEF VALVE DUE TO ACCIDENTAL IMPACT.
2017-09-29 08:50 | YES | NO | 19960155 | 1996-10-16 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-09-16 | 736 | KS | BUTLER |  | NO |  | NO | T-29-S R-6-E SECTION 18. 10 MILES SOUTH AND 3 MILES WEST OF LEON, KANSAS |  | LINE PIPE | PIPE |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 116878 | 84263.3705 | 169993.2537 | NATURAL GAS LIQUID | 2 | 3684 | 25 | NO | NO | 7 | 0.13 | 60000 | WELDED |  | 1630 | 790 | YES | 24 | 2223 | 7 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | JOHNNY CAVITT | 9185993795 | SCADA SYSTEM WAS UTILIZIED TO INITIALLY DETECT A POTENTIAL LEAK. THE LEAK WASPHYSICALLY CONFIRMED, AND THE PIPELINE AND LEAK IMPACT AREAS WERE ISOLATEDAND SECURED. PIPELINE REPAIR WORK DISCOVERED EVIDENCE OF PREVIOUS MECHANICALEXCAVATION DAMAGE AS THE PROBABLE CAUSE OF THE INCIDENT. REPORT REVISED TOREFLECT DECREASE IN TOTAL BARRELS FROM THE ESTIMATE 2652 BBLS NATURAL GAS AND2016 BBLS ISO-BUTANE TO THE ACTUAL LOSS OF 2652 BBLS NATURAL GAS AND ONLY 1032BBLS OF ISO-BUTANE. SUPPLEMENTAL RECEIVED 11/19/1996.
2017-09-29 08:50 | YES | NO | 19960156 | 1996-10-11 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | NO | 1996-09-24 | 1540 | OK | BLAINE | WATONGA | NO |  | NO | SE/4SE/4 SECTION 12-T16N-R12W, BLAINE CO. OK |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6040 | 4354.5471 | 8784.8804 | CRUDE OIL | 1 | 100 | 75 | NO | NO | 6 | 0.24 | 42000 | WELDED |  | 920 | 240 | YES | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | Null | JAMES HENRY | 4058784122 | EARTH MOVING EQUIPMENT HIT PIPELINE RESULTING IN RELEASE. RECORDS NOT LOCATED. WRONG LOCATION GIVEN.
2017-09-29 08:50 | YES | YES | 19960157 | 1996-10-29 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-10-02 | 1155 | TX | ECTOR |  | NO |  | NO | T &P RR CO. BLOCK 44 T-1-S 6 MILES SOUTH OF GOLDSMITH, TX. |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 2 | 0 | 2 | 4 | 0 | 4 | 5000 | 3604.7575 | 7272.252 | NOT GIVEN | 1 | 0 | 0 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1318 | 600 | YES | 24 | 1726 | 6 | 88 | NO DATA | Null | Null | NO DATA |  | OTHER | NONE SPECIFIED | Null | ONE CALL | PIPELINE SIGNS & POSTS | NO | NO | SID RUETER | 9185811538 | COLD CUT WHEN THE PIPE FAILED, RELEASING THE NITROGEN PRESSURE. CAUSE OF ACCIDENT: CAUSED BY THIRD PARTY'S CONTRACTOR.
2017-09-29 08:50 | YES | NO | 19960158 | 1996-10-24 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-09-30 | 1025 | TX | CARSON |  | NO |  | NO | I.& G.N. R.R. BLOCK 4, SECTION 88 EIGHT MILES WEST OF PAMPA, TX ON US 152, TO CARSON ROAD 2400, THEN 3 MILES NORTH. |  | LINE PIPE | WELDING FITTING |  | 1969 | FAILED WELD | OTHER | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14419.0302 | 29089.008 | BUTANE | 2 | 20 | 0 | NO | NO | 10 | 0.19 | 52000 | WELDED |  | 1198 | 1156 | YES | 24 | 1497 | 9 | 69 | NO DATA | Null | Null | NO DATA |  | OTHER | NONE SPECIFIED | Null | NO DATA |  | Null | Null | JOHNNY CAVITT | 9185993795 | LONGITUDINAL WELD ON SPLIT TEE FAILED.
2017-09-29 08:50 | YES | NO | 19960159 | 1996-10-24 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1996-09-11 | 540 | CA | SOLANO | ELMIRA | NO |  | NO | LS-25, MP 31.3. CITY OF ELMIRA NEAR THE INTERSECTION OF ELMIRA RD. AND A ST. SE SIDE OF RAILROAD TRACKS, EAST OF ELMIRA ROAD. |  | LINE PIPE | LONGITUDINAL WELD |  | 1968 | OTHER | SEAM WELD DEFECT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 900000 | 648856.3586 | 1309005.3588 | GASOLINE | 3 | 5 | 5 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1170 | 1108 | YES | 24 | 1464 | 3 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JM ABBOUD | 7145604720 | THE LOCAL SERVER UTILITY AGENCY HAD REPORTS OF ELEVATED VAPOR CONCENTRATIONSIN A SECTION OF SEWER PIPE. AFTER SOME INVESTIGATION THEY CONTACTED SFPP,L.P. A SECTION OF PIPE WAS EXCAVATED IN THE VICINITY OF A SEWER CROSSING AND A WELD SEAM WEEP WAS FOUND. THE LEAK WAS REPAIRED AND A SUBSURFACE INVESTIGATIONAND CLEANUP HAS BEEN INITIATED .
2017-09-29 08:50 | YES | NO | 19960160 | 1996-10-25 | 2767 | COOK INLET PIPELINE CO | NO | 1996-10-05 | 1030 | AK |  |  | NO |  | NO | SEL 5 TWP 8N RG 14W |  | LINE PIPE | PIPE |  | 1968 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 72095.151 | 145445.0399 | CRUDE OIL | 1 | 90 | 80 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 640 | 90 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | INTERNAL PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | AR YURKIERRAY | 9072431166 | AT APPROX. 1030 ON OCTOBER 5, 1996, KEITH WOOD, AN OPERATOR AT THE UNOCAL PRODUCTION STATION, TRADING BAY, NOTICED OIL OOZING OUT OF THE GROUND AT THE BYPASS VALVE OF THE 20" PIG TRAP. HE IMMEDIATELY SHUT DOWN THE SHIPPING PUMPS WHICH STOPPED THE OIL FROM OOZING. HE THEN REPORTED IT TO HIS SUPERVISOR, TOMGILES, WHO DISPATCHED A VAC TRUCK TO THE LOCATION, INITIATING AN IMMEDIATE RESPONSE WHILE MR. WOOD CONTACTED THE DRIFT RIVER TERMINAL SUPERVISOR, RON WILD. DAVID STRAWSER, UTILITY OPERATOR, WAS SENT TO THE SPILL SITE TO ISOLATE THE LEAK BY CLOSING ALL VALVES AND INITIATING THE LOCKOUT TAG OUT ON ALL VALVESAND SWITCHES. MR. STRAWSER DUG DOWN TO FIND A CORROSION HOLE IN THE 20" PIPE. CERTIFIED WELDER, DAVID CASSTEVENS OUT PROCEDURE AND OPENED THE VALVE TO RESUME SHIPPING CRUDE TO DRIFT RIVER.
2017-09-29 08:50 | YES | YES | 19960161 | 1996-10-28 | 30899 | WOLVERINE PIPELINE CO | NO | 1996-09-26 | 1442 | MI | GRAND HAVEN |  | NO |  | NO | THIS PIPELINE TRAVELS ALONG US HWY31. 120 FEET WEST OF HWY US 31 ON NORTH SIDE OF FERRIS ST. THERE IS A RR TRACK THAT RUNS ALONGSIDE THE LINE, 50' FROM THE LINE |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 126560 | 91243.6231 | 184075.2425 | GASOLINE | 1 | 102 | 4 | YES | NO | 8 | 0.19 | 1759 | WELDED |  | 1400 | 41 | YES | 8 | 1820 | 11 | 62 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | DALE MAY | 8154237760 | A CONSTRUCTION CONTRACTOR WIDENING A ROAD FOR SCHOOL IN GRAND HAVEN, MI., STRUCK THE WOLVERINE PIPELINE. WOLVERINE PERSONNEL IMMEDIATELY SHUTDOWN THE LINE DUE TO THE RATE FLUCTUATION BEFORE 911 CONTACTED THEM. THE FIRE DEPARTMENT WAS DISPATCHED BY THE 911 OPERATOR. THE BULLDOZER OPERATOR WAS TRANSPORTED TOTHE HOSPITAL WITH 2ND DEGREE BURNS TO HIS HANDS AND FACE. AFTER THE FIRE DEPARTMENT PUT THE FIRE OUT, THE WOLVERINE PERSONNEL PUT A CLAMP ON THE 8" LINE AND THE PIPELINE WAS DOWN FOR APPROX 48HRS. AT THIS TIME WE PUT A TEST ON THECLAMP AND THEN PUT IT BACK INTO SERVICE. NOTE: PART J-#4 CONTRACTOR DID NOT TIMELY PERFORM WORK AFTER CALL. OTHER SPECIFIED: A CONTRUCTION CONTRACTOR NOTWORKING FOR WOLVERINE PIPELINE CO. WAS DIGGING WITH A BULLDOZER TO WIDEN A ROAD, AND HIT THE PIPELINE.
2017-09-29 08:50 | YES | YES | 19960162 | 1996-10-28 | 15490 | PHILLIPS PIPE LINE CO | YES | 1996-09-24 | 630 | TX | COCHRAN |  | NO |  | NO | ODESSA-BORGER LINE "WA"-MP 126-00+00 -SRW-37-29 MIDLAND CO. SCHOOL LAND SURV, BLOCK A-62, LEAGUE 64, SEC. 8A 271' NORTH OF THE CENTERLINE OF FM 769. |  | LINE PIPE | OTHER | TAPPING MACHINE | 1966 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 | 38000 | 27396.1574 | 55269.1151 | CRUDE OIL | 1 | 370 | 365 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LJ SCHMITZ | 9186614814 | EMPLOYEES WERE REMOVING STOPPLE TEE COMPLETION PLUG. WHILE DOING SO, THE PLUG BECAME DISCONNECTED FROM THE MACHINE. THE TAPPING MACHINE TO VALVE ADAPTOR WAS NOT EQUIPPED WITH AN EQUALIZATION PORT. AS A RESULT, WHEN LINE PRESSURE ROSE DURING NORMAL OPERATION, DIFFERENTIAL PRESSURE COULD NOT BE RELIEVED ACROSS THE COMPLETION PLUG AND THE TAPPING MACHINE WAS OVERSTRESSED. ONE EMPLOYEEWAS INJURED WHEN STRUCK BY THE FAILED MACHINE. NOTE: WHILE LINE PIPE WAS SYSTEM SUBPART, FAILURE DID NOT OCCUR IN LINE PIPE. CAUSE OF ACCIDENT: DESIGN OFTAPPING MACHINE ADAPTER.
2017-09-29 08:50 | YES | NO | 19960163 | 1996-10-23 | 22610 | WILLIAMS PIPELINE CO | YES | 1996-09-19 | 1055 | OK | PAYNE |  | NO |  | NO | NORTHWEST 1/4 OF SECTION 3 IN TOWNSHIP 17N, RANGE 6E IN PAYNE COUNTY, OKLAHOMA. |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 90118.9387 | 181806.2998 | CRUDE OIL | 1 | 200 | 80 | NO | NO | 12 | 0.3 | 24000 | WELDED |  | 650 | 0 | YES | 8 | 937 | 0 | 95 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN BALL | 9185883850 | ON THE AFTERNOON OF SEPT.18, 1996, OPERATIONS CONTROL RECEIVED A CALL FROM ALANDOWNER WEST OF DRUMRIGHT, OK, STATING THAT HE HAD CRUDE OIL PRESENT ON THE GROUND NEAR HIS HOUSE. THE DISPATCHER INFORMED THE LANDOWNER THAT THE LEAK COULD NOT BE OURS BECAUSE WE DID NOT PUMP CRUDE OIL IN THAT AREA AND SUGGESTED THAT HE CALL OUR SOUTHERN REGION FOR ASSISTANCE IN HELPING HIM LOCATE THE SOURCE OF THE CRUDE OIL. THE NEXT MORNING, UPON FURTHER INVESTIGATION, IT WAS DETERMINED THAT IT COULD POSSIBLY BE THE LEF PRODUCT THAT WE DID PUMP IN THATAREA. AT THAT TIME THE SOUTHERN REGION OFFICE WAS NOTIFIED THAT WE HAD A POSSIBLE LEAK. AT 825HRS, ON SEPT.19, WPL FIELD PERSONNEL WERE DISPATCHED TO DRIVE THE LINE BETWEEN CUSHING AND DRUMRIGHT TO LOOK FOR THE POSSIBLE LEAK. AT 952HRS, WPL DISCOVERED THE LEAK AREA AND ORDERED EQUIPMENT TO THE SITE TO EXCAVATE THE LINE AND CONTROL THE RUN-OFF. AT 1045HRS, THE FIRST BACKHOE ARRIVED AT THE SITE TO BEGIN CONSTRUCTING CONTAINMENT DIKES AND A VACUUM TRUCK ARRIVED AT THE SIT TO BEGIN RECOVERING PRODUCT. AT 1340HRS, A TRACKHOE ARRIVED TO BEGIN EXCAVATING THE LINE TO LOCATE THE LEAK. AT 1747HRS, THE LEAK WAS LOCATEDAND AT 1840HRS THE LEAK WAS CLAMPED OFF. AT 0049HRS ON SEPT.20, THE WELDING OF THE PATCH WAS COMPLETED. REMEDIATION OF THE LEAK SITE IS CONTINUING WITH WPL ENVIRONMENTAL ENGINEERS WORKING WITH OKLAHOMA ENVIRONMENTAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19960164 | 1996-10-28 | 21038 | VALERO MARKETING CO | NO | 1996-09-25 | 830 | TX | NUECES |  | NO |  | NO | FM 1694; 2.7 MILES SOUTH OF HWY44 |  | LINE PIPE | PIPE |  | 1939 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 81000 | 58397.0723 | 117810.4823 | BUTANE | 2 | 83 | 37 | NO | NO | 6 | 0.25 | 24000 | WELDED |  | 794 | 400 | YES | 4 | 1293 | 1 | 96 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN SOMMER | 2102462395 | PIPELINE SYSTEM WAS BEING PLACED IN SERVICE WHEN LEAK WAS DISCOVERED BY AERIAL PATROL.
2017-09-29 08:50 | NO | NO | 19960165 | 1996-10-29 | 18273 | SHELL PIPELINE CORP | NO | 1996-09-23 | 1030 | CA | KERN |  | NO |  | NO | BAKERSFIELD 14" CRUDE PIPELINE, NN 1/4, SE 1/4, SECTION 22, T-27-S, R-23-E |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 39652.333 | 79994.7719 | CRUDE OIL | 1 | 24 | 10 | NO | NO | 14 | 0.22 | 52000 | WELDED |  | 1150 | 0 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | TE GREEN | 7132414506 | LINE WAS DOWN FOR ANNUAL SMART PIG RUN. RELATIVELY HIGH COSTS DUE TO ALMOND ORCHARD DAMAGE.
2017-09-29 08:50 | YES | NO | 19960166 | 1996-10-31 | 12127 | MARATHON PIPE LINE CO | YES | 1996-10-02 | 1135 | IL | CRAWFORD |  | NO |  | NO | 1 MILE SOUTH OF THE CITY OF ROBINSON, SECTION 2, T6N, R12W |  | LINE PIPE | VALVE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 72095.151 | 145445.0399 | GASOLINE | 3 | 1 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH FISHER | 4194213201 | ON 10/2/96, A MARATHON PIPE LINE CO.(MPL) EMPLOYEE WAS PERFORMING SCHEDULED BLOCK VALVE INSPECTIONS ON THE ROBINSON-LOUISVILLE 16" PRODUCTS PIPELINE SYSTEM. AT 1100, UPON APPROACHING THE VALVE, THE EMPLOYEE NOTICED DISCOLORATION ON THE OUTSIDE OF A 10-12" PVC PIPE USED AS PROTECTION FOR A 1/2" PIPE RISER COMING FROM THE BLOCK AND BLEED PORT ON THE MAINLINE VALVE. THE EMPLOYEE ALSO HEARD A NOISE COMING FROM THE AREA. THE EMPLOYEE LIFTED THE LID ON THE CASINGAND SAW LIQUID SPRAYING HORIZONTALLY AGAINST THE SIDE OF THE CASING. THE PRODUCT IN THE LINE WAS REGULAR UNLEADED GASOLINE. AFTER DISCOVERING THE RELEASE, THE EMPLOYEE EXITED THE SITE TO HIS TRUCK AND CONTACTED THE MARATHON PIPE LINE COMPANY WABASH STATION AT APPROX 1120. THE EMPLOYEE INFORMED THE STATION OPERATOR OF THE RELEASE. THE STATION OPERATOR, IN CONJUCTION WITH THE OPERATIONS CENTER, LOCATED IN FINDLAY, OH, IMMEDIATELY SHUT DOWN THE LINE. MPL EMERGENCY RESPONSE PERSONNEL RESPONDED TO THE SITE BETWEEN 1230-1300. A SITE SAFETY ASSESSMENT WAS CONDUCTED AND THE BLOCK VALVE WAS CLOSED. A MPL BACKHOE AND OPERATOR ARRIVED ONSITE AT APPROX 1400. THE SOIL AROUND THE RISER WAS EXCAVATED AND THE RISER WAS EXPOSED. THE RISER, WHICH WAS THE SOURCE OF THE RELEASE,WAS REMOVED AND THE 1/2" BLOCK AND BLEED PORT WAS PLUGGED. THE PIPELINE WAS STARTED BACK UP ON 10/2 AT 1830 AND RETURNED TO REGULAR OPERATION. ON 10/2/96THE ILLINOIS EMERGENCY MANAGEMENT AGENCY WAS NOTIFIED OF THIS INCIDENT. A SIGHT REMEDIATION ASSESSMENT WAS COMPLETED ON 10/29/96. THIS ASSESSMENT PROJECTED CLEANUP COSTS TO EXCEED $50,000, SO THE NATIONAL RESPONSE CENTER WAS ALSO NOTIFIED AT THAT TIME. PLANS ARE BEING PREPARED TO REMEDIATE THE SIGHT.
2017-09-29 08:50 | YES | NO | 19960167 | 1996-11-12 | 15490 | PHILLIPS PIPE LINE CO | YES | 1996-10-08 | 1030 | CO | ELBERT |  | NO |  | NO | BORGER-DENVER LINE -LRW 7/13/76-MP 320-25+00 SEC.23, T7S, R64W, ELBERT CO., CO 3.5 MILES EAST AND 5 MILES NORTH OF ELIZABETH, CO. |  | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 49000 | 35326.624 | 71268.0695 | GASOLINE | 2 | 100 | 72 | NO | NO | 8.63 | 0.16 | 52000 | WELDED |  | 1270 | 682 | YES | 24 | 1757 | 8 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | LINUS SCHMITZ | 9186614814 | A 3RD PARTY CONTRACTOR, EXCAVATING WITH A TRACK-HOE TO INSTALL A FOREIGN PIPELINE CROSSING, STRUCK AND PUNCTURED PHILLIPS PIPE LINE'S 8" PIPELINE. PHILLIPS PIPE LINE SHUT DOWN THE LINE IMMEDIATELY AND CLOSED THE VALVES. A ONE-CALLHAD BEEN PLACED AND THE LINE WAS LOCATED, MARKED, AND VISIBLE AT THE TIME OFTHE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19960168 | 1996-11-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1996-10-08 | 2138 | MO | CLAY |  | NO |  | NO | MID-AMERICA PIPELINE'S KEARNEY STATION 1015 N. JEFFERSON, KEARNEY, MO T-53-N R-31-W SEC 33, 1/4 MILE NORTH OF KEARNEY ON HWY 33 |  | TANK FARM | OTHER | LOADING PUMP | 1962 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1400 | 1009.3321 | 2036.2306 | L. P. G. | 2 | 8 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHNNY CAVITT | 9185993795 | SEAL FAILED ON LOADING PUMP.
2017-09-29 08:50 | NO | NO | 19960169 | 1996-11-06 | 2564 | COLORADO INTERSTATE GAS CO | NO | 1996-10-15 | 2255 | KS | MORTON |  | NO |  | NO | 1/4 MILE EAST OF COLORADO INTERSTATE GAS MORTON COUNTY COMPRESSOR STATION WHERE PIPELINE NO. 184A CROSSES COUNTY ROAD "P". |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2883.806 | 5817.8016 | NATURAL GAS LIQUID | 2 | 0 | 0 | NO | NO | 2 | 0.15 | 35000 | WELDED |  | 1440 | 1350 | YES | 8 | 1900 | 5 | 88 | EXTERNAL | Null | YES | OTHER | SEE COMMENTS | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD FLINT | 7195204350 | INVESTIGATION OF A HYDROCARBON ODOR BY A CIG EMPLOYEE LEAD TO THE CASING VENT AT COUNTY ROAD "P". VAPORTS WERE DISCOVERED TO BE COMING OUT OF THE SOUTH CASING VENT ON THE LIQUID PIPELINE NO. 184A. GATE VALVE NUMBER 1 ON THE PIPELINE WAS IMMEDIATELY CLOSED AND THE PUMP SHUT DOWN. DUE TO THE WIND SPEED, TIMEOF DAY, AND SMALL VOLUME OF VAPORS VENTING FROM THE 2" PIPELINE, FURTHER ACTIONS TO PROTECT THE PUBLIC WERE DETERMINED NOT TO BE NECESSARY. THE PIPE WAS DEPRESSURIZED, REMOVED FROM ITS CASING, AND INSPECTED. THE CAUSE OF THE LEAK WAS EXTERNAL CORROSION OF THE PIPELINE AT A POINT 13 FEET FROM THE NORTH END OF THE 81-FOOT-LONG CASING. ATMOSPHERIC; INSIDE A CASING.
2017-09-29 08:50 | YES | YES | 19960170 | 1996-11-06 | 26304 | UNOCAL PIPELINE CO - WESTERN REGION | NO | 1996-10-23 | 500 | CA | SHANDON |  | NO |  | NO | NEAR THE INTERSECTION OF HIGHWAY 46 AND 41, APPROX. 1/2 MILES FROM TOWN OF SHANDON IN SAN LUIS OBISPO COUNTY CA. |  | LINE PIPE | PIPE |  | 1951 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | NOT GIVEN | 1 | 0 | 0 | NO | NO | 8 | 0.25 | 2430 | NO DATA |  | 1000 | 100 | YES | 4 | 1300 |  | 94 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PATRICK ARMSTRONG | 8055477200 | A 20 MILES PIPELINE SEGMENT BETWEEN CRESTON AND SHANDON STATIONS WAS BEING PURGED WITH NITROGEN SO THAT A PIPELINE REPLACEMENT SECTION COULD BE TIED-IN. DURING THE BLOWDOWN OPERATION OF THE NITROGEN, SOME ODOROUS HYDROCARBON VAPORS WERE RELEASED WITH THE NITROGEN. THE VAPORS CONTAINED ODOR BEARING SULFUR COMPOUNDS. THE ODORS WERE DETECTED BY A NEARBY RESIDENT. THE RESIDENT SUFFEREDA RESPIRATORY ATTACK AND CALLED THE FIRE DEPARTMENT. THE FIRE DEPARTMENT CALLED FOR AN AMBULANCE. THE PARAMEDICS ADMINISTERED OXYGEN FOR 30 MINUTES TO THE RESIDENT. RELEASE OF ODORS DURING PIPELINE PURGING OPERATION.
2017-09-29 08:50 | YES | NO | 19960171 | 1996-11-12 | 15774 | PORTAL PIPELINE CO | YES | 1996-10-26 | 1035 | ND | WILLIAMS |  | NO |  | NO | PORTAL PIPE LINE COMPANY'S BEAVER LODGE STATION LOCATED 3 MILES SOUTH OF COUNTY HIGHWAY 40 AND US HIGHWAY 2 NEAR TIOGA, ND |  | PUMPING STATION | SCRAPER TRAP |  | 1983 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 70 | 60 | NO | NO | 8 | 0.16 | 1881 | NO DATA |  | 1354 | 200 | YES | 6 | 1833 | 11 | 83 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD SANDAHL | 2187250102 | ON OCTOBER 25, 1996, FIELD PERSONNEL REMOVED CLEANING PIG FROM RECEIVER TRAP. IT IS BELIEVED A SMALL AMOUNT OF PARAFFIN MAY HAVE PREVENTED THE GASKET FROMSEALING PROPERLY. THE TRAP DOOR DID NOT LEAK WHEN THE RECEIVER BARREL FILLEDWITH CRUDE AFTER CLOSING. LATER IN THE DAY, WHEN UPSTREAM PUMP WERE STARTED AND LINE PRESSURE ON THE TRAP INCREASED TO NORMAL CONDITIONS, THE TRAP LID BEGAN TO LEAK. FIELD PERSONNEL HAD LEFT THE STATION AND THE OPERATOR WAS NOT ABLE TO DISCERN A PROBLEM ON THEIR SCADA TERMINAL. LEAKING GASKET ON TRAP CLOSURE DOOR.
2017-09-29 08:50 | YES | NO | 19960172 | 1996-11-15 | 2552 | COLONIAL PIPELINE CO | YES | 1996-08-05 | 900 | NC | GUILFORD | GREENSBORO | NO |  | NO | SEE ATTACHED MAP |  | TANK FARM | PIPE | THREADED COUPLING | 1963 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 129771.2717 | 261801.0718 | FUEL OIL | 3 | 18 | 18 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JA COX | 4048412296 | AT APPROX 9:00AM ON 8/5/96, A GREENSBORO JUNCTION TANK FARM EMPLOYEE DISCOVERED STAINED GRAVEL IN THE AREA OF THE OIL MANIFOLD. MAINTENANCE PERSONNEL WERECALLED IN AND BEGAN EXCAVATION TO DETERMINE THE SOURCE OF RELEASE AND REMOVAL OF FUEL OIL AND CONTAMINATED SOIL. ENVIRONMENTAL PERSONNEL BEGAN INVESTIGATING THE EXTENT OF THE CONTAMINATION. ON 8/20/96, MAINTENANCE PERSONNEL LOCATED PRODUCT ORGINATING FROM THE 1 1/2-INCH SUN PRESSURE RELIEF AND DRAIN LINE LOCATED IN THE VICINITY OF THE NO.02 LINE HEADER AND THE TANK LINE FOR TANK NO.878. THE 1 1/2-INCH LINE WAS BROKEN AT A THREADED COUPLING. THE COUPLING WASREMOVED AND FLEXIBLE CONNECTOR WAS INSTALLED AS A TEMPORARY REPAIR UNTIL SUCH A TIME AS THE AFFECTED DRAIN LINE CAN BE REPLACED. NOTIFICATION WAS MADE TOTHE NORTH CAROLINA DEPARTMENT OF HEALTH, ENVIRONMENT AND NATURAL RESOURCES ON 8/20/96. AFTER IT WAS DETERMINED THAT THE COST ESTIMATE WOULD EXCEED THE DEPARTMENT OF TRANSPORTATION'S REPORTING REQUIREMENTS, THE INCIDENT WAS REPORTED TELEPHONICALLY TO THE NATIONAL RESPONSE CENTER ON OCTOBER 14, 1996, (REPORTNO. 364296)
2017-09-29 08:50 | YES | NO | 19960173 | 1996-11-19 | 18273 | SHELL PIPELINE CORP | YES | 1996-06-17 | 1100 | IL | MARION |  | NO |  | NO | CAPLINE 40" PIPELINE SYSTEM - PATOKA STATION. |  | TANK FARM | WELDING FITTING |  | 1968 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 66285 | 47788.2708 | 96408.2447 | CRUDE OIL | 1 | 50 | 50 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | INTERNAL | Null | YES | OTHER | STRAY CURRENT | NO DATA |  | Null | NO DATA |  | Null | Null | SH HANSSON | 7132411751 | REPORT IS BEING FILED DUE TO CLEAN-UP AND REPAIR COSTS EXCEEDING $50,000. AMOUNT OF OIL SPILLED WAS APPROX. 42 BARRELS. RELEASE OCCURRED IN NECK OF 36-INCH 150# RAISED WELD NECK FLANGE ON TANK. OIL WAS CONTAINED WITHIN THE TANK DIKE AREA.
2017-09-29 08:50 | YES | NO | 19960174 | 1996-11-26 | 1734 | BRIDGELINE GAS DISTRIBUTION CO | NO | 1996-10-29 | 915 | LA | ST CHARLES | MONTZ | NO |  | NO | REMOTE SWAMPY AREA 1 MILE NORTH OF US HWY 61 AND 500 YDS WEST OF BONNIE CARRIE CORP OF ENGRS FLOOD SPILLWAY T-11S, R-8E, S-42 NEAR MONTZ LA. |  | LINE PIPE | PIPE |  | 1966 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 79000 | 56955.1693 | 114901.5815 | L. P. G. | 2 | 0 | 0 | NO | NO | 6 | 0.25 | 35000 | WELDED |  | 1440 | 650 | YES | 8 | 1825 | 0 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | ONE CALL |  | NO | NO | AF GILES | 5045951886 | ON 10/29/96, THE PIPELINE PATROL PILOT REPORTED A LEAK IN THE SAME VICINITY AS THE PREVIOUS LEAK IN SEPTEMBER, 1996. BRIDGLINE PERSONNEL WERE DISPATCHED AND CONFIRMED THAT THE LEAK WAS AT THE SAME LOCATION. IMMEDIATELY FIELD PERSONNEL SWITCHED THE FLOW OF PROPANE TO THE BUTANE PIPELINE AND SHUT-N THE PROPANE PIPELINE. THE PRODUCT IN THE PROPANE PIPELINE WAS PIGGED TO PARADIS STORAGE. THE PROCEDURE WAS ESTABLISHED IN SEPTEMBER BECAUSE OF THE FIRST LEAK. BY DOING THIS, IT ALLOWED US TO KEEP ALL CUSTOMERS ON-LINE. DIVERS WERE SENT DOWNAND VERIFIED THAT THE CLAMP INSTALLED IN SEPTEMBER WAS LEAKING AROUND THE SEALS. WITH THE INFORMATION, A DECISION WAS MADE TO PULL THE CLAMP AND WELD TAFULL ENCIRCLEMENT SADDLE FOR A PERMANENT REPAIR. AT THE FIRST LEAK, THE AREAGAVE NO CONTINOUS LEL HYDROCARBON READINGS. AT NO TIME WAS ANY OF THIS ACTIVITY A SAFETY RELATED CONDITION BECAUSE OF THE LOCATION AND SIZE OF THE LEAK. IN THE PROCESS OF REMOVING THE PRODUCT FROM THE PROPANE PIPELINE, WE NOTICED SOME LEAKING VALVES. WE TOOK THIS OPPORTUNITY TO CHANGE OUT THESE VALVES. ON 11/2/96 THE LINE WAS REPAIRED. WE USED THE PROPANE PRODUCT WITH 2 PIGS IN FRONT OF IT TO DE-AIR THE PIPELINE AND PRESSURE UP AT THE SAME TIME. ON 11/96 THE PROPANE PIPELINE WAS PUT BACK INTO SERVICE. ALL OF THE REPAIRS OF BOTH THE SPTEMBER AND OCTOBER LEAKS WERE PERFORMED IN ACCORDANCE WITH THE REGULATORY AGENCIES INVOLVED. IN FACT MR. DANA ARABIE, THE DOT AUDITOR ON THE LINE, WAS INVOLVED IN FIELD ACTIVITIES ON BOTH REPAIRS. THE SEPT LEAK REPAIR COST APPROX$40,000 AND THE LEAK REPAIR ON 10/29 COST APPROX $39,000. BECAUSE OF BOTH THE SEPT AND OCT LEAK BEING THE SAME SMALL HOLE IN THE PIPE, THE COMBINED REPAIR COST OF $78,989 MAKE THIS A REPORTABLE INCIDENT.
2017-09-29 08:50 | YES | NO | 19960175 | 1996-11-25 | 30900 | PROMIX,L.L.C. | YES | 1996-10-26 | 1630 | LA | ASSUMPTION | BELLE ROSE | NO |  | NO | 1/2 MILE SOUTHWEST OF UNICAR UNDERGROUND STORAGE IN BELLE ROSE, LA |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 360475.7548 | 727225.1993 | NOT GIVEN | 1 | 5900 | 0 | NO | NO | 10.75 | 0.25 | 46000 | WELDED |  | 1440 | 500 | YES | 24 | 1820 | 10 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | KEN DAYTON | 5043695002 | CONTRACTOR DIGGING NEAR A PROMIX PIPELINE STRUCK THE PIPELINE, CAUSING ABREAK IN THE PIPE AND RELEASING THE DMI PRODUCT.
2017-09-29 08:50 | YES | NO | 19960176 | 1996-11-26 | 2731 | CHEVRON PIPELINE CO | YES | 1996-10-28 | 700 | TX | FREESTONE | WORTHAM | NO |  | NO | 3 MILES EAST OF WORTHAM TEXAS ON HWY 27. THE CHEVRON PIPELINE CO. WORTHAM TANK FARM. |  | TANK FARM | PIPE |  | 1987 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2162.8545 | 4363.3512 | CRUDE OIL | 1 | 75 | 75 | NO | NO | 4 | 0.25 | 24000 | WELDED |  | 85 | 30 | NO | 0 | 0 |  |  | INTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM JOHNSON | 2813637156 | THE SPILL WAS FROM A DRAIN LINE OFF A 24" SUCTION/FILL LINE. THE DRAIN LINE IS OFF THE BOTTOM OF THE 24" LINE WHICH ALLOWS WATER TO COLLECT IN THE DRAIN LINE CAUSING CORROSION. THE SPILL WAS ORIGINALLY REPORTED AS 300 BBLS. THE FINAL TOTAL OF THE SPILL WAS 250, WITH 175 BBLS REMAINING IN A CONCRETE CONTAINMENT AREA AND 75 BBLS SPILLED TO THE SOIL. THE DRAINS WILL BE MODIFIED AND REPLACED TO MINIMIZE FUTURE CORROSION.
2017-09-29 08:50 | YES | NO | 19960177 | 1996-11-21 | 443 | AMOCO PIPELINE CO | YES | 1996-10-17 | 1400 | IN | LAKE | HAMMOND | NO |  | NO | INTERSECTION OF INDIANAPOLIS BLVD AND 165TH STREET |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1441903.0192 | 2908900.7973 | TRANSMIX (PART. REFINED PETRO) | 2 | 1250 | 370 | NO | NO | 12 | 0.28 | 1111 | WELDED |  | 720 | 640 | NO | 0 | 0 |  |  | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GW WHITE | 6309906105 | ON 10/17/96 AT 1400HRS, THE SMELL OF POSSIBLE HYDROCARBONIC VAPORS IN HAMMOND, INDIANA WAS REPORTED TO AMOCO PIPELINE COMPANY. APL HAD SEVERAL PIPELINES IN THE AREA AND IMMEDIATELY BEGAN INVESTIGATING THE SOURCE OF ODORS. AS A PARTOF THIS EFFORT THE LINES WERE SHUT DOWN AND THEIR INTEGRITY TESTED. THE CITYOF HAMMOND, INDIANA DEPT OF ENVIRON MGMT, AND NATL RESPONSE CENTER WERE NOTIFIED AT 1400, 1550, AND 1555 HRS RESPECTIVELY AS WE SEARCHED FOR THE SOURCE CONTAMINATION. THE SOURCE WAS FOUND TO BE AN APL LINE ON THE WEST SIDE OF INDIANAPOLIS BLVD AND 165TH STREET IN HAMMOND. APL EMPLOYEES BEGAN EXCAVATION ANDREPAIR OF THE PIPELINE EARLY IN THE MORNING OF 10/18/96. EXTENSIVE REMEDIATION EFFORTS WERE ALSO INITIATED AT THIS TIME. THE LINE WAS REPAIRED AND RETURNED TO SERVICE ON 10/22/96. REMEDIATION WORK AT THE SITE IS STILL IN PROGRESS.AMOCO PIPELINE IS COORDINATING REMEDIATION OF THE SITE WITH THE HAMMOND DEPTOF ENVIRONMENTAL MGMT AND THE INDIANA DEPT OF ENVIRONMENTAL MGMT.SUPPLEMENTAL REPORT 12/17/1996 CHANGED TOTAL BARRELS LOST AND RECOVERED FROM500 LOST TO 300 RECOVERED TO 1250 LOST TO 370 RECOVERED, RESPECTIVELY.
2017-09-29 08:50 | YES | NO | 19960178 | 1996-11-20 | 4492 | ENTERPRISE PRODUCTS CO | YES | 1996-10-19 | 1545 | MS | PERRY |  | NO |  | NO | HICKORY GROVE CHURCH RD, SECTION 21 T4N, R10W PERRY CNTY, MISSISSIPPI LOCATION WAS APPROX 600' EAST OF ROAD. THERE WAS A HOUSE APPROX 200' NORTHEAST. |  | LINE PIPE | OTHER | NONE SPECIFIED | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 360475.7548 | 727225.1993 | L. P. G. | 2 | 2000 | 0 | YES | YES | 6.63 | 0.16 | 52000 | WELDED |  | 1440 | 500 | YES | 24 | 2160 | 0 | 79 | NO DATA | Null | YES | OTHER | NONE SPECIFIED | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | PARIS WALTMAN | 3346758562 | ON THE AFTERNOON OF 10/19/96, A RELATIVE OF A LANDOWNER IN THE BUCK CREEK AREA OF PERRY COUNTY, MISSISSIPPI, WAS WORKING WITH A LARGE FRONT-END LOADER ONTHIS OWNER'S PROPERY. HE BEGAN REMOVING DIRT FROM A PIPELINE RIGHT-OF-WAY AND STRUCK A BURIED PIPELINE (ENTERPRISE PRODUCTS COMPANY'S 6" LPG PIPELINE) WITH THE LOADER. THE PIPELINE RUPTURED AND RELEASED PRODUCT. ENTERPRISE WAS NOTIFIED OF THE RUPTURE, AND ENTERPRISE EMPLOYEES CLOSED BLOCK VALVES TO ISOLATETHE PORTION OF THE LINE WHERE THE DAMAGE OCCURRED. THE PERRY COUNTY SHERIFF EVACUATED RESIDENCES IN THE AREA, BECAUSE A VAPOR CLOUD REACHED AN IGNITION SOURCE, AND AN EXPLOSION/FIRE RESULTED. THE FIRE WAS ALLOWED TO BURN UNTIL ALLOF THE RELEASED PRODUCT HAD BEEN CONSUMED AND PRODUCT REMAINING IN THE PIPELINE WAS DISPLACED. THE INCIDENT RESULTED IN PROPERY DAMAGE TO THREE RESIDENCES BUT NO BODILY INJURIES OF FATALITIES. REPAIRS WERE MADE, AND THE PIPELINE WAS RETURNED TO SERVICE ON 10/22.
2017-09-29 08:50 | YES | NO | 19960179 | 1996-11-22 | 300 | ALL AMERICAN PIPELINE CO | NO | 1996-10-21 | 635 | CA | KERN | MARICOPA | NO |  | NO | 2311 BASIC SCHOOL RD APPROX 1/4 MILE SOUTH OF HWY 166. |  | TANK FARM | TANK |  | 1988 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18023.7877 | 36361.26 | CRUDE OIL | 1 | 86 | 75 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JORDAN JANAK | 8056645345 | THIS INCIDENT INVOLVED THE OVERFLOW OF A CRUDE OIL PIPELINE BREAKOUT STORAGETANK. A MECHICAL FAILURE ON THE VAREC TANK LEVEL INDICATOR CAUSED THE LEVEL INDICATION IN THE CONTROL ROOM TO BE LESS THAN THE ACTUAL TANK LEVEL. THE TANK IS EQUIPPED WITH A HI ALARM AND A HI HI ALARM. THE HI ALARM IS ACTUATED FROM THE VAREC INPUT AND HAS A VARIABLE SETPOINT CONTROLLED BY THE OPERATOR FOR OPERATIONAL PURPOSED. TH HI HI ALARM IS ACTUATED MECHANICALLY AT AN ESTABLISHED TANK LEVEL. THE HI ALARM SHOULD ACTIVATE PRIOR TO THE HI HI ALARM AS THE TANK WAS BEING FILLED, THE FAULTY VAREC CAUSED THE HI HI ALARM TO ACTUATE PRIOR TO THE HI ALARM. THE HI HI ALARM FOR THIS TANK WAS INCORRECTLY DISPLAYED ONTHE CONTROL PANEL AS A HI ALARM INSTEAD OF A HI HI ALARM. ALERTED BY WHAT THE OPERATOR OBSERVED AS A HI ALARM INDICATING THAT THE TANK WAS APPROACHING THE PREDETERMINED FILL LEVEL, HE CONTINUED FILLING TO THE DESIRED LEVEL BASED ON THE VAREC INDICATION. THE TANK BEGAN OVERFLOWING ABOUT THE SAME TIME THE OPERATOR OBSERVED THAT THE TANK HAD REACHED THE DESIRED LEVEL AND STOPPED FLOW INTO THE TANK. THE PRIMARY CAUSES OF THIS INCIDENT WERE: 1) A FAULTY TANK LEVEL INDICATOR PRESENTING THE CONTROL ROOM OPERATOR WITH AN INACCURATE TANK LEVEL INDICATION AND CAUSING THE HI ALARM TO ACTIVATE AT AN INCORRECT TANK LEVELAND 2) THE INCORRECT DISPLAY OF A TANK HI HI ALARM AS A HI LEVEL ALARM ON THE OPERATOR'S CONTROL PANEL. THE INCORRECT ALARM DISPLAY WAS CAUSED BY A PROGRAMMING ERROR WHICH PRIOR TO THE TIME OF THIS INCIDENT HAD NOT BEEN DETECTED. CAUSE OF ACCIDENT: MECHANICAL FAILURE OF VAREC TANK LEVEL INDICATOR AND MISLEADING AND IMPROPER HIGH TANK LEVEL ALARM DISPLAY ON CONTROL PANEL.
2017-09-29 08:50 | YES | NO | 19960180 | 1996-12-06 | 2552 | COLONIAL PIPELINE CO | NO | 1996-11-05 | 937 | TN | RUTHERFORD | MURFREESBORO | NO |  | NO | SEE ATTACHED |  | LINE PIPE | PIPE |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 6987365 | 5037551.3449 | 10162775.8097 | DIESEL FUEL | 3 | 2017 | 924 | NO | NO | 8 | 0.19 | 1830 | WELDED |  | 1318 | 1820 | YES | 24 | 1649 | 12 | 1963 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JA COX | 4048412296 | IT IS ESTIMATED THAT 2017 BBLS. OF LOW SULFUR DIESEL FUEL SPILLED FROM THE PIPELINE, MOST OF IT FLOWING THROUGH A SINKHOLE INTO THE SUBSURFACE WATER SYSTEM. PROTECTIVE BOMBING WAS DEPLOYED AT FIVE SITES ALONG THE NEARBY MIDDLE FORK OF THE STONE RIVER AND LONG CREEK. THERE HAS BEEN NO INDICATION OF IMPACT TO THE RIVERS OF CREEKS. THE PIPE RUPTURE WAS LOCATED IN A 65 FOOT PIECE OF 85/8 INCH O.D., .188 WT., API5LX-Z42. THE ENTIRE JOINT WAS REPLACED WITH NEW .322 INCH WT.,API5LX-X42 STEEL PIPE. A SECTION OF THE FAILED JOINT CONTAININGTHE RUPTURE WAS SHIPPED TO A METALLURGICAL LABORATORY FOR FAILURE ANALYSIS. THE PIPELINE WAS RESTARTED WITH THE U.S. OFFICE OF PIPELINE SAFETY APPROVAL AT 1437 ON NOVEMBER 6TH, AT A REDUCED LINE PRESSURE. A REVIEW OF THE EVENTS RELATING TO THE FAILURE INDICATED THAT THE CONTROLLER ATTEMPTED UNSUCESSFULLY TO OPEN A CLOSED BLOCK VALVE AT MURFREESBORO. THIS RESULTED IN OVER PRESSURIZATION OF THE LINE AND THE SUBSEQUENT RUPTURE THAT WAS LATER ESTIMATED TO HAVE OCCURED AT 0937 EST. THE ENTIRE INCIDENT IS STILL UNDER INVESTIGATION. A WATER WELL SAMPLING AND ANALYSIS PROGRAM WAS ESTABLISHED TO ENSURE THAT THE RESIDENTS NEAR THE LEAK SITE WOULD NOT BE EXPOSED TO A HEALTH THREAT FROM POTENTIALLY IMPACTED WATER WELLS. AS A PRECAUTION, BOTTLED WATER HAS BEEN INSTALLED IN AND AROUND THE LEAK SITE TO IDENTIFY THE EXTENT OF SUBSURFACE FREE PRODUCT MIGRATION. AS OF DEC.4, 1996, APPROX 493 BBLS. OF PRODUCT HAVE BEEN RECOVEREDFROM THE WELLS. PRODUCT RECOVERY AND SOIL REMEDIATION ACTIVITY CONTINUES IN COORDINATION WITH GOVERNMENT AGENCIES. PLEASE REFER TO REPORT FOR FURTHER INFO.
2017-09-29 08:50 | YES | NO | 19960181 | 1996-12-03 | 13131 | CONOCO INC | YES | 1996-10-26 | 1503 | OK | TULSA | BROKEN ARROW | NO |  | NO | SW/4 SECTION 8, TOWNSHIP 18N, RANGE 14E,TULSA COUNTY, OKLAHOMA BETWEEN GARNETT AND 129TH STREET, JUST NORTH OF 81ST STREET IN BROKEN ARROW, OK MP 94.8 WR NO.1 |  | LINE PIPE | PIPE |  | 1930 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 21628.5453 | 43633.512 | DIESEL FUEL | 1 | 600 | 586 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 900 | 169 | YES | 8 | 1130 | 8 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL | SEE COMMENTS | Null | Null | VANCE WEBB | 4056764845 | ON OCTOBER 26, 1996, AT 03:15 HRS. CONOCO PIPE LINE'S(CPL'S)LINE NO.1 OF THEWOOD RIVER SYSTEM WAS RUPTURED BY AN EARTH MOVER/SCRAPER OWNED AND OPERATED BY STRAIGHT LINE CONSTRUCTION CO. THE SCRAPER PUNCTURED THE LINE WHILE UNLAWFULLY REMOVING COVER FROM OVER THE PIPELINE. THE LINE WAS WELL MARKED AND THE SCRAPER OPERATER INDICATED THAT HE WAS AWARE OF THE PIPELINES LOCATION. UPON PUNCTURING THE LINE, MR. TRACY KELLY, THE SCRAPER OPERATOR, NOTIFIED CPL'S OIL MOVEMENTS GROUP IN HOUSTON OF THE INCIDENT BY TELEPHONE, USING THE 1-800 EMERGENCY CONTACT PHONE NUMBER. THE LINE WAS IMMEDIATELY ISOLATED AND THE OIL SPILL FACILITY RESPONSE PLAN IMPLEMENTED. BECAUSE OF THE CLOSE PROXIMITY OF THE INCIDENT TO ONE OF CPL'S MANNED FACILITIES, THE RESPONSE TIME TO REACH THE LOCATION WAS SHORT. EARTHEN DIKES WERE CONSTRUCTED TO CONTAIN THE DIESEL FUELIN THE IMMEDIATE AREA AND RECOVERY OPERATIONS WERE INIATED. AFTER THE RELEASE PRODUCT WAS RECOVERED, AND CONDITIONS WERE WITHIN ALLOWABLE PARAMETERS, REPAIRS WERE MADE TO THE PIPELINE BY REPLACING THE DAMAGED SECTION OF LINE WITH APPROX 23 FEET OF NEW PIPE. UNDER THE DIRECTION OF MR. JOHN ZIMMER OF THE TULSA COUNTY HEALTH DEPT. ENVIRONMENTAL DIV., AFFECTED SOIL WAS TRANSPORTED TO CPL'S GLENPOOL FACILITY AND PLACED INSIDE A CONTAINMENT AREA ON LINER MATERIAL. THE MATERIAL WILL BE SAMPLED AND DISPOSED OF AT AN APPROVED LANDFILL. PART J - ANNUAL CONTRACTOR/EXCAVATOR EDUCATION PROGRAM.
2017-09-29 08:50 | YES | NO | 19960183 | 1996-12-16 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1996-10-22 | 1245 | TX | WHARTON | BAY CITY | NO |  | NO | 6 MI. NORTH OF BAY CITY; EAST SIDE OF COLORADO RIVER. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 21628.5453 | 43633.512 | L. P. G. | 2 | 1352 | 0 | NO | NO | 8.63 | 0.32 | 25000 | WELDED |  | 750 | 450 | YES | 24 | 924 | 6 | 74 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PERMANENT LINE MARKERS | NO | NO | WD PARTLOW | 7138777370 | A FARMER STRUCK THE HOUSTON 8" LPG PIPELINE SYSTEM WHILE PLOWING. THE PROPERTY OWNER WAS FULLY AWARE OF THE PIPELINE EXISTENCE AND WAS MARKED WITH PERMANENT LINE MARKERS. LINE SECTION WAS BLOCKED IN, PRODUCT WAS EMPTIED OUT OF LINE THROUGH TEMPORARY FLARE @ BAY CITY STATION AND SPLIT SLEEVE CLAMP WAS INSTALLED. PART G - LINE SEGMENT WAS EMPTIED BY TEMPORARY FLARE.
2017-09-29 08:50 | YES | NO | 19960184 | 1996-12-17 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1996-11-19 | 1102 | CA | KERN |  | NO |  | NO | APPROX 200' SOUTH OF HWY 46 AND HWY 33 JUNCTION AT BLACKWELLS CORNER, WEST SIDE OF HWY 33. |  | LINE PIPE | PIPE |  | 1982 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 1245 | 1045 | NO | NO | 20 | 0.28 | 0 | NO DATA |  | 1152 | 850 | YES | 8 | 1753 | 7 | 82 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD KELLEY | 8053282331 | PIPELINE RUPTURED DUE TO EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19960185 | 1996-12-16 | 19223 | SUN PIPELINE CORP | YES | 1996-11-16 | 1200 | PA | PHILADELPHIA | PHILADELPHIA | NO |  | NO | INCIDENT OCCURED ON THE GROUNDS OF THE POINT BREEZE PUMP STATION WHICH IS LOCATED AT 64TH AND PASSYUNK AVE., PHILADELPHIA, PA. |  | PUMPING STATION | OTHER | SUMP TANK | 1971 | INCORRECT OPERATION BY OPERATOR PERSONNEL | SEE COMMENTS | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 100 | 97 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALAN GILLIE | 2159773344 | ON NOVEMBER 16, 1996 JUST AFTER 12:00 A.M. A SUN PIPELINE OPERATOR DRAINED THE POINT BREEZE PROOVER LOOP INTO #4,#5,#6 SLOP TANKS. ONCE THIS WAS DONE, THE OPERATOR FAILED TO CLOSE THE INLET VALVE (S-31) TO #4,#5,#6 SLOP TANKS. WHEN THE OPERATOR REFILLED THE PROVER, THE INLET VALVE (S-31) ALLOWED PRODUCT TOFLOW INTO #4,#5,#6 SLOP TANKS WHICH EVENTUALLY OVERFILLED AND OVERFLOWED ONTO THE GROUND AND INTO AN OPEN DITCH. WE SUSPECT A PROVER DRAIN VALVE LEAK, BUT IF OPERATOR WOULD HAVE CLOSED BACK-UP VALVE, THIS WOULD HAVE PREVENTED THE RELEASE. THE INCIDENT INVESTIGATION IS ON-GOING.
2017-09-29 08:50 | YES | NO | 19960186 | 1996-12-16 | 10318 | KOCH REFINING CO | YES | 1996-11-10 | 1100 | WI | DANE | MCFARLAND | NO |  | NO | OUR FUEL TERMINAL AT 4505 TERMINAL DRIVE MCFARLAND, WI |  | TANK FARM | TANK |  | 1959 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 90118.9387 | 181806.2998 | GASOLINE | 1 | 350 | 180 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY GENEVICH | 6124381261 | OUR HI LEVEL AND HI HI LEVEL ALARMS ON THE TANK WERE UNINTENTIONALLY BYPASSED. THE ALARMS WERE RECEIVED INTO THE OFFICE, BUT DID NOT REACH OUR WICHITA CONTROL CENTER OR ACTIVATE A STATION LOCK OUT AS DESIGNED.
2017-09-29 08:50 | NO | NO | 19960187 | 1996-12-24 | 13131 | CONOCO INC | NO | 1996-12-12 | 1340 |  |  |  | YES | X=2496757.7 Y=101227.68 | NO | LEAK WAS LOCATED APPROX 900 FEET NORTH OF THE PLATFORM AT THE ABOVE COORDINATES. |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 25233.3028 | 50905.764 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 6 | 0.43 | 4565 | WELDED |  | 1440 | 360 | YES | 2 | 1260 | 8 | 77 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN WOMACK | 3182692400 | ON DEC. 12, 1996, AT 13:40 HRS, THE PLATFORM OPERATOR DISCOVERED A LEAK IN THE 6" OIL PIPELINE FROM WD 94-G TO WD 71-O SEGMENT #565. THE PIPELINE WAS SHUT-UP AND THE LEAK WAS STOPPED. THE DIVE BOAT AMERICAN TRIUMPH ARRIVED ON LOCATION ON DEC 13, 1996 AT APPROX 6:00 HRS. DIVERS INSPECTED THE PIPELINE AND DISCOVERED A PINHOLE LEAK IN THE PIPELINE LEAK IN THE PIPELINE APPROX 900' NORTH OF WD 94-G. THE M/V SOROLTA MARIE WAS ON LOCATION WITH A FAST RESPONSE UNIT(FRU) ON BOARD IN PREPARATION FOR SPILL CLEAN-UP IF NEEDED. DIVERS INSTALLEDA 6" PLIDCO PRESSURE CLAMP, (SERIAL #830715) WITH A DESIGN WORKING PRESSURE OF 1500PSI. UPON COMPLETION OF THE REPAIR, THE PIPELINE WAS PRESSURED TO 750 PSI FOR APPROX 30 MINUTES AND OBSERVED FOR LEAKAGE. DIVERS WERE THEN SENT DOWN TO INSPECT THE CLAMP AND NO LEAKAGE WAS OBSERVED. THE PIPELINE WAS RETURNED TO SERVICE ON DEC 13, 1996, AT 18:00 HRS.
2017-09-29 08:50 | YES | NO | 19960188 | 1996-12-26 | 15851 | PRIDE REFINING INC | NO | 1996-11-19 | 715 | TX | COMANCHE |  | NO |  | NO | GO EAST OF DELEON TX APPROX 5 MILES TO FM ROAD 1496 TURN SOUTH APPROX 5 MILES TO PRIDE PIPELINE COMYN STATION |  | LINE PIPE | PIPE |  | 1991 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 360.4758 | 727.2252 | CRUDE OIL | 1 | 200 | 0 | NO | NO | 4 | 0.24 | 35000 | WELDED |  | 275 | 50 | NO | 0 | 0 |  |  | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN MACON | 9156748231 | WHILE STATION OPERATOR WAS CHECKING STATION HE NOTICED A SPOT OF OIL. HE THEN CONTACTED HIS SUPERVISOR, HIS SUPERVISOR THEN DISPATCHED A CREW TO COMYN STATION TO DIG-OUT AND INVESTIGATE CAUSE OF SPILL. LINE WAS THEN ISOLATED AND ATEMPORARY CLAMP WAS PLACED ON LINE. PERMANENT REPAIRS ARE BEING SCHEDULED.
2017-09-29 08:50 | YES | NO | 19960189 | 1996-12-26 | 22855 | KOCH PIPELINE INC (EX WOOD RIVER PIPELINE CO) | YES | 1996-11-21 | 1309 | OK | WOODS | ALVA | NO |  | NO | 16 MILES SW OF ALVA, OK SW/4 SEC 11 T26N R16W WOODS COUNTY, OK |  | LINE PIPE | PIPE |  | 1970 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 11500 | 8290.9424 | 16726.1796 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 6 | 0.22 | 46000 | WELDED |  | 1440 | 970 | YES | 24 | 2029 | 9 | 70 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | JERRY ROGERS | 4053952377 | THIRD PARTY CONTRACTOR HIT PIPELINE WITH TRENCHING EQUIPMENT CAUSING DAMAGE TO PIPELINE.
2017-09-29 08:50 | YES | NO | 19960190 | 1996-12-23 | 19237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1996-11-21 | 1100 | MO | STODDARD |  | NO |  | NO | INTERSECTION OF STATE ROADS Y AND DD |  | LINE PIPE | OTHER | 1/2" TAP ON PIPELINE | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 51000 | 36768.527 | 74176.9703 | L. P. G. | 2 | 0 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | ERNEST HAGAN | 7137593845 | AT APPROX 1100 HRS CST, ON 11/21/96, A TEPPCO CONTRACT MAINTENANCE CREW, WORKING IN STODDARD COUNTY, MO, CAUSED AN INCIDENT ON TEPPCO'S 20" LINE P2. THEIR BACKHOE WAS PUSHING DIRT FROM THE TOP OF THE PIPELINE WHEN THE BACKHOE HIT AND BROKE THE THREADED AREA ON A 1/2" PIPE NIPPLE. THE CONTRACT CREW IMMEDIATELY NOTIFIED OPERATIONS PERSONNEL. TEPPCO'S EMERGENCY PLAN WAS IMMEDIATELY INITIATED, THE PIPELINE SYSTEM WAS SHUT DOWN, AND THE SECTION CONTAINING THE LEAK WAS ISOLATED. LOCAL AUTHORITIES WERE NOTIFIED AND ASSISTED IN COORDINATINGAN EVACUATION OF THE IMMEDIATE AREA AS A PRECAUTIONARY MEASURE. STOPPLES WERE SET, PRODUCT WAS FLARED AND THE NECESSARY REPAIRS WERE COMPLETED. THE PIPELINE WAS RETURNED TO SERVICE 11/21/96.
2017-09-29 08:50 | YES | NO | 19960191 | 1996-12-23 | 18718 | SUN PIPELINE CO | NO | 1996-12-03 | 1530 | OK | PAYNE | CUSHING | NO |  | NO | FROM THE INTERSECTION ON HWY. 33 & LINWOOD AVENUE IN CUSHION, OK. NORTH ON LINWOOD AVENUE APPROX 4 BLOCKS EAST INTO |  | TANK FARM | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 100 | 100 | NO | NO | 8 | 0.22 | 24000 | WELDED |  | 70 | 70 | NO | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | EW NASALROAD | 9183529442 | THIRD PARTY (WESTERN ENVIRONMENTAL SERVICES) WERE DEMOLISHING IDLED TANKS. CONTRACTOR WAS WORKING OUTSIDE OF AREA OF CLEARANCE WHEN THE 8" LINE WAS RUPTURED BY HIS EQUIPMENT. CONTRACTOR NOTIFIED SUN PIPELINE OFFICE AND CONTAINED SPILL WITHIN A SMALL DIAMETER AREA. OIL WAS PICKED UP BY VACUUM TRUCKS AND RETURNED TO THE SYSTEM. LINE WAS PURGED AND CAPPED.
2017-09-29 08:50 | YES | NO | 19960192 | 1996-12-30 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1996-09-28 | 1220 | TX | MILAM |  | NO |  | NO | APPROX 8 MILES W/SW OF CALVERT, TX, 0.5 MILES, WEST OF BRAZOS RIVER (0.4 MILES WEST OF FM-979 RD) |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 42000 | 30279.9634 | 61086.9167 | CRUDE OIL | 1 | 210 | 160 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1050 | 350 | YES | 8 | 1279 | 9 | 88 | EXTERNAL | Null | YES | OTHER | SEE COMMENTS | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED | 9152639256 | AT 0935AM, 09/28/96, A MRS. LOUIS ARBAN (409-364-2170) CALLED FINA'S BIG SPRING, TX, CONTROL CENTER, REPORTING A VERY STRON ODOR OF CRUDE OIL ON FM-979. THE CONTROL CENTER NOTIFIED THE PIPELINE'S MAINTENANCE PERSONNEL, BASED IN BROWNWOOD, TX. FINA'S GANG LEADERMAN WAS ENROUTE TO THE AREA FROM BROWNWOOD AT 10:00 AM AT 10:10AM, A MR. LON DODD (817-697-1635) CALLED ON A MOBILE PHONE TO THE CONTROL CENTER, REPORTING A STRONG CRUDE OIL ODOR WEST OF FM-979, WEST OF THE BRAZOS RIVER BRIDGE. AT 10:15 AM, THE MILAM COUNTY SHERIFF'S OFFICE CALLED THE CONTROL CENTER, ALSO REPORTING THE ODOR AND ADVISING THAT THEY WOULDBE CHECKING IT OUT. ONE ADDITIONAL CALL CAME IN TO THE CONTROL CENTER FROM AMR. TOMMY CHAMERLAND, AGAIN REPORTING THE ODOR, AT 11:10 AM. AT 12:20PM, THEFIRST FINA REPRESENTATIVE WAS ON-SCENE, FOLLOWED BY THE GANG LEADERMAN AT 12:30, BOTH HAVING SEEN AND REPORTED THE SOURCE OF THE LEAK. AT 12:50PM, THE PIPELINE PATROL PILOT REPORTED IN, ADVISING THAT HE HAD TAKEN PICTURES OF THE LEAK. BY 5:55PM, THE LEAK SITE WAS BLOCKED-IN BY CLOSURE OF VALVES. THE PIPELINE HAD BEEN SHUT-DOWN BETWEEN 11:00 - 11:15AM. THE RECOVERY OF THE OIL WAS COMPLETED BY THE END OF THE DAY, OCTOBER 1ST. FIVE HUNDRED FEET (500') OF PIPE WAS REPLACED AND 2,000' OF PIPE WAS RECONDITIONED. SUCH WORK HAVING BEEN COMPLETED OCT. 8, 1996. PREVIOUS RECONDITIONING WORK HAD BEEN DONE IMPROPERLY AS TO CLEANING AND WRAPPING PIPE. COATING DISBONDMENT/SLOUGHING OF SCALE. COATING WAS DISBONDED, CAUSING CATHODIC PROTECTION SHIELDING AND SLOUGHING OF SCALE: IMPROPER PREVIOUS RECONDITIONING WORK HAD CAUSED PROBLEM. TOTAL PROPERTY DAMAGE (INCL. REPLACEMENT AND RECONDITIONING OF PIPE).
2017-09-29 08:50 | YES | NO | 19960193 | 1996-12-30 | 22610 | WILLIAMS PIPELINE CO | YES | 1996-11-21 | 11 | KS | WYANDOTTE | KANSAS CITY | NO |  | NO | LOCATED IN THE SE 1/4 OF THE NE 1/4 OF SECTION 34 IN TOWNSHIP 10S, RANGE 25E AT 401 EAST DONOVAN ROAD IN WYANDOTTE COUNTY, KS |  | TANK FARM | OTHER | NONE SPECIFIED | 1978 | OTHER | PUMP BEARING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 18023.7877 | 36361.26 | FUEL OIL | 3 | 1 | 1 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN BALL | 9185883850 | AT 00:11 HRS ON 11/21/96, THE MAINLINE PUMPING UNIT SHUT DOWN DUE TO LOW SUCTION. WHEN THE OPERATOR CHECKED FOR THE CAUSE, HE DISCOVERED THAT THE BOOSTERPUMP ON TANK 1506 SUPPLYING THE MAINLINE UNIT HAD CAUGHT ON FIRE. THE LOCAL FIRE DEPARTMENT WAS CONTACTED IMMEDIATELY. AT 00:17 HRS THE FIRE DEPARTMENT ARRIVED AT THE SITE AND EXTINGUISHED THE FIRE IN APROX 30 MINS. DUE TO THE DIRECTION OF THE WIND BLOWING THE FLAMES AWAY FROM THE TANK AND QUICK RESPONSE FROM THE FIRE DEPARTMENT, THE FIRE WAS ISOLATED DAMAGING ONLY THE BOOSTER PUMPAND MOTOR. AN INVESTIGATION AT THE SITE INDICATED ONLY ONE BARREL OF FUEL OIL WAS LOST, WHICH WAS CONSUMED IN THE FIRE. AN ANALYSIS WAS PERFORMED ON THE DAMAGED MOTOR AND PUMP WHICH CONCLUDED THAT THE FAILURE OCCURED DUE TO LACK OF THE PROPER AMOUNT OF GREASE IN THE MOTOR THRUST BEARING. THE MOTOR IS NOW BEING REBUILT TO INCLUDE A SELF-LUBRICATING THRUST BEARING WITH AN OIL RESERVOIR.
2017-09-29 08:50 | YES | NO | 19960194 | 1996-12-30 | 3012 | PRIDE TEXAS PLAINS, L.P. | NO | 1996-10-30 | 1030 | TX | KNOX |  | NO |  | NO | TAKE FM RD 222 WEST NW OF KNOX CITY, TX APPROX 6MI TO CATUS FARM SIGN TURN RIGHT APPROX 1 1/2MI TURN LEFT APPROX 3/4MI TO STOCK TANK FOLLOW TRACK TO LEAK SITE. |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 150 | 120 | NO | NO | 10.75 | 0.37 | 25000 | WELDED |  | 800 | 550 | YES | 8 | 0 | 6 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN MACON | 9156748231 | ON 10/30/96 OUR AIR PATROL PILOT SPOTTED A POSSIBLE SPILL AT APPROX 10:30AM.HE THEN CONTACTED PRIDE EMPLOYEE IN THE AREA TO VERIFY THE LEAK. UPON VERIFICATION THE LINE WAS SHUT DOWN AND CREWS WERE DISPATCHED TO CLAMP THE LINE. CLEAN-UP HAS BEGUN IN ACCORDANCE WITH STATE REGULATIONS. DOT #366128
2017-09-29 08:50 | YES | NO | 19960195 | 1997-01-24 | 3445 | DIXIE PIPELINE | NO | 1996-12-26 | 1550 | LA |  | POINTE COUPEE | NO |  | NO | THE LOCATION IS APPROXIMATELY 2 MILES EAST OF MARINGOUIN, LA FROM THE INTERSECTION OF STATE HIGHWAY 41 AND JACK TORRES RD | 371452 | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 270000 | 194656.9076 | 392701.6076 | PROPANE | 2 | 5356 | 0 | NO | NO | 0 | 0.219 | 52000 | WELDED |  | 1360 | 383 | YES | 8 | 1749 | 8 | 1991 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DAN S MULLER | 7703790419 | A TENANT WAS EXCAVATION TO BURY DEBRIS AND PUNCTURED THE PIPELINE. TENANT HAD NOT NOTIFIED ONE CALL SYSTEM OR OPERATOR.
2017-09-29 08:50 | YES | NO | 19970001 | 1997-01-10 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1996-11-14 | 1233 | TX | CORYELL |  | NO |  | NO | APPROX 12 MI SW OF GATESVILLE, TX; 1 MI SOUTH OF THE COMMUNITY OF KING, & APPROX 411' WEST OF FM-1783 AT KING RANCH RD |  | LINE PIPE | PIPE |  | 1928 | FAILED WELD | FAILED WELD | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 41000 | 29559.0119 | 59632.4663 | CRUDE OIL | 1 | 675 | 600 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1050 | 1179 | YES | 14 | 1400 | 9 | 88 | NO DATA | Null | Null | NO DATA | SEE COMMENTS | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED | 9152639256 | THE PIPELINE HAD BEEN INACTIVE FOR 10 DAYS (NOV. 4-14TH). THE STARTUP PROCEDURE WAS BEGUN AT 0810 ON 11/14. THE PIPELINE WAS ONLY VERY GRADUALLY BROUGHT UP TO A STEADY, REDUCED PRESSURE DUE TO ITS HAVING BEEN SHUT-DOWN FOR SO LONG. THIS PROCESS TOOK ABOUT 2.75 HRS. THE PIPELINE WAS THEN OPERATED AT THE REDUCED RATE FOR APPROX 1.5HRS. (TO 12:20HRS.) AT 1220 HRS. THE REMAINING BOOSTER STATIONS WERE REMOTELY STARTED FROM THE BIG SPRING (TX) CONTROL CENTER. WHEN THE LAST (EASTERN-MOST) STATION WAS STARED, ELECTRICAL OVERLOAD SHUT-DOWN DEVICES CAUSED THIS STATION TO SHUT-DOWN. THE CONTROL CENTER OPERATOR THEN HADTO MAKE ADJUSTMENTS AT OTHER STATIONS IN RESPONSE TO PRESSURE BUILD-UP AND SUBSEQUENT AUTOMATIC SHUT-DOWNS HAVING ACTIVATED AT SOME STATIONS. FROM THE TIME OF THE OCCURRENCE OF THE FIRST OVERLOAD, AND SUBSEQUENT SHUT-DOWN, TO THE INDICATION OF A HIGH DISCHARGE PRESSURE ALARM AT 1233HRS., COULD BE THE TIME OF THE OCCURRENCE OF THE RUPTURE, ALTHOUGH THAT WAS NOT KNOWN AT THAT TIME. FOLLOWING THAT EVENT, ONLY 3 STATIONS REMAINED "ON" ALONG WITH ONE PUMP AT THEEASTERN-MOST STATION. WITHIN 8 MINUTES, 3 STATION SHUT-DOWN AUTOMATICALLY ONLOW SUCTION PRESSURE (BY 1241 HRS). THE CONTROL CENTER OPERATOR, UNAWARE OF ANY LEAK AT THIS TIME, ATTEMPTED TO RESTART THE PIPELINE. AT 1245 HRS., THE CONTROL CENTER RECEIVED THE FIRST CALL, FROM THE GATESVILLE POLICE DEPT., REPORTING A PIPELINE LEAK. A CALL FROM A LOCAL PROPERTY-OWNER FOLLOWED AT 1250 HRS., WITH THE PIPELINE BEING SHUT-DOWN AND BLOCKED-IN BY 1252 HRS. TEST- PRESSURE AT EVANT (UPSTREAM STATION) WAS 1,115 PSI. CALCULATED PRESSURE, BASED ON UPSTREAM STATIONS SUCTION/DISCHARGE PRESSURES, AND CALCULATED FRICTION LOSS TO POINT OF LEAK. THE CAUSE IS CURRENTLY UNDER INVESTIGATION. HOWEVER, THE PIPE DID RUPTURE ALONG THE LONGITUDINAL SEAM, POSSIBLY INDICATING A DEFECT IN THEORIGINAL CONSTRUCTION OF THE PIPE. ACTUAL EXPENSES TO-DATE $32,937. PLUS: ESTIMATED DAMAGES PAYMENTS TO BE INCURRED: $8,000.
2017-09-29 08:50 | YES | NO | 19970002 | 1997-01-06 | 26103 | TEXAS EASTMAN CO | NO | 1996-12-04 | 1845 | TX | BRAZORIA |  | NO |  | NO | COUNTY RD 23 ABOUT 3.3 MILES EAST OF HWY. 36 AT VALVE STATION 31. |  | LINE PIPE | PIPE |  | 1961 | OTHER | VANDALISM-GUNSHOT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 79304.6661 | 159989.5439 | L. P. G. | 2 | 1500 | 0 | NO | NO | 6 | 0.22 | 46000 | WELDED |  | 1480 | 590 | YES | 24 | 2100 | 0 | 95 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RL HARRIS | 9032375180 | AT APPROX 6:45PM, 12/4/96, TEXAS EASTMAN(TEX) RECEIVED A PHONE CALL FROM A CITIZEN REGARDING A POSSIBLE RELEASE FROM A PIPELINE. THE INDIVIDUAL REPORTINGTHE POSSIBLE RELEASE WAS DRIVING A VEHICLE IN THE VICINITY OF VALVE STATION 31 ON TEX'S GULF COAST PIPELINE (GCPL) AT TIME OF THE OBSERVATION. VALVE STATION 31 IS LOCATED IN BRAZORIA COUNTY. AT THE TIME OF THE REPORT, THE 6" GCPL WAS NOT IN OPERATION AND WAS ISOLATED BY CLOSED VALVES FROM SUPPLIERS. AFTER RECEIVING THE REPORT OF A POSSIBLE RELEASE, TEX PERSONNEL AT LONGVIEW IMMEDIATELY CLOSED A REMOTE OPERATED VALVE (VS-22) NORTH OF THE LEAK SITE AND SHORTLY AFTER ALSO CLOSED REMOTE OPERATED VS-27. IN ADDITION, TEX IMMEDIATELY: (1) CONTACTED TEX SUPERVISION; (2) DISPATCHED PERSONNEL TO THE RELEASE SITE, INCLUDING TWO BENSON PIPELINE MAINTENANCE PERSONNEL FROM THE HOUSTON AREA AND ONETEX PIPELINE INSPECTOR FROM LONGVIEW, AND (3) CONTACTED THE WEST COLUMBIA FIRE DEPARTMENT BY TELEPHONE. TEX PERSONNEL CONTINUED TO EVALUATE AVAILABLE INFORMATION AND BY APPROX 8:15 P.M. HAD CONCLUDED THAT THE RELEASE WAS SIGNIFICANT AND INVOLVED THE TEX 6" GCPL. ADDITIONAL TEX PERSONNEL WERE THEN DISPATCHED TO THE RELEASE SITE. BY APPROX 8:30 PM, BENSON PIPELINE MAINTENANCE REPS COMPLETED ON-SITE INSPECTIONS OF THE PIPELINE VALVES IMMEDIATELY NORTH (VS-32) OF THE RELEASE AT VALVE STATION 31. THE BENSON REPS FOUND THAT BOTH VALVES, VS-30, AND VS-32, HAD CLOSED PRIOR TO ARRIVAL THROUGH AUTOMATIC ACTIVATION OF THE LOW PRESSURE SHUTDOWNS. TO REDUCE PIPELINE PRESSURE AT THE RELEASE SITE, FLARING WAS PROMPTLY ACTIVATED AT VALVE STATION 30. AS CONDITIONS IMPROVED ATTHE SITE, VISUAL INSPECTION CONFIRMED THAT VALVE STATION 31 HAD REMAINED IN THE OPEN POSITION, AND THAT THE RELEASE WAS ORIGINATING FROM A SMALL HOLE LOCATED ON THE WEST SIDE OF ABOVE GROUND PIPING A FEW FEET SOUTH OF VALVE 31. TOEXPEDITE TERMINATING THE RELEASE, TEX INSTALLED ADDITIONAL HIGH CAPACITY FLARING EQUIPMENT AT VS-30. TEX ALSO MADE ARRANGEMENTS FOR INSTALLATION OF A STOPPLE IN THE PIPELINE APPROX TWO MILES SOUTH OF THE RELEASE SITE IN ORDER TO REDUCE THE LENGTH OF PIPELINE REQUIRED TO BE FLARED. BY 11:00PM, 12/06, THE CONTROLLED FLARING PROCESS HAD SUBSTANTIALLY REDUCED THE RATE OF RELEASE AT VS-31. TEX REPS THEN MANUALLY CLOSED VS-31 AND APPLIED A CLAMP OVER THE BULLET HOLE IN THE PIPING. APPLICATION OF THE CLAMP TERMINATED THE RELEASE AT ABOUT 11:15PM ON 12/06. THE BRAZORIA COUNTY SHERIFF'S OFFICE INSPECTED THE 1/2" DIAMETER HOLE IN THE ABOVE GROUND PIPING CONFIRMED THAT THE LINE HAD BEEN SHOT BYAN UNKNOWN PERSON. SPENT SHELL CASINGS, INCLUDING ONE 30-06 CASING, WERE FOUND ON THE COUNTY ROAD AND ESTIMATED 150 FEET FROM AND WITHIN CLEAR SIGHT OF THE HOLE. THE BRAZORIA COUNTY SHERIFF'S OFFICE TOOK POSSESSION OF THE SPENT RIFLE CARTRIDGES AND IS PROCEEDING TO INVESTIGATE THE CASE (BRAZORIA COUNTY CASE NO. 96-92152).
2017-09-29 08:50 | YES | NO | 19970003 | 1996-12-30 | 30765 | SHELL OIL PRODUCTS COMPANY | YES | 1996-12-02 | 845 | IL | COOK | ARLINGTON HEIGHTS | NO |  | NO | DES PLAINES PLANT |  | TANK FARM | TANK |  | 1966 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4325.7091 | 8726.7024 | JET FUEL | 3 | 162 | 136 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | SH HANSSON | 7132411751 | THE OPERATOR AT THE TANK'S LOCATION GAUGED EACH JET-A TANK WHILE PREPARING TO RECEIVE JET FUEL. WHILE RECORDING THE GAUGING RESULTS, HE TRANSPORTED THE PRODUCT LEVELS FOR TWO TANKS, WITH THE RESULT THAT THE JET FUEL WAS DELIVERED TO A NEARLY FULL TANK RATHER THAN WITH ADEQUATE EMPTY VOLUME.
2017-09-29 08:50 | YES | NO | 19970004 | 1997-01-03 | 19226 | TEXACO PIPELINE INC | NO | 1996-11-25 | 537 | TX | ELLIS | MAYPEARL | NO |  | NO | 5601 FM 66 AT GREAT HOUSE RD, APPROX 2MILES NORTHEAST OF THE CITY OF MAYPEARL |  | PUMPING STATION | OTHER | SEE COMMENTS | 1948 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 39652.333 | 79994.7719 | DIESEL FUEL | 3 | 450 | 428 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BL LEDNICKY | 7134323401 | PUMP STATION DISCHARGE CONTROL VALVE FLANGE GASKET FAILED, CAUSING THE LOSS OF PRODUCT. THE PRODUCT RAN DOWN HILL FROM THE PUMP STATION AND COLLECTED ON THE SURFACE OF 2 LIVESTOCK WATERING TANKS LOCATED APPROX 1500 FEET AWAY FROM THE PUMP STATION. THE WAXAHACHIE POLICE DEPT NOTIFIED THE TEXACO PIPELINE INC(TPLI) OPERATIONS CONTROL CENTER, AT THE ABOVE INDICATED TIME, TO ADVISE THAT THEY HAD RECEIVED A REPORT THAT PRODUCT WAS ESCAPING FROM THE TPLI MAYPEARLSTATION FACILITY. THE LINE WAS IMMEDIATELY SHUT DOWN, LOCAL PESONNEL WERE ALERTED AND A CLEAN UP RESPONSE WAS INITIATED. AT THIS TIME ALL FREE PRODUCT HAS BEEN PICKED UP AND AN INVESTIGATION IS UNDERWAY TO DETERMINE REMEDIATION STEPS THAT MAY BE REQUIRED FOR RESTORATION OF THE AREA AFFECTED BY THE SPILL. FLANGE GASKET FAILED ON PUMP STATION CONTROL VALVE. FAILED CONTROL VALVE FLANGE GASKET.
2017-09-29 08:50 | NO | NO | 19970005 | 1997-01-03 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1996-12-11 | 1000 | NE | WASHINGTON |  | NO |  | NO | T-20N, R-11E, SEC.32, APPROX 3/4 MILES SOUTH & EAST OF HERMAN, NE ON COUNTY ROAD P-201 |  | PUMPING STATION | VALVE |  | 1970 | OTHER | STEM PACKING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 2 | 0 | NO | NO | 6.63 | 0 | 0 | NO DATA |  | 1420 | 210 | YES | 4 | 1924 | 5 | 70 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARC DEVARENNES | 5734865488 | STATION BLOCK VALVE CLOSED AT 210 PSI AS PART OF PIPELINE MAINTENANCE PROJECT. PRODUCT MOVEMENT COORDINATOR IN WICHITA, KS NOTICED PRESSURE DROP FROM 210PSI TO 84 PSI AND CONTACED FIELD PROJECT PERSONNEL. PERSONNEL FOUND LEAKING STEM PACKING ON MAINLINE VALVE INSIDE STATION. NO DANGER TO KOCH PERSONNEL ORNON-COMPANY PERSONNEL. STATION IS LOCATED IN RURAL AREA. NO EVACUATIONS OR ROAD CLOSINGS NEEDED. PRODUCT LOSS CALCULATED AT 663 POUNDS, WORST CASE, ASSUMING ALL OF THE PRODUCT INSIDE THE AFFECTED PIPING RELEASED. UP TO HALF OF THEPRODUCT (APPROX. 300 LBS) COULD HAVE REMAINED INSIDE THE PIPING, BUT CANNOT BE DETERMINED. GAVE ORIGINAL ESTIMATE OF 2,100 POUNDS LOST TO NRC BELIEVING UP TO 30 MILES OF PIPELINE COULD HAVE BEEN AFFECTED. FOUND ONLY PIPING INSIDE STATION AFFECTED. PACKING REPLACED AND PROJECT CONTINUED.
2017-09-29 08:50 | YES | NO | 19970006 | 1997-01-14 | 809 | ARCO PIPE LINE CO | YES | 1996-12-21 | 1600 | TX | JACK | JACKSBORO | NO |  | NO | JACKSBORO STATION IS LOCATED APPROX 6 MILES SOUTHEAST OF JACKSBORO, TX IN JACK COUNTY AT LAT 33 08' 12N", LONGITUDE 98 07'26"W. |  | TANK FARM | BOLTED FITTING |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | CRUDE OIL | 1 | 1413 | 1133 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 |  |  | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | JACK AMBERG | 7139865408 | IMMEDIATELY AFTER REVIEWING THE 1500 HR RUN ON 12/21/96, THE PIPELINE SYSTEMCONTROLLER IN ARCO PIPELINE COMPANY'S (APL) OPERATIONS CONTROL CENTER ADVISED LOCAL APL OPERATIONS PERSONNEL AT JACKSBORO STATION OF A DECREASE IN LEVEL IN STATION BREAKOUT TANK 603. AT THE TIME TANK 603 AND ASSOCIATED PIPING WEREISOLATED AND NOT IN OPERATION. APL FIRST RESPONDERS ARRIVED AT 1525 TO INVESTIGATE THE CONDITION AND CONFIRMED THAT A 6-INCH VALVE ON THE TANK HAD FAILED, RELEASING CRUDE OIL INTO THE SECONDARY CONTAINMENT AREA AROUND THE TANK. ATAPPROX 1530 A TRANSFER OF CRUDE OIL FROM TANK 311 WAS INITIATED. THE OIL TRANSFER WAS COMPLETED AND THE RELEASE WAS STOPPED AT 2040 THAT DAY. RELEASE CRUDE OIL WAS COLLECTED BY VACUUM TRUCK AND TRANSFERRED TO TANK 311. CONTAMINATED SOIL WAS REMOVED AND STOCKPILED AT THE FACILITY FOR HANDLING AT A LATER DATE. ALL RELEASED MATERIAL WAS CONTAINED WITHIN THE SECONDARY CONTAINMENT OF THE FACILITY. PRELIMINAY INCIDENT INVESTIGATIONS INDICATE THAT EXTREME WEATHER CONDITIONS CAUSED THE VALVE RESULTING IN THE RELEASE. THERE WERE NO INJURIES,FIRES OR EXPLOSIONS ASSOCIATED WITH THIS RELEASE.
2017-09-29 08:50 | YES | NO | 19970007 | 1997-01-21 | 2330 | CHEVRON PIPELINE CO | YES | 1996-12-16 | 1530 | UT | DAVIS | WOODS CROSS | NO |  | NO | 1887 SOUTH 1800 WEST REDWOOD ROAD |  | LINE PIPE | OTHER | NONE SPECIFIED | 1957 | OTHER | PIN HOLE IN GIRTH WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 129771.2717 | 261801.0718 | DIESEL FUEL | 2 | 50 | 10 | NO | NO | 8.63 | 0.25 | 40000 | WELDED |  | 1950 | 1750 | YES | 4 | 2340 | 0 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GERALD MCKEE | 8012685774 | LEAK REPORTED BY THIRD PARTY AFTER SMELLING DIESEL FUEL FUMES ALL DAY. DIESEL FUEL WAS FOUND ON BOTH SIDES OF REDWOOD ROAD. THE PIPELINE WAS SHUT DOWN. CHEVRON PIPE LINE EXCAVATED AROUND THE PIPE, FOUND THE WELD LEAKING. THEN REPLACED PIPE WITH A NEW JOINT OF PIPE. REMEDIATION IS IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19970008 | 1997-01-21 | 15851 | PRIDE REFINING INC | NO | 1996-12-21 | 1430 | TX | PARKER |  | NO |  | NO | APPROX 3 MILES SOUTH OF WEATHERFORD, TX IN PARKER COUNTY ON THE WEST SIDE OF TIN TOP ROAD. |  | LINE PIPE | PIPE |  | 1920 | OTHER | COLLAR BROKE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 36047.5755 | 72722.5199 | DIESEL FUEL | 1 | 200 | 35 | NO | NO | 6.63 | 0.25 | 400 | THREADED |  | 351 | 75 | YES | 8 | 439 | 0 | 85 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN MACON | 9156748231 | AT APPROX 2:30PM ON 12-21-96 WE RECEIVED A CALL INTO OUR PIPELINE DISPATCHEROFFICE THAT WE HAD A SPILL OCCURRING AT TIN TOP ROAD IN PARKER COUNTY, TX. THE PIPELINE WAS THEN SHUT DOWN AND THE VALVES CLOSED. PRIDE EMPLOYEES WERE DISPATCHED TO THE SCENE AND OUR EMERGENCY RESPONSE CONTRACTOR WAS MOBILIZED. ATAPPROX 6:50PM THE LEAK WAS CLAMPED AND THE CLEAN-UP PROCESS BEGAN. APPROX 80' OF PIPE WAS REPLACED ON 12-22-96. CLEAN-UP PLANS ARE BEING DEVELOPED WITH THE TNRCC.
2017-09-29 08:50 | YES | NO | 19970010 | 1997-01-23 | 12127 | MARATHON PIPE LINE CO | YES | 1996-12-26 | 1045 | NE | NUCKOLLS |  | NO |  | NO | SEC. 15 T3N, R8W, APPROX. 5 MILES SE OF LAWRENCE, NE |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1300000 | 937236.9625 | 1890785.5182 | CRUDE OIL | 1 | 4900 | 4868 | NO | NO | 20 | 0.31 | 52000 | WELDED |  | 1082 | 1077 | YES | 24 | 1353 | 0 | 74 | INTERNAL | Null | YES | OTHER | MIC | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEPH FISHER | 4194213201 | AT APPROX 1045HRS, ON 12/26/96 A HUNTER, WALKING IN THE AREA OF THE PLATTE PIPE LINE COMPANY 20" PIPELINE RIGHT-OF-WAY, DISCOVERED CRUDE OIL IN AN EXCAVATED AREA ALONG THE PIPELINE. SUBSEQUENTLY, THE RELEASE WAS ALSO REPORTED TO MARATHON BY OUR CONTRACT AERIAL PATROL PILOT. THE AREA HAD BEEN EXCAVATED IN PREPARATION FOR REPLACING THIS SECTION OF PIPE WHICH HAD BEEN IDENTIFIED, BY APREVIOUS SMART PIG INSPECTION, TO CONTAIN INTERNAL PITTING. THE CRUDE ESCAPED THE EXCAVATION AND RAN DOWN A DRAW INTO ELK CREEK. THE CREEK WAS FROZEN OVER AND NO WATER WAS FLOWING. THE OIL WAS CONFINED TO A LENGTH OF THE CREEK WHICH WAS APPROX 4300 FEET LONG. CONTRACTORS WERE DISPATCHED TO THE SCENE AND THE OIL WAS CONFINED TO THE AREA AND CLEANED UP. VAC TRUCKS WERE USED TO RECOVER THE OIL AND EFFECTED SOIL WAS REMOVED TO AN APPROVED LAND FILL. ALL OF THE OIL, EXCEPT 30BBLS, WAS RECOVERED AND RETURNED TO THE PIPELINE SYSTEM. THE FAILED PIPE WAS REPLACED WITH PRETESTED PIPE AND THE LINE WAS RETURNED TO SERVICE. AT THE DISCOVERY OF THIS INCIDENT THE NATIONAL RESPONSE CENTER (FOR THE OFFICE OF PIPELINE SAFETY), AND THE NEBRASKA DEQ WERE NOTIFIED AND RESPONSE ACTIVITIES WERE COORDINATED WITH THESE AGENCIES.
2017-09-29 08:50 | YES | NO | 19970011 | 1997-01-28 | 22610 | WILLIAMS PIPELINE CO | YES | 1996-12-26 | 1501 | OK | CREEK |  | NO |  | NO | NW 1/4 OF SECTION 29 IN TOWNSHIP 18N AND RANGE 7E, IN CREEK COUNTY, OK. |  | LINE PIPE | GIRTH |  | 1929 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 43257.0906 | 87267.0239 | CRUDE OIL | 1 | 175 | 150 | NO | NO | 12 | 0.3 | 24000 | WELDED |  | 650 | 400 | YES | 8 | 960 | 0 | 95 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN BALL | 9185883850 | ON 12/26/96, OUR OPERATION CONTROL DEPT. NOTICED A DISCREPANCY BETWEEN THE METERED-IN AND METERED-OUT VOLUMES ON WPL'S LEF LINE, WHICH IS A LINE THAT PUMPS AN EXTRACTED LUBE OIL FEED. THE LINE WAS IMMEDIATELY SHUT DOWN AND PRESSURED TO 400 PSI FOR A STATIC LINE INTEGRITY CHECK. WHEN THE STATIC PRESSURE ON THE LINE WOULD NOT HOLD, OPERATIONS CONTROL IMMEDIATELY NOTIFIED REGION AND FIELD PERSONNEL OF A POSSIBLE LEAK AT 13:33HRS. A REQUEST WAS ISSUED TO THE AIR PATROL PILOT TO BEGAN FLYING THE LINE AND FIELD PERSONNEL WERE DISPATCHED TO DRIVE THE LINE. AT 15:00HRS, THE PATROL PILOT NOTIFIED EVERYONE OF THE LEAKLOCATION. AT 15:20HRS, A VACUUM TRUCK CONTRACTOR AND WPL FIELD PERSONNEL ARRIVED AT THE SITE AND THE VALVE AT MILE POST 74.60 WAS CLOSED. AT 16:00 HOURS,THE VALVE AT MILE POST 67.14 WAS CLOSED ISOLATING THE LEAK. AT 16:20HRS, THEFIRST BACKHOE ARRIVED ON SITE AND BY 17:50HRS THE CRACK BELL AND SPIGOT WELDWAS EXPOSED. THE LINE CONTINUED TO SLOWLY DRAIN-UP THROUGH THE NIGHT UNTIL 07:30 HRS ON 12/27/96. AT THAT TIME, WPL FIELD PERSONNEL BEGAN REPAIRING THE LIEN WHICH WAS COMPLETED AT 14:00 HRS. AT 17:00HRS, WITH THE DRUMRIGHT FIRE DEPT PRESENT AND APPROVAL OBTAINED FOR INSITUBURNING, THE CONTAMINATED SITE WASSET ON FIRE WHICH COMPLETED AT 11:45HRS. SOIL REMEDIATION WAS STARTED AND ISCONTINUING TODAY. AT THIS TIME, AND ACCIDENT INVESTIGATION HAS NOT DETERMINED THE CAUSE FOR THE FAILED WELD. VISUAL INSPECTION OF THE WELD INDICATES THATFULL WELD PENETRATION HAD NOT BEEN REACHED IN THE CRACKED AREA. THE CRACKED WELD HAS BEEN SENT TO A METALLURGICAL CONSULTANT FOR A STRESS ANALYSIS. DUE TO THE FACT THAT WPL FIELD PERSONNEL HAD EXPOSED 360' OF LINE CONTAINING THE FAILED WELD IN APRIL OF 1996 TO REMOVE AN ABANDONED CASING AND TO RE-COAT THE LINE, THE PROCEDURES THAT WERE USED ARE ALSO BEING INVESTIGATED. WHEN THE INVESTIGATION IS COMPLETED, A REVISED REPORT WILL BE ISSUED.
2017-09-29 08:50 | YES | NO | 19970012 | 1997-01-29 | 19223 | SUN PIPELINE CORP | YES | 1996-12-30 | 622 | NY | BROOME | VESTAL | NO |  | NO | AT THE INTERSECTION OF OLD VESTAL AND BUNN HILL RDS IN THE TOWN OF VESTAL, NY. SPECIFIC LOCATION IS LATITUDE 75DEG58'33" AND LONGITUDE 42DEG05'51". |  | LINE PIPE | LONGITUDINAL WELD |  | 1969 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1400000 | 1009332.1134 | 2036230.5581 | DIESEL FUEL | 1 | 986 | 572 | YES | NO | 8 | 0.22 | 42000 | WELDED |  | 1200 | 1224 | YES | 8 | 1885 | 7 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVE MEADOWS | 6106703203 | LONGITUDIAL WELD SPLIT AT LINE PIPE BEND LOCATION CAUSED A RELEASE OF REFINED PETROLEUM PRODUCTS TO LOCAL STORM AND SANITARY SEWERS, BUNN CREEK, SUSQUEHANNA RIVER, AND SOIL AND GROUND WATER. LOCAL EVACUATION OF RESIDENTIAL AND COMMERCIAL BUILDINGS OCCURRED, WITH RESULTING VAPOR ABATEMENT MEASURES AND MONITORING RESULTS ENABLING RESIDENTS AND COMMERCIAL ESTABLISHMENT PATRONS TO REOCCUPY SAME. AN INCIPIENT, FLASH FIRE OCCURRED IN THE BASEMENT OF ONE RESIDENTIAL HOME RESULTING IN MINIMAL DAMAGE. CLEAN-UP ACTIVITIES INCLUDED CONTAINMENT, PHYSICAL REMOVAL AND ABSORPTION ON SURFACE WATERS. REMEDIATION CONSISTS OF SOIL EXCAVATION, SOIL VAPOR EXTRACTION AND GROUND WATER PUMPING AND TREATING.FLASH FIRE OCCURRED IN THE BASEMENT OF ONE RESIDENCE RESULTING IN MINIMAL DAMAGE.
2017-09-29 08:50 | YES | NO | 19970014 | 1997-02-04 | 30907 | ASHLAND PETROLEUM CO. | NO | 1997-01-03 | 1620 | MN | WASHINGTON | COTTAGE GROVE | NO |  | NO | COTTAGE GROVE TANK FARM, COTTAGE GROVE, MN |  | TANK FARM | TANK |  | 1963 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 165000 | 116894.4259 | 235823.2725 | CRUDE OIL | 1 | 475 | 474 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R. SCOTT, ADMIN SUPERINTENDENT | 6124586458 | THE FLOATING ROOF ON TANK #204 SANK, DAMAGING THE TANK MIXER SEAL CAUSING ACRUDE OIL SPILL. THE CRUDE OIL STORED IN TANK #204 WAS CHARGED TO THEREFINERY AND TRANSFERRED TO OTHER TANKAGE TO STOP THE SEAL LEAK AND MINIMIZETHE LOSS OF CRUDE OIL. CAUSE STILL UNDER INVESTIGATION (PROBABLE ICE & SNOW).
2017-09-29 08:50 | YES | NO | 19970015 | 1997-02-03 | 26041 | GATX TERMINALS CORP | NO | 1997-01-13 | 1500 | CA | LOS ANGELES | PARAMOUNT | NO |  | NO | PARAMOUNT REFINERY- 14700 DOWNEY AVE - PARAMOUNT, CA |  | LINE PIPE | PIPE |  | 1929 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14169.0213 | 28584.6391 | DIESEL FUEL | 3 | 277 | 275 | NO | NO | 6 | 0.28 | 2160 | WELDED |  | 600 | 575 | YES | 4 | 775 | 5 | 96 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | DAVID KINGSTON | 3105187705 | RECEIVED A TELEPHONE CALL FROM PARAMOUNT PETROLEUM CORP THAT OUR GX-145PIPELINE WAS LEAKING ON THEIR REFINERY PROPERTY. AFTER GATX PERSONNEL ARRIVEDAT THE SCENE AND DISCUSSED THE INCIDENT WITH PARAMOUNT PETROLEUM PERSONNEL,THEY INDICATED THEIR CONTRACTOR FUGRO GEOSCIENCES, INC. HAD PUNCTURED GATX'SPIPELINE. UPON EXCAVATION AND INSPECTION OF THE DAMAGED PORTION OF PIPELINE ITWAS DISCOVERED THE CONTRACTOR HAD DRILLED TWO HOLES, ONE APPROX 2 1/2 INCHESAND THE OTHER 1-INCH IN DIAMETER, THROUGH THE GATX PIPELINE. THE PIPELINE WASNOT RUNNING WHEN THE DAMAGE OCCURRED. ALTHOUGH THE FURGO GEOSCEINCES HAD USEDTHE ONE-CALL SYSTEM, THEIR ORIGINAL TICKET HAD EXPIRED AND HAD NOT BEENRENEWED PRIOR TO PERFORMING THEIR WORK. THE DAMAGED PIPE WAS REMOVED AND ASEVEN FOOT SECTION OF NEW PRETESTED PIPE WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19970016 | 1997-01-28 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1997-01-02 | 1234 | WY | SWEETWATER |  | NO |  | NO | T-19-N R-98-W SECTION 23 (P.H.LIVESTOCK PROPERTY) |  | LINE PIPE | GIRTH |  | 1980 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 169994 | 120432.4305 | 242960.8569 | NATURAL GAS LIQUID | 2 | 6870 | 0 | NO | NO | 6.63 | 0.13 | 52000 | WELDED |  | 1440 | 1002 | YES | 24 | 1984 | 12 | 80 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALAN WOLFF | 9185811538 | PINHOLE LEAK DISCOVERED, EXCAVATED AND REPAIRED BY INSTALLATION OF A FULLENCIRCLEMENT WELDED SLEEVE.
2017-09-29 08:50 | YES | NO | 19970017 | 1997-01-28 | 9175 | JAYHAWK PIPELINE CORP | YES | 1997-01-10 | 1135 | KS | BUTLER |  | NO |  | NO | NW 1/4 SECTION 6, TOWNSHIP 27 SOUTH, RANGE 8 EAST OF BUTLER COUNTY, KS 5 MILES SOUTH AND 1 MILE EAST OF ROSALIA, KS |  | PUMPING STATION | TANK |  | 1946 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2479.5787 | 5002.3118 | CRUDE OIL | 1 | 889 | 865 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN WILKERSON | 3162419270 | A 1 INCH TEE, CONNECTED TO BOTTOM OF LOW SUCTION SWITCH ON TANK, BROKE-LETTING THE OIL COME OUT OF THE TANK. A VALVE NEXT TO TANK WAS CLOSED TO STOPLEAKING. ALL OIL WAS CONTAINED INSIDE TANK DIKE. THE SYSTEM IS SHUT DOWN ANDIN PROCESS OF PURGING AND TO BE ABANDONED. SOIL REMEDIATION ON SITE FOR FINALCLEAN UP. PART D - 1 INCH TEE CONNECTED TO LOW SUCTION SWITCH ON TANK.
2017-09-29 08:50 | YES | NO | 19970018 | 1997-02-04 | 6911 | GULF STATE PIPELINE CO INC | NO | 1996-12-24 | 1150 | TX | HARDIN |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1975 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 32442.8179 | 65450.2679 | NATURAL GAS LIQUID | 1 | 80 | 71 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 1186 | 500 | YES | 24 | 1878 | 7 | 75 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | HANK BOWMAN | 4093851400 | THE PIPELINE LEAK WAS DISCOVERED AT 11:50AM, 12/24/96 FOLLOWING A CALL TO 911THAT THERE WAS AN ODOR OF HYDROCARBON IN A YARD OFF NEYLAND RD, NORTH OFSILSBEE, TX. WHILE RESPONDING, SILSBEE VOLUNTEER FIRE DEPT PERSONNEL NOTIFIEDGULF STATE PIPE LINE. AFTER GSPL PERSONNEL WERE AT THE SITE HYDROCARBON CAMETO THE SURFACE, PIPELINE PUMPING WAS IMMEDIATELY STOPPED AND THE LINE FILLALLOWED TO GRAVITATE BACK TOWARD THE SOUTH. THE SPILL AREA WAS SECURED; THESILSBEE FIRE DEPT PROVIDED FIRE WATCH EQUIPMENT AND PERSONNEL, AND THE COUNTYSHERIFF PROVIDED ACCESS CONTROL. ADDITIONALLY, GSPL HAD THE ENTIRE PIPELINEINSPECTED BY AIRCRAFT TO ASCERTAIN THE INTEGRITY OF THE REST OF THE PIPELINE.ON 12/26/96 THE LINE WAS UNCOVERED, EXPOSING THE BREAK, A VACUUM TRUCK REMOVEDTHE HEEL OF LINE FILL THAT WAS FORCED SOUTH WITH NITROGEN, 1500 GALLONS OFHYDROCARBON WAS RECOVERED PRIMARILY FORM PIPELINE FILL, REMOVED SOIL WASPLACED IN ROLLOFF BOXES AND TRANSPORTED TO A STAGING AREA. ON THE 27TH THEREMAINING SOIL WAS REMOVED, THE TRENCH TESTED FOR VAPORS AND THE PREPAREDSECTION OF REPLACEMENT PIPE INSTALLED AND X-RAYED. THE PIPELINE WAS PUT BACKINTO SERVICE THAT AFTERNOON. FINAL CLEANUP, BACKFILL AND FINEGRADING WASCOMPLETED IN EARLY JANUARY 1997.
2017-09-29 08:50 | YES | NO | 19970019 | 1997-02-04 | 12626 | MOBIL PIPELINE CO - EMPIRE | NO | 1997-01-05 | 1300 | TX | MIDLAND |  | NO |  | NO | 2200 COUNTY ROAD 90E, APPROX. 3 MILES EAST OF MIDLAND, TX OF BUS. 20 |  | TANK FARM | VALVE |  | 1970 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 7250 | 5136.2702 | 10361.9317 | CRUDE OIL | 1 | 150 | 50 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DG SCOTT | 2146585914 | OPERATING/CONSTRUCTION PERSONNEL WERE BLEEDING DOWN A LINE INSIDE TANK FARM TOMAKE A TIE-IN AND INADVERENTLY LEFT A 1/2" BLEEDER VALVE OPEN CAUSING SPILLAGEOF CRUDE OIL INSIDE TANK DIKE AREA. THE SPILL WAS CONTAINED INSIDE THE TANKDIKE. MAINTENANCE PERSONNEL DISPATCHED TO AREA AND RECOVER AND CLEAN UPPROCEDURES INITIATED. ALL REQUIRED GOVERNMENTAL AGENCIES NOTIFIED. NO INJURIESWERE ASSOCIATED WITH THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 19970020 | 1997-02-12 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1997-01-09 | 1030 | TX | BRAZORIA | DAMON | NO |  | NO | APPROX 1/2 MILE EAST OF SH36 NEAR DAMON, TX |  | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 38000 | 26921.1405 | 54310.8143 | L. P. G. | 2 | 320 | 0 | NO | NO | 8.63 | 0.19 | 2005 | WELDED |  | 1315 | 450 | YES | 24 | 1650 | 7 | 74 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN THOMAS | 7138773802 | AT APPROX 10:30AM ON 01/09/97, DON ENLOE, PIPELINE PILOT REPORTED TO GLENELSTER AN ICE FORMATION APPROX 1 1/2 MILES NORTH OF DAMON STATION. GLEN WENTTO REPORTED LOCATION AND FOUND ICE FROST OF TOP OF THE GROUND (17" HIGH BY 20'IN DIAMETER) NO VAPORS WERE VISIBLE. DUG AREA AROUND ICE FORMATIONS, VAPORTSSTARTED ESCAPING. COVERED AREA BACK UP. THE LINE WAS STOPPLED AND REPLACEDWITH 118' OF NEW 8 5/8 X 42, EPOXY COATED, TESTED TO 1800 PSI. 10/95, PIPE INORDER TO REMOVE BAD SECTION. INSPECTED OLD PIPE AND DISCOVERED A HOLE APPROX3/32" CAUSED BY PRIOR CORROSION. CP LEVEL AT THIS LOCATION ARE 1.94.
2017-09-29 08:50 | YES | NO | 19970021 | 1997-02-05 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1996-11-01 | 530 | OK | BECKHAM |  | NO |  | NO | SE/4 SECTION 15-T10N-R21W |  | NO DATA | PUMP |  |  | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 14400 | 10381.7017 | 20944.0857 | CRUDE OIL | 1 | 140 | 40 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES HENRY | 4052557151 | SHIPPING PUMP PACKING GLAND BECAME LOOSE RESULTING IN RELEASE OF PRODUCT. PARTD: LEAKING PACKING GLAND ON PUMP.
2017-09-29 08:50 | YES | NO | 19970022 | 1997-02-05 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1997-01-09 | 1430 | TX | DENTON |  | NO |  | NO | 3 MILES SE OF AUBREY, TX. J. BRIDGES, JR. SURVEY A-36 DENTON COUNTY, TX |  | LINE PIPE | PIPE |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14169.0213 | 28584.6391 | L. P. G. | 2 | 477 | 0 | NO | NO | 4 | 0.19 | 42000 | WELDED |  | 1440 | 496 | YES | 20 | 1990 | 1 | 82 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | NO | JERRY ROGERS | 4053952377 | PIPELINE STRUCK BY THIRD PARTY EXCAVATION EQUIPMENT CAUSING DAMAGE AND RELEASEOF PRODUCT.
2017-09-29 08:50 | YES | NO | 19970023 | 1997-02-05 | 22855 | KOCH PIPELINE COMPANY, L.P. | YES | 1997-01-02 | 1340 | TX | HEMPHILL |  | NO |  | NO | 10 MILES S. OF CANADIAN, TX. SEC 21 BLOCK 1, L.G. & N RR SURVEY. HEMPHILL COUNTY, TX. |  | LINE PIPE | PIPE |  | 1974 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 64000 | 45340.8682 | 91470.8451 | NATURAL GAS LIQUID | 2 | 1955 | 0 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1440 | 650 | YES | 24 | 2150 | 10 | 74 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JERRY ROGERS | 4053952377 | PIPELINE STRUCK BY THIRD PARTY DITCHER CAUSING DAMAGE AND RELEASE OF PRODUCT.
2017-09-29 08:50 | YES | NO | 19970024 | 1997-02-07 | 30917 | PANENERGY PIPE LINE COMPANY | YES | 1996-02-05 | 710 | OK | JEFFERSON |  | NO |  | NO | SE/4, SECTION 33, TOWNSHIP 3 SOUTH, RANGE 7 WEST |  | TANK FARM | PIPE |  |  | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 13324 | 9605.9579 | 19379.0971 | CRUDE OIL | 1 | 500 | 495 | NO | NO | 10 | 0.32 | 0 | THREADED |  | 15 | 15 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | DON ALLEN | 8174952224 | 10" SUCTION LINE HAD BEEN HIDDEN YEARS AGO AND THE PIPE SPLIT. IT WAS ON ASUCTION LINE FROM THE TANK TO THE SUCTION OF THE BOOSTER UNIT. INCIDENTOCCURRED ON 02/05/96. THIS INCIDENT WAS WITHIN THE BOUNDARIES OF OUR PROPERY,ADDINGTON STATION, AND NEVER LEFT OUR PROPERTY. SUPPLEMENTAL SUBMITTED 2/11/97INDICATES THAT 10" SUCTION LINE HAD BEEN HIT AT SOME PREVIOUS TIME, AND THEEXTREMELY COLD WEATHER PROBABLY CAUSED A STRESS FRACTURE AND CAUSED THE PIPETO SPLIT. IT WAS ON A SUCTION LINE FROM THE TANK TO THE SUCTION OF THEBOOSTER UNIT.
2017-09-29 08:50 | YES | NO | 19970026 | 1997-02-20 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1997-01-25 | 900 | CA | KERN |  | NO |  | YES | NE 1/4 SEC 32, T31S, R23E |  | LINE PIPE | PIPE |  | 1911 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7084.5107 | 14292.3195 | CRUDE OIL | 1 | 580 | 80 | NO | NO | 6 | 0.25 | 0 | WELDED |  | 480 | 800 | YES | 4 | 600 | 11 | 95 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD KELLEY | 8053282310 | THIS 6" PIPELINE FAILED DUE TO EXCESSIVE PRESSURE DUE TO PUMP RELIEF VALVEMALFUNCTION. THIS PIPELINE WAS SOLD TO TARGET DRILLING IN 1993 WITH THE SALEOF INTEREST IN PROPERTY BY TEXACO.
2017-09-29 08:50 | YES | NO | 19970027 | 1997-02-21 | 4472 | ENRON LIQUIDS PIPELINE LTD PARTNERSHIP | YES | 1997-01-29 | 500 | IL | WILL | LEMONT | NO |  | NO | NE 1/4 SEC 36, T.37N-RIDE, DUPAGE TOWNSHIP WILL COUNTY, 1240 SMITH ROAD, LEMONT, IL 60447 |  | TANK FARM | OTHER | SEE COMMENTS | 1979 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 354.2255 | 714.616 | CONDENSATE | 3 | 2 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD FENT | 7138449526 | ELECTRICAL POWER TO ACCUMULATOR DUMP WAS TURNED OFF ON 1/22/97 WHILE EMPLOYEESINSTALLED HEAT TRACING TAPE ON NEW WATER TANK. AFTER THE WORK WAS COMPLETED,EMPLOYEES FAILED TO RESTORE POWER TO ACCUMULATOR PUMP. ON 1/29/97 AT 0035HRS., LEMONT FIELD BEGAN RECEIVING NATURAL GASOLINE FROM EPLC'S 107 PIPELINEAT 2900 BPH. WHEN THE PRESSURE IN THE SPHERE REACHED 6.7 PSIG, THE VENT RELIEFOPENED TO THE ACCUMULATOR/FLARE STACK. AT APPROX 0500 HRS. THE RELIEVEDPRODUCT FROM THE SPHERE MOVED SOME TRAPPED CONDENSATES FROM THE ACCUMULATOROUT TO THE FLARE STACK. UNBURNED LIQUIDS AND VAPORS FELL TO THE BASE OF THEFLARE AND CONTINUED TO BURN. THE OPERATOR ON DUTY WAS ABLE TO EXTINGUISH THEFIRE WITHA 30LB. FIRE EXTINGUISHER. PART C: FLARE STACK AND ACCUMULATOR TANK.PART D: ACCUMULATOR PUMP TURNED OFF.
2017-09-29 08:50 | YES | NO | 19970028 | 1997-02-19 | 2731 | CHEVRON PIPELINE CO | YES | 1997-01-24 | 350 | TX | COKE | SILVER | NO |  | NO | SEE ATTACHED MAP |  | NO DATA | OTHER | 1" PRESSURE RELIEF VALVE | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 863.6018 | 1742.2338 | L. P. G. | 2 | 53 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WJ JASPER | 2813635422 | AT APPROX 4:00AM A PLANT OPERATOR NOTIFIED CPL OF A PRESSURE RELIEF VALVESPILLING PRODUCT. THE OPERATOR SHUT DOWN THE PRODUCT FLOW AND CPL PERSONNELWERE DISPATCHED TO THE AREA. THE 1" RELIEF VALVE WAS RECALIBRATED TO 1440 PSIAND PRODUCT FLOW RESUMED. THREE HOURS LATER THE VALVE WAS CHECKED AND THESETTING HAD DRIFTED DOWNARD TO 930 PSI. THE RELIEF VALVE WAS DETERMINED FAULTYAND REPLACED.
2017-09-29 08:50 | YES | NO | 19970029 | 1997-02-18 | 12622 | MOBIL EXPLORATION & PRODUCING US INC | YES | 1997-01-29 | 2000 | UT | SAN JUAN |  | NO |  | NO | SECTION 32, T-41-S, R-25-E ON THE NAVAJO INDIAN RESERVATION. |  | LINE PIPE | VALVE |  | 1984 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1416.9021 | 2858.4639 | CARBON DIOXIDE | 2 | 1159 | 0 | NO | NO | 8.63 | 0.34 | 4786 | WELDED |  | 3650 | 2746 | YES | 24 | 4566 | 12 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GE WILKINSON | 9156882024 | AT APPROX 2000 HRS ON 01/29/97, A PRESSURE RELIEF VALVE FAILED ON THE SYSTEM.THE VALVE IN QUESTION IS A PILOT TYPE 2"X3" FULL RELIEF VALVE. AFTER ANINVESTIGATION IT WAS DETERMINED THAT AN "0" RING FAILURE CAUSED THE VALVE TOFAIL AND OPEN.
2017-09-29 08:50 | YES | NO | 19970030 | 1997-03-04 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-01-18 | 1217 | OK | LOGAN | ORLANDO | NO |  | NO | NW/4, SECTION 12, TOWNSHIP 19N, RANGE 2W, LOGAN COUNTY, OK 1 MILE EAST OF ORLANDO, OK AND HWY 77 ON SECTION LINE RD |  | LINE PIPE | PIPE |  | 1923 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10626.766 | 21438.4793 | DIESEL FUEL | 1 | 1600 | 1590 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1882 | 1375 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | VANCE WEBB | 4057674845 | ON JANUARY 18, 1997 AT 10:50 HRS, CONOCO PIPE LINE OIL MOVEMENTS CENTERRECEIVED A PHONE CALL FROM A MR. JOHN HAFNER, INFORMING CPL, OF A POSSIBLERELEASE NEAR THE TOWN OF ORLANDO. THE CALLER INDICATED THAT HE COULD SMELLDIESEL, AND SO LINE PRESSURES WERE CHECKED FOR THE PONCA CITY TO OK CITY 8"PRODUCT SYSTEM. HOWEVER, NO ABNORMAL READINGS INDICATING A LOSS OF LINEINTEGRITY WERE FOUND. AS A PRECAUTION THE LINE WAS SHUT DOWN AND ISOLATED VIAREMOTELY OPERATED BLOCK VALVES AT 11:08 HRS. LOCAL SPILL RESPONSE PERSONNELWERE DISPATCHED TO THE LOCATION TO ASCERTAIN IF LINE INTEGRITY HAD BEENCOMPROMISED. THE AREA SUPERVISOR CONFIRMED THAT A DIESEL FUEL RELEASE HADOCCURRED AT 12:17 HRS. ON ITS PONCA CITY TO OK CITY 8" PRODUCTS PIPELINE. THESPILL WAS CONTAINED IN THE IMMEDIATE VICINITY OF THE RELEASE, ( A PASTURE) ANDRECOVERY EFFORTS STARTED. DUE TO THE FROZEN GROUND CONDITIONS AND WATER FLUDHACTIVITIES DURING THE CLEANUP, IMPACT TO THE AREA WAS GREATLY REDUCED. THECAUSE OF THE RELEASE WAS DETERMINED TO BE AN ISOLATED CORROSION PIT, CAUSED BYEXTERNAL CORROSION. THE DAMAGED SECTION OF THE LINE WAS REPLACED, AND NORMALOPERATIONS WERE RESUMED.
2017-09-29 08:50 | YES | NO | 19970031 | 1997-03-04 | 15851 | PRIDE REFINING INC | NO | 1997-01-07 | 1400 | TX | TARRANT | FORT WORTH | NO |  | NO | ON THE EAST SIDE OF HWY 183 APPROX 1/2 MILE FROM CARSWELL NAVAL AIR STATION, FORT WORTH, TX |  | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | JET FUEL | 3 | 149 | 130 | NO | NO | 6 | 0.28 | 25000 | THREADED |  | 355 | 150 | YES | 8 | 444 | 8 | 84 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN MACON | 9156748231 | ON SUNDAY AFTERNOON, 01/19/97 OUR TERMINAL AT ALEDO, TX WAS CONTACTED BY ACARSWELL BASE EMPLOYEE THAT THERE HAD BEEN REPORTED A FUEL ODOR NEAR THE BASE.FUEL WAS SEEPING INTO A CREEK APPROX 1500' FROM THE PIPELINE. AT THE TIME THESOURCE OF THE FUEL WAS UNKNOWN. AFTER SAMPLING AND TESTING IT WAS DETERMINEDTHE PRODUCT WAS JP-8 JET FUEL. ON 01/20 PRIDE TOOK RESPONSIBILITY FOR THESPILL. THE PIPELINE WAS THE NITROGEN PURGED. CLEAN UP OF THE AREA AND CREEK ISNOW IN PROGRESS UNDER THE SUPERVISION OF PRIDE AND THE TNRCC. INVESTIGATIONDETERMINED LEAK OCCURRED DURING SHIPMENT ON 01/07/97. NO FURTHER SHIPMENTSHAVE BEEN MADE ON THIS SEGMENT OF THE SYSTEM.
2017-09-29 08:50 | YES | NO | 19970032 | 1997-02-25 | 18718 | SUN PIPE LINE CO | YES | 1997-01-19 | 1034 | OK | POTTAWATOMIE |  | NO |  | NO | SE 1/4 SEC 12 9N 4E FROM THE JUNCTION OF HWY 9 AND HWY 9A TO MAUD, WEST OF EARLSBORO, GO 1/4 MILE NORTH. |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 708.4511 | 1429.232 | CRUDE OIL | 1 | 175 | 165 | NO | NO | 8 | 0.28 | 1818 | WELDED |  | 604 | 200 | YES | 8 | 954 | 12 | 86 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | EF COEN | 9185866942 | PIPE FAILURE DUE TO 3RD PARTY HIT PRIOR TO 1990. PIPE WAS DENTED (FLATTENED)ON ONE SIDE AND DEVELOPED A STRESS FRACTURE.
2017-09-29 08:50 | YES | NO | 19970034 | 1997-02-25 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-01-18 | 1505 | KS | BUTLER |  | NO |  | NO | AT WPL'S EL DORADO STATION AT 1309 SUNSET ROAD IN EL DORADO, KS IN BUTLER COUNTY, KS |  | PUMPING STATION | PUMP |  | 1988 | OTHER | EQUIPMENT FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 6376.0596 | 12863.0876 | DIESEL FUEL | 3 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN BALL | 9185883850 | ON 1/18/97, AT APPROX 15:05 HRS, THE WPL OPERATOR RECEIVED A CALL FROM KANEBPIPELINE NOTIFYING US OF A FIRE IN OUR MANIFOLD. AFTER VERIFYING THE FIRE, THEOPERATOR IMMEDIATELY STOPPED THE PUMP, ISOLATED THE TANK THAT WAS SUPPLYINGSUCTION TO THE PUMP AND CALLED DISPATCHING TO SHUT DOWN THE PIPELINE. THEOPERATOR THEN WENT BACK TO THE FIRE WITH A FIRE EXTINGUISHER AND EXTINGUISHEDTHE FIRE BY APPROX 15:20 HRS, JUST PRIOR TO THE ARRIVAL OF THE EL DORADO FIREDEPT. AN INVESTIGATION OF THE ACCIDENT INDICATED THAT THE THRUST BEARING OFTHE VERTICAL BOOSTER PUMP MOTOR FAILED WHICH DAMAGED THE PUMP BEARING SEAL.THE DAMAGED PUMP BEARING SEAL THEN SPRAYED PRODUCT ON THE OVERHEATED MOTOR,WHICH SUBSEQUENTLY IGNITED WHEN THE PRODUCT REACHED ITS AUTO IGNITIONTEMPERATURE. THERE WAS MINIMUM ENVIRONMENTAL CLEANUP SINCE THE MAJORITY OF THE.7 BARREL LEAK WAS CONSUMED BY THE FIRE.
2017-09-29 08:50 | YES | NO | 19970035 | 1997-03-03 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-01-29 | 1455 | OK | TULSA | TULSA | NO |  | NO | 2120 SOUTH 33RD WEST AVENUE, TULSA, OK IN TULSA COUNTY |  | TANK FARM | VALVE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14169.0213 | 28584.6391 | GASOLINE | 3 | 108 | 108 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | STEVEN BALL | 9185883850 | ON 01/29/97, AT 14:30 HRS, AN OPERATOR NOTICED THE SMELL OF GASOLINE AT WPL'SWEST TULSA TERMINAL. THE OPERATOR IMMEDIATELY BEGAN SEARCHING FOR THE POSSIBLELEAK LOCATION AND DISCOVERED THAT IT HAD ORIGINATED FROM A VLAVE IN A MANIFOLDNEAR WPL'S MIX TANK #590. THE OPERATOR IMMEDIATELY TOOK STEPS TO ISOLATE THELEAKING VALVE BY CLOSING OFF OTHER VALVES IN THE IMMEDIATE AREA. ACCORDING TODISPATCHER RECORDS, 108 BARRELS OF GASOLINE RICH PRODUCT THAT ORIGINATED FROMTHE MIX TANK HAD BEEN DISCHARGED TO THE GROUND. OF THIS AMOUNT, 75 BARRELS WASRETURNED TO THE TANK BY VACUUM TRUCK. THE REMAINING PRODUCT WAS REMOVEDTHROUGH SOIL EXCAVATION. BY 18:00 HRS SITE CLEAN-UP WAS COMPLETED AND ARECONDITIONED VALVE WAS INSTALLED IN THE MANIFOLD. AN INVESTIGATION OF THEVALVE BODY INDICATED THAT WATER HAD COLLECTED IN THE VALVE CAVITY WHICHSUBSEQUENTLY FROZE AND EXPANDED CAUSING THE VALVE BODY TO CRACK.
2017-09-29 08:50 | YES | NO | 19970036 | 1997-02-24 | 13162 | NAVAJO REFINING CO | YES | 1997-02-05 | 1437 | NM | OTERO |  | NO |  | YES | SW QTR. S31, T26S, R11E |  | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 561 | 511 | NO | NO | 6.63 | 0.16 | 1978 | WELDED |  | 1100 | 100 | YES | 9 | 1300 | 0 | 59 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | JIM TOWNSEND | 5057483311 | NAVAJO'S CONTACTED MAINTENANCE CRW, WHILE IN THE PROCESS OF PREPARING TO SETMAGNETS FOR AN INTERNAL INSPECTION DEVICE (LINALOG), HIT AN UNKNOWNUNDERGROUND 3/4" BLEEDER VALVE WHICH WAS WELDED TO OUR PIPELINE AT THE 12O'CLOCK POSITION. THIS VALVE WAS NOT KNOWN TO BE ON OUR PIPELINE. WE BELIEVENOW THAT IT WAS INSTALLED WHEN THE PIPELINE WAS BUILT AS A BLEEDER VALVE USEDDURING HYDROSTATIC TESTING. THERE WERE NO MARKINGS OR RECORDS TO INDICATE THEPRESENCE OF THIS VALVE. THE BACKHOE USED TO EXCAVATE THE PIPELINE CAUSED THEVALVE TO BEGIN TO LEAK AT THE WELD. THE LEAK WAS CONFINED TO THE BELLHOLE,WHERE VACUUM TRUCKS RECOVERED IT IMMEDIATELY. THE RECOVERED PRODUCT WASTRANSPORTED TO OUR TERMINAL IN EL PASO, TX. THE PIPELINE WAS REPAIRED ANDRETURNED TO SERVICE EARLY THE NEXT MORNING.
2017-09-29 08:50 | YES | NO | 19970037 | 1997-03-07 | 1734 | BRIDGELINE GAS DISTRIBUTION LLC | Null | 1997-02-01 | 915 | LA | ST MARY |  | NO |  | NO | SEC 1 T16S R8E, ST. MARY PARISH, LA ON KEARNY PROPERTY |  | LINE PIPE | PIPE |  | 1971 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 85176 | 60343.028 | 121736.261 | NATURAL GAS LIQUID | 2 | 2 | 0 | NO | NO | 6.63 | 0.2 | 0 | WELDED |  | 1440 | 850 | YES | 24 | 2700 | 8 | 71 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | JW SIMPSON | 5045951886 | HENRY PLANT CONTROL ROOM RECEIVED A PHONE CALL FROM DWIGHT PLAISANCE (LAUDOVERSEER) AT 9:15 AM ON 02-01-97 INDICATING THAT A LEAK HAD BEEN NOTICED,WHICH ALSO CONTAINED BUBBLES, ADJACENT TO A TEXACO PIPELINE SIGN. PIPELINEPERSONNEL WERE DISPATCHED TO THE LEAK SITE VIA THE COMPANY BOAT TO VERIFY THEEXISTENCE OF THE LEAK. THE BRIDGELINE INSPECTOR, R.P. SUIRE, NOTIFIED W.J.LEBLANC AT THE HENRY PLANT TO CONFIRM THE LEAK WAS ON BRIDGELINE'S INTRACOATALSYSTEM PIPELINE. THAT PORTION OF THE LINE WAS ISOLATED AND SECURED IMMEDIATELYTO ENSURE PUBLIC SAFETY PRIOR TO COMMENCING WITH REPAIR ACTIVITIES. THE ST.MARY PARISH SHERIFF'S DEPT ASSISTED WITH SECURING THE AREA.
2017-09-29 08:50 | YES | NO | 19970038 | 1997-03-05 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1997-02-03 | 1500 | CA | FRESNO |  | NO |  | NO | SECTION 18, TOWNSHIP 20 SOUTH, RANGE 15 EAST, COALINGA OIL FIELDS |  | LINE PIPE | PIPE |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6300 | 4463.2417 | 9004.1613 | CRUDE OIL | 1 | 408 | 120 | NO | NO | 10 | 0.25 | 0 | WELDED |  | 200 | 0 | YES | 4 | 720 | 11 | 96 | EXTERNAL | Null | NO | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | GARY HOHNSTEIN | 8053282329 | UPON EXCAVATION OF THE PIPE, IT WAS FOUND THAT A FARM IMPLEMENT DAMAGED THEPIPE'S COATING AND LEFT A VISIBLE SCRAPE ON THE PIPE. THIS BECAME THE LOCATIONOF CONCENTRATED CORROSION AND SUBSEQUENT LEAK. STEPS HAVE BEEN TAKEN TO REVIEWTHE CONDITION OF THE REST OF THE PIPELINE ACROSS THE FARMER'S FIELD.
2017-09-29 08:50 | YES | NO | 19970039 | 1997-03-06 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1997-02-06 | 201 | IA | WOODBURY | MOVILLE | NO |  | NO | SECTION 2 TOWNSHIP 88N RANGE 45W |  | PUMPING STATION | PUMP |  | 1979 | OTHER | PUMP SEAL FAIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 42507.064 | 85753.9173 | GASOLINE | 2 | 5 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL PEARSON | 9185994043 | INBOARD PUMP SEAL FAILED RESULTING IN RELEASE OF PRODUCT FROM THE PUMP. THEPRODUCT IGNITED AND WAS DETECTED BY SAFETY EQUIPMENT, WHICH RESULTED IN THEAUTOMATIC SHUTDOWN OF THE PUMP STATION, THE AUTOMATIC ISOLATION OF THE PUMPHEADERS VIA MOTOR OPERATED VALVES, AND THE NOTIFICATION OF CENTRAL CONTROLLERPERSONNEL VIA THE SCADA SYSTEM. LOCAL PERSONNEL AND EMERGENCY PERSONNEL WERESUBSEQUENTLY NOTIFIED AND RESPONDED TO THE SCENE. THE PUMP STATION WAS SECUREDAND THE FIRE WAS ALLOWED TO NATURALLY BURN TO EXTINCTION.
2017-09-29 08:50 | YES | NO | 19970040 | 1997-03-11 | 12626 | MOBIL PIPELINE CO - EMPIRE | NO | 1997-02-04 | 130 | TX | GAINES | SEMINOLE | NO |  | NO | APPROX 1 MILE SOUTH OF SEMINOLE, TX GAINES COUNTY, TX |  | LINE PIPE | PIPE |  | 1947 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | CRUDE OIL | 1 | 200 | 175 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 100 | 80 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT | 2146585914 | EXTERNAL CORROSION WAS THE CAUSE OF THE INCIDENT. THIS IS A LOW STRESSPIPELINE FORMERLY CLASSIFIED AS A GATHERING SYSTEM PIPELINE. LEAK WASDISCOVERED AT 0130 HRS. BY COMPANY GAUGER ON CALL-OUT TO RESTART A LACT UNIT.LINE WAS IMMEDIATELY SHUT DOWN AND ISOLATED. MAINTENANCE CREWS WERE DISPATCHEDTO THE SITE TO INITIATE TEMPORARY REPAIR AND CLEANUP OPERATIONS. PERMANENTREPAIR WILL BE MADE BY REPLACING AT A LATER DATE.
2017-09-29 08:50 | YES | NO | 19970041 | 1997-03-15 | 4906 | EXXON PIPELINE CO | YES | 1997-02-19 | 500 | TX | HARRIS | BAYTOWN | NO |  | NO | EXXON PIPELINE COMPANY BAYTOWN CRUDE RECEIVING STATION PARK STREET BAYTON, TX. |  | PUMPING STATION | PIPE |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 37500 | 26566.915 | 53596.1983 | CRUDE OIL | 1 | 75 | 55 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | JB BACON | 7136560227 | SPILL OCCURRED ON RELIEF LINE AT EPC BAYTOWN CRUDE RECEIVING STATION, LOCATEDWITHIN THE EXXON BAYTOWN REFINERY COMPLEX IN BAYTOWN, TX. THE SPILLEDCRUDE/SLOP OIL MIX WAS CONTAINED IN A DITCH ALONG A PRIVATE ROAD IN THEREFINERY, AND WAS RECOVERED USING VACUUM TRUCKS. IMPACTED SOILS WERE EXCAVATEDAND REMOVED FOR OFF-SITE DISPOSAL IN A PROPERLY PERMITTED FACILITY. THEPIPELINE WAS REPAIRED AND PLACED BACK IN SERVICE BY 13:00 HRS ON THE DATE OFTHE SPILL, 02/19/97. THE CAUSE OF THE SPILL WAS INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19970042 | 1997-03-15 | 18718 | SUN PIPE LINE CO | NO | 1997-03-04 | 855 | OK | NOBLE |  | NO |  | NO | NW/4 SEC. 33, TOWNSHIP 24 NORTH, RANGE 1 WEST 3/8 MI. E. FROM JUNCTION OF HWY 15 AND 77 ON SOUTH SIDE OF ROAD |  | LINE PIPE | PIPE |  | 1972 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5313.383 | 10719.2397 | CRUDE OIL | 1 | 60 | 0 | NO | NO | 4 | 0.24 | 2528 | WELDED |  | 725 | 472 | YES | 8 | 1713 | 9 | 96 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDITH COEN | 9185866942 | WELD FAILED AT LOCATION WHERE PIPELINE DOES A 90 DEGREE BEND AND CAME ABOVEGROUND. PIPE WAS ALSO DAMAGED. OIL RAN DOWN DITCH ALONGSIDE ROAD, THROUGH ACULVERT, ACROSS A FIELD AND INTO A LOW LYING AREA WHERE WATER WAS STANDINGFROM RECENT RAIN.
2017-09-29 08:50 | YES | NO | 19970043 | 1997-03-19 | 4805 | EXPLORER PIPELINE CO | YES | 1997-01-23 | 1230 | TX | MONTGOMERY |  | NO |  | NO | 6 MILES EAST OF IH 45 ON FM105 (EAST OF CONROE, TX); 0.2 MILES NORTH ON MIL MAC RD; 3/4 MILE WEST ON CRYSTAL CREEK ROAD. |  | LINE PIPE | PIPE |  | 1971 | OTHER | SEE COMMENTS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | FUEL OIL | 3 | 265 | 260 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RODNEY SANDS | 9184935106 | ON 01/21/97 EXPLORER INITIATED A PROJECT TO REPLACE AN EXISTING 28" BLOCKVALVE AT MILEPOST 114.3 IN MONTGOMERY COUNTY, TX. PRODUCT WAS EVACUATED FROMTHE PIPELINE AT THE WORK SITE BY INSERTING (PASADENA, TX) AND STOPPING THEM ATTHE SITE. AIRE WAS ALLOWED TO ENTER THROUGH A TAP ON THE LINE BETWEEN TWO OFTHE SPHERES AS 7900 BARRELS OF PRODUCT DRAINED BACK INTO TANKAGE AT AN ORIGINFACILITY. THE PLAN WAS FOR THE UPSTREAM SPHERE TO REMAIN IN PLACE WHILE THETWO DOWNSTREAM SPHERES DISPLACED PRODUCT FROM THE WORK SITE AS PRODUCT WASDRAINED INTO TANKAGE. AT APPROX 1230 HRS ON 01/21/97 THE FIRST LINE CUT WASMADE TO REMOVE THE OLD VALVE. WHEN THE LINE WAS CUT, FUEL OIL BEGAN DRAININGINTO THE EXCAVATED TRENCH. VACUUM TRUCKS ALREADY ON SITE BEGAN RECOVERING THERELEASED PRODUCT AND NOTIFICATION OF THE REQUIRED FEDERAL AND STATE GOVERNMENTAGENCIES WAD MADE. THE RELEASE WAS CONTAINED WITHIN THE EXCAVATED WORK SITEWHILE VACUUM TRUCKS RECOVERED 260 BARRELS OF FUEL OIL. IT WAS LATER DETERMINEDTHAT A MALFUNCTIONING SPHERE DETECTOR CAUSED MISINTERPRETATION OF THE EXACTLOCATION OF THE SPHERES AND IT WAS NOT KNOWN THAT SOME FUEL OIL WAS TRAPPED INTHE VICINITY OF THE LINE CUT. REMEDIATION OF CONTAMINATED SOILS IS IN PROGRESSWITH OVERSIGHT BY THE TNRCC. MALFUNCTIONING PIG SIG CAUSED MISPLACEMENT OFSPHERES USED TO DISPLACE FUEL OIL FROM WORK AREA. RELEASE OCCURED FROMPIPELINE CUT FOR VALVE INSTALLATION.
2017-09-29 08:50 | YES | NO | 19970044 | 1997-03-15 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1997-02-24 | 1640 | LA | UNION PARISH |  | NO |  | NO | APPROX 5 MILES WEST OF STERLINGTON, LA ON HWY 2, SOUTH 2 MILES ON PARKS RD. (T-20N, R-3E, SEC.21). |  | NO DATA | OTHER | SEE PART K | 1981 | OTHER | FAILED MATERIAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 106267.6599 | 214384.7932 | ANHYDROUS AMMONIA | 2 | 10 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM NORVELL | 5734865488 | SMELL OF AMMONIA (NH3) REPORTED TO KOCH'S PIPELINE CONTROL CENTER (PCC) INWICHITA, KS. BY LANDOWNER EVA PARKS AT APPROX 16:40. PCC NOTIFIED KOCHEMPLOYEE WHO INVESTIGATED AND CONFIRMED AMMONIA SMELL. FOUR HOUSEHOLDS IN NEARPROXIMITY WERE EVACUATED AS A PRECAUTIONARY MEASURE. LINE PRESSURE REDUCED BYPCC AND SECTION OF AFFECTED LINE WAS ISOLATED. CAUSE OF RELEASE WAS FOUND TOBE A CRACK IN THE 1/2" BLOCK AND BLEED LINE ON AN UNDERGROUND 6" VALVE. THEBLOCK AND BLEED LINE IS USED WHEN PERFORMING VALVE MAINTENANCE. THE BLOCK ANDBLEED LINE WAS REMOVED AND THE VALVE WAS REPLACED WITH A VALVE WHICH DOES NOTREQUIRE A BLOCK AND BLEED LINE. AMMONIA CONTAMINATED SOIL WAS DISPOSED OFACCORDING TO APPROPRIATE LOUISIANA REGULATIONS. THERE WERE NO KNOWN ORANTICIPATED HEALTH RISKS ASSOCIATED WITH THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 19970046 | 1997-03-15 | 11237 | TEXAS EASTERN PRODUCT PIPELINE CO | YES | 1997-02-24 | 1545 | OH | BUTLER | ROSS | NO |  | NO | NEAR INTERSECTION OF NEW LONDON AND LAYHIGH RD APPROX 2.8 MILES NORTHEAST OF ROSS OHIO. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 54000 | 38256.3576 | 77178.5256 | KEROSENE | 3 | 306 | 272 | NO | NO | 6.63 | 0.25 | 35000 | WELDED |  | 1440 | 640 | YES | 24 | 1895 | 0 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ERNEST P HAGAN | 7137593845 | AT APPROX 1545 HRS CDT 02/24/97 TEPPCO PERSONEL RECIEVED TELEPHONICNOTIFICTION OF A THIRD PARTY INCIDENT. A BULLDOZER CLEARING BRUSH FROM THEBANKS OF A SMALL TRIBUTARY TO DRY RUN CREEK APPROX 2.8 MILES NORTYHEAST OFROSS OHIO HAD HIT TEPPCO'S 6" LINE TO-1.THE TEPPCO EMERGENCY PLAN WASIMMEDIATELY INITIATED THE SYSTEM WAS ISOLATED AND THE VALVE NEAR THE INCIDENTSITE WERE CLOSED. JET A KEROSENE RELEASED FROM THE SITE FLOWED ONTO THETRIBUTARY. TEPPCO PERSONNEL PLACED COFFER DAMS ALONG DRY RUN CREEK BEGINNINGJUST SOUTH OF THE TRIBUTARY JUNCTION AND WAS ABLE TO CONTAIN ALL THE PRODUCTFROM REACHING ADDITIONAL WATERWAYS. THE DAMAGED PIPE WAS REMOVED AND NEW PIPEPLACED INTO THE SYSTEM. TEPPCO RESTARTED THE PIPELINE ON 02\25\97. REMEDIATIONOF THE US ENVIROMENTAL PROTECTION AGENCY.
2017-09-29 08:50 | YES | NO | 19970047 | 1997-03-15 | 19226 | TEXACO PIPELINE INC | YES | 1997-03-14 | 1630 |  |  |  | YES | LAT29 DEG 09' LONG 90 33' | NO | TERREBONNE BAY - TIMBALIER ISLAND |  | LINE PIPE | PIPE |  |  | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 177112.7665 | 357307.9887 | CRUDE OIL | 1 | 20 | 0 | NO | NO | 10 | 0.31 | 0 | WELDED |  | 325 | 100 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | OTHER | CO. AERIAL SURVEILLANCE | NO | NO | GW SCHULZE | 5048765645 | EXTERNAL MECHANICAL DAMAGE-4-1\2 GASH IN 10" PIPELINE IN TERREBONNE BAYTIMBALIER ISLAND. SHUT IN LAKE BARRE AND CAILLOU ISLAND FIELDS. BOOMEDSOURCE. JUMPED DIVERS TO JET THE PIPELINE. CALLED OUT CENAC ENVIROMENTAL ANDCLEAN GULF.
2017-09-29 08:50 | YES | NO | 19970048 | 1997-03-15 | 443 | AMOCO PIPELINE CO | YES | 1997-02-25 | 540 | WY | NATRONA |  | NO |  | NO | S6,T 33 N, R 79W |  | PUMPING STATION | PUMP |  | 1993 | OTHER | INTERNAL PUMP FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 354.2255 | 714.616 | CRUDE OIL | 1 | 250 | 246 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. PETERSON | 3038305067 | THIS INCIDENT OCCURED 2/25/97 AT ABOUT 5:40 AM MST. THE NRC REPORT IS 378186.THIS INCIDENT RESULTED FROM AN INTERNAL PUMP FAILURE WHICH CAUSED THE PUMPSEAL FAILURE. APPROX. 250 BARRELS WERE RELEASED WITH 246 BARRELS RECOVERED.THE REPONSE CREW REPONDED TO THE SCENE PROMPTLY.
2017-09-29 08:50 | YES | NO | 19970049 | 1997-03-15 | 12622 | MOBIL EXPLORATION & PRODUCING US INC | NO | 1997-03-05 | 1612 |  |  |  | YES | N30 13'3 W 88 03'3 | NO | SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1996 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 224000 | 158693.0388 | 320147.9579 | OIL AND GASOLINE | 3 | 3 | 0 | NO | NO | 4.5 | 0.24 | 60000 | WELDED |  | 2100 | 1200 | YES | 8 | 2625 | 10 | 96 | INTERNAL | Null | YES | OTHER | STILL INVESTIGATING | NO DATA |  | Null | NO DATA |  | Null | Null | BILL G WRIGHT | 5045665535 | BOAT CAPTAIN NOTICED BUBBLING ON TOP OF WATER COMING FROM PIPELINE BOTH ENDSOF THE LINE WERE ISOLATED AND DEPREDDURED. DIVERS DISCOVERED A 1/4" INDIAMETER HOLE IN PIPELINE.
2017-09-29 08:50 | YES | NO | 19970050 | 1997-03-24 | 4906 | EXXON PIPELINE CO | NO | 1997-02-24 | 1200 | TX | HARRIS | HOUSTON | NO |  | NO | NEAR 1014 WEST GULF BANK RD (APPROX. 1/8-MI SOUTH OF ROAD) HOUSTON TX |  | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 147000 | 104142.3067 | 210097.0974 | TURBINE FUEL | 3 | 2 | 2 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 720 | 350 | YES | 0 | 1706 | 0 | 69 | EXTERNAL | Null | YES | GALVANIC |  | OTHER | NONE SPECIFIED | Null | NO DATA |  | NO | NO | J.B. BACON | 7136562275 | AT 1200 ON 2/24/97 EPC RECIEVED NOTIFICATION OF A POSSIBLE RELEASE ON EPC'SALDINE-HIA TFA PIPELINE. EPC IMMEDIATELY DISPATCHED PERSONNEL TO THE SITE TOINVESTIGATE. EPC PERSONNEL DETERMINED THAT THE PIPELINE COULD BE THE SOURCE OFTHE LEAK AND THE LINE WAS SHUT DOWN. ADDITIONAL EPC AND CONTRACT PERSONNELWERE DISPATCHED TO THE SITE FOR SPILL RESPONSE AND CLEAN UP, AND PIPELINEREPAIR. A PINHOLE LEAK WAS LOCATED AND REPAIRED ON 2/25/97. PERMANENTREPAIRS(FULL WRAP) WERE COMPLETED 2/26/97 AND THE LINE WAS PLACED BACK INSERVICE. SITE CLEAN UP CONSISTED OF RECOVERING RELEASED PRODUCT FROM A NEARBYDRAINAGE DITCH AND THE REPAIR EXCAVATION AND EXCAVATING IMPACTED SOILS.
2017-09-29 08:50 | YES | NO | 19970051 | 1997-04-07 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1997-03-01 | 1649 | CA | PLACER |  | NO |  | YES | PLMP 41.9 1,000 FT. SOUTH OF OLD HWY 40 (DONNER PASS RD) |  | LINE PIPE | PIPE |  | 1957 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2500000 | 1771127.665 | 3573079.887 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 8 | 0.25 | 46000 | WELDED |  | 1920 | 810 | YES | 24 | 2550 | 0 | 57 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 7145604720 | A THIRD PARTY NOTIFIED US FOREST SERVICE OF FUEL ODORS IN THE ARE OF SUMMITCREEK AT DONNER LAKE. THE US FOREST SERVICE ALERTED SFPP, AND OUR RENOPIPELINE WAS INSPECTED. A LEAK WAS FOUND AND SUBSEQUENTLY REPAIRED. A LARGEENVIRONMENTAL CLEANUP WAS UNDERTAKEN IN COOPERATION WITH FEDERAL, STATE, ANDLOCAL OFFICIALS.
2017-09-29 08:50 | YES | NO | 19970052 | 1997-04-15 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-03-11 | 1000 | IA | POLK |  | NO |  | NO | 2503 SOUTHEAST 43RD STREET, DES MOINES, IOWA 50317 IN POLK COUNTY, IOWA |  | TANK FARM | PIPE |  | 1979 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3402983 | 2410846.934 | 4863652.0452 | GASOLINE | 3 | 30000 | 28571 | NO | NO | 18 | 0.31 | 60000 | WELDED |  | 285 | 30 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | STEVEN S. BALL | 9185883850 | ON MARCH 9 1997 WPLS LEAD OPERATOR AT DES MOINES STATION NOTICED THAT TANK1310 HAD DECREASED IN LEVEL EVEN THOUGH THE PRODUCT TEMPERATURE IN THE TANKHAD INCREASED. AS A RESULT OF THIS FACT THE TANK WAS CLOSED OFF TO PERFORM A 24 HR STATIC CHECK. ON MONDAY WPLS AREA MANAGER WAS ADVISED THAT THE STATICCHECK WAS CONTINUING TO INDICATE A LOSS OF TANK LEVEL. WPL PERSONNEL WERE DISPATCHED TO THE FIELD TO INVESTIATE THE TANK LINES AND THE AREA AROUND TANK 1310. AT THIS TIME IT WAS DISCOVERED THAT THE PUMP RECIEVE VALVE ON THE PUMP MANIFOLD WAS CLOSED. THIS INDICATED THAT 18" LINE TOTANK 1310 WAS ALSO INCLUDED IN THE STATIC CHECK OF THE TANK ONLY. WHILE INSPECTING THE AREA AROUND TANK 1310, DEAD VEGETATION WAS FOUND NORTH OF THETANK. IT APPEARED THAT THIS WAS A RESULT OF WEED SPRAYING THAT WAS APPLIED IN 1996. THE AREA WAS PROBED BUT NO DETECTION OF PRODUCT COULD BE FOUND. ON TUESDAY, MARCH 11, 1997, THE RESULTS OF THE STATIC TANK CHECK INDICATED THATTHE TANK WAS NOT LEAKING. AT THIS TIME, IT APPEARED THAT EITHER THE MANIFOLD VALVE WAS LEAKING, ALLOWING PRODUCT TO MOVE FROM TANK 1310 TO TANK 836, WHICH SHARES THE SAME HEADER, OR THAT THE UNDERGROUND LINE WAS LEAKING. THEMAINTENANCE CREW WAS SENT TO PERFORM A PRESSURE TEST ON THE 18" LINE. AT 0905 HOURS, THE MAINTENANCE CREW PROBED THE LINE A SECOND TIME IN THE SAME AREA THAT WAS PREVIOUSLY TESTED AND DETECTED A PRODUCT ODOR. A BACKHOE WAS BROUGHT TO THE SITE AT AT 1000 HOURS THE LEAK WAS CONFIRMED. THE BACKHOE CONTINUED TO DIG IN THE AREA UNTIL THE LEAK WAS LOCATED AND CLAMPED OFF AT APPROX. 1130 HOURS. THE QUARTER INCH HOLE IN THE 6 OCLOCK POSITION OF THEPIPE WAS IDENTIFIED AS INTERNAL CORROSION. AN ULTRASONIC EXAMINATION IN THE AREA AROUND THE LEAK INDICATED THAT THIS WAS AN ISOLATED CONDITION. IN THE EARLY AFTERNOON, SAND WAS BROUGHT IN TO LINE THE DITCH TO ISOLATE THE HYDROCARBON VAPORS IN ORDER THAT A PATCH COULD BE SAFELY WELDED ON THE LINE.THIS WAS COMPLETED AT 1430 HOURS. REMEDIATION OF THE SITE CONTINUED BY DIGGING TRENCHES AND USING VACUUM TRUCKS AND SKIMMERS TO PICK UP THE FREE PRODUCT. IN ORDER TO DETERMINE THE EXTENT OF THE PLUME, DRILLING RIGS WERE BROUGHT IN TO DRILL 28 MONITORING WELLS. FROM THE INFORMATION OF FREE PRODUCT STANDING IN EACH WELL, AS WELL AS FROM REVIEWING PAST RECORDS REGARDING TANK 1310 OPERATION, IT WAS CONCLUDED THAT 30,000 BARRELS HAD LEAKED OUT OF THE LINE OVER A 2.5 YEAR PERIOD. THE REMEDIATION OF THIS SITE IS EXPECTED TO CONTINUE FOR THE NEXT TWO TO THREE YEARS AND THE ESTIMATED TOTAL PROPERTY DAMAGE RECORDED EARLIER IN THIS REPORT REFLECTS ANTICIPATED COSTS FOR THE ENTIRE REMEDIATION PERIOD. AFTER THE VACUUM TRUCKS AND SKIMMERS BECOME INEFFECTIVE, IT IS ANTICIPATED THAT AN AIR SPARGING/SOIL VAPOR EXTRACTION SYSTEM WILL BE INSTALLED FOR THE DURATION OF THE REMEDIATION PERIOD.
2017-09-29 08:50 | YES | NO | 19970053 | 1997-04-15 | 18273 | SHELL PIPELINE CORP | NO | 1997-03-07 | 700 | CA | FRESNO |  | NO |  | NO | CALIOLA TANK FARM{BAKERSFIELD 14 INCH} |  | TANK FARM | SCRAPER TRAP |  | 1980 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 17711.2767 | 35730.7989 | CRUDE OIL | 1 | 320 | 300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.H. HANSSON | 7132411751 | RELEASE OCCURED WHEN ONE INCH SCRAPER BARREL VALVE WAS ERRONEOUSLY LEFT IN THEOPEN POSITION
2017-09-29 08:50 | YES | NO | 19970054 | 1997-04-21 | 15490 | PHILLIPS PIPE LINE CO | YES | 1997-03-18 | 741 | TX | OCHILTREE |  | NO |  | NO | BEAVER STATION -=BEAVER BORGER LINE- SRW 419-11-MP O SEC 78 BLOCK 11, W. AHRENBECKBROS. SURVEY, OCHILTREE CO.,TX |  | PUMPING STATION | PIPE |  | 1964 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5667.6085 | 11433.8556 | CRUDE OIL | 1 | 527 | 345 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L.J.SCHIMTZ | 9186614814 | A 1/2 PIPE NIPPLE LOCATED ON THE DISCHARGE PIPING FROM PUMP#1, BROKE AT THETHREADS WHILE THE UNIT WAS RUNNING. UPON NOTIFICATION FROM AN INDEPENDENTLEASE OPERATOR, THE LINE WAS BLOCKED IN AND THE LEAK PLUGGED.
2017-09-29 08:50 | YES | NO | 19970055 | 1997-04-15 | 15490 | PHILLIPS PIPE LINE CO | YES | 1997-03-15 | 1140 | OK | ROGER MILLS |  | NO |  | NO | BUXTON-BORGER LINE SRW-401-25- MP 98-46+65 SEC 12,T11N,R24,ROGER MILLS CO, OK NORTH OF SAYRE, OK, AND ABOUT 3 MILES NORTH OF HWY 6. |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 66000 | 46757.7704 | 94329.309 | CRUDE OIL | 1 | 290 | 250 | NO | NO | 10.75 | 0.2 | 42000 | WELDED |  | 1140 | 750 | YES | 24 | 1450 | 8 | 78 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | LINUS SCHMITZ | 9186614814 | A LAND TENNANT WAS AERATING PASTURE LAND AND PUNCTURED OUR PIPELINE. AFTERWHICH HE NOTIFIED THE CONTROL CENTER AND THE LINE WAS SHUT AND BLOCKED IN. THEDAMAGED PIPE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19970056 | 1997-04-11 | 15116 | PANOLA / RUSK GATHERERS | NO | 1997-03-13 | 800 | TX | LIBERTY |  | NO |  | NO | NEAR THE BRIDGE WHERE MENARD CREEK CROSSES TEXAS HGWY 146 |  | LINE PIPE | PIPE |  | 1994 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 425070.6396 | 857539.1729 | NATURAL GAS LIQUID | 2 | 4985 | 0 | NO | NO | 10 | 0.5 | 52000 | WELDED |  | 1480 | 650 | YES | 8 | 2092 | 1 | 95 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | MICHAEL REAGAN | 8178777106 | THE FOLLOWING LOG IS THE OFFICIAL LOG OF EVENTS STARTING WITH THE LAST KNOWNNORMAL OPERATING CONDITIONS UP TO THE RETURN TO NORMAL OPERATING CONDITIONSPURSUANT TO TH LEAK BEING REPAIRED. THIS LEAK WAS CAUSED BY THIRD PARTYDAMAGE, IE;LANEY DIRECTIONAL DRILLING CO ATTEMPTING A DIRECTIONAL DRILLPARALLEL TO PANOLA PRODUCTS PIPELINE. LANEY DIRECTIONAL DRILLING CO. IS ASUBCONTRACTOR TO TROY PIPELINE PARALLELING PANOLA PRODUCTS PIPELINE CO. THEAFFECTED SECTION IS LOCATED APROX. NINE FEET EAST OF THE WEST EWDGE OF THETEXAS STATE HWY 146 RIGHT-OF-WAY. THE INCIDENT HAPPENED APPROX. 1.5 MILESNORTH OF RYE, TEXAS ON THE NORTH SIDE OF THE BRIDGE FOR MENARD CREEK. MENARDCREEK IS THE AREA OF THE DIRECTIONAL DRILL. A FULL ACCOUNT OF EVENTS ISATTACHED WITH THE ORIGINAL REPORT.
2017-09-29 08:50 | YES | NO | 19970057 | 1997-04-28 | 2371 | CINIZA PIPELINE INC | NO | 1997-04-01 |  | NM | MCKINLEY | HOSPAH | NO |  | NO | SECTION 1 TOWNSHIP 17N RANGE 9W |  | PUMPING STATION | SCRAPER TRAP |  | 1991 | OTHER | VALVE LEFT OPEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 137 | 135 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY ARMENTA | 5056328006 | A VALVE ON SCRAPER TRAP WAS OPENED TO DRAIN DOWN A LINE WHICH WAS BEINGCONNECTED TO A NEW TANK. AFTER TANK WAS PUT INTO SERVICE PRODUCT FILLED THELINE WHICH DRAINED INTO THE SUMP THROUGH THE OPEN VALVE. TRE AUTOMATIC SUMPPUMP WAS OFF AND LOCKED OUT DO TO CONSRUCTION. THE CRUDE OIL INTO ACONSTRUCTION DITCH. AN ESTIMATEED 135 BARRELS OF OIUL WAS BACK INTO THESTORAGE TANK.
2017-09-29 08:50 | YES | NO | 19970058 | 1997-04-28 | 2731 | CHEVRON PIPELINE CO | YES | 1997-04-07 | 1030 | TX | CULBERSON | VAN HORN | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2080 | 1473.5782 | 2972.8025 | CRUDE OIL | 1 | 50 | 1 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 920 | 40 | YES | 0 | 1180 | 0 | 81 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | W.J. JASPER | 2813635422 | THE SPILL WAS CAUSED BY EWXTERNAL CORROSION. THE LINE WASD TEMPORARILYREPAIRED WITH A FULL WRAP. PERMANENT REPAIRS INCLUDING PIPE REPLACEMENT ISSCHEDULED AT A FUTURE DATE.
2017-09-29 08:50 | YES | NO | 19970059 | 1997-04-28 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-03-27 | 1520 | IL | LOGAN |  | NO | NA | NO | SW1/4 NE1/4 SECTION 25 T19 NORTH R4 WEST IN LOGAN COUNTY IL. |  | LINE PIPE | PIPE |  | 1936 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 283380.4264 | 571692.7819 | FUEL OIL | 3 | 250 | 0 | NO | NO | 12.75 | 0.25 | 35000 | WELDED |  | 750 | 480 | YES | 8 | 983 | 0 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN S BALL | 9185883850 | AT 1250 HOURS ON MARCH 27,1997 THE ILLINOIS ENVIROMENTAL PROTECTION AGENCY METWITH THE WILLIAMS PIIPE LINE OPERATOR AT OUR MENARD TERMINAL TO INFORM HIM OFA SHEEN OF PRODUCTR ON A CREEK ABOUT 10 MILES NORTH OF THE TERMINAL.OPERATIONS CONTROL WAS CALLED BY THE WPL OPERATOR AND INSTRUCTED TO SHUT DOWNTHE #3-12 LINE RUNNING FROM WILMINGTON TO MADISONVILLE. OPERATIONS CONTROLIMMEDIATELY STOPPED THE LINE AND CLOSED THE MAINLINE VALVE AT MENARD TERMINAL.AT 1605 HOURS THE WPL OPERATOR CALLED OPERATIONS CONTROL TO CONFIMR THAT ITWAS WPL'S LEAK AND REPAIR THE LEAK.AT 1730 HRS. THE LEAK WAS FOUND BY WPLOPERATIONS PERSONNEL IN AN ABANDONED PIG SIG BOX. AT 1740 HRS. TWO BOOMS WEREDEPLOYED ON THE CREEK. THE MAINTENANCE CREW ARRIVED ON SITE AT 2130 HRS.DRAIN-UP OF THE LINE AT THE SITE BEGAN AT 2300 HRS. DUE TO THE FLAT TERRAINTHE DRAIN-UP CONTINUED UNTIL 1130 HRS. ON MARCH 29, 1997, AND REPAIR WASFINALIZED AT 1530 HRS. THE SAME DAY. AT APPROX. 0200 HRS. ON MARCH 28 1997INTERCEPTOR TRENCHES WERE DUG TO SLOW THE MIGRATION OF PRODUCT FROM THE GROUNDINTO THE CREEK. THE SPILL ON THE SURFACE OF THE CREEK WAS CONTAINED WITHIN THEFIRST 1/2 MILE OF THE CREEK BY THE MORNING OF MARCH 28 1997 BY USING SEVERALBOOMS. THE SITE REMEDIATION IS CONTINUING UNDER THE INSPECTION OF THE IEPA.WPL WAS DRANTED PERMISSION TO PERFORM INSITU BURNING OF THE FREE PRODUCT THATSURFACED ON THE WATERIN THE TRENCHES. PERMISSION IS PRESENTLY BEING SOUGHTFROM THE IEPA TO LAND-FARM THE CONTAMINATED SOIL REMOVED FROM THE LEAK SITE.IT IS EXPECTED THAT AN AIR SPARGING WILL BE INSTALLED AT THE SITE TO COMPLETETHE FINALREMEDIATIONPROCESS.
2017-09-29 08:50 | YES | NO | 19970060 | 1997-05-09 | 9175 | JAYHAWK PIPELINE CORP | YES | 1997-04-30 | 1515 | KS | SEDGWICK |  | NO |  | NO | NE OF SE1/4 SECTION 12, TOWNSHIP 26 SOUTH RANGE 1 WEST OF SEDGWICK COUNTY KANSAS. 2 MILES SOUTH OF VALLEY CENTER KANSAS. |  | PUMPING STATION | PIPE |  | 1984 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2833.8043 | 5716.9278 | CRUDE OIL | 1 | 260 | 250 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 275 | 50 | YES | 8 | 1400 | 0 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | FILL LINE TO TANK DEVELOPED AN EXTERNAL CORRRISION LEAK INSIDE DIKE. ALL OILWAS CONTAINED INSIDE DIKE AND RECOVERED. SOIL CONTAMINATION WILL BE REMEDIATEDINSIDE DIKE. THE PIPE WAS REPLACED WITH PRETESTED 10-INCH PIPE.
2017-09-29 08:50 | YES | NO | 19970061 | 1997-05-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1997-04-15 | 1610 | WI | LA FAYETTE |  | NO |  | NO | ONE MILE SOUTH OF WIOTA ON LARS ROAD, SECTION 31, TOWNSHIP 2N RANGE 5 EAST |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 73650 | 52177.421 | 105262.9335 | BUTANE | 2 | 2700 | 0 | YES | YES | 6 | 0.19 | 46000 | WELDED |  | 1273 | 600 | YES | 24 | 1746 | 0 | 60 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MICHEAL C PEARSON | 9185994043 | A THIRD PARTY HEAVY EQUIPMENT OPERATOR WAS EXCAVATING A PIT TO BURY DEBRIS ANDDURING THIS PROCESS PUNCTURED THE PIPELINE.
2017-09-29 08:50 | YES | NO | 19970062 | 1997-05-08 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1997-04-13 | 320 | TX | ECTOR |  | NO |  | NO | T&P RAILROAD COMPANY , BLOCK 42, SECTION 38, ECTOR COUNTY, TEXAS ONE MILE SOUTH OF DIXIE BLVD. AND I-20 |  | LINE PIPE | PIPE |  | 1961 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 22200 | 15727.6137 | 31728.9494 | BUTANE | 2 | 660 | 0 | NO | NO | 6.63 | 0.16 | 1978 | WELDED |  | 936 | 1254 | YES | 4 | 1170 | 10 | 85 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHEAL C. PEARSON | 9185994043 | THIRD PARTY DELIVERY VALVE WAS CLOSED WHEN PRODUCT SHIPMENT WAS INITIATED.THE PIPELINE OVER PRESSURED AND FAILED.
2017-09-29 08:50 | YES | NO | 19970063 | 1997-05-05 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1997-04-04 | 900 | TX | TERRY |  | NO |  | NO | MALLET TO SEMINOLE MAINLINE AT MILE POST 14-APPROX. 4 MILES NORTH AND 1 MILE WEST OF TOKIO, TEXAS WHICH IS APPROX. 20 MILES NORTH ODF SEAGRAVES, TEXAS. |  | LINE PIPE | PIPE |  | 1940 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | CRUDE OIL | 3 | 85 | 70 | NO | NO | 8.63 | 0.28 | 35000 | WELDED |  | 1200 | 100 | YES | 24 | 1500 | 2 | 71 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER |  | NO | YES | D.G. SCOTT | 2146585914 | TERRY COUNTY TEXAS MAINT. CREW WAS CLEANING OUT DRAINAGE DICHES WITH A ROADGRADER AND STRUCK PIPELINE WITH BLADE CAUYSING PIPELINE TO RUPTURE. THE COUNTYMAINT. CREW NOTIFIED MOBIL'S SEMINOLE AREA OFFICE WHO IN TURN NOTIFIED THEPIPELINE CONTROL CENTER IN DALLS. THE PIPELIONE WAS IMMEDIATELY SHUT DOWN ANDISOLATED. COMPANY MAINT. PERSONNEL WERE DISPATCHED TO SCENE TO INITIATECONTAINMENT AND CLEAN-UP OPERATIONS. PERMANENT REPAIRS WERE MADE BY REPLACINGDAMAGED SECTION OF PIPE.ALL REQUIRED NOTIFICATIONS WERE MADE IN ACCORDANCEWITH DOT REGULATIONS.
2017-09-29 08:50 | YES | NO | 19970064 | 1997-05-05 | 2814 | FINA PIPE LINE CO | NO | 1997-03-17 | 1915 | TX | MITCHELL |  | NO |  | NO | APPROX, 3 MI , SW OF COLORADO CITY, TEXAS; 0.5 MI, SE OF STATE HWY. 163/FM-1229 INTERSECTION. SECTION 60, BLK. 27, T&P RR SURVEY |  | LINE PIPE | NO DATA |  | 1926 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | 9564.0894 | 19294.6314 | CRUDE OIL | 1 | 234 | 214 | NO | NO | 10 | 0.28 | 0 | THREADED |  | 360 | 100 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED | 9152639256 | PROPERTY OWNER (HOBIE BOLIN) DISCOVERED LEAK IN LATE P.M. , MARCH 17TH.MR.BOLIN BELIEVED THE LEAK TO HAVE ORIGINATED FROM CHEVRON'S PIPELINE, WHICH ALSOCROSSES HIS PROPERTY WITHIN THE SAME ROW AS THE FINA PIPELINE, THEREFORE BOLINCROSSES HIS PROPERTY WITHIN THE SAME ROW AS THE FINA PIPELINE CALLED VERNONDUNCAN WHO IS WITH CHEVRON P/L.DUNCAN THEN CALLED FINA'S PIPELINE MANAGER,CHUCK MARTIN, AT APPROX. 1915 HRS. MR. MARTIN IMMEDIATELY CONTACTED WESLEYMCINTOSH DISPATCHED HIM TO THE PROPERTY. MR MARTIN ALSO CALLED THE BIG SPRINGPIPELINE CONTROL CENTER TO SHUT DOWN WESTBROOK STATION WHICH FEEDS THEPIPELINE THAT RUPTURED:TIME OF THIS CALL WAS 1935HRS. MR. MCINTOSH PROCEEDEDTO THE PROPERTY, A DISTANCE OF APPROX. 25MI. BY 2230 MCINTOSH HAD 2 CLAMPSINSTALLED ON THE PIPELINE AND ALL LEAKEGE STOPPED. ALL NOTIFICATIONS WERE MADETO APPROPIATE GOV. AGENCIES BETWEEN 2124-2225 HRS. ON 2-17-96. LANDOWNER BOLINWOULD NOT ALLOW VACUM EQUIPMENT ON HIS PROPERTY BEFORE 0730.ON 3/18, SO THEACTUAL CLEANUP BEGAN SHORTLY THEREAFTER WITH THE USE OF 2, 120BBL. VACUMTRANSPORTS. ALL CLEANUP ACTIVITIES (EXCEPT FOR SOIL REMEDIATION)WAS COMPLETEDBY THE END OF THE DAY, FRIDAY, 3/21/97. APPROX. 374(8.5 JOINTS) OF 10"DIAMETER PIPE WAS REPLACED BY 6" DIAMETER PIPE DURING THE WEEK OF 3/24/97.
2017-09-29 08:50 | YES | NO | 19970065 | 1997-05-13 | 12127 | MARATHON PIPE LINE CO | NO | 1997-03-24 | 915 |  |  |  | YES | 28 23'31.620:92 31 01.963 | NO | ABOUT 3 MILES SOUTHWEST OF HALL HOUSTON'S PLATFORM IN VERMILION BLOCK 299 |  | LINE PIPE | BOLTED FITTING |  | 1974 | OTHER | LEAKING GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 106267.6599 | 214384.7932 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 8 | 0.5 | 35000 | FLANGED |  | 2920 | 800 | NO | 0 | 0 | 0 | 74 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.L. WIELAND | 7132962426 | AT APROX. 0915 HRS. ON MARCH 24, 1997 A SLIGHT RAINBOW SHEEN (ESTIMATED AT 1.5GALLONS) WAS OBSERVED IN THE VICNITY OF THE SUBSEA ASSEMBLY OF MARTATHON PIPELINE'S 8" EAST CAMERON PIPELINE SYSTEM IN VERMILION BLOCK 299. PRODUCINGPLATFORM OPERATYORS WERE REQUESTED TO SHUT DOWN THE SYSTEM, SHUTDOWN WASCOMPLETE AT APPROX. 1000 FRS. THE MINOR LEAK WAS FOUND TO BE COMING FROM A 4"BLIND FLANGE JOINT AT A FUTURE TIE-I CONNECTION ASSEMBLY. THE 4" BLIND FLANGE,A SPOOL PIECE CHECK VALVE AND VALVE ON THIS ASSEMNLY WERE REMOVED AND REPLACEDWITH A NEW 4" VALVE AND BLIND. THE SPOOL PIECE APPEARED TO HAVE BEEN SLIGHTYLYBENT BY A FISHERMAN'S NET OR ANCHOR CABLE. SANBAGS WERE PLACED OVER THE ENTIREASSEMBLY TP PROVIDE PROTECTION AND THE PIPELINE WAS RESTARTED AT APPROX. 1215HRS. ON MARCH 27.
2017-09-29 08:50 | YES | NO | 19970066 | 1997-05-16 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1997-04-18 | 1200 | NY | ONONDAGA |  | NO |  | NO | SEE ATTACHED DRAWING #11773-A |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 53133.83 | 107192.3966 | GASOLINE | 3 | 12 | 8 | NO | NO | 10 | 0.2 | 1740 | WELDED |  | 910 | 0 | YES | 24 | 1190 | 5 | 68 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL LARKIN | 6107704507 | ON FRIDAY APRIL 18, 1997 A MANINTENANCE CREW WAS PERFORMING A ROUTINE VEHICLEPATROL WHEN THEY NOTICED A SMALL PATCH OF DEAD GRASS AROUND A CASING VENTPIPE. AFTER FURTHER INVESTIGATOIN THE RELEASE WAS LOCATED IN THE LINE PIPEWITHIN THE CASING UNDER MUD MILL ROAD. THE DEFECTIVE LINE PIPE WS SUBSEQUENTLYREMOVED FROM THE CASING AND A SMALL PIN HOILE WAS DISCOVERED. THE DEFECTIVELINE PIPE WAS CUT OUT AND REPLACED WITH A CERTIFIED HYDROSTATICALLY TESTEEDLINE PIPE SECTION SPANNING THE CASED ROADWAY. ALL APLLICABLE AGHENCIES WERENOTIFIED AND ALL RELEASED PRODUCT WAS CONTAINED IN THE IMMEDIATE AREA.RECOVERY AND CLEANUP ACTIVITIES WERE CONDUCETD UNDER THE SUPERVISION OF THENY PUBLIC SERVICE COMMISION AND THE NY DEPT. FO ENVIROMENTAL CONSERVATION.
2017-09-29 08:50 | YES | NO | 19970067 | 1997-05-15 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1997-04-10 | 855 | OK | GRANT |  | NO |  | NO | EAST SIDE OF RAILROAD TRACKS- SEC. 5 TOWNSHIP 26 NORTH, RANGE 5 WEST IN GRANT COUNTY OKLAHOMA |  | LINE PIPE | PIPE |  | 1972 | OTHER | CORROSION, EXTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 24795.7873 | 50023.1184 | NATURAL GAS LIQUID | 2 | 568 | 70 | NO | NO | 6.63 | 0.16 | 1978 | WELDED |  | 1331 | 1370 | YES | 24 | 1750 | 0 | 72 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB AEBI | 4053952377 | THE LINE WAS STARTED A 07:00 IN THE MORNING OF 4/10/1997. AT 08:55 THE PMCNOTICED A PRESSURE DROP. THE PIPELINE WAS SHUT DOWN AND THE VALVES CLOSED AT09:15. KOCH PERSONNEL WAS SENT SOUTH ALONG THE PIPLEIN APPROX. 1/4 MILE WHERETHE RELEASE WAS SPOTTED. THE OKLAHOMA CORP. COMMISION WAS NOTIIFED AT 10:20 ,THE NATIONAL RESPONSE CENTER AT 10:21 AND THE UNION PACIFIC RAILROAD AT 10:28.THE PIPELINE WAS REPAIRED AND RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19970068 | 1997-05-14 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1997-04-17 | 1950 | AR | PHILLIPS |  | NO |  | NO | APPROX. 2 MILES NORTH OF LAKEVIEW |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 27000 | 19128.1788 | 38589.2628 | DIESEL FUEL | 3 | 275 | 250 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ERNEST HAGAN | 7137593845 | ON FRIDAY , APRIL 17, 1997 AT APPROX. 1950 HRS. CDT , TEPPCO'S 10" LILNE P-31WAS STRUCK BY A FARM IMPLEMENT USED FOR BUILDING RICE FEILD LEVEES. THISINCIDENT RESULTED IN THE RELEASE OF 275 BARRELS OF NUMEBER 2 DEISEL FUEL. UPONNOTIFICATION, THE EMRGENCY PLAN WAS IMMEDIATLY INITIATED WITH PERSONNEL ANDRESPONSER EQUIPMENT MOBILIZED. THE PIPELINE WAS ISOLATED BY CLOSING BLOCKVALVES NEAR THE INCIDENT SITE. DAMGED PIPE WAS REMOVED AND NEW PIPE PLACEDINTO THE SYSTEM. TEPPCO' RESTARTED THE SYSTEM ON APRIL 18, 1997. REMDIATION TOTHE SURRONDING TERAIN IS BEING COMPLETED TO THE SATISFACTION OF THE STATEENVIROMENTAL AGENCY.
2017-09-29 08:50 | YES | NO | 19970069 | 1997-05-14 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1997-04-15 | 1106 | AR | ARKANSAS |  | NO |  | NO | APPROX. 1 MILE SOUTHWEST OF DELUCE, AR. |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 17711.2767 | 35730.7989 | DIESEL FUEL | 3 | 250 | 230 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS | AGRICULTURAL IMPLEMENT | Null | ONE CALL |  | NO | NO | ERNSET HAGAN | 7137593845
2017-09-29 08:50 | YES | NO | 19970070 | 1997-05-19 | 30903 | ARCO PIPE LINE COMPANY | NO | 1997-04-23 | 1220 | CA | LONG BEACH | LOS ANGELES | NO |  | NO | WEST INTERSECTION OF SPRING AND JUNIPERO STREETS, SIGNAL HILL AREA OF LONG BEACH |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 159401.4899 | 321577.1898 | CRUDE OIL | 1 | 58 | 58 | NO | NO | 6 | 0.37 | 35000 | WELDED |  | 600 | 400 | YES | 4 | 870 | 4 | 90 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAN HISEY | 5624289000 | A NITROGEN PURGE PROJECT WAS UNDERWAY FOR LINE 8. DURING THE PURGE PERSONNELWERE DISPATCHED TO PATROL THE LINE. OIL WAS OBSERVED COMING UP FROM BELOW THESTREET AT ASPHALT/CURB JUNCTION. THE PURGE WAS SHUT DOWN . EXCAVATION REVEALEDTHAT THE OIL WAS RELEASED FROM AN INTERNAL CORROSION HOLE ON A 6 " LATERAL .THE 6" INCH LATERAL WAS A DEAD-LEG(IT ENDED INTO A CLOSED AND BLINDED VALVE)OFF OF THE MAIN LINE.
2017-09-29 08:50 | YES | NO | 19970071 | 1997-05-19 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-04-16 | 1730 | KS | WYANDOTTE |  | NO |  | NO | THE BREAK WAS LOPCATED IN THE SW1/4 OF SECTION 24, T1OS, R24E IN WYANDOTTE COUNTY, KANSAS |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 42507.064 | 85753.9173 | GASOLINE | 3 | 120 | 90 | NO | NO | 10.75 | 0.2 | 46000 | WELDED |  | 1150 | 150 | YES | 10 | 1597 | 0 | 91 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RICHARD HARRIS | 9185883454 | ON APRIL 16 AT 1722 HRS. FRANK LAVENDER A THIRD PARTYLANDOWNER STRUCK WILLIAMS PIPE LINE'S #6-10 AT MILE POST 163 WHILE OPERATING AFRONT END LOADER. FRANK LAVENDER CALLED 911 AT 1732 HRS. THE FIRE DEPT.ARRIVED ON THE SITE AT 1739 HRS. THEY EVALUATED THE SITUATION AND THEN CALLEDWPL'S FAIRFAX PUMP STATION AT 1745HRS. TO INFORM THEM THAT ONE OF THEIR LINESWAS SPRAYING EITHER GASOLINE OR NATRUAL GAS.WPL FAIRFAX PUMP STATIONDISPATACHED MAINLINE MAINTENCE PERSONNEL TO INVESTIGATE AT 1750 HRS. THEMAINLINE MAINTENANCE PERSONNEL INFORMED THE STATION PERSONNEL THAT THE 6-10LINE. OPERATIONS CONTROL SHUT DOWN THE ORIGINATING PUMP STATION AT 1804 HRS.AND CLOSED THE KANSAS CITY DELIVERY VALVE AT 1808HRS. THEY FOUND THAT THE FIREDEPT. HAD ALREADY CONTAINED THE RELEASE. OPERATIONS CONTROL OPENED THE KANSASCITY DELIVERY VALVE AT MILEPOST 156 AT 1853 HRS. MAINTENANCE PERSONNEL STOPPEDTHE LEAK AT 2315 HRS. TH ELINE WAS REPAIRED ON 04\17\1997 AT 1730 HRS. ANDRETURNED TO SERVICE AT 1800 HRS. THE IMPACTED SOILS WILL BE REMEDIATED TOKANSAS DEPT. OF HEALTH AND SAFETY (KDHE) ACCEPTABLE LEVELS BY DISCING IN PLACEAND EXCAVATING AND LAND FARMING. FIELD MEASUREMENTS AND LABORATORYCONFIRMATION SAMPLES WILL BE USED TO DOCUMENT REMEDIATION OF THE IMPACTEDSOILS. THE REMEDIATION PROCESS SHOULD BE COMPLETE BY THE END OF THE YEAR.
2017-09-29 08:50 | YES | NO | 19970072 | 1997-05-21 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-04-10 | 1700 | WY | PLATTE |  | NO |  | NO | CONOCO PIPELINE CO.PUMP STATION AND TANK FARM, T26N,R65W, SECTION 17 |  | TANK FARM | PUMP |  | 1981 | OTHER | SEAL FAILURE ON BOOSTER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 1771.1277 | 3573.0799 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY BEGGS | 3036494090 | DURING A DELIVERY OUT OF TANK 1158, THE THRUST BEARING WENT OUT ON THE BOOSTERPUMP. THIS CAUSED A VIBRATION THAT CAUSED THE LOCKNUT ON THE THRUST BEARINGTO BACK OFF OPENING A GAP BETWEEN THE SEAL FACES.
2017-09-29 08:50 | YES | NO | 19970073 | 1997-05-30 | 4805 | EXPLORER PIPELINE CO | YES | 1997-05-02 | 920 | OK | TULSA | GLENPOOL | NO |  | NO | TANK FARM AT INTERSECTION OF 126TH ST. SOUTH, AND HWY.75 GLENPOOL, OKLAHOMA |  | TANK FARM | TANK |  | 1971 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 100 | 90 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RODNEY E SANDS | 9184935106 | AT 0920 HOURS ON MAY 2, 1997 AN EXPLORER PIPLEINE CO. OPERATIONS TECHNICIANDRAINING WATER FROM OPEN FLOATING ROOF TANKS AT GLENPOOL TANK FARM NOTICEDVAPOR COMING FROM THE VICINITY OF GASOLINE TANK 321. HE BEGAN SEARCHING THEAREA DOR THE SOURCE OF VAPORS. AT 0930 HOURS THE GLENPOOL FIRE DEPT. ARRIVEDIN RESPONSE TO A REPORT OF VAPORS FROM A NEARBY RESIDENT. AT 0935 PRODUCT WASDICOVERED LEAKING FROM THE BOTTOM OF THE OPEN FLOATING ROOF TANK 322. THEEXPLORER EMERGENCY RESPONSE TEAM CASCADE SYSTEM OF NOTIFICATION WAS INITIATED,THE ROAD ADJACENT TO THE TANK FARM WAS BLOCKED BY THE FIRE DEPT., ROOF DRAINSAND DIKE DRAINS WERE CLOSED AND GRAVITY FLOW EVACUATION OF TANK 322 INTO OTHEREMPTY TANKS WAS STARTED. VACUUM TRUCKS AND MAINTENANCE CONTRACTOR WEREDISPATCHED TO THE SITE TO RECOVER PRODUCT AS IT ESCAPED FROM THE TANK ANDCLEAN-UP PRODUCT RELEASED INDE THE TANK DIKE. ALL PRODUCT WAS CONTAINED WITHINTHE TANK DIKE AREA. A TOTAL OF 87,627 BARRELS OF PRODUCT WAS TRANSFERRED BYGRAVITY FLOW AND BOODSTER PUMP TRANSFERFROM THE TANK. EVACUATION OF THE TANKWAS COMPLETED BY 1345 HOURS THE SAME DAY AS WELL AS RECOVERY AND CLEAN-UP OFPRODUCT RELEASED IN THE TANK DIKE. IT WAS ESTIMATED THAT 100 BARRELS ESCAPEDFROM THE TANK AND 90 BARRELS WAS RECOVERED. ON MAY 3, 1997 INTERNAL CLEANINGOF THE TANK WAS STARTED. THE CAUSE OF FAILURE WAS DETERMIONED TO BE A CRAK INTHE TANK FLOOR APRROX. 1/2 INCH IN FROM THE SHELL WALL. THE CRACK WAS IN ANAREA AHERE THE PLATE THICKNESS HAD ,BEEN REDUCED BY INTERNAL CORROSION. REPAIRBY REPLACEMENT OF ALL BOTTOM SKETCH PLATES IS IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19970074 | 1997-05-29 | 3445 | DIXIE PIPELINE | YES | 1997-05-08 | 915 | MS | FORREST | PETAL | NO |  | NO | 1.5 MI NORTH OF HATTIEBURG ON US HWY 11 WITHIN THE DIXIE PIPELINE CO. |  | NO DATA | OTHER | 1/2 " SS TUBING UNION |  | OTHER | TUBING FITTING IMPROPERLY | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 177.1128 | 357.308 | L. P. G. | 2 | 10 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | P.A. LOGSDON | 5046544137 | HEAVY EQUIPMENT AND EXCAVATING EQUIPMENT PREVIOUSLY OPERATING IN THE VICINITYCHANGED THE SOIL STRESES ON THE FITTING AND TUBING ALLOWING THE TUBING TOSEPERATE FROM THE FITTIN. THE FITTING WAS NOT PROPERLY ASSEMBLED WHENINTSALLED. DIXIE PERSONELL WERE ON SITE AND IMMEDIATLEY TOOK STEPS TO PROTECTTHE PUBLIC AND COMTROL THE RELEASES BY CLOSING ISOLATING VALVES AND BLOCKINGTRAFFIC ON THE ADJACENT HIGHWAY.
2017-09-29 08:50 | YES | NO | 19970076 | 1997-05-27 | 10012 | KANEB PIPELINE CO | YES | 1997-05-07 | 2030 | KS | MC PHERSON |  | NO |  | NO | SW1/4, NW1/4, SECTION 4, TOWNSHIP 20 SOUTH, RANGE 3 WEST AT MCPHERSON STATION |  | PUMPING STATION | VALVE |  | 1973 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 3 | 140 | 110 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES REITER | 3612621408 | WHILE PERFORMING A ROUTINE MAINTENCE A M/L DRAIN VALVE WAS LEFT OPEN. UPONSTARTUP PRODUCT DRAINED CAUSING A SUMP OVERFILL. CONTROL DEVICES FAILED TOWORK.
2017-09-29 08:50 | YES | NO | 19970077 | 1997-06-02 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-04-30 | 745 | KS | CRAWFORD |  | NO |  | NO | THE LEAK WAS LOCATED IN THE SW 1/4 OF THE SE 1/4 OF T31S, R25E IN CRAWFORD COUNTY, KS |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | GASOLINE | 3 | 50 | 10 | NO | NO | 12 | 0.3 | 35000 | OTHER |  | 730 | 150 | YES | 8 | 968 | 7 | 83 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD HARRIS | 9185883850 | AT 0745 ON WED. 04/30/1997 THE WILLIAMS PIPELINE IOLA MAINTENACE CREWDICOVERED CONTAMINATED SOIL AND GASOLINE NEAR MILE POST 214 WHLE PERFORMINGPIPELINE RECONDITIONNG WORK. OPERATIONS CONTROL WAS IMMEDIATELY NOTIFIED OFTHE CONDITION AND ASKED TO REMOVE PRESSURE FROM THE LINE. THIS WASACCOMPLISHED BY SHUTTING DOWN THE ORIGINATING PU,P STATION AT TULSA ANDSALLOWIG THE DOWNSTREAM PUMP SATION AT SHELPDON TO REMAIN ON LINE TO PUMPPRODUCT AWAY FROM THE LEAK SITE UINTIL THE PUMPING UNIT WENT DOWN ON LOWSUCTION PRESSURE. THE GATE VALVES WERE THEN CLOSED AT MILE POST 207 AND 218ISOLATING THE SUSPECTED LEAK AT APPROX. 0845 HRS. VACUMM TRUCKS ARRIVED ONSITE AT APPROX. 1330 HRS. TO BEGIN PICKING UP FREE PRODUCT THAT HAD CREWACCUMULAETD IN DITCHES DUGWITH THE BACKHOE THAT WAS ALREADY ON SITE WITH THERECONDITIONG CREW. ADDITIONAL TRACKHOES ANDDUMP TRUCKS ARRIVED ON THE SITE ATAPPROX. 1420 HRS. TO ASSIST WITH EXCAVATING THE LINE AND STOCKPILING THECONTAMINATED SOIL FOR LAND FARMING. HE ACTUAL LEAK LOCATION WAS FOUND AT ALINE DEPTH OF TWELEVE TO FIFTHTEEN FEET AT APPROX. 22230 HRS. THE LEAKS TWOSEEPERS WERE IMMEDIATLEY CLAMPED OFF FOR THE LATER PERMANENT REPAIRS WHICHOCCURRED ON MONDAY ,MAY 5 1997. THE IMPACTED SOILS WILL BE REMEDIATED TOKANSAS DEPT. OF HEALTH AND SAFETY ACCEPTABLE LEVELS BY DISCING IN PLACE ANDEXCAVATING AND LAND FARMING. FIELD MEASUREMENTS AND LABORATORY CONFIRMATIONSSAMPLES WILL BE USED TO DOCUMENT REMEDIATION OF HTE OMPACTED SOILS AS REQUIREDBY THE KDHE. THE REMEDIATION PROCESS SHOPULD BE COMPLETE BY THE END OF THEYEAR.
2017-09-29 08:50 | YES | NO | 19970078 | 1997-06-09 | 30907 | ASHLAND PETROLEUM CO. | NO | 1997-05-04 | 28 | OH | MORROW |  | NO |  | NO | APPOX. 3/4 MILE WEST OF SR 309 AND 1/2 MILE NORTH OF SR 288 |  | LINE PIPE | PIPE |  | 1952 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 531338.2995 | 1071923.9661 | CRUDE OIL | 1 | 1998 | 1280 | NO | NO | 12 | 0.38 | 24000 | WELDED |  | 605 | 553 | YES | 24 | 770 | 0 | 72 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TIFFANY DONNULLY | 6063293909 | AT APPROX. 11:00 PM ON MAY 3 1997 THE ASHLAND CONTROL CENTER NOTIFIED THELEXINGTON OFFICE OF A POSSIBLE PIPELINE LEAK. ASHLAND OPERATIONS PERSONNELWERE DISPATCHED TO CLOSE MAINLINE BLOCK VALVES ALONG THE PIPELINE. AT 12:28AM ON MAY 4 , 1997 FILED PERSONNEL DISCOVERED A LEAK ON A 12" CRUDE OILPIPELINE IN A FIELD AT THE COBEY FARM INSTRUCTED OF SEVERAL SECTIONS RUNSFROM A TANK FARM IN LIMA TO A REFINERY IN CANTON. EMERGENCY RESPONSE PERSONNELWERE DISPATCHED TO THE SITE OF THE LEAK IMMEDIATELY FOLLOWING ITS DETECTION.THE SURROUNDING AREA WAS SURVEYED AND THE EXTENT OF THE LEAK WAS QUICKLYASSESSED. RESPONSE CREWS IDENTIFIED SEVERAL SMALL DITCHES AND UNNAMEDWATERWAYS WHICH AFFECTED, AND TOOK REACTIVE MEASURES TO CONTAIN THE SPILL.BOOMS AND SIPHON DRAINS WERE INSTALLED AND PRODUCT WAS COLLECTED AND TAKEN TONEARBY PORTABLE HOLDING TANKS. A PRELIMINARY INVESTIGATION REVEALED A MATERIALDEFECT AS THE PROBABLE CAUSE OF THE FAILURE. THE DEFECTIVE JOINT OF PIPE WASREPLACED WITH PRE-TESTED, ERW PIPE AND THE PIPELINE SYSTEM WAS RETURNED TOSERVICE ON MAY 5, 1997, IN PROGRESSIVE STAGES
2017-09-29 08:50 | YES | NO | 19970079 | 1997-06-04 | 443 | AMOCO PIPELINE CO | YES | 1997-04-26 | 1500 | ND | KIDDER |  | NO |  | NO | SECTION 30 TOWNSHP 139N, RANGE 74W |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | GASOLINE | 1 | 943 | 0 | NO | NO | 10 | 0.28 | 42000 | WELDED |  | 1570 | 1000 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | SANDI BRAUN | 6309903781 | A DAMAGED AREA OF PIPE CONSISTING OF A SCRAPE/DENT DEVELOPED INTO A SMALLHAIRLINE CRACK APPROX. 3 1/2" LONG. THE SCRAPE/DENT WAS CAUSED BY OUTSIDEFORCE HOWEVER, IT IS CERTAIN WHETHER THAT OUTSIDE FORCE OCCURRED AS A RESUKTOF MILL DAMAGE, ORIGINAL CONSTRUCTION DAMAGE, OR A THIRD PARTY HIT.
2017-09-29 08:50 | YES | NO | 19970080 | 1997-06-16 | 26041 | GATX TERMINALS CORP | NO | 1997-05-16 | 2300 | CA | CARSON |  | NO |  | NO | GATX CARSON TERMINAL- 2000 EAST SEPULVEDA BLVD. CARSON CA |  | TANK FARM | TANK |  | 1924 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10626.766 | 21438.4793 | CRUDE OIL | 1 | 120 | 118 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID KINGSTON | 3105187705 | THE SPILL WAS A DIRECT RESULT OF NOT USING TH ECORRECT GAUGE HEIGHT FOR THETANK. A HERMATIC GAUGING APPARATUS IS SUED IN MOST CASES TO GAUGE THE CRUDETANK. THE GAUGING POINT OF THE MMC IS 16.5 ABOVE THE TANKS POSTED GAUGEHEIGHT. TO ACCOUNT FOR THIS DIFFERENCE, A SECOND GAUGE HEIGHT IS POOSTED ONTHE TANK FOR THE MMC. WHILE GAUGING THE TANK WITHA THIRD PARTY INSPECTOR, ASHIFT SUPERVISOR NOTICED THE ORIGINAL GAUGE HEIGHT POSTING BUT DID NOT NOTICETHE SECOND POSTING OF THE HERMATIC GAUGE HEIGHT. AFTER CONFRIMING WITH THEMEASUREMENT ANALYST THAT THE POSTD GAUGE HEIGHT WAS CORRECT, THE SHIFTSUPERVISOR PROCEEDED TO CHANGE THE GAUGE HEIGHT BASED ON THE MMC HEIGHT ANDUNDERSTATING OF THE LEVEL OF THE PRODUCT IN THE TANK WAS NOW UNDERSTATED BY16.5 THE NEXT TIME THE TANK WAS FILLED WOULD RESULT IN A TANK OVERFILL. GATXPROCEDURES HAVE BEEN CHANGED TO PERMIT ONLY THYE TERMINAL SUPERINTENDENT ORTHE MEASUREMENT ANALYST TO AUTHORIZE GAUGE HEIGHT CHANGES AND ALL VARECADJUSTMENTS MUST BE CONFIRMED BY AN INNAGE HAND GAUGE.
2017-09-29 08:50 | YES | NO | 19970081 | 1997-06-13 | 18273 | SHELL PIPELINE CORP | YES | 1997-05-12 | 1100 | LA | PLAQUEMINES PARISH |  | NO |  | NO | DELTA 20 INCH PIPELINE STATION 785+74, MILE 54.2 |  | LINE PIPE | LONGITUDINAL WELD |  | 1958 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 325000 | 230246.5965 | 464500.3853 | CRUDE OIL | 1 | 4 | 0 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 832 | 450 | YES | 24 | 1040 | 0 | 59 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | S.J. LANDERVILLE | 7132412953
2017-09-29 08:50 | YES | NO | 19970082 | 1997-06-12 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-04-28 | 1719 | OK | COTTON |  | NO |  | NO | SW/4 SECTION 8, TOWNSHIP 5 SOUTH RANGE 10 WEST COTTON COUNTY |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | SUBSIDENCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7084.5107 | 14292.3195 | CRUDE OIL | 1 | 500 | 0 | NO | NO | 12 | 0.25 | 46000 | WELDED |  | 1300 | 600 | YES | 8 | 1625 | 0 | 90 | NO DATA | Null | Null | NO DATA |  | SUBSIDENCE |  | Null | NO DATA |  | Null | Null | VANCE WEBB | 4057674845 | ON APRIL 18 1997 AT 1537 HRS OPERATIONS CONSOLE 2 OF THE CONOCO PIPELINE OILMOVEMENT CENTER IN HOUSTON TX RECIEVED VIA AUTOMATED MONITORING EQUIPMENT ANINDICATION THAT AN ABNORMAL OPERATING CONDITION MAY EXIST ON THE WICHITAFALLS PUMP STATION AND VERIFYING THAT AN ABNORMAL CONDITION DID EXIST ,PROCEDURES WERE IMPLEMENTED TO SHUT DOWN THE PIPELINE SYSTEM AT 1556 HRS.EMERGENCY CREWS WERE DISPATCHED FROM OKLAHOMA CITY AND WICHITA FALLS TX, TOISOLATE THE PIPELINE AND LOOK FOR THE POSSIBLE LINE FAILURE. THE AERIAL PATROLUNIT CONFIRMED A LINE FAILURE IN THE RED RIVER CROSSING AT 1715 HRS. THE REDRIVER WAS AT A HIGHER THAN AVERAGE WATER LEVEL AND FLOW RATE AND BECAUSE OFTHIS THE RELEASED CRUDE OIL APPEARED TO REMAIN NEAR THE CENTER OF THE CHANNELAND WAS ONLY VISIBLE IN AN AREA APPROX. 500 FT LONG BY 4FT WIDE. THE QUANITYOF THE RELEASE WAS ESTIMATED TO BE 500BBLS. EMERGENCY CREWS WERE DISPATCHEDTO LOACTIONS. DOWN STREAM OF THE RELEASE TO SETUP DIVERSION AND CONTAINMENTBOOM IN AN ATTEMPT TO MITIGATE THE POSSIBLE IMPACT OF RELEASED CRUDE OIL.HOWEVER , NO OIL WAS EVER ENCOUNTERED AT ANY OF THE BOOM LOCATIONS. THE AERIALPATROL FLEW SEVERAL RECONNAISSANCE FLIGHTS FOLLOWING THE RIVER FROM THERELEASE SITE TO LAKE TEXOMA, NO VISIBLE OIL WAS FOUND WITH THE EXCEPTION OFTHAT FOUND AT THE RELEASE SITE ON THE FIRST FLIGHT. PERIODIC OVER FLIGHTS OFTHE AREA WERE CONTINUED FOR TWO DAYS WITH NO FURTHER SIGHTINGS OF OIL. DUE TOTHE LOCATION OF THE LINE FAILURE AND THE HIGH WATER LEVEL AND FAST CURRENTS OFTHE RIVER, CPL ELECTED TO ISOLATE, PURGE, AND CAP THE EXISTING RIVER CROSSING.A NEW DIRECTIONALLY DRILLED CROSSING WILL BE INSTALLED RATHER THAN ATTEMPTINGTO REPAIR THE OLD ONE. THE NEW RIVER CROSSING WILL BE APPROX. 40 FEET BELOWTHE FLUIDIZED BED OF THE RIVER AND BE APPROX. 3000 FEET IN LENGTH. AT THISTIME THE EXACT CAUSE OF THE FAILURE IS NOT KNOWN. OPERATINAL ERROR ANDPRESSURE RELATED CAUSES HAVE BEEN RULED OUT. SUBSIDENCE OF THE RIVER BED ANDCONSEQUENT PIPE MOVEMENT OR DEBRIS IMPACT MAY BE THE CAUSE OF THE FAILURE.HOWEVER INVESTIGATION BY DIVERS REVEALED THAT THE LINE WAS NOT ABLE TO LOCATEAND EXAMINE THE PIPELINE IT WAS NOT POSSIBLE TO DETERMINE THE TYPE OF FAILURETHAT OCCURED. BECAUSE THE NEW DIRECTIONALLY DRILLED CROSSING WILL NOT BEEXPOSED TO ANY OF THE FORCES THAT MAY HAVE CONTRIBUTED TO THE FAILURE OF THEOLD RIVER CROSSING, NO FURTHER INVESTIGATION OF THE INCIDENT IS PLANNED ATTHIS TIME.
2017-09-29 08:50 | YES | NO | 19970083 | 1997-06-06 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-05-06 | 2120 | WY | SUMMIT |  | NO |  | NO | T6N, R8E, NE1/4 SECTION 20 APPROX 3/4 MILE OF THE UTAH -WYOMING BORDER |  | LINE PIPE | PIPE |  | 1954 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 305000 | 216077.5751 | 435915.7462 | GASOLINE | 3 | 1386 | 158 | NO | NO | 8.63 | 0.32 | 42000 | WELDED |  | 2258 | 1850 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY BEGGS | 3036494090 | ON MAY 6 1997 APPROX. 2120 HRS CONOCO PIPELINE OPERATIONS IN HOUSTON TX,DETECTED A PRESSURE DROP ON PIONEEL PIPELINE IN THE AREA OF THE WYOMING-UTAHBORDER. OPERATIONS REMOTELY SHUT DOWN AND BLOKCED IN THR PIPELINE AND CALLEDOUT LOCAL RESPONSE PERSONNEL TO INVESTIGATE. AT APPROX. 0030 HRS MAY 7 1997OPERATIONS PERSONNEL DISCOVERED A GASOLKINE LEAK FROM THE EIGHT INCH PIPELINEAT A BLOCK VAVE SITEIN SUMMIT COUNTY UTAH APPROX. 3/4 MILE EAST OF THEUTAH-WYOMING BORDER NEAR EVANSTON, WY. THE PIPELKINE HAD RUPTURED RESULTING INAPPROX. 1386 BARRELS OF UNLEADED GAS BEING RELEASED TO THE GROUND. THE FAILUREWAS A OVERBEND AT AN ABOVE GROUND BLOCK VALVE SITE.VISUAL APPEARENCE DOES NOTINDICATE A ERW SEAM FAILURE. WHILE THE VAST MAJORITY OF THIS MATERIAL SOAKEDINTO THE SANDY SOLID NEAR THE RELEASE SITE, A PORTION OF THE PRODUCT RAN DOWNAN UNAMED DRY WASH AND ENTERED WASATCH CREEK. THE WASATCH CREEK IS A SMALLCREEK THAT COMBINES WITH YELLOW CREEK IN WYOMING PRIOR TO EMPTYING INTO THEBEAR RIVER IN WYOMING. RESPONSE PERSONNEL DEPLOYED SEVERAL CONTAINMENT BOOMSIN THE WASATCH CREEK ONE BOOM IN YELLOW CREEK AND ANOTHER IN THE BEAR RIVER. ASMALL AMOUNT OF PRODUCT WAS VACUMMED UP AT THE FIRST DOWNSTRAM BOOM. NOINDICATION OF PRODUCT WAS DETECTED IN YELLOW CREEK OR BEAR RIVER.
2017-09-29 08:50 | YES | NO | 19970084 | 1997-06-06 | 19226 | TEXACO PIPELINE INC | YES | 1997-05-16 | 1630 |  |  |  | YES | LAT 29/14/49N;LONG 90/27/ | NO | WATERWAY-LAKE BARRE, TERREBONNE PARISH LA |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 708451.066 | 1429231.9548 | CRUDE OIL | 1 | 5000 | 2495 | NO | NO | 16 | 0.31 | 1638 | WELDED |  | 1180 | 1120 | YES | 24 | 1476 | 0 | 76 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | M.O. CLEMENT | 5048733411 | ON 5/16/97 AT 1630 HRS, SPILL NOTED BY TPLI EMPLOYEE. REPORTED TO DISTRICTMANAGER. SHUT IN PIPELINE SYSTEM. CONTRACTED CENAC ENVIROMENTAL AS CLEANUPOSRO. DEPLOYED BOOM AND SHALLOW WATER SKIMMERS. CLAMPED AFFECTED PIPE WITHDAPSIT CLAMP AND DISPLACED PIPELINE WITH WATER FOR BIG INCH COLD FORGE REPAIR.FOUND 30.5 X 1 15/16 LONGITUDINAL OPENING LOCATED AT A 5"X8" DENT ON THEPIPELINE CAUSED BY UNKNOWN EXTERNAL MECHANICAL DAMAGE.
2017-09-29 08:50 | YES | NO | 19970085 | 1997-06-13 | 443 | AMOCO PIPELINE CO | YES | 1997-05-08 | 845 | IL | OGLE | OREGON | NO |  | NO | T 24N R 10E, SECTION 18 OGLE COOUNTY ILLINIOS, APPROX. 7 MILES NORTHWEST OF OREGON, IL, ON THE WEST SIDE OF SILVER CREEK ROAD. |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 700000 | 495915.7462 | 1000462.3684 | GASOLINE | 3 | 2490 | 60 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 1299 | 1280 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | SANDI BRAUN | 6309903781 | ON 5/8/97 AMOCO'S TULSA CONTROL CENTER CONTROLLERS IN TULSA, OK, AND FIELDSPECILAITS IN OREGON, IL WERE ELECTRONICALLY TUNING THE CONTROL VALVE ATOREGON STATION. AT APPROX. 0845 HRS ELECTRONIC DATA RECIEVED AT TCC INDICATEDLOW SUCTION PRESSURE AT THE OREGON STATION. TAKING PRECAUTION IN CASE OF ANOUTAGE, TCC PERSONNEL IMMEDIATELY OPENED UPSTREAM VALVES INTO ROCHELLETERMINAL WHILE RUNNING A DOWNSTREAM PUMP AT STOCKTON STATION IN ORDER TOEVACUATE THE PIPELINE FILL IN VICINITY OF OREGON STATION. FIELD SPECIALISTVERIFIED INSTRUMNETS WITH FIELD GAUGES AN D CLOSED MANUAL BLOCK VALVES AT MP140, 124, AND 123. TCC NOTIFIED THE MAINTENANCE TEAM LEADER AND INSTRUCTED ACOMPANY PATROL PLANE TO FLY THE SEGMENT FROM OREGON TO DUBUQUE, WHILE FIELDSPECIALIST PATROLLED THE SAME SEGMENT IN THE GROUND. THE SEARCH CONTINUED ANDTHE LEAK WAS FOUND BY GROUND PATROL AT APPROX. 1100 ON 5/9/97. THIRD PARTYDAMAGE IS SUSPECTED. VACUUM EQUIPMENT AND ADDITIONAL EMERGENCY RESPONSEPERSONENEL WERE SENT TO THE SITE AND BEGAN CLEANUP AND REPAIR OPERATIONS.
2017-09-29 08:50 | YES | NO | 19970086 | 1997-06-10 | 443 | AMOCO PIPELINE CO | YES | 1997-05-20 | 1200 | TX | ANDREWS | ANDREWS | NO |  | NO | 17 MILES W ON HWY 176 TO WHALEN LAKE RD, S ON WHALEN LAKE RD 2.5 MILES THEN 1 MILE WEST |  | PUMPING STATION | PIPE |  | 1948 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10626.766 | 21438.4793 | CRUDE OIL | 3 | 250 | 175 | NO | NO | 6 | 0.03 | 25000 | WELDED |  | 940 | 250 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | POSSIBLE BACTERIAL | NO DATA |  | Null | NO DATA |  | Null | Null | TOM MCGEEHAN | 9156879914 | A 6" DRAIN LINE SPLIT IN A SEAM OF WHAT APPEARS TO BE LAP WELD PIPE. THE SEAMMAY HAVE BEEN WEAKEND BY INTERNAL CORROSION. THE PIPE HAS BEEN SENT TO AMETALURGY LAB FOR ANALYSIS.
2017-09-29 08:50 | YES | NO | 19970087 | 1997-06-06 | 22855 | KOCH PIPELINE COMPANY, L.P. | YES | 1997-05-07 | 1700 | OK | LINCOLN |  | NO |  | NO | NE/4 SECTION 31-T16N-R5E |  | LINE PIPE | NO DATA |  | 1928 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | CRUDE OIL | 1 | 100 | 35 | NO | NO | 10 | 0.37 | 30000 | WELDED |  | 846 | 0 | YES | 8 | 1060 | 0 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES HENRY | 4052557151 | SEAM FAILURE IN PIPELINE RESULTED IN RELEASE OF PRODUCT.
2017-09-29 08:50 | NO | NO | 19970088 | 1997-06-17 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1997-06-05 | 340 | IL | COLES |  | NO |  | NO | 5051 E. COUNTY RD. OOON, MATTOON, IL 61938 |  | LINE PIPE | VALVE |  | 1997 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 3896.4809 | 7860.7758 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARC DEVARENNES | 5734865488 | 3:40 PASSER-BY NOTIFIED SHERIFFS DEPT. OF A VAPOR CLOUD FROM KOCH FACILITY.SHERRIFS DEPT. NOTIFIED KOCH EMPLOYEE. 4:04 AM KOCH EMPLOYEE FOUND 1/2 RELIEFVALVE ON TOP OF FILTER VESSEL RELEIVING. CLOSED BALL VALVE AT BOTTOM OF RELEIFVALVE TO STOP RELEASE. THREE NEARBY RESIDENCES WERE ASKED TO EVACUATE AS APRECAUTIONARY MEASURE. NO INJURIES OR CHRONIC AFFECTS RESULTED FROM THERELEASE. INVESTIGATION OF RELEASE BY KOCH DETERMINED THAT WHILE IN THE PROCESSOF REPLACING RELIEF VALVES WITHIN THE FACILITY, A 1440 PSI RELIEF VALVE ON THEPIPELINE FILTER VESSEL WAS INADVERTENTLY REPLACED WITH A 720PSI RELIEF VALVE.PIPELINE OPERATING PRESSURE OF APPROXIMATELY 800 PSI CAUSED VALVE TO RELEASE.
2017-09-29 08:50 | YES | NO | 19970089 | 1997-06-23 | 30781 | OLYMPIC PIPE LINE COMPANY | YES | 1997-05-27 | 725 | WA | COWLITZ | CASTLE ROCK | NO |  | NO | CASTLE ROCK PUMP STATION-185 KALMBACH QUARRY RD, CASTLE ROCK WA 98611 |  | PUMPING STATION | VALVE |  | 1994 | OTHER | FAILURE IN CONTROL VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | DIESEL FUEL | 1 | 150 | 13 | NO | NO | 14 | 0.28 | 52000 | WELDED |  | 1440 | 1600 | YES | 8 | 1875 | 10 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM MULKEY | 4252357745 | OPERATOR DISCOVERED LEAK INTO VALVE DURING ROUTINE STATION CHECK.
2017-09-29 08:50 | YES | NO | 19970090 | 1997-06-24 | 26024 | COASTAL CORP | YES | 1997-05-09 | 800 | NY | RICHMOND |  | NO |  | NO | SOUTH OF OLD PLACE CREEK , ON 6TH STREET, WITHIN GATX TERMINAL AT INTERSECTION OF 5TH STREET . |  | NO DATA | VALVE |  | 1985 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 53133.83 | 107192.3966 | DIESEL FUEL | 1 | 48 | 29 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | REX PROSSER | 7138777370 | A SPILL OCCURED AT COASTAL'S GATX METER STATION LOCATED ON STATEN ISLAND NEWYORK. THIS METER STAION IS LOCATED WITHIN THE GATX BULK LIQUID STORAGEFACILITY. THE PROPERTY WHICH THE METER STATION IS LOCATED IS LEASED FROM GATX.AN IUNVESTIGATION REVEALED A TWO INCH BALL VALVE CONNECTING THE PIPELINE METERTOTH E SUMP SYSTEM WAS PARTIALLY OPEN.THIS PARTIALLY OPEN VALVE CAUSED THESUMP TO FILL WITH PETROLEUM PRODUCT AND EVENTUALLY OVERFLOW. ALL VALVESCONNECTING THE SUMP SYSTEM HAVE BEEN REMOVED AND ASSOCIATED PIPING CAPPED OFFTO PREVENT ANY FUTURE OCCURANCE.
2017-09-29 08:50 | YES | NO | 19970091 | 1997-06-25 | 26024 | COASTAL CORP | YES | 1997-05-23 | 950 |  |  |  | YES | N 74 8' 42"LAT W 40 39' | NO |  |  | NO DATA | PIPE |  | 1986 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 530000 | 375479.065 | 757492.936 | DIESEL FUEL | 1 | 75 | 55 | NO | NO | 12.75 | 0.38 | 36000 | WELDED |  | 425 | 425 | YES | 8 | 535 | 0 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | REX PROSSER | 7138777370 | MAY 23 1997 AT APPROX 0800 HRS, AND EMPLOYEE OF BEST FOODS REPORTED AHYDROCARBON LEAK ON THE BAYONNE, NEW JERSEY SHORELINE. THE US COAST GUARD WASCONTACTED AND BEGN BY CLOSING THE CLOSEST PIPELINE BLOCK VALVES. OIL SPILLRESPONSE CONTRACTORS BEGAN THE INITIAL SITE CLEANUP AND CONTAINMENT. DRYDENDIVING SUCCESSFULLY LOCATED THE SOURCE OF THE HYDROCARBON LEAK. MAPP GRECOUTILIZED A PORTABLE COFFERDAM TO SUCCESSFULLY ISOLATE THE PIPELINE AND REPLACETHE DAMAGED SECTION OF LINE. APPROX. 15 FEET OF LINE WAS REPLACED. THE DIVERSCONFIRMED THAT THE PIPELINE HAD SUSTAINED THIRD PARTY DAMAGE. THE CONCRETECOATING WAS DISLODGED AND GOUGES AND DENTS WERE FOUND. IT IS SUSPECTED THATTHE THIRD PARTY EXTERNAL DAMAGE TO THE PIPELINE WAS CAUSED BY A VESEL ANCHOROR OTHER HEAVY OBJECT BEING DRAGGED ACROSS THE PIPELINE. THE PIPELINE SEGMENTFROM COASTAL'S GATX METER STATION TO COASTAL'S BERGEN POINT METER STATION WASTESTED TO 550 PSIG FOR 8 HRS. APPROX. 125 PERCENT OF THE NORMAL OPERATINGPRESSURE.
2017-09-29 08:50 | YES | NO | 19970092 | 1997-07-01 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1997-06-07 | 1855 | NM | SANDOVAL |  | NO |  | NO | 3 MILES SOUTH OF HWY 25 NORTH OF PLACITAS SSECTION 25, TOWNSHIP 13 NORTH, RANGE 4 EAST |  | LINE PIPE | VALVE | VALVE ON TOP OF A T.D. WILLISAM'S THREAD O RING | 1980 | OTHER | OTHER OF ROUND TOR FITTING | ALL OTHER CAUSES | MISCELLANEOUS | [7 empty] | 0 | 0 | COMM: NATURAL GAS LIQUID; CLASS: 2; LOSS: 228; RECOV: 0; FIRE: NO; EXP: NO; PRTST: Null; FACTD: Null; FACAT: Null; PREVT: Null; EXCAL: Null; TMPMK: Null; PNAME: MICHAEL PEARSON; PHONE: 9185994043
2017-09-29 08:50 | YES | NO | 19970095 | 1997-06-30 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1997-05-25 | 720 | CA |  | CONTRA COSTA | NO |  | NO | 14150 SOLANO WAY, CONCORD, CALIFORNIA |  | NO DATA | NO DATA |  | 1968 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | CRUDE OIL | 3 | 60 | 50 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | OTHER | SCRAPERTRAP DOOR GASKET | Null | NO DATA |  | Null | Null | RICHARD JELLEY | 8053270110 | SCRAER TRAP DOOR GASKET(O-RING) FAILED.
2017-09-29 08:50 | YES | YES | 19970096 | 1997-08-07 | 1044 | WESTTEX 66 PIPELINE CO | YES | 1997-07-05 | 904 | CO | ELBERT |  | NO |  | NO | POWDER RIVER LINE-MP 304+ 23+47- SEC. 20, T9S,R62W, ELBERT CO., CO APPROX. 7 MILES SE OF KIOWA, CO, ON HWY. 86, THEN SOUTH 4 MILES ON FRIESE RD. |  | LINE PIPE | PIPE |  | 1951 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 60000 | 42507.064 | 85753.9173 | NATURAL GAS LIQUID | 2 | 5000 | 0 | NO | NO | 6.63 | 0.19 | 42000 | WELDED |  | 1440 | 888 | YES | 8 | 1918 | 10 | 81 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | L.J. SCHMIDTZ | 9186614814 | LANDOWNER HIT LINE WITH GRADER WHILE CUTTING A DRAINAGE DITCH IN PASTURE.AFTER THE RUPTURE , THE LANDOWNER MADE CONTACT WITH OUR CONTROL CENTER ANDSHERIFF WHO SUSEQUENTLY REPORTED THE PRECAUTINARY EVACUATION OF 2 HOUSES. THEPIPELINE WAS SHUT DOWN AND VALVES WERE CLOSED TO ISOLATE THE LEAKINGSEGMENT.THE EQUIPMENT OPERATOR RECIEVED MINOR CUTS WHILE EXITING THE MACHINE.THE LANDOWNER IS ALSO A CONSTRUCTION CONTRACTOR FAMILIAR WITH LOCAL ONE-CALLPROVISIONS. HE REPROTED NOT MAKING NOTIFICATION BECAUSE HE WAS FARRMING ANDNOT EXCAVATING. HE WAS AWARE OF THE OF THE PIPELINES. PERMANENT PIPELINEMARKERS WERE INSTALLED IN A FENCE RIGHT-OF-WAY APPROX. 3000 FT.AWAY.
2017-09-29 08:50 | YES | NO | 19970097 | 1997-07-01 | 443 | AMOCO PIPELINE CO | YES | 1997-05-29 |  | IN | LAKE |  | YES | SECTION 19, 737N, R9W | NO | LEAK OCCURED ON AMOCO PROPERTY IN THE J&L TANK FIELD |  | LINE PIPE | PIPE |  | 1947 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 354225.533 | 714615.9774 | TRANSMIX (PART.REFINED PETRO) | 3 | 1200 | 0 | NO | NO | 12 | 0.37 | 35000 | WELDED |  | 720 | 700 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID MC MASTERS | 2196596904 | MAY 29 1997, AMOCO OIL CO. PERSONNEL ON ROUTINE GROUNDS CHECK NOTICED STAINEDSOIL. HE REPORTED THIS ONFORMATION TO WHITING REFINERY RESPONSE OFFICIALS.NOTIFICATIONS WERE MADE TO THE CITY OF HAMMOND IN, INDIANA DEPT./ OFENVIROMENTAL MANAGEMENT RESPONSE CTR. AMOCO PIPLEINE/WEST SHORE PIPELINEBEGIN EXCAVATION MAY 30, 1997. THE PRELIMINARY EXCAVATION INDICATED THATONE OFTHE AMOCO PIPELINES WAS LEAKING. EXCAVATION BEGAN ON THE DUBUQUE SYSTEM MAY31, 1997. THE DUBUQUE SYSTEM WAS EXCAVATED FOR 200 FEET AND THE PROTECTIVECONCRETE COATING REMOVED FOR 50 FEET. THE TULSA CONTROL CENTER PRESSURED THELINE TO 100 PSI IN THE LINE SEGMENT AND THE LEAK WAS FOUND. JUNE 1, 1997 LINEREPLACEMENT PREPARATIONS WERE COMPLETED. JUNE 2, 1997, TWENTY-SIX FEET OF PIPEWAS REPLACED. THE SYSYTEM RETURNED TO OPERATION AT 11:00 AM., JUNE 3, 1997.
2017-09-29 08:50 | YES | NO | 19970098 | 1997-08-04 | 9175 | JAYHAWK PIPELINE CORP | YES | 1997-07-15 | 1345 | KS | PRATT |  | NO |  | NO | NE OF SE QUARTER- SECTION 11 TOWNSHIP, 26 SOUTH -RANGE 15 WEST, 1 MILE NORTH , 3 MILES WEST AND 3/4 SOUTH OF BYERS, KANSAS. |  | NO DATA | VALVE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2125.3532 | 4287.6959 | CRUDE OIL | 1 | 300 | 295 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN WILKERSON | 3162419270 | DRAIN VALVE ON BLOCK VALVE BODY CORRODED AND BROKE OFF. BLOCK VALVE WASINSPECTED AND NEW DRAIN WAS INSTALLED, RESTORING BLOCK VALVE BACK IN SERVICE.
2017-09-29 08:50 | YES | NO | 19970099 | 1997-08-04 | 9175 | JAYHAWK PIPELINE CORP | YES | 1997-07-23 | 840 | KS | KIOWA |  | NO |  | NO | SE QUARTER SECTION 28 TOWNSHIP 27 SOUTH RANGE 16 WEST 3 MILES NORTH AND 1 1/2 MILES EAST OF HAVILAND, KS. |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10626.766 | 21438.4793 | CRUDE OIL | 1 | 117 | 0 | NO | NO | 12.75 | 0.25 | 46000 | WELDED |  | 1250 | 150 | YES | 8 | 1612 | 0 | 58 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN WILKERSON | 3162419270 | JAYHAWK PIPELINE PATROL PILOT NOTIFIED DISPATCHER OF POSSIBLE LEAK AT 840 HRS.ON JULY 23, 1997. JAYHAWK'S CREW WAS DISPATCHED TO SPILL AND UNCOVERED PIPETO FIND PINHOLE LEAK ON BUTTOM OF PIPE. A CLAMP WAS INSTALLED TO STOP LEAK ANDTHE PIPE IN THIS AREA WILL BE REPLACED.
2017-09-29 08:50 | YES | NO | 19970100 | 1997-07-25 | 443 | AMOCO PIPELINE CO | YES | 1997-04-26 | 830 | TX | GREGG |  | NO |  | NO | LOCATED ON AMOCO PIPELINE CO. SABINE STATION FACILITY INSIDE TANK DIKE #405. |  | TANK FARM | TANK |  | 1950 | OTHER | SEAL FAILED ON TANK MIXER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | CRUDE OIL | 1 | 2301 | 2300 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | F. GABRIEL OTHON | 9037597131
2017-09-29 08:50 | YES | NO | 19970101 | 1997-07-10 | 12127 | MARATHON PIPE LINE CO | YES | 1997-06-11 | 2025 | IN | LAKE | GRIFFITH | NO |  | NO | INCIDENT OCCURED INSIDE MARATHON PIPELINE COMPANY'S GRIFFITH STATION , LOCATED AT 1900 WEST H, GRIFFITH, IN |  | PUMPING STATION | OTHER | FLANGE GASKET FAILED | 1997 | OTHER | INCORRECT OPERATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 210000 | 148774.7239 | 300138.7105 | GASOLINE | 1 | 235 | 135 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOSEHP FISHER | 4194213201 | AT 20:25 ON JUNE 11, 1997, MARATHON PIPELINE COMPANY'S LOCAL OPERATIONSPERSONNEL RECEIVED NOTIFICATION OF A HAZARDOUS ATMOSPHERE ALARM AT ITSGRIFFITH, IN STATION. UPON RESPONDING TO THE ALARM, MPL PERSONNEL DISCOVERED AGASKET ON A MPL STATION MANIFOLD VALVE HAD FAILED AND PRODUCT BEING RELEASED.THE SECTION OF THE PIPING IN WHICH THE GASKET FAILED CONNECTS THE DISCHARGE OFA MPL BOOSTER PUMP TO A POINT BETWEEN TRANSMONTAIGNE PIPELINE COMPANY'SBOOSTER AND MAINLINE PUMPS LOCATED ADJACENT TO THE MPL FACILITY. UPONINVESTIGATION BY MPL PERSONNEL IT WAS DISCOVERED THAT AFTER A PREVIOUSMOVEMENT, FROM MPL TO TRANSMONTAIGNE THROUGH THIS PIPING, TRANSMONTAIGNEPERSONNEL HAD NEGLECTED TO CLOSE THEIR VALVE AT THE CONNECTION TOTRANSMONTAIGNE'S PUMPING FACILITY. PLEASE SEE REPORT FOR FURTHER DETAILS.
2017-09-29 08:50 | YES | NO | 19970102 | 1997-07-30 | 12127 | MARATHON PIPE LINE CO | YES | 1997-07-02 | 1030 | NE | GARDEN |  | NO |  | NO | SECTION 25, T15N, R46W |  | LINE PIPE | PIPE |  | 1952 | OTHER | STRESS INDUCED SEAM FAILU | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 420000 | 297549.4477 | 600277.421 | CRUDE OIL | 1 | 7026 | 265 | NO | NO | 20 | 0.31 | 52000 | WELDED |  | 955 | 897 | YES | 8 | 1548 | 12 | 1974 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JOSEPH FISHER | 4194213201 | AT APPROX. 1030 HRS. ON JULY 2 1997, THE OPERATIONS CENTER ANALYST OBSERVED ASUDDEN PRESSURE DROP IN THE PIPELINE. THE ANALYST IMMEDIATELY BEGAN SHUT DOWNPROCEDURES. APPROX. 15 MINUTES LATER, WHILE CONDUCTING A ROUTINE SCHEDULEDFLOVER THE AERIAL PATROL PILOT OBSERVED THE RELEASE AND REPORTED IT TO THEOPERATIONS CENTER. MARATHON AS OPERATOR OF PLATTE MOBILIZED PERSONNEL ANDCONTRACTORS TO THE RELEASE SITE. THE CRUDE OIL WAS CONFINED T APPROX. 5 ACRESOF A WHEAFILED AND DID NOT REACH ANY SURFACE WATER. BERMS WERE CONSTRUCTEDAROUND THE IMPACTED AREATO ASSURE THE CONTAINMENT OF THE CRUDE AT THE RELEASESITE. THE NEAREST RESIDENCE IS APPROX. A QUARTER MILE AWAY FROM THE SITE.PLANS ARE BEING MADE TO LAND FARM THE IMPACTED SOIL IN PLACE. THIS REPORT WAS AMENDED AUGUST 20, 2001 TO UPDATE THE PROPERTY DAMAGE ESTIMATE.
2017-09-29 08:50 | YES | NO | 19970104 | 1997-07-28 | 443 | AMOCO PIPELINE CO | YES | 1997-06-24 | 1300 | OK | PAYNE |  | NO |  | NO | SW SECTION 14 T17N R5E |  | TANK FARM | VALVE |  | 1976 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7084.5107 | 14292.3195 | CRUDE OIL | 1 | 150 | 140 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | FRED HESSER | 9184913567 | ONE INCH BLEEDER VALVE ON TANK FILL LINE INADVERTENTLY LEFT OPEN.
2017-09-29 08:50 | YES | NO | 19970105 | 1997-07-29 | 443 | AMOCO PIPELINE CO | Null | 1997-06-26 | 1430 | WY | HOT SPRINGS | THERMOPOLIS | NO |  | NO | SW/4 , SE/4, SECTION 31, TOWNSHIP 47N, RANGE 98W |  | LINE PIPE | WELDING FITTING |  | 1944 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 700 | 645 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAMES RAND | 3072663611 | PIPLEINE WAS PUNCTURED BY PRIVATELY OWNED MOTOR GRADER WHO WAS CUTTING DITCHESALONG LU RANCH RD. ONCE NOTIFIED AMOCO PERSONNEL DAMAGED DITCHES FORCONTAINMENT AND FREE OIL WAS PICKED UP WITH VACUUM TRUCKS AND TRANSPORTED TOAN AMOCO FACILITY. WYOMING DEQ GRANTED A PERMIT FOR THE BURNING OF OILYVEGITATION AND RESIDUED OIL. THIS WAS PERFORMED ON MONDAY JUNE 30, 1997.
2017-09-29 08:50 | YES | NO | 19970106 | 1997-07-28 | 443 | AMOCO PIPELINE CO | YES | 1997-06-16 | 915 | OK | PAYNE |  | NO |  | NO | NW 1/4 OF SW 1/4 OF SECTION 24 T17N R5E |  | TANK FARM | WELDING FITTING |  | 1974 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | CRUDE OIL | 1 | 1200 | 1100 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | FRED HESSER | 9184913567 | LEAK OCCURED IN WELDED 6"X12" REDUCER.
2017-09-29 08:50 | YES | NO | 19970107 | 1997-07-25 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1997-06-24 | 1430 | IN | GIBSON |  | NO |  | NO | INTERSECTION OF COUNTY ROADS 350S & 950E |  | PUMPING STATION | BOLTED FITTING |  | 1979 | OTHER | FAILED GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 38964.8086 | 78607.7575 | DIESEL FUEL | 3 | 100 | 14 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM | 7137593615 | AT APPROX. 1430 HRS. , CDT, ON JUNE 23 1997 , TEPPCO EXPERIENCED THE FAILUREOF A GASKET AT IT'S PRINCETON TERMINAL. THE PUMPS WERE SHUT DOWN IMMEDIALTELYUPON DICOVERY AND THE TEPPCO EMERGENCY PLAN WAS INITIATED. ONCE PRODUCT WASEVACUATED FROM THE PIPING SECTION, GASKET WAS REPLACED BACK INTO THE SERVICEON JUNE 25, 1997. REMEDIATION IS CURRENTLY BEING CONDUCTED TO AFFECTED SOIL.
2017-09-29 08:50 | YES | NO | 19970108 | 1997-07-22 | 19522 | TOSCO CORP | NO | 1997-06-09 | 1320 | CA | MARTINEZ |  | NO |  | NO | WEST OF AND ADJACENT TO WICKERLAND OIL TERMINAL AND NORTH OF WATERFRONT RD IN MARTINEZ, CA. |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 354225.533 | 714615.9774 | GASOLINE | 3 | 0 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 285 | 140 | YES | 8 | 356 | 8 | 95 | EXTERNAL | Null | YES | OTHER | PITTING CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL DE LEON | 5103723115 | ON JNE 9, 1997 GASOLINE WAS DICOVERED ON THE GROUND NEAR THE LOCATION OFUNDERGROUND PIPELINES OPERATED BY SEVERAL DIFFERENT COMPANIES. AFTER SHUTTINGDOWN ALL THE PIPELINES PRESSURE TESTING AND EXCAVATION, IT WAS DETERMINED TOHAVE BEEN CAUSED BY A LEAK ON AN UNDERGROUND PIPLEINE OPERATED BY TOSCOREFINING COMPANY. THE LEAK WAS APPARENTELY CAUSED BY EXTERNAL CORROSION OF THEPIPE. EMERGENCY RESPONSE ACTIONS WERE INITIATED IMMEDIATELY UPON DICOVERY OFTHE LEAK TO RECOVER PRODUCT AND MINIMIZE THE AREA IMPACTED. STATE AND LOCALAGENCIES HAVE BEEN INVOLVED FROM THE BEGINING IN THE EMERGENCY RESPONSE AND INPLANNING FOR THE REMEDIATION ACTIVITIES TO BE UNDERTAKEN.
2017-09-29 08:50 | YES | NO | 19970109 | 1997-07-21 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1996-12-24 | 930 | TX | REFUGIO |  | NO |  | NO | 1/2 MILE OFF 136 AND 1/4 MILE WEST OF STEINDORF RD. |  | LINE PIPE | PIPE |  |  | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3604.7575 | 7272.252 | CRUDE OIL | 1 | 100 | 100 | NO | NO | 8.63 | 0.32 | 1881 | WELDED |  | 756 | 240 | YES | 8 | 945 | 0 | 91 | NO DATA | Null | YES | GALVANIC |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | VISUAL SIGNS W/EMERGENCY# | YES | YES | MARK GRAHAM | 5122425509 | CONTRACTOR WAS DRESSING UP LAND WHERE A CHANGE OUT HAD BEEN MADE, DURINGRECONDITOINING OF LINE. THE CHISEL HIT THE LINE CAUSING THE LINE TO RUPTURE.LINE WAS SHUT DOWN AND REPAIRED AND SPILL WAS CLEANED UP.
2017-09-29 08:50 | YES | NO | 19970110 | 1997-07-21 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1997-05-12 |  | TX | REFUGIO |  | NO |  | NO | FORD RANCH, SOUTH ON STEINDORF RD |  | NO DATA | GIRTH |  | 1971 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | CRUDE OIL | 1 | 1800 | 230 | NO | NO | 12 | 0.22 | 0 | WELDED |  | 983 | 200 | YES | 24 | 983 | 0 | 91 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | GORDON WARE | 5122415624 | GROUND SHIFTED AND WELD BROKE.
2017-09-29 08:50 | YES | NO | 19970111 | 1997-07-22 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1997-06-23 | 650 | CA | FRESNO |  | NO |  | NO | 14150 SOLANO WAY, CONCORD, CA. |  | TANK FARM | TANK |  | 1968 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25500 | 18065.5022 | 36445.4148 | CRUDE OIL | 1 | 607 | 180 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | OTHER | SCRAPER TRAP DOOR GASKET | Null | NO DATA |  | Null | Null | RICHARD E KELLEY | 8053270110 | TANK MIXER PIVOT PIN CAME LOOSE AND MIXER BECAME UNSEALED FROM TANK.
2017-09-29 08:50 | YES | NO | 19970112 | 1997-07-01 | 10315 | KOCH OIL CO | NO | 1997-04-17 | 730 | CA | KERN |  | NO |  | NO | SECTION 26 RANGE 32 TOWNSHIP 32 |  | LINE PIPE | PIPE |  | 1987 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7300 | 5171.6928 | 10433.3933 | CRUDE OIL | 1 | 50 | 0 | NO | NO | 6 | 0.19 | 1716 | WELDED |  | 720 | 100 | YES | 4 | 1001 | 6 | 87 | EXTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BRYAN GORELL | 8053973900 | LOCAL EXTERNAL CORROSIN REDUCED THE PIPE WALL CAUSING A FAILURTE ON THE
2017-09-29 08:50 | YES | NO | 19970113 | 1997-07-01 | 10315 | KOCH OIL CO | NO | 1997-06-18 | 1025 | CA | KERN |  | NO |  | NO | SECTION 13 TOWNSHIP 325 RANGE 26E |  | LINE PIPE | PIPE |  | 1943 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 266000 | 188447.9836 | 380175.7 | CRUDE OIL | 1 | 632 | 270 | YES | NO | 6 | 0.22 | 1666 | WELDED |  | 720 | 150 | YES | 4 | 1000 | 12 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BRYAN GORRELL | 8053973900 | BONANZA FARMS WAS USING A GRADER TO CREAT AN IRRAGATION DITCH THAT CROSSEDKOC OIL'S WELL MARKED PIPLINE. THE GRADER HIT AND PUNCTURED THE PIPELINE. THECRUDE OIL LEAKED FROM THE PIPELINE AND CAUGHT FIRE. THE FIRE BURNT FOR 6 HPURSCAUSING AN ESTIMATED DAMAGE OF 250,000 TO THE GRADER.
2017-09-29 08:50 | YES | NO | 19970114 |  | 2552 | COLONIAL PIPELINE CO | YES | 1997-05-30 | 525 | GA | CLARKE |  | NO |  | NO | NORTHWEST OF THE CITY OF ATHENS, MA,INLINE BLOCK VALVE EAST OF BIG BEAR RD. ON THE UPSTREAM SIDE OF THE OCONEE RIVER. |  | LINE PIPE | VALVE |  | 1978 | OTHER | UNSUCCESSFUL NITROGEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 354225.533 | 714615.9774 | GASOLINE | 1 | 450 | 330 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES COX | 4048412296 | SEE ATTACHED NARRATIVE/REPORT.
2017-09-29 08:50 | YES | NO | 19970115 | 1997-07-09 | 19226 | TEXACO PIPELINE INC | NO | 1997-06-13 | 1244 | TX | JEFFERSON |  | NO |  | NO | 1/2 MILE NORTH OF PORT ARTHUR, TX, ON HWY 90 (MAP ATTACHED) |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 21253.532 | 42876.9586 | CRUDE OIL | 1 | 75 | 73 | NO | NO | 12 | 0.25 | 24000 | WELDED |  | 400 | 350 | YES | 8 | 508 | 0 | 90 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. LEDNICKY | 7137526514 | LEAK CAUSED BY EXTERNAL CORROSION AT A POINT WHERE PIPELINE WAS EXPOSED TO THEATMOSPHERE.
2017-09-29 08:50 | YES | NO | 19970116 | 1997-07-07 | 2552 | COLONIAL PIPELINE CO | YES | 1997-05-20 | 1100 | SC | SPARTANBURG |  | NO |  | NO | SEE ATTACHED SKETCH |  | LINE PIPE | PIPE |  | 1963 | OTHER | BUCKLE IN LINE PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | FUEL OIL | 1 | 55 | 55 | NO | NO | 36 | 0.31 | 52000 | WELDED |  | 275 | 209 | YES | 24 | 698 | 8 | 1963 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J.A. COX | 4048412296 | ON MAY 20, 1997 AT 11:00 AM WHILE PERFORMING A PIG DIG ON LINE NO.2MAINTENANCE PERSONNEL NOTICED SATUREATED COATING ON THE LINE. THE CONTROLLERWAS NOTIFIED AT 11:05 AM AND THE LINE WAS SHUTDOWN AND ISOLATED UPON CLOSERINVESTIGATION , A 1.5 - INCH CRACK WAS FOUND IN THE CREASE OF A BUCKLE. THEPRODUCT WAS CONTAINED AND CONTAMINATED SOIL WAS STOCKPILED ON A PLASTIC SHEET.THE REPAIR WAS ACCOMPLISHED BY THE INSTALLATION OF A THREE FT. LONG FULLENCIRCLEMENT WELDED REPAIR SLEEVE OVER THE BUCKLE. RECOVERY AND MONITORINGWELLS WERE INSTALLED THE WEEK OF JUNE 2 AND RECOVERY SYSTEM WAS INSTALLED THEWEEK OF JUNE 9. ON JUNE 67, 1997, THE REVISED ESTIMATE EXCEEDED THE PART 19550,000 REPORTING LIMIT AND THE NATION RESPONSE CENTER WAS NOTIFIED AT 1406.
2017-09-29 08:50 | YES | NO | 19970117 | 1997-08-08 | 26134 | MOBIL OIL CORP - WEST COAST SUPPLY & LOGISTICS | Null | 1997-07-28 | 1030 | CA | KERN | GRAPEVINE | NO |  | NO | GRAPEVINE STATION |  | PUMPING STATION | OTHER | FOILUTE OF SEAL |  | OTHER | PUMP SEAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 80 | 78 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ANDY ANDERSON | 8057637602 | FOR UNKNOW REASON OUTBOARD SEAL FOILED & ALLOWED OIL TO DISCHARGE AT HIGH RATEUNDER PRESSURE. OPERATOR ISOLATED PUMP. OIL CONFINED TO PUMP STATIONCONTAINMENT AREA.
2017-09-29 08:50 | NO | NO | 19970118 | 1997-07-08 | 26127 | CHEVRON PIPELINE CO | NO | 1997-06-03 | 900 | CA | FRESNO |  | NO |  | NO | 1/2 MILE WEST OF HWY 5 AND 1/2 MILE . SOUTH OF HWY 198 LOCATION WAS ON THE PAPPAS FARM PROPERTY. |  | LINE PIPE | PIPE |  | 1936 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | CRUDE OIL | 1 | 46 | 46 | NO | NO | 8 | 0.32 | 0 | WELDED |  | 1000 | 750 | YES | 4 | 828 | 6 | 92 | NO DATA | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB FRAGIUNE | 8053923355 | RELEASE OCCURED DURING HYDROTESTING OF PIPELINE
2017-09-29 08:50 | YES | NO | 19970119 | 1997-07-21 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-06-20 | 849 | MT | BIG HORN |  | NO |  | NO | Y85N, R34E, N1/2 SECTION 21 APPROXIMATELY 8 MILES WEST OF WYOLA, MT ON THE CROW INDIAN RESERVATION. |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | LANDSLIDE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | 0 | 0 | 0 | 0 | 0 | 0 | 900000 | 637605.9594 | 1286308.7593 | GASOLINE | 3 | 1612 | 18 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1632 | 1310 | YES | 8 | 2040 | 0 | 88 | NO DATA | Null | Null | NO DATA |  | LANDSLIDE |  | Null | NO DATA |  | Null | Null | RANDY BEGGS | 3036494090 | ON JUNE 20, 1997, AT APPROX. 0849 HRS. CONOCO PIPE LINE CO. OPERATIONS INHOUSTON , TX. DETECTED A PRESSURE DROP ON THE SEMINOE PIPELINE SYSTEM AND ITSBILLINGS, MT. PUMP STATION. AT 0852 THE OPERATIONS CENTER REMOTELY SHUT DOWNTHE SYSYTEM AND BLOCKED IN THE PIPELINE AND CALLED OUT OCAL RESPONSE PERSONNELTO INVESTIGATE THE PRESSURE DEVIATION. AT 0905 , THE AREA SUPERVISORDISPATCHED RESPONSE PERSONNEL TO MAJOR RIVER AAN CREEK CROSINGS AND TO CLOSEMANUALLY OPERATED BLOCK VALVES DOWNSTREAM OF BILLINGS, MT. AIRCRAFT WASLOCATED TO BEGIN AIR SEARCH FOR THE LEAK. THIS CRAFT MADE FOUR FLIGHTS ALONGTHE RIGHT OF WAY AND DID NOT SEE THR LEAK. A HELICOPTER WAS LOCATED TO HELP INTHE SEARCH AND MADE NUMEROUS FLIGHTS ALONGF THE RIGHT OF WAY ALSO, BUT THELEAK COULD NOT BE FOUND. ALSO DURING THIS PERIOD, THERE WERE FOUR GROUPS OFPEOPLE DRIVING AND WALKING THE LINE IN TEH SUSPECTED AREA OF WHERE THE LEAKWAS TO BE. THE FLIGHT AND GROUND SEARCH FOR THE LEAK SITE WAS SUSPENDED FORTHE NIGHT AT MIDNIGHT DUE TO DARKNESS AND SAFETY CONCERNS FOR THE PEOPLE THATHAD BEEN OUT ALL DAY LOOKING FOR THE LEAK. TWO ENVIROMENTAL CONTRACTORS WEREDISPATCHED TO MONITOR ALL THE MAJOR RIVER AND CREEK CROSSINGS THROUGHOUT THENIGHT. ON SAT. JUNE 21, 1997 ONCE AGAIN A HELICOPTER WAS PUT INTO THE AIR TOCONTINUE THE SEARCH AND TRANSPORT PEOPLE IN TO SUSPECTED AREAS WHERE THE LEAKHAD BEEN DETERMINED TO BE. NUMEROUS PEOPLE WERE ALSO ON TEH RIGHT OF WAYCONTINUING THE GROUND SEARCH BY FOOT AND 4 WHEEL ATV'S. AT 1000 , THE LEAKSITE WAS LOCATED AT MILEPOST 65.7 THE CONTAINMENT AND CLEAN UP PROCESS BEGAN.PRODUCT HAD REACHED BEAR CREEK WHICH WAS IMMEDIATELY BOOMED TO PREVENT THEPRODUCT FROM ADVANCING FURTHER DOWNSTREAM. THE CAUSE OF THE FAILURE WAS DUE TOA DUCTILE, TENSILE FAILURE MODE DUE TO LONGITUDINAL STRESS FROM THE GROUNDMOVEMENT. APPROX. 3400 FEET OF THE PIPELINE WAS REPLACED AT A DEEPER LEVEL,STRAIN GAUGES WERE INSTALLED AND DATA WILL BE GATHERED/ ANALYZED PERIODICALLY.
2017-09-29 08:50 | YES | NO | 19970120 | 1997-07-24 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-06-26 | 1717 | WY |  | SHERIDAN | NO |  | NO | T53N, R83W, SW 1/4 SECTION 10 NEAR BANNER , WYOMING |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 354225.533 | 714615.9774 | GASOLINE | 3 | 704 | 245 | NO | NO | 8.63 | 0.22 | 52000 | WELDED |  | 1901 | 1500 | YES | 8 | 2376 | 0 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | RANDY BEGGS | 3036494090 | ON JUNE 26, 1997 AT APPROX. 5:17 , CONOCO PIPELINE OPERATIONS IN HOUSTON TX,DETECTED A PRESSURE DEVIATION ON THE SEMINOE PIPELINE SYSTEM SOUTH OF THESHERIDAN, WYOMING TERMINAL. OPERATIONS IMMEDIATELY BEGAN SHUT DOWN PROCEDURESAND HAD THE LINE SHUT DOWN BY APPROX. 5:22 P.M. CONOCO STAFF AT THE SHERIDANTERMINAL WAS NOTIFIED IMMEDIATELY FIVE MINUTES TO INVESTIGATE. UPONINVESTIGATION CONOCO RESPONDERS DISCOVERED A GASOLINE LEAK FROM THE EIGHT INCHLINE APPROX. FIVE ILES SOUTH OF THE TERMINAL NEAR BANNER, WYOMING. CONOCOPERSONNEL WERE DISPATCHED TO CLOSE MANUALLY OPERATED VALVES DOWNSTREAM OF THELEAK SITE. THE REPONDING PERSONNEL IMMEDIATELY CALLED EMERGENCY RESPONSEAGENCIES AND INITIATED CONOCO'S REGIONAL RESPONSE TEAM. CONOCO RESPONSEPERSONNEL WERE ABLE TO DEPLOY FIRST BOOM BY APPROX. 6:30. SUBSEQUENTLY SEVERALOTHER BOOMS WERE DEPLOYED AND COFFER DAMS BUILT AS ADDITIONAL PERSONNEL ANDEQUIPMENT ARRIVED ON SITE. THE RELEASE WAS COMPLETELY CONTAINED BY TRAVELEDAPPRX.2/3 MILES INTO A STOCK POND. ANY FREE PRODUCT THAT LEFT THE POND WASCONTAINED IN A COFRFER DAM CONSTRUCTED SEVERAL HUNDRED YARDS DOWNSTREAM OF THEPOND. THE CAUSE OF THE FAILURE WAS DUE TO STRESSES IMPARTED ON THE LINE BYLATERAL LAND MOVEMENT IN THE AREA. 1392.7 FEET OF .219 WALL PIPE WAS REPLACEDWITH .322 WALL X46 LINE PIPE. VIBRATING STRAIN GAUGES WERE INSTALLED ON THISNEW SECTION TO MONITOR PIPE MOVEMNET DURING OPERATION. A GEOTECHNICALCONSULTANT HAS BEEN HIRED TO CONDUCT A STUDY OF THE AREA, TO DETERMINE OURPERMANENT REPAIR.
2017-09-29 08:50 | NO | NO | 19970121 | 1997-08-08 | 2325 | CHEVRON USA INC | YES | 1997-04-28 | 915 |  |  |  | YES | 29DEG0207N 89DEG1910.10W | NO | SOUTH PASS 49 |  | LINE PIPE | OTHER | GASKET FAILURE |  | OTHER | OVER PRESSURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MARK BOONE | 5043642020 | OVERPRESSURE IN LINE CAUSED FAILURE OF STRAINER GASKET. LEAK DRAINED TO SUMPWHICH OVERFLOWED. REPAIR MADE, OIL RECOVERED AND RETURNED OIL TO SYSTEM ANDWATER TO NORTH CENTRAL BARGE FOR DISCHARGE.
2017-09-29 08:50 | YES | NO | 19970122 | 1997-08-20 | 809 | ARCO PIPE LINE CO. | NO | 1996-07-27 | 1500 | TX | HARRIS | CHANNELVIEW | NO |  | NO | THE ACCIDENT OCCURED AT AN ARCO PIPELINE CO. METER STATION LOCATED WITHIN THE LYNDELL PETROCHEMICAL FACILITY LOCATED AT 8280 SHELDON RD. IN CHANNELVIEW TX. |  | LINE PIPE | BOLTED FITTING |  | 1996 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8250000 | 5947849.9543 | 11999215.7888 | NOT GIVEN | 2 | 757 | 0 | YES | YES | 0 | 0.5 | 0 | FLANGED |  | 2000 | 1730 | YES | 4 | 3380 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null |  |  | AT APPROX. 1500 ON JULY 27, 1997, THE ARCO PIPELINE CO. OPERATIONS CONTROLCENTER WAS NOTIFIED OF AN ETHYLENE RELEASE BY LYONDELL PETROCHEMICAL COMPANYPERSONNEL. ETHYLENE WAS BEING RELEASED FROM A 12 INCH FLANGE CONNECTION WITHINARCO PIPELINE COMPANY METER STATION INSIDE THE LYONDELL FACILITY. ATAPPROXIMATELY 1545 THE VAPOR CLOUD IGNITED; FIRE AND RUPTURES FOLLOWED. AT1700 THE FIRE BEGAN TO SUBSIDE AND BURNED ITSELF OUT IVER THE NEXT SEVERALHRS. IT WAS THIS FIRE AND EXPLOSION THAT CAUSED THESE PIPELINES AT THE METERSTATION TO FAIL.
2017-09-29 08:50 | YES | NO | 19970123 | 1997-08-20 | 18718 | SUN PIPE LINE CO | YES | 1997-07-24 | 1120 | OK | PONTOTOC | ADA | NO |  | NO | SE-SW/4 SEC. 9,4-N, 6E, FROM HWY 1 AND HWY 99 IN ADA, GO 2 1/2 MILES NORTH ON HWY 99, WEST SIDE OF HWY. |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 500 | 495 | NO | NO | 6 | 0.23 | 1471 | NO DATA |  | 782 | 200 | YES | 8 | 1165 | 0 | 74 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | YES | EDITH COEN | 9185866942 | ASPLUNDH BRUSH CONTROL WAS CLEARING THE ROW ON THE ADA TO NAHOLA 6". THEOPERATOR BACKED INTO THE PIPE WITH THE BRUSH HOG ENGAGED. IT CUT A 32" GASH INTHE NORTH SIDE OF THE PIPE.
2017-09-29 08:50 | YES | NO | 19970126 | 1997-09-03 | 3012 | PRIDE TEXAS PLAINS L.P. | NO | 1997-08-13 | 1430 | TX | GRAY |  | NO |  | NO | APPROX. 2 MILE NORTH OF ALANREED, TX OFF OF HWY 291 |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 7084.5107 | 14292.3195 | CRUDE OIL | 1 | 200 | 0 | NO | NO | 6 | 0.28 | 25000 | THREADED |  | 770 | 50 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN MACON | 9156748231 | LEAK WAS REPORTED ON 8/13/1997 BY PRIDE'S PIPELINE PATROL PLANE. CREWS WEREDISPATCHED FOR SPILL CONTAINMENT AND TO CLAMP THE LINE.
2017-09-29 08:50 | YES | NO | 19970127 | 1996-09-03 | 2339 | CHEVRON USA INC - HAWAII | NO | 1996-05-13 | 2250 | HI |  | HONOLULU | NO |  | NO | THE LEAK WAS LOCATED AT MILEPOST 12.97 BEHIND HECO POWER PLANT AT WAIAU. |  | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 720951.5096 | 1454450.3986 | NOT GIVEN | 3 | 600 | 600 | NO | NO | 8 | 0.22 | 46000 | WELDED |  | 1440 | 576 | YES | 8 | 1800 | 1 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | T.J. SIMONS | 8086822239 | A LEAK OCCURED DURING A ROUTINE SHIPMENT TO HECO POWER PLANT. EXTERNALCORROSION CASUED A HOLE TO DEVELOP IN THE PIPELINE AND OIL SURFACED TO GRADE.THE OIL FLOWED INTO AN ADJACENT DRAINAGE DITCH WHICH EMPTIED INTO PEARL HARBOR.
2017-09-29 08:50 | YES | YES | 19970128 | 1997-09-15 | 3466 | DOME PIPELINE CORP | YES | 1997-08-04 | 1400 | MN | STEVENS |  | NO | \ | NO | MP 992.5 (MN R/W TRACT 157) NE/4 SECTION 12, T123N, R42W, STEVENS COUNTY, MN |  | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 2 | 0 | 2 | 1500000 | 1062676.599 | 2143847.9322 | NOT GIVEN | 2 | 15000 | 0 | YES | YES | 12.75 | 0.21 | 60000 | WELDED |  | 1440 | 800 | YES | 24 | 2004 | 11 | 77 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | WALLACE HALL | 3193547722 | ON FRI. MORNING 8/1/97 A GOPHER ONE-CALL TICKET WAS RECIEVED AT BENSON PROPANETERMINAL. THE GOPHER ONE-CALL TICKET WAS FOR THE INSTALLATION OF FIELDDRAINAGE IN SE/4 OF SEC. 12, T123N,R42W, STEVENS COUNTY. THE ORIGINALNOTIFICATION WAS RECIEVED BY GOPHER ONE-CALL ON JULY 3197, AT 11:07 AM ANDINDICATED WORK TO BEGIN DATE 8/4/97 AT 11:15 AM. WHEN DONE PERSONNEL ARRIVEDAT THE LOCATE SITE AT APPROX. 9:30 AM THE LANDOWNER APPEARED TO BE EXPLANINGHIS PROPOSED ACTIVITIES TO A REPRESENTATIVE OF A SECOND UTILITY. THE LANDOWNERINDICATED HE WOULD RETURN IN A FEW MINUTES SO THE DOME PERSONNELCOMMENCEDHOOKING UP HIS LINE LOCATOR TO THE PIPELINE AWAITING THE RETURN OFTHE LANDOWNER AND TILER. THE PIPELINE WQAS LOCATED AND FLAGGED AS REQUESTED INTHE SE/4 AND NW/4 OF SECTION 12.HOWEVER THE LANDOWNER ALSO INSTALLED SIX-FOOTBICYCLE FALGS OVER THE PIPELINE WHERE THEY WERE PLANNING OM CROSSING TO INSUREVISIBILITY. ONCE THE PIPELINE WAS LOCATRED AND FLAGGED BY DOME IN THE NW/4,THE LANDOWNER PROCEEDED TO KNOCK DOWN CORN IN A 15FT. RADIUS. AS THEY WERELEAVING THE FIELD, DOME ASKED WHEN THEY WOULD BE CROSSING OR WORKING IN THEVICINITY OF THE PIPELINE, AND THE LANDOWNER INDICATED MON. 8/4/97. DOME STATEDTHEY MUST BE PRESENT WHEN EXCAVATION WAS PERFORMED IN THE VICINITY OF THEPIPELINE( ON DO'S RIGHT OF WAY). SEE REPORT.
2017-09-29 08:50 | YES | NO | 19970129 | 1997-09-08 | 2731 | CHEVRON PIPELINE CO | YES | 1997-08-11 | 1415 | TX | LIBERTY | DAYTON | NO |  | NO | SEE MAP |  | NO DATA | VALVE |  | 1997 | OTHER | MECHANICAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 240000 | 170028.2558 | 343015.6691 | L. P. G. | 2 | 5041 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BILL JASPER | 2813635422 | TWO EMPLOYEES WERE ATTEMPTING TO OPERATE A CHECK VALVE TO FREE A PIG THAT HADBECOME LODGED IN THE VALVE , WHEN THE CLAPPER SHAFT EXITED THE VALVE BODY. LPGESCAPED FROM THE OPEN 1" SHAFT TUNNEL. BLOCK VALVES UP AND DOWN STREAM WERECLOSED AND THE LINE WAS ALLOWED TO DEPRESSURE. A NEW VALVE OF DIFFERENT DESIGNWAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19970130 | 1997-09-05 | 6856 | KOCH PIPELINE COMPANY, L.P. | NO | 1997-06-23 | 2255 | OK | CUSHING |  | NO |  | NO | SE/4 SECTION 15-T17N-R5E, PAYNE COUNTY, OK |  | TANK FARM | OTHER | STAINER ON ACT UNIT |  | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 6517.7498 | 13148.934 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES HENRY | 4052557151 | CUSTOMER'S REPRESENTATIVE CLOSED VALVE AT THEIR REMINAL, BLOCKING IN KOCH'SPIPELINE WHILE KOCH WAS MAKING DELIVERY. OPERATOR BYPASS MALFUNCTION DUE TOOBSTRUCTION OF THE BYPASS VALVE. THIS RESULTED IN THE FAILURE OF THE ACT UNITSTRAINER, ALLOWING PRODUCT TO BE RELEASED. INVESTIGATION OF THE ACCIDENTREVEALED THE BYPASS OBSTRUCTION WAS CAUSED BY A PORTION OF POLY-PIG WHICH HADBEEN FORCED INTO BYPASS VALVE AND PREVENTED THE BYPASS FROM FUNCTIONING.
2017-09-29 08:50 | YES | NO | 19970131 | 1997-08-12 | 443 | AMOCO PIPELINE CO | YES | 1997-07-24 | 1400 | TX | GRAYSON | LUELLA | NO |  | NO |  |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 141690.2132 | 285846.391 | CRUDE OIL | 1 | 500 | 470 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | GABRIEL OTHON | 9037597131 | LINE WAS HIT BY TRACKHOE. NRC REPORT # 396541. LT HUDSPETH WAS CONTACTED AT6:05 P.M.
2017-09-29 08:50 | YES | NO | 19970132 | 1997-09-10 | 25067 | PGC PIPELINE (DIV OF LPC ENERGY INC) | NO | 1997-08-16 | 1030 | TX | NUECES | CORPUS CHRISTI | NO |  | NO | .25 MILE WEST OF CORN PRODUCTS RD. NORTH SIDE OF NORTHBOUND IH-37 ACCES RD. |  | LINE PIPE | PIPE |  | 1964 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 101600 | 71978.6283 | 145209.9666 | GASOLINE | 2 | 595 | 0 | NO | NO | 12 | 0.25 | 46000 | NO DATA |  | 600 | 130 | YES | 8 | 751 | 11 | 96 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MIKE PAWELEK | 2102463067 | A LEAK WAS FOUND ON THE NORTH END OF THE IH-37 CROSSING IN CORPUS CHRISTI, TX.THE EXISTING HWY CROSSING WAS ABANDONED IN PLACE AND FILLED WITH MUD. THE HWYCROSSING WAS REBORED AND APPROX. 700' OF NEW PIPE WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19970133 | 1997-09-19 | 4805 | EXPLORER PIPELINE CO | YES | 1997-08-19 | 1015 | OK | CREEK COUNTY |  | NO |  | NO | 1/2 MILE NORTH OF STATE HWY.117 ON 33RD WEST AVENUE. |  | LINE PIPE | NO DATA |  | 1971 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 106267.6599 | 214384.7932 | GASOLINE | 3 | 5 | 0 | YES | NO | 28 | 0.28 | 32000 | WELDED |  | 751 | 160 | YES | 24 | 1044 | 5 | 71 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RODNEY SANDS | 9184935106 | ON AUG.19, 1997 AT APPROX. 1015 HRS. EXPLORER PIPELINE COMPANY CENTRAL CONTROLCENTER IN TULSA, OK RECIEVED A PHONE CALL FROM A LOCAL RESIDENT REPORTINGSTRONG ODOR OF GASOLINE COMING FROM THE AREA OF A NEARBY CREEK. COMPANYPERSONNEL AT OUR GLENPOOL , OKLAHOMA OFFICE WERE NOTIFIED AT APPROX. 1020 HRS.AND ARRIVED AT THE SITE 1030 HRS. A SHEEN ON THE WATER AND GASOLINE VAPORSWERE DISCOVERED AT THE SEGMENT WAS IMMEDIATELY SHUT DOWN AND PRESSURE REDUCEDBY DRAINING BACK INTO GLENPOOL TANK FARM. BLOCK VALVES WERE CLOSED AT GLENPOOLTANK FARM AND WEST TULSA STATION. (SEE REPORT)
2017-09-29 08:50 | YES | NO | 19970134 | 1997-09-15 | 19522 | TOSCO CORP | NO | 1997-09-06 | 1645 | CA | SANTA BARBARA |  | NO |  | NO | 300 YARDS SOUTHEAST OF BETTERAVIA RD. OFF ROSEMARY RD |  | LINE PIPE | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 28338.0426 | 57169.2782 | CRUDE OIL | 1 | 175 | 195 | NO | NO | 12 | 0.25 | 0 | WELDED |  | 500 | 90 | YES | 4 | 690 | 12 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | DENNIS GILMORE | 8059251468 | TRACTOR OPERATOR USING 36" RIPPERS WAS PLOWING IN AN EAST TO WEST DIRECTION ,WHEN ONE THE TIME ON THE RIPPER. STRUCK AND PUNCTURED THE 12" CRUDE OIL LINE.THE OPERATOR CALLED HIS FOREMAN WHO CALLED OUR CONTROL CENTER. THE CONTROLCENTER CONTACTED SANTA MARIA DISTRICT PIPELINE OFFICE WHEN RESPONDED TO THESPILL. THE AREA WAS MONITORED FOR SAFETY AND NO HAZARDOUS CONDITIONS WEREFOUND. THE FLOW OF OIL WAS STOPPED AND A 15" SECTION OF PIPE WAS REPLACED ANDTHE LINE WAS RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19970135 | 1997-09-22 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1997-08-19 | 2000 | PA | DAUPHIN |  | NO |  | NO | CONRAIL ROCKVILLE BRIDGE OVER THE SUSQUEHANNA RIVER NORTH OF HARRISBURG, PA |  | LINE PIPE | PIPE |  | 1965 | OTHER | STRUCTURAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 106267.6599 | 214384.7932 | DIESEL FUEL | 2 | 42 | 5 | NO | NO | 4 | 0.16 | 2430 | WELDED |  | 152 | 0 | YES | 24 | 1123 | 5 | 96 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOEL LARKIN | 6107704507 | ON AUG. 19,1997 THE ROCKVILLE RAILROAD SUFFERED A STRUCTURAL FAILURE DERAILINGFOUR CARS INTO THE SUSQUEHANNA RIVER. THE DERAILMENT RUPTURED BUCKEYE PIPELINECOMPANY'S 4" PIPELINE ATTACHED TO THE BRIDGES STRUCTURE. THE CONDITION OF THEPIPELINE WAS STATIC AT THE TIME OF THE BRIDGE FAILURE.
2017-09-29 08:50 | YES | NO | 19970136 | 1997-09-22 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-08-24 | 1630 | WY | PLATTE |  | NO |  | NO | CONOCO PIPELINE CO. GUERNSEY, WY PUMP STATION AND TANK FARM, T26N, R65W, SECTION 17 |  | TANK FARM | PUMP |  | 1997 | OTHER | THRUST BEARING LOCKINGNUT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | CRUDE OIL | 1 | 130 | 120 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY BEGGS | 3036494090 | T-158 BOOSTER PUMP THRUST BEARING LOCKING NUT BECAME LOSSENED FROM THE PUMPSHAFT, ALLOWING THE PUMP IMPELLER TO BE PULLED INTO THE PUMP CASE. THE RESULTWAS A RELEASE OF 130 BBLS OF CRUDE OIL IN THE TANK DIKE OF TANK 1158.
2017-09-29 08:50 | YES | NO | 19970138 | 1997-09-24 | 2387 | CITGO PIPELINE CO | YES | 1997-08-25 | 1730 | OK | POTTAWATOMIE |  | NO |  | NO | SOUTHEAST 1/4 SECTION 6 TSP 8 N, RANGE 3 E, 4 MILES SOUTH OF #9 HIGHWAY ON BETHEL RD. |  | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 49591.5746 | 100046.2368 | GASOLINE | 1 | 900 | 70 | NO | NO | 12 | 0.32 | 35000 | THREADED |  | 428 | 125 | YES | 8 | 563 | 0 | 91 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JIM SANDERS | 9184954786 | AUGUST 25, 1997---1200 ADJ LINE WAS SHUTDOWN BECAUSE OF SUSPECTED LEAK, BASEDON HOURLY SHORTAGE. PIPELINE WAS BLOCKED IN AND LEAKING SECTION IDENTIFIED.1730- LEAK WAS LOCATED AND CONTRACTORS WERE MOBILIZED. 2015- LEAK HAD BEENCLAMPED. 8/26/1997 - 0700 REMEDIATION AND CLEAN UP STARTED.
2017-09-29 08:50 | YES | NO | 19970139 | 1997-09-26 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-08-21 | 1035 | MO | ST. CHARLES |  | NO |  | NO | THE LEAK OCCURED IN GOVERNMENT SURVEY NUMBERS 762 AND 1779 IN T47N R4E IN ST. CHARLES COUNTY, MO. |  | LINE PIPE | VALVE |  | 1996 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 123978.9366 | 250115.5921 | FUEL OIL | 3 | 143 | 143 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1250 | 138 | YES | 8 | 2037 | 0 | 92 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEVEN BALL | 9185883850 | AT APPROX. 1035 HRS. ON AUGUST 21, 1997 A RELEASE OF FUEL OIL OCCURED FROM AHALF INCH FITTING ON WILLIAMS PIPELINE 8" COLUMBIA- ST. CHARLES LINE. THECAUSE OF THE RELEASE WAS DUE TO A WPL OPERATOR ERRROR. (SEE REPORT)
2017-09-29 08:50 | YES | NO | 19970140 | 1997-10-08 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1997-09-08 | 1620 | AR | WOODRUF |  | NO |  | NO |  |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 70845.1066 | 142923.1955 | BUTANE | 2 | 1442 | 91 | NO | NO | 12 | 0.25 | 46000 | WELDED |  | 1200 | 600 | YES | 24 | 1508 | 0 | 83 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ERNEST HAGAN | 7137593845 | AT APPROX. 1620 HRS, SEPT 8, 1997 , TEPPCO OPERATIONS PERSONNEL NOTICED ACHANGE IN THE RATES AND PRESSURE ON OUR 12" LINE P-74. THE PIPELINE SYSTEM WASIMMEDIATELY SHUT DOWN AND EMERGENCY PLAN WAS INITIATED. AN OUTSIDE TELE[PHONECALL WAS RECIEVED FROM A CONTRACOR STATING HE HAD STRUCK OUR PIPELINE AND THISHAD RESULTED IN A RELEASE IN WOODRUFF COUNTY, ARKANSAS NEAR THE WHITE RIVER.PERSONNEL WERE DISPATCHED TO THE SITE, AND THE AFFECTED LINE SECTION WASBLOCKED IN. THE REQUIRED ONE-CALL NOTIFICATION HAD NOT BEEN MADE TO THECONTRACTOR. THE AFFECTED SECTION OF PIPING WAS EXCUVATED OF PRODUCT, AND NEWPIPING WAS PLACED INTO THE SYSTEM. THE SYSTEM WAS PLACED BACK INTO SERVICE ONSEPT. 10, 1997. THE CONTAMINATED SOIL HAS BEEN STOCK PILE ON SITE INPREPARATION FOR DISPOSAL IN A SUITABLE LANDFILL.
2017-09-29 08:50 | YES | NO | 19970141 | 1997-10-06 | 22610 | WILLIAMS PIPELINE CO | YES | 1997-08-29 | 1438 | NE | WASHINGTON |  | NO |  | NO | THE LEAK OCCURED IN THE NE1/4 OF THE SW1/4 OF SECTION 7 IN T18N, R12E, IN WASHINGTON COUNTY, NE. |  | LINE PIPE | NO DATA |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 85014.1279 | 171507.8346 | L. P. G. | 2 | 2285 | 0 | YES | NO | 6.63 | 0.22 | 35000 | WELDED |  | 1440 | 509 | YES | 8 | 1984 | 0 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | STEVEN BALL | 9185883850 | AT 14:24 HRS ON AUG. 30, 1997 , OPERATIONS CONTROL RECIEVED A CALL FROM ALANDOWNER INDICATING THAT A LINE HAD BEEN PUNCTURED NEAR BLAIR, NEBRASKA.OPERATIONS CONTROL IMMEDIATELY NOTIFIED WPL'S SOUTHERN REGION OFFICE.(NOATTEMPT WAS MADE TO SHUT DOWN OUR 6" LINE IN THE AREA SINCE IT WAS ALREADYDOWN DUE TO NORMAL OPERATIONS.) AT 14:45 HOURS, THE LOCAL AREA MAINTENANCESUPERVISOR WAS NOTIFIED BY THE SOUTHERN REGION OFFICE TO GO TO THE SITE TOVERIFYTHAT IT WAS IN FACT WPL'S LEAK AND TO BEGIN CLOSING VALVES ACCORDINGLY.WHEN THE AREA MAINTENANCE SUPERVISOR ARRIVED AT THE SITE AT 15:30 HOURS, HEWAS GREETED NY MEMBERS OF THE BLAIR FIRE DEPT. IT WAS IMMEDIALTELY DETERMINEDTHAT IT WAS WPL'S #26 PROPANE LINE BY THE PRESSURE OF CLEARLY VISIBLE PIPELINEMARKERS. THE UPSTREAM VALVE ON THE LINE WAS THEN CLOSED AT MP 179 AT APPROX.15:40 HOURS. IT WAS DECIDED TO KEEP THE DOWNSTREAM VALVE AT MP 192 OPEN TORELIEVE PRESSURE FROM THE LEAK. THIS VALVE WAS THEN CLOSED AT 16:20 HOURS.SEE REPORT.
2017-09-29 08:50 | NO | NO | 19970143 | 1997-10-02 | 809 | ARCO PIPE LINE CO. | YES | 1997-08-26 | 1530 | CA | SAN BERNARDINO |  | NO |  | YES | APPROX. 5 MILES EAST OF DANBY PUMP STATION |  | LINE PIPE | NO DATA |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 46049.3193 | 92900.0771 | CRUDE OIL | 1 | 48 | 48 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1170 | 900 | YES | 12 | 1480 | 9 | 97 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAN HISEY | 5627282000 | CONTRACTORS FOR ARCO PIPELINE WERE IN THE PROCESS OF RECOATING A SECTION OFLINE 90 WHEN A PINHOLE CASUED BY CORROSION WAS DISCOVERED. APPARENTLY THEPIPELINE HAD BEEN LEAKING AT THIS LOCATION FOR AN INDETERMINATE AMOUNT OFTIME. THE OPERATIONS CONTROL CENTER WAS NOTIFIED IMMEDIAELEY AND THE PIPELINEWAS SHUT DOWN. SUBSEQUENTLY REMEDIATION EFFORTS RESULTED IN THE REMOVAL OFAPPROX. 675 TONS OF CRUDE OIL-IMPACTED SOIL.
2017-09-29 08:50 | YES | NO | 19970144 | 1997-10-06 | 19522 | TOSCO CORP | NO | 1997-09-09 | 1045 | CA | KERN |  | NO |  | NO | SECTION 9 T28S, R20E MDM; APPROX. 5 MILES SE/INTERSECTION OF STATE HIGHWAY 33 AND BROWN MATERIAL RD., KERN COUNTY CA. |  | LINE PIPE | PIPE |  | 1921 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | 9564.0894 | 19294.6314 | CRUDE OIL | 1 | 135 | 85 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 812 | 801 | YES | 4 | 1016 | 7 | 95 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID KINSER | 8057656092 | ON THE MORNING OF 9/9/97 THE MIDDLEWATER #2 LINE WAS OPERATING AT 800 PSI. ATAPPROX. 0815 A PRESSURE DROP OCCURRED AND TRHE PIPELINE WAS SHUT DOWN. FIELPERSONNEL WERE DISPATCHED TO DETERMINE THE CAUSE. AT APPROX. 0930, THEPIPELINE WAS RESTATRTED WITH ONE PUMP TO CHECK RELEIF VALVES, CONTROL VALVES,PRESSURE TRANSMITTERS, ETC., AND THE FLOW RATE AND OPERATING PRESSUREPARAMETERS APPEARED NORMAL. AT APPROX. 1022, HRS A SECOND PUMP WAS STARTED ANDTHE CONTROL CENTER DETERMINED THAT THE PIPELINE PRESSURE DID NOT MEETEXPECTATIONS, AND THE PIEPLINE WAS SHUT DOWN. AT APPROX. 1045 HRS, FIELDPERSONNEL REPORTED FINDING A CRUDE OIL LEAK ON THE MIDDLEWATER #2 LINE APPROX.3/4 MILE NORTH OF THE MIDDLEWATER PUMP STATION.
2017-09-29 08:50 | YES | NO | 19970145 | 1997-10-06 | 15674 | PLANTATION PIPE LINE CO | YES | 1997-09-09 | 845 | VA | FAIRFAX |  | NO |  | NO | SITE IS LOCATED ON THE NORTH SIDE OF BRADOCK ROAD ACROSS FROM ADDRESS 12915 BRADDOCK RD. THE PROPERTY IS LOCATED ION THE ROAD ROW BEHIND HAMPTON FOREST. |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 98000 | 69428.2045 | 140064.7316 | TURBINE FUEL | 1 | 52 | 52 | NO | NO | 6.58 | 0.19 | 42000 | WELDED |  | 1480 | 60 | YES | 8 | 2100 | 12 | 1995 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | KAREN BANE | 7035418101 | THIS SECTION OF BRADDOCK RD WAS BEING WIDENED BY VDOT. VDOT EMPLOYED ASUBCONTRACTOR, A&W CONSTRUCTION TO DO PORTIONS OF THIS WORK. A & W HAD CALLEDTHE ONE CALL SYSTEM AND THE LINE WAS MARKED. PLANTATION PERSONNEL HAD MADEARRANGEMENTS TO MET A & W ON SITE THE MORNING OF THE ACCIDENT. A & W BEGANWORK PRIOR TO THE PLANTATION REPRESENTATIVE'S ARRIVAL AND STRUCK THE LINE WITHA FRONT END LOADER. THE OPERATOR IMMEDIATELY CONTACTED PLANTATION AFTERHITTING THE LINE AND THE PIPELINE WAS SHUTDOWN.
2017-09-29 08:50 | YES | NO | 19970146 | 1997-10-06 | 26304 | UNOCAL PIPELINE CO - WESTERN REGION | NO | 1997-09-08 | 2100 |  |  |  | YES | X=1,938,603 Y=217,526 | NO | ACCIDENT OCCURED AT SPIRIT ENERGY 76, EUGENE ISLAND BLOCK 372A |  | LINE PIPE | PIPE |  | 1987 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 106267.6599 | 214384.7932 | CRUDE OIL | 1 | 3 | 0 | NO | NO | 6 | 0.43 | 35000 | WELDED |  | 1440 | 1000 | YES | 8 | 1800 | 9 | 87 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | PHILLIP PLAISANCE | 5048682186 | PLATFORM OPERATOR HEARD A LOUD BOOM SOUND. PIPELINE PUMP SHUT DOWN ON LOWPRESSURE, OPERATOR NOTICED OIL LEAKING OUT THE TOP OF THE J-TUBE. COATINGFAILED IN SPLASH ZONE AND RUPTURED AT THE + 3' ELEVATION.
2017-09-29 08:50 | YES | NO | 19970147 | 1997-10-06 | 19226 | TEXACO PIPELINE INC | NO | 1997-09-18 | 157 | LA | ST JAMES PARISH |  | NO |  | NO | FLANGE DISCHARGE OF METER SKID. |  | PUMPING STATION | OTHER | FLANGE | 1984 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 3 | 300 | 220 | NO | NO | 0 | 0 | 0 | FLANGED |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | OTHER | GASKET FAILURE | Null | NO DATA |  | Null | Null | RICHARD GARY | 5048733415 | GASKET ON FLANGE BLEW OUT & DIESEL FUEL ON GROUND WAS SEEN BY LA PLANTEMPLOYEE MAKING NORMAL INSPECTION OF THE AREA. HE SHUT DOWN THE STATION USINGTHE EMERGENCY SHUTDOWN BUTTON AT THE STATION SITE.
2017-09-29 08:50 | YES | NO | 19970148 | 1997-10-20 | 2552 | COLONIAL PIPELINE CO | YES | 1997-09-11 | 1300 | SC | ANDERSON | BELTON | NO |  | NO | 1916 CAMELOT FOREST BELTON,SC 29627 |  | TANK FARM | TANK |  | 1963 | OTHER | UNKNOWN AT THIS TIME | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 190010 | 134612.7871 | 271568.3637 | GASOLINE | 1 | 10 | 6 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES A COX | 4048412296 | ON SEPTEMBER 11, 1997 THE ENVIROMENTAL TECHNICIAN WAS CHECKING THE MONITORINGWELL ADJACENT TO TANK NO. 513 AND DISCOVERED FREE PRODUCT IN WELL. THETECHNIICIAN THEN BEGAN CHECKING OTHER MONITORING WELLS TO ISOLATE THE PROBLEM.IT WAS DETERMINED THE PRODUCT WAS ONLY IN TANK NO. 13 DIKE AREA. OTHER WELLSWERE DRILLED AND CONFIRMED TANK 513 WAS LEAKING. THE DITRCT ENVIROMENTALPROJECT MANAGER CALLED SOUTH CAROLINA DEPTMENT OF HEALTH AND ENVIROMENTALCONTROL(SCDHEC) ON 9/15/97 AND ADVISED THEM OF THE SITUATION. AS OF 9/16/97COLONIAL HAD ONLY RECOVERED 15 GALLONS OF PRODUCT, BUT ANTICIPATED REPAIR ANDCLEAN-UP WERE EXPECTED TO EXCEED 50000. ON 9/16/97, THE OPERATIONS MANAGERADVISED THE NATIONAL RESPONSE CENTER (NRC REPORT NO. 403845) AND ANDERSONCOUNTY EMRGENCY PREPARDNESS AGENCY. APPROX. 5 BARRELS HAVE BEEN RECOVERED ASOF 10/14/1997. THE CAUSE OF THE LEAK IS UNDER INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19970149 | 1997-10-15 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-09-16 | 1700 | OK | PAYNE |  | NO |  | NO | NW/4 SECTION 16 TOWNSHIP 20 NORTH, RANGE 3 EAST PAYNE COUNTY, OK |  | LINE PIPE | PIPE |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 4959.1575 | 10004.6237 | CRUDE OIL | 1 | 340 | 330 | NO | NO | 12.75 | 0.25 | 42000 | WELDED |  | 1186 | 17 | YES | 8 | 1524 | 12 | 94 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | VANCE WEBB | 4057674845 | ON SEPT. 16,1997 AT 1915HRS., THE CONOCO PIPELINE(CPL) OIL MOVEMENTS CENTER INHOUSTON, TX RECIEVED A REPORT OF A POTENTIAL RELEASE ON THE CUSHING TO PONCACITY 12" CRUDE OIL PIPELINE SYSYTEM VIA TELEPHONE. THE PIPELINE WAS IN ASTATIC MODE ( NOT PUMPING) AT THE TIME OF THE REPORT, FOR THIS REASON IT WASNOT NECESSARY TO IMPLEMENT EMERGENCY SHUT DOWN PROCEDURES. CUSHING AND POCACITY, OK TO INVESTIGATE THE POSSIBLE RELEASE. RESPONSE CREWS CONFIRMED THEEXISTENCE OF A RELEASE @ 20:10 HRS. THE REPSONSE CREWS FOUND THAT OKEMAHCONSTUCTION HAD PUNCTURED THE CPL LINE WHILE IN THE PROCESS OF EXCAVATING TOBURY A NEW PIPELINE FOR THE PHILLIPS PIPELINE CO. BECAUSE THE RELEASED OIL WASCONTAINED IN THE NEWLY EXCAVATED PIPELINE TRENCH, CLEANUP REQUIREMENTS WEREMINIMAL. THE DAMAGED SEGMENT OF LINE WS REPLACED AND THE SYSTEM WAS PLACEDBACK IN OPERATION. SEE REPORT.
2017-09-29 08:50 | YES | NO | 19970150 | 1997-10-09 | 25146 | LYONDELL PETROCHEMICAL CO | NO | 1997-09-09 | 1030 | TX | HARRIS |  | NO |  | NO | THE VALVE IS INSIDE THE HESS GALENA PARK TERMINAL, NEXT TO THE PTRA RAILROAD TRACKS. APPROX. 300 YARDS EAST OF FEDERAL RD. |  | LINE PIPE | VALVE |  | 1955 | OTHER | POLYMER BUILDUP IN VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 2550.4238 | 5145.235 | BUTANE | 2 | 17 | 164 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null
2017-09-29 08:50 | YES | NO | 19970151 | 1997-10-10 | 19335 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1997-09-14 | 1700 | TX | CRANE |  | NO |  | NO | 4 MILES NORTH OF CRANE TX, SECTION 9 BLOCK X, CCSD & RGNGRRCO. SURVEY |  | TANK FARM | PIPE |  | 1965 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10626.766 | 21438.4793 | CRUDE OIL | 1 | 400 | 270 | NO | NO | 16 | 0.31 | 24000 | WELDED |  | 125 | 20 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL |  |  | Null |  |  | Null | Null | EDWIN GRIPP | 9159479000 | THE HYDROCARBON RELEASE WAS REPORTED BY CRANE STATION TOUR ENGINEER AT 5:00 PMCDST ON SEPT. 14, 1997. CAUSE OF THE RELEASE WAS DETERMINED TO BE INTERNALCORROSION IN A 16" TANK LINE SERVICING A CURRENTLY IDLE STORAGE TANK. THEREALEASE WAS CONTAINED WITHIN THE TANKS FIREWALL. THE LINE WAS CLAMPED ANDFREE OIL RECOVERED WITH VACUUM TRUCKS. CLEANUP WILL BE ACCORDANCE WITH STATEOF TEXAS STATEWIDE RULE 91. PERMANENT REPAIRS WILL BE COMPLTETED BYDICONNECTING AND PURGING THE TANK LINE FROKM STATION MANIFOLD.
2017-09-29 08:50 | YES | NO | 19970152 | 1997-10-14 | 26041 | GATX TERMINALS CORP | NO | 1997-09-09 | 1500 | CA | RANCHO DOMINGUEZ |  | NO |  | NO | 18900 SANTA FE AVE, RANCHO DOMINGUEZ, CA |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 85014.1279 | 171507.8346 | DIESEL FUEL | 1 | 50 | 29 | NO | NO | 6 | 0.28 | 2160 | WELDED |  | 600 | 200 | YES | 4 | 775 | 5 | 96 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID KINGSTON | 3105187705 | RECIEVED A TELEPHONE CALL FROM THE LOS ANGELES BAIN CALL WHEEL REPORTING ADIESEL FUEL SPILL LOCATED IN THE 18900 BLOCK OF SANTA FE AVE. IN RANCHODOMINGUEZ. AFTER GATX PERSONNEL ARRIVED AT THE SCENE, A STAND UP PRESSURE TESTWAS CONDUCTED TO DETERIMNE IF GATX'S PIPLINE WAS LEAKING. THE STAND UPPRESSURE REST FUEL HAD BREACHED THE NEARBY COMPTON CREEK. GATX, WORKING INCONCERT WITH THE DEPT. OF FISH AND GAME INITIATED CLEANUP OF THE CLEANUP OFTHE CREEK BED. ONCE THE RELEASE IN TEH CREEK WAS UNDER CONTROL, GATX BEGANEXCAVATION OF THE PIPELINE RELEASE AREA. WHEN THE LEAK AREA WAS EXPOSED, ASMALL AREA OF LOCALIZED CORROSION WAS DISCOVERED. THE CORROSION PROBABLYOCCURED BECAUSE THE CARIER PIPE WAS SHORTED TO THE CAUSING PIPE. APPROX. 120FEET OD CASING PIPE WAS PERMANENTLY REMOVED AND APPROX. 170 FEET OF NEW 6-INCHPIPE WAS INSTALLED.
2017-09-29 08:50 | YES | NO | 19970153 | 1997-10-27 | 3012 | PRIDE TEXAS PLAINS L.P. | NO | 1997-10-01 | 1030 | TX | COTTLE |  | NO |  | NO | APPROX. 12 MILES SOUTH EAST OF PADUCAH, TX OFF FM RD 1038 ON COUNTY RD 485. |  | LINE PIPE | PIPE |  | 1927 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 17711.2767 | 35730.7989 | CRUDE OIL | 1 | 2643 | 0 | NO | NO | 10 | 0.37 | 25000 | WELDED |  | 800 | 700 | YES | 8 | 1000 | 4 | 76 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN MACON | 9156748231 | PIPELINE WAS SHUT DOWN AT 6:30 PM ON 9-30-97 DUE TO PRESSURE IRREGULARITIES.QUESTIONABLE PIPELINE SECTION WAS ISOLATED BY CLOSING MAINLINE VALVES ANDPIPELINE LEFT DOWN FOR THE NIGHT. LEAK WAS REPORTED ON 10/1/97 BY PRIDE'SPIPELINE PATROL PLANE. CREWS WERE DISPATCHED FOR SPILL CONTAINMENT AND TOCLAMP THE LINE. CLEAN UP ONGOING PER STATE WIDE RULE 91.
2017-09-29 08:50 | YES | NO | 19970154 | 1997-11-26 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1997-10-28 | 1245 | NJ | SOMERSET |  | NO |  | NO | SEE ATTACHED DRAWING NO. -11789-A |  | NO DATA | OTHER | 1/2" PRESSURE SENSE LINE | 1974 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1416902.132 | 2858463.9096 | GASOLINE | 3 | 50 | 35 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | C.A. OSTACH, MANAGER, OPERATIONS SERVICES | 6107704495 | ON TUESDAY, OCTOBER 28, 1997, WHILE PERFORMING A ROUTINE MAIN LINE VALVEINSPECTION, A BUCKEYE MAINTENANCE EMPLOYEE DISCOVERED PETROLEUM PRODUCT ATBUCKEYE'S HAMILTON ROAD MAIN LINE VALVE SITE. AFTER ON SITE INVESTIGATIN, A1/2 INCH PRESSURE SENSE LINE WAS DISCOVERED RELEASING PETROLEUM PRODUCT. ALLAPPLICABLE REGULATORY AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIESWERE PERFORMED UNDER THE SUPERVISION OF THE NEW JERSEY DEPARTMENT OFENVIRONMENTAL PROTECTION; HILLSBOROUGH FIRE DEPARTMENT; HILLSBOROUGHTOWNSHIP; OFFICE OF EMERGENCY MANAGEMENT; AND SOMERSET COUNTY; OFFICE OFEMERGENCY MANAGEMENT.
2017-09-29 08:50 | YES | NO | 19970155 | 1997-12-10 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1997-11-07 | 1710 | OK | NOBLE |  | NO |  | NO | 4 MILES N OF PERRY, OK, SECTION 33 T22N R1W |  | LINE PIPE | PIPE |  | 1970 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 22670.4341 | 45735.4226 | NATURAL GAS LIQUID | 2 | 722 | 0 | NO | NO | 6 | 0.22 | 46000 | WELDED |  | 1431 | 625 | YES | 24 | 1898 | 9 | 70 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | JERRY ROGERS, REGULATIONS, HEALTH & SAFETY MANAGER | 5803952377 | FARMER PLOWING IN FIELD HITTING PIPELINE CAUSING RELEASE.
2017-09-29 08:50 | YES | YES | 19970156 | 1997-12-09 | 30991 | MOBIL OIL CORPORATION | NO | 1997-10-31 | 1715 | TX | NAVARRO |  | NO |  | NO | MERTENS STATION - 23 MILES WEST OF CORSICANA, TEXAS ON STATE HWY. 22 |  | LINE PIPE | SCRAPER TRAP |  | 1971 | OTHER | INCRECT CNSTRCT MAINTEN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 22500 | 15940.149 | 32157.719 | NOT GIVEN | 2 | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT, MANAGER, MAINLINE CRUDE/NGL OPERATIONS | 2146585914 | SEE ATTACHED INVESTIGATION REPORT (4 PAGES)
2017-09-29 08:50 | YES | NO | 19970157 | 1997-12-08 | 12106 | MAPCO INC | YES | 1997-11-12 | 345 | MN | DAKOTA |  | NO |  | NO | THREE QUARTERS OF A MILE WEST OF HIGHWAY 52 AND 55 ON 117TH STREET, PINE BEND, MINNESOTA |  | NO DATA | OTHER | PUMP SEAL | 1960 | OTHER | SEAL FAILURE ON TERMINAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 552.5918 | 1114.8009 | BUTANE | 2 | 20 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL C. PERSON, P.E., MANAGER, PIPELINE ENGINEERING | 9185994043 | SEAL ON LOADING PUMP FAILED CAUSING A PRODUCT RELEASE. LOADING PUMP WASISOLATED AND THE SEAL WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19970158 | 1997-12-04 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1997-11-03 | 1045 | IL | SALINE |  | NO |  | NO | ALLENTOWN ROAD, EAST OF HARCO, IL |  | LINE PIPE | OTHER |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 88556.3833 | 178653.9943 | BUTANE | 1 | 210 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | ERNEST P. HAGAN, VICE PRESIDENT-OPERATIONS | 7137593845 | AT APPROXIMATELY 1045 HOURS EST, ON NOVEMBER 3, 1997, A TEPPCO CONTRACTMAINTENANCE CREW, WORKING IN SALINE COUNTY ILLINOIS, WAS PUSHING DIRT OFF THETOP OF TEPPCO'S 20"LINE P-2 AT A PIPELINE REHABILITATION DIG SITE. IN THEPROCESS, THEIR BACKHOE HIT A 1/2-INCH NIPPLE EXTENDING OFF THE PIPELINE,BREAKING THE NIPPLE IN THE THREADED AREA. THIS BREAK CAUSED A RELEASE OFPROPANE. THE CONTRACT CREW IMMEDIATELY NOTIFIED TEPPCO OPERATIONS PERSONNEL.THER EMERGENCY PLAN WAS IMMEDIATELY INITIATED, THE LINE WAS SHUT DOWN ANDMAINLINE BLOCK VALVES WERE CLOSED TO ISOLATE THE AFFECTED SECTION OF PIPING.LOCAL AUTHORITIES WERE NOTIFIED AND ASSISTED IN CORRDINATING AN EVACUATION OFTHE IMMEDIATE AREAS AS A PRECAUTIONARY MEASURE. STOPPLES WERE SET, PRODUCTWAS FLARED AND NECESSARY REPAIRS WERE ACCOMPLISHED. THE PIPELINE WAS RETURNEDTO SERVICE ON NOVEMBER 6, 1997.
2017-09-29 08:50 | YES | NO | 19970159 | 1997-11-26 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-11-02 | 1345 | MT | YELLOWSTONE |  | NO |  | NO | T2S, R24E, SECTION 10, MILEPOST 16. APPROXIMATELY 1.5 MILES EAST OF LAUREL, MONTANA. |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 28338.0426 | 57169.2782 | DIESEL FUEL | 3 | 150 | 95 | NO | NO | 4.5 | 0.21 | 35000 | WELDED |  | 500 | 40 | YES | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W. BEGGS, DIRECTOR OF REGUALTORY COMPLIANCE | 3036494090 | THIS PIPELINE SYSTEM IS A 4" 16 MILE PIPELINE THAT SUPPLIES DIESEL FUEL TOMONTANA RAIL LINK. THIS SYSTEM IS A LOW STRESS PIPELINE THAT IS AUTOMATICALLYACTIVATED BY FLOAT SWITCHES IN TANKAGE AND IS METERED AT BOTH ENDS. OPERATORSIN THE BILLINGS OFFICE BEGAN TO NOTICE ABNORMAL DIFFERENCES BETWEEN UPSTREAMAND THE DOWNSTREAM METER TOTALS DURING WEEKLY CLOSEOUTS. ON OCTOBER 30, 1997,THE LINE WAS BLOCKED IN AND TESTED IN SECTIONS FOR A LEAK. THE SECOND TESTSECTION, 1.1 MILES IN LENGTH, SHOWED A DEFINITE PRESSURE DROP AND BY NARROWINGTHE TESTS IN THIS SECTION A PIN-HOLE LEAK WAS DISCOVERED IN THE PIPELINE ONNOV. 2, 1997. INSPECTION OF THE PIPE SHOWED THE LEAD TO BE IN AN AREA, THATAT SOME POINT, HAD BEEN RE-WRAPPED WITH A DIFFERENT COATING. THE LEAK WAS ANISOLATED CORROSION PIT. THE CORROSION LOOKED NONACTIVE AND COULD HAVE BEENCAUSED PRIOR TO THE INSTALLATION OF A ADDITIONAL RECTIFIER IN 1987. CATHODICPROTECTION READINGS INDICATED PROTECTION LEVELS IN THE LEAK AREAS ARE HIGHERTHAN THAT REQUIRED TO CONTROL CORROSION.
2017-09-29 08:50 | YES | NO | 19970160 | 1997-11-25 | 4805 | EXPLORER PIPELINE CO | YES | 1997-10-27 | 1130 | OK | OKFUSKEE |  | NO |  | NO | NW 1/4 OF SE 1/4 OF SECTION 36 T12NR11E. 6 MILES WEST AND 3 MILES NORTH OF HENRYETTA |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 425070.6396 | 857539.1729 | FUEL OIL | 3 | 2000 | 1689 | NO | NO | 28 | 0.28 | 52000 | WELDED |  | 672 | 175 | YES | 24 | 1048 | 3 | 71 | EXTERNAL | Null | YES | OTHER | BACTERIA | NO DATA |  | Null | NO DATA |  | Null | Null | RODNEY E. SANDS, VICE PRESIDENT OPERATIONS | 9184935100 | SEE ATTACHMENT "A"
2017-09-29 08:50 | NO | NO | 19970161 | 1997-11-20 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1997-10-20 | 945 | IA | HANCOCK |  | NO |  | NO | ONE MILE SOUTH AND ONE MILE EAST OF GARNER, IA |  | NO DATA | OTHER | THREADED NIPPLE FOR 1" VA | 1970 | OTHER | FAILED NIPPLE FOR 1" VALV | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14169.0213 | 28584.6391 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | YES | YES | MARC DEVARENNES, OPERATIONS MANAGER | 5734865488 | 86 TONS WERE RELEASED. KOCH CONTRACTOR WAS HAND REMOVING SOIL FROM TOP OF THEPIPELINE TO COMPLETE EXCAVATION FOR VALVE MAINTENANCE. NH3 VAPORS PRESENTCAUSED CONTRACTOR TO LEAVE HOLE FOR MORE PPE. WHILE PUTTING ON PPE, AMMONIABEGAN RELEASING FROM A 1" THREADED VALVE FITTING. LINE WAS ISOLATEDIMMEDIATELY. NO INJURIES, EXPLOSION, OR FIRE. FOUND THE 1" THREADED FITTINGWAS CRACKED AT THE BASE. SENT TO METALURGIST FOR EVALUATION. PRELIMINARYINDICATIONS SHOW CORROSION NOT A FACTOR. COMPLETE ANALYSIS HAS NOT BEENRECEIVED AT THE TIME OF THIS REPORT.
2017-09-29 08:50 | YES | NO | 19970162 | 1997-11-19 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1997-11-10 | 630 | NM | LEA |  | NO |  | NO | SEC. 27, T-21-S, R-36-E. APPROXIMATELY 5 MILES WEST OF EUNICE, NEW MEXICO |  | PUMPING STATION | PUMP |  | 1995 | OTHER | SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4250.7064 | 8575.3917 | CRUDE OIL | 1 | 721 | 325 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LENNAH FROST, ENVIRONMENTAL ENGINEER | 9156872040 | GAUGER CHECKED STATION AND EQUIPMENT AT 7:30 A.M. ON 11/9/97-NO PROBLEMS.GAUGER RETURNED AT 7:30 A.M. ON 11/10/97 AND FOUND SEAL HAD FAILED ON PUMP.HE SHUT DOWN STATION AND BEGAN EMERGENCY RESPONSE NOTIFICATIONS ANDPROCEDURES. MAINTENANCE CREW RECOVERED 325 BARRELS OF CRUDE OIL. AREA WILL BEREMEDIATED ON SITE.
2017-09-29 08:50 | YES | NO | 19970163 | 1997-11-18 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1997-10-22 | 715 | KS | KIOWA |  | NO |  | NO | SE 1/4 SECTION 19, TOWNSHIP 30 SOUTH, RANGE 18 WEST IN KIOWA COUNTY, KANSAS 13 MILES SOUTH OF GREENSBURG, KANSAS |  | PUMPING STATION | PUMP |  | 1966 | OTHER | STARTER RELAY SWITCH FAIL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 708.4511 | 1429.232 | CRUDE OIL | 1 | 80 | 77 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA | UNDER DEPOSIT CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON, SUPERINTENDENT OF OPERATIONS | 3162419270 | THE STARTER RELAY SWITCH HAD BURNED OUT, WHICH DID NOT ALLOW THE STATION PUMPTO START. OIL RAN OUT OF OVERFLOW LINE ON TANK AND WAS CONTAINED INSIDE TANKDIKE.
2017-09-29 08:50 | YES | NO | 19970166 | 1997-11-07 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1997-10-09 | 1326 | MI | WAYNE | MELVINDALE | NO |  | NO | SEE ATTACHED DRAWING NO. 11783-A |  | LINE PIPE | LONGITUDINAL WELD |  | 1955 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 46049.3193 | 92900.0771 | DIESEL FUEL | 3 | 1677 | 1650 | NO | NO | 10 | 0.28 | 2390 | WELDED |  | 1120 | 680 | YES | 24 | 1502 | 10 | 75 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | C.A. OSTACH, MANAGER, OPERATIONS SERVICES | 6107704495 | ON THURSDAY, OCTOBER 9, 1997, AT 1222, BUCKEYE COMMENCED PUMPING FROM ITSDETROIT STATION WESTWARD TOWARD ITS WAYNE STATION. AT 1250, BUCKEYE'S DETROITSTATION PUMP UNITS WENT DOWN ON LOW SUCTION. GIVEN ABNORMAL PRESSURE AND FLOWRATE CONDITIONS, DETROIT STATION REMAINED SHUTDOWN. PERSONNEL BEGANIMMEDIATELY TO WALK AND INVESTIGATE THE DETROIT TO WAYNE 10" LINE SECTION. ONFRIDAY, OCTOBER 10, 1997, BUCKEYE CONFIRMED AND LOCATED A RELEASE FROM THE 10"DETROIT TO WAYNE STATIONS LINE SECTION. THE RELEASE WAS LOCATED ON THEMARATHON REFINERY PROPERTY, INSIDE MARATHON'S TANK #110 DIKE AREA. ALLAPPPLICABLE REGULATORY AGENCIES WERE NOTIFIED AND ALL RELEASED PRODUCT WASCONTAINED AND COLLECTED IN MARATHON'S TANK DIKE DRAIN SYSTEM THT FEEDS INTO ANOIL/WATER SEPARATOR. RECOVERY AND CLEANUP ACTIVITIES WERE CONDUCTED UNDER THESUPERVISION OF THE MICHIGAN DEPARTMENT OF ENVIRONMENTAL QUALITY.
2017-09-29 08:50 | NO | NO | 19970167 | 1997-11-07 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1997-10-04 | 815 | MO | STODDARD |  | NO |  | NO | 12 MILES WEST OF SIKESTON, MO ON STATE ROAD AB |  | LINE PIPE | OTHER |  | 1978 | OTHER | FAILED GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | JET FUEL | 1 | 18 | 10 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | O.H. CUNNINGHAM, VICE PRESIDENT TECHNICAL SERVICES | 7137593615 | ON OCTOBER 4, 1997, AT APPROXIMATELY 0815 HOURS, CDT, TEPPCO PERSONNELRECEIVED A TELEPHONIC NOTICE OF POTENTIAL RELEASE OF PRODUCT. THE EMERGENCYPLAN WAS IMMEDIATELY INITIATED AND THE LINE WAS SHUT DOWN. PERSONNEL ANDTEPPCO'S OSRO WERE IMMEDIATELY DISPATCHED TO THE LOCATION IDENTIFIED BY THECALLER. ON ARRIVAL AT THE SCENE, IT WAS IMMEDIATELY DETERMINED A GASKETBETWEEN THE VALVE FLANGE AND THE PIPE FLANGE HAD FAILED. THE GASKET WASREMOVED AND REPLACED. REMEDIATION TO THE AFFECTED AREA BEGAN IMMEDIATELY.THE SYSTEM WAS PLACED BACK INTO THE SERVICE LATE EVENING, OCTOBER 4, 1997.
2017-09-29 08:50 | YES | NO | 19970168 | 1997-10-28 | 18519 | SANTA FE PACIFIC PIPELINE CO | NO | 1997-04-17 | 838 | CA | IMPERIAL |  | NO |  | NO | 2 MILES NO. OF SHANK ROAD, BRAWLEY, CA, LS-58 PLMP 15.6 |  | LINE PIPE | PIPE |  | 1958 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 106267.6599 | 214384.7932 | DIESEL FUEL | 3 | 70 | 50 | NO | NO | 6 | 0.22 | 0 | WELDED |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD, SENIOR VICE PRESIDENT, OPERATIONS & ENGINEERING | 7145604720 | A LEAK OF DIESEL FUEL WAS OBSERVED BY A FARMER WORKING IN A FIELD NEXT TO THEBURIED PIPE. THE PIPE IS IN A CASING THAT CROSSES BENEATH A SET OF RAILROADTRACKS. THE LEAKED FUEL ESCAPED FROM THE CASING THROUGH A VENT PIPE ANDSTAINED THE SURFACE SOILS. THE LEAK WAS REPAIRED BY REPLACING THE PIPE ANDSEVERAL HUNDRED CUBIC YARDS OF AFFECTED SOIL WERE EXCAVATED AND TREATED.
2017-09-29 08:50 | YES | NO | 19970169 | 1997-11-04 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1997-10-01 | 1120 | KS | SEDGWICK |  | NO |  | NO | , NE QUARTER SECTION 12-TOWNSHIP 26 SOUTH-RANGE 1 WEST, 4 MILES SOUTH OF VALLEY CENTER, KANSAS |  | LINE PIPE | PIPE |  | 1925 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 42600 | 30180.0154 | 60885.2813 | CRUDE OIL | 1 | 160 | 145 | NO | NO | 8.63 | 0.32 | 42000 | WELDED |  | 900 | 9 | YES | 0 | 1440 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | ALLEN R. WILKERSON, SUPERINTENDENT OF OPERATIONS | 3162419270 | THE PIPELINE WAS DOWN, AND ON AN UNKNOWN DATE, THE PIPELINE WAS HIT ON THE TOPOF THE LINE, PIERCING THE PIPE. NO CALLS WERE MADE TO JAYHAWK CONCERNING THELINE BEING DAMAGED. ON OCTOBER 1, 1997, JAYHAWK OPENED LINE FOR DELIVERIESAND SPILL OCCURRED FROM DAMAGED PIPE. THE PIPELINE WAS UNCOVERED AND REPLACEDWITH PRETESTED PIPE ON OCTOBER 1,1997 AND CLEANUP WAS FINISHED OCTOBER 2, 1997.
2017-09-29 08:50 | YES | NO | 19970170 | 1997-11-03 | 22855 | KOCH PIPELINE COMPANY, L.P. | YES | 1997-09-29 | 908 | OK | BEAVER |  | NO |  | NO | N1/2 OF SEC. 12 T4N R20E, 2 MILES S & 1/2 MILE E ON SOUTH SIDE OF HWY. 83 NEAR TURPIN, OK |  | LINE PIPE | PIPE |  | 1984 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 16250 | 11512.3298 | 23225.0193 | NOT GIVEN | 2 | 749 | 0 | NO | NO | 4 | 0.16 | 42000 | WELDED |  | 1440 | 1018 | YES | 8 | 1834 | 3 | 94 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | JERRY ROGERS, HEALTH & SAFETY MANAGER | 4053952377 | THIRD PARTY DOZER STRUCK PIPELINE CAUSING RELEASE OF PRODUCT.
2017-09-29 08:50 | YES | NO | 19970171 | 1997-11-04 | 15774 | PORTAL PIPELINE CO | YES | 1997-09-20 | 800 | ND |  |  | NO |  | NO | PORTAL PIPE LINE COMPANY'S MAXBASS STATION, LOCATED 3 MILES WEST OF MAXBASS, ND |  | TANK FARM | OTHER | TANK SUCTION LINE | 1962 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | CRUDE OIL | 1 | 50 | 45 | NO | NO | 12.75 | 0.25 | 42000 | WELDED |  | 15 | 10 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D. BURGESS, MANAGER OPERATIONS SERVICES | 2187250540 | ON SEPTEMBER 20TH AT 8:00 A.M., A MAXBASS GAUGER WHILE DOING ROUTINE DUTIES,FOUND 50 BARRELS OF CRUDE OIL INSIDE THE DIKE OF TANK 4004. ALL OF THE OILWAS CONTAINED BY THE TANK DIKE. AFTER THE OIL WAS RECOVERED AND THE 12"SUCTION PIPE WAS EXPOSED, DRAINED, AND REMOVED, IT WAS FOUND TO HAVE INTERNALCORROSION. THIS ENTIRE 12" PIPELINE WAS REPLACED WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 19970172 | 1997-11-24 | 18273 | SHELL PIPELINE CORP | NO | 1997-10-20 | 1005 | TX | RUSK |  | NO |  | NO | KILGORE-HOUSTON 10", MILE POLE 158, 30 MILES SOUTH OF KILGORE NEAR HWY. 1798/839 INTERSECTION IN A SMALL CREEK BED. |  | LINE PIPE | PIPE |  | 1931 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 127521.1919 | 257261.7519 | CRUDE OIL | 1 | 500 | 340 | NO | NO | 10 | 0.28 | 35000 | WELDED |  | 800 | 605 | YES | 0 | 1000 | 0 | 31 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | S.J. LANDREVILLE | 7132412953 | AT AN UNKNOWN TIME, THE PIPE WAS DAMAGED BY UNKNOWN THIRD PARTY. MECHANICALDAMAGE, COATING DAMAGE AND EXTERNAL CORROSION WERE PRESENT. AN 8-INCH SPLITWAS LOCATED AT THE TOP OF THE PIPE. THE FAILED PIPE WAS SENT TO AMETALURGICAL LABORATORY FOR ANALYSIS.
2017-09-29 08:50 | YES | NO | 19970173 | 1997-11-24 | 15851 | PRIDE REFINING INC | NO | 1997-10-23 | 1700 | TX | FISHER |  | NO |  | NO | 2 MILES NE OF MCCAULLEY, TEXAS ON COUNTY ROAD 277 |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 4 | 0.24 | 25000 | WELDED |  | 876 | 150 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON, PIPELINE MANAGER | 9156748231 | AT APPROXIMATELY 5:00 P.M. ON 10-23-97 MCCAULLEY WATER DEPARTMENT CALLED OUROFFICE AND REPORTED A SPILL. THE LINE WAS SHUT DOWN AND REPAIR CREWS WEREDISPATCHED. BY APPROXIMATELY 11:00 P.M. ON 10-23-97 THE SECTION OF THE LINEWAS REPLACED. CLEAN UP PROCEDURES ARE NOW IN PROGRESS PER STATE WIDE RULE #91.
2017-09-29 08:50 | YES | NO | 19970174 | 1997-11-24 | 443 | AMOCO PIPELINE CO | NO | 1997-10-16 | 920 | TX | GRIMES | ROANS PRAIRIE | NO |  | NO | APPROXIMATELY 1/4 EAST OF HIGHWAY 90 ON COUNTY ROAD 238 IN GRIMES COUNTY, TEXAS |  | LINE PIPE | PIPE |  | 1923 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 141690.2132 | 285846.391 | CRUDE OIL | 1 | 200 | 175 | NO | NO | 8 | 0.29 | 25000 | THREADED |  | 400 | 220 | YES | 24 | 700 | 0 | 76 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | ANDRE PARKER, SUPERVISOR CRUDE | 4099386909 | GRIMES COUNTY MAINTAINER WAS GRADING DITCH ALONGSIDE COUNTY ROAD 238 (CR238)WHEN HE STRUCK PIPELINE WITH BLADE OF MAINTENER CREATING A 4" GASH INPIPELINE. PIPELINE WAS IN OPERATION AT THE TIME. EMPLOYEE ON MAINTAINERNOTIFIED HIS SUPERVISOR WHO IN TURN NOTIFIED EMERGENCY PERSONNEL AND AMOCOPIPELINE CONTROL CENTER IN TULSA, OKLAHOMA. AMOCO PIPELINE'S CONTROL CENTERHAD ALREADY SHUT THE PIPELINE DOWN AND WERE IN THE PROCESS OF DISPATCHINGPERSONNEL TO ISOLATE THE SYSTEM WHEN THEY WERE NOTIFIED.
2017-09-29 08:50 | YES | NO | 19970176 | 1997-11-21 | 30779 | TORCH OPERATING COMPANY | YES | 1997-09-28 | 2200 |  |  |  | YES | 34/40/3 N 120/39/18.2 W | NO | LAT. 34 40 MIN. 03 SEC. NO. LONG. 120 39 MIN. 18.2 SEC W, SEE DRAWING ATTACHED |  | LINE PIPE | WELDING FITTING |  |  | OTHER | FLANGE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000000 | 3542255.3301 | 7146159.774 | CRUDE OIL | 1 | 170 | 78 | NO | NO | 20 | 0.69 | 46000 | FLANGED |  | 1354 | 600 | YES | 12 | 2532 | 12 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT K. SMALLEY, DOT COORDINATOR |  | THE FAILURE OCCURRED UNDERWATER IN THE OCEAN DURING A PIG RUN. A 20" FLANGEFAILED AT THE NECK AREA BETWEEN THE ATTACHMENT WELD AND THE BOLTED AREA.
2017-09-29 08:50 | YES | NO | 19970177 | 1997-11-20 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1997-10-20 | 1324 | OK | OTTAWA |  | NO |  | NO | 1 MILE SOUTHWEST OF WYANDOTTE, OK, NE/4 OF SECTION 32, TOWNSHIP 27 NORTH, RANGE 24 EAST, OTTAWA CO., OK |  | LINE PIPE | PIPE |  | 1930 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | GASOLINE | 1 | 1959 | 5 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 856 | 980 | YES | 8 | 1070 | 8 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | VANCE WEBB, DIRECTOR REGULATORY COMPLIANCE | 4057674845 | SEE ATTACHMENT A.
2017-09-29 08:50 | YES | NO | 19970178 | 1997-11-12 | 2731 | CHEVRON PIPELINE CO | YES | 1997-10-30 | 900 | TX | FREESTONE | WORTHAM | NO |  | NO | 3 MILES EAST OF WORTHAM TEXAS ON HWY 27 |  | TANK FARM | TANK |  | 1920 | OTHER | ROOF DRAIN HOSE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2400 | 1700.2826 | 3430.1567 | CRUDE OIL | 1 | 150 | 135 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BILL JASPER | 2813635422 | AN EMPLOYEE FOUND OIL COMING FROM THE TANK ROOF DRAIN. THE ROOD DRAIN VALVEWAS CLOSED AND THE LEVEL IN THE TANK WAS LOWERED TO PREVENT FURTHER LEAKAGE.THE TANK WAS TAKEN OUT OF SERVICE.
2017-09-29 08:50 | YES | NO | 19980001 | 1997-12-18 | 443 | AMOCO PIPELINE CO | NO | 1997-11-10 | 15 | TX | HARRIS | HOUSTON | NO |  | NO | 9140 CURLEE ROAD (NEAR I-45 AND ALMEDA ROAD), HOUSTON, TX |  | PUMPING STATION | OTHER | METER CASE | 1994 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 708451.066 | 1429231.9548 | CRUDE OIL | 1 | 5843 | 5800 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ANDRE PARKER - SUPERVISOR CRUDE | 4099386909 | ON OCTOBER 1, 1997, METER #3 WAS REMOVED FROM SERVICE FOR REPAIRS, THE METEROUTLET MOV WAS PLACED IN THE "OFF" POSITION FOR THE PURPOSE OF LOCK-OUT. ONNOVEMBER 9, 1997, AT 7:04 P.M., THE CONTROLLER SELECTED THE "AUTO" PROCEDUREFOR THE SYSTEM START-UP. THIS INCLUDED THE SELECTION OF METER #3 OUTLET MOV.AT 12:15 A.M. ON NOVEMBER 10, 1997, THE DELIVERY STARTED UP REMOTELY AND METER#3 MOV OPENED. THIS ALLOWED OIL TO BACK FLOW INTO THE OPEN METER CASE. THEMOV BREAKER WAS NOT IN THE "OFF" POSITION, ONLY THE LOCAL POSITIONER. A TOTAL5843 BBLS WERE SPILLED -- 5800 BBLS WERE RECOVERED
2017-09-29 08:50 | YES | NO | 19980002 | 1998-01-23 | 12127 | MARATHON PIPE LINE CO | NO | 1997-12-24 | 300 |  |  |  | YES | 28:07:41.031N 92:48:55.6W | NO | LAT 28:07':41.031" LONG 92:48':55.656" POINT OF CONTACT WITH PIPELINE IS APPROXIMATELY 4600' NE OF ORYX'X PLATFORM "A" IN EAST CAMERON BLOCK |  | LINE PIPE | PIPE |  | 1975 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 5000000 | 3542255.3301 | 7146159.774 | CRUDE OIL | 1 | 15 | 0 | NO | NO | 8 | 0.5 | 42 | WELDED |  | 2920 | 750 | YES | 24 | 3650 | 7 | 1975 |  | Null | Null |  |  | SHIP ANCHOR |  | Null |  |  | Null | Null | G.L. WIELAND, GULF COAST DISTRICT SUPERINTENDENT | 7132962426 | ON THE MORNING OF DECEMBER 24, 1997, MARATHON WAS INFORMED BY ORYX OF AN INCIDENT ON OUR EAST CAMERON 338 TO EAST CAMERON 321 8" CRUDE OIL LINESEGMENT. AN OUTSIDE FORCE (PRESUMABLY A SHIP ANCHOR OR DRILLING RIG) DRAGGEDTHE 8" LINE CAUSING DAMAGE AT THE POINT OF CONTACT AS WELL AS TO PIPING,VESSELS AND DECKING ON ORYXX PLATFORM. PIPING AND EQUIPMENT ON THE PLATFORMWAS DISPLACED SEVERAL FEET CAUSING A 4" SECTION OF THE PLATFORM PIPING TOPART, RELEASING AN ESTIMATED 5 TO 15 GARRELS OF CRUDE OIL. THE PRESSURE LOSSIN THE SYSTEM THEN CAUSED THE PLATFORM EMERGENCY SHUTDOWN SYSTEM TO BEACTIVATED.
2017-09-29 08:50 | YES | NO | 19980003 | 1998-01-22 | 30991 | MOBIL OIL CORPORATION | YES | 1997-12-23 | 2321 | TX | TRINITY | GROVETON | NO |  | NO | WOODED AREA 8 MILES SW OF GROVETON, TX OFF FM 355 HIGHWAY. 200' SOUTH OF FM 355 AT MOBIL PIPE LINE COMPANY'S GROVETON NGL STATION. |  | PUMPING STATION | VALVE |  | 1971 | OTHER | GASKET FAIL FLANG CHK VLV | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 14169.0213 | 28584.6391 | NATURAL GAS LIQUID | 2 | 40 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.G. SCOTT, MANAGER, MAINLINE CRUDE/NGL OPERATIONS & MAINT. | 2146585914 | ON 12/23/97 AT 2310 HRS, THE CO. SHERIFF'S OFFICE IN GROVETON, TX CALLED MOBILPIPE LINE COMPANY'S DALLAS OPERATIONS CONTROL CENTER TO REPORT THAT THEY HADRECEIVED A CALL COMPLAINING OF A GAS ODOR OFF FM ROAD 355, JUST SOUTH OF THECITY OF GROVETON, TX. MOBIL VERIFIED THRU DELHI PERSONNEL IN THE VINCINITYTHAT A "CLOUD" WAS ORIGINATION FROM MOBIL'S GROVETON NGL PUMP STATION. DALLASOPERATIONS CONTROL CENTER IMMEDIATELY NOTIFIED THE GROVETON CO. SHERRIF'SOFFICE TO BLOCK TRAFFIC IN THE AREA AND THEN DISPATCHED MOBIL PERSONNEL TO THESITE. CONTROL CENTER PERSONNEL BEGAN SHUTTING DOWN THE PIPELINE SYSTEMFEEDING FROVETON NGL PUMP STATION. THE STATION WAS ISOLATED AND REPAIR ANDCLEAN UP PROCEDURES INITIATED. THE WAS NO FIRE, EXPLOSION, DEATHS ORINJURIES. ALL REQUIRED GOVERNMENTAL AGENCIES WERE NOTIFIED IN ACCORDANCE WITHDOT REGULATIONS.
2017-09-29 08:50 | YES | NO | 19980004 | 1998-01-16 | 4906 | EXXON PIPELINE CO | NO | 1997-12-18 | 930 | LA |  | MINDEN | NO |  | YES | HWY 159 NORTH PAST MINDEN 1/2 PAST CANEY LAKE RD. TURN RIGHT AT PARISH 15 RD TILL IT FORKS. TURN RIGHT AT FORK TO PIPELINE CROSSING. 1/4 MILE TO LEAK SITE |  | PUMPING STATION | PIPE |  | 1919 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | NOT GIVEN | 1 | 160 | 160 | NO | NO | 8 | 0.32 | 25 | WELDED |  | 248 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | OTHER | IMPRSD CURRENT | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.B BACON AREA MANAGER | 7136560649 | DAMAGE BY OUTSIDE FORCES (3RD PARTY) THE PIPELINE WAS HIT BY A BRUSHHOG MOWINGEPC'S ROW.
2017-09-29 08:50 | YES | NO | 19980005 | 1998-01-15 | 4805 | EXPLORER PIPELINE CO | YES | 1997-12-16 | 1150 | TX | TARRANT |  | NO |  | NO | HERITAGE INDUSTRIAL PARK - NORTH SIDE OF STATE HIGHWAY 26 APPROXIMATELY 1 MILE WEST OF STATE HIGHWAY 114. |  | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 70845.1066 | 142923.1955 | JET FUEL | 3 | 64 | 40 | NO | NO | 8 | 0.19 | 35000 | WELDED |  | 800 | 20 | YES | 24 | 1000 | 8 | 73 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ROD E. SANDS - VICE PRESIDENT OPERATIONS | 9184935106 | ON DECEMBER 16, 1997 AT 1150 HOURS EXPLORER'S CENTRAL CONTROL CENTER IN TULSA,OK RECEIVED A PHONE CALL FROM A LANDSCAPE CONTRACTOR PLANTING TREES IN THECITY OF SOUTHLAKE, TX. THE CALLER REPORTED THAT HE HAD HIT A PIPELINE WHILEEXCAVATING WITH A TREE PLANTING MACHINE AND FUEL WAS ESCAPING. HE USED ACELLULAR PHONE TO CALL EXPLORER'S EMERGENCY NUMBER SHOWN ON A NEARBY LINEMARKER AND CALL 911 TO ADVISE LOCAL RESPONSE AUTHORITIES. EXPLORER'S 8"JET FUEL LINE WAS NOT OPERATING AT THE TIME OF DAMAGE. THE 8" LINE IN THISAREA IS LOCATED ON THE NORTH SIDE AND WITHIN DALLAS AREA RAPID TRANSIT(DART) RAILROAD RIGHT-OF-WAY. EXPLORER'S RESPONSE TEAM WAS ACTIVATED AND ANEMPLOYEE FROM THE GREENVILLE AREA OFFICE ARRIVED ON THE SITE AT 1220 HOURS.IT WAS CONFIRMED THAT EXPLORER'S 8" LINE HAD BEEN PUNCTURED AND JET FUEL WASESCAPING AND RUNNING DOWN A DRAINAGE DITCH PARALLEL TO A RAILROAD TRACK,THROUGH A CULVERT, AND UNDER THE TRACK AND UNDER ADJACENT HIGHWAY 26. VACUMNTRUCKS, EXPLORER'S MAINTENANCE CONTRACTOR AND ENVIRONMENTAL CONTRACTOR WEREDISPATCHED TO THE SITE. THE BLOCK VALVE AT MILEPOST 53.2 WAS CLOSED. THECITY OF SOUTHLAKE FIRE DEPARTMENT ALSO RESPONDED, CONTROLLING VEHICLE TRAFFICAT THE SITE AND BUILDING A SMALL EARTHEN DAM APPROXIMATELY 100 FEET SOUTH OFHIGHWAY 26 TO PREVENT POSSIBLE MIGRATION OF PRODUCT BEYOND THAT POINT. THETREE PLANTING MACHINE WAS REMOVED FROM OVER THE PIPELINE AND THE AREA AROUNDTHE DAMAGED PIPE WAS EXCAVATED. PRODUCT WAS EVACUATED FROM THE LINE WITHVACUMN TRUCKS AND A TEMPORARY PLIDCO SPLIT SLEEVE WAS INSTALLED BY 1900 HOURSTO PREVENT ANY ADDTIONAL JET FUEL RELEASE. ON DECEMBER 17, 1997, THE ENTIREAREA OF 8" LINE WHERE THE LANDSCAPE CONTRACTOR HAD BEEN PLANTING TREES WASEXCAVATED AND INSPECTED. THREE ADDITIONAL AREAS OF PIPE DAMAGE WERE FOUND.THE FOUR DAMAGED AREAS OF PIPE WERE REMOVED AND REPLACED WITH HYDROSTATICALLYTESTED PIPE. THE LINE WAS REFILLED AND RETURNED TO SERVICE AT 0900 HOURSDECEMBER 17, 1977. CONTAMINATED SOIL IS BEING REMOVED FROM THE AREA ANDTRANSPORTED TO AN APPROVED DISPOSAL SITE.
2017-09-29 08:50 | YES | NO | 19980006 | 1998-01-09 | 300 | ALL AMERICAN PIPELINE CO | YES | 1997-12-13 | 945 | CA | SAN BERNARDINO |  | NO |  | NO | SECTION 5, T5N, R12E (MAP ATTACHED) |  | LINE PIPE | PIPE |  | 1985 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 290000 | 205450.8091 | 414477.2669 | CRUDE OIL | 1 | 12884 | 5212 | NO | NO | 30 | 0.28 | 70000 | WELDED |  | 944 | 696 | YES | 24 | 1189 | 5 | 86 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JORDAN JANAK, DIRECTOR, REGULATORY COMPLIANCE | 8056645345 | ON DECEMBER 13, 1997 AT APPROXIMATELY 0945 PST, ALL AMERICAN PIPELINECOMPANY'S AERIAL SURVEY PILOT REPORTED A SMALL AREA ON THE RIGHT-OF-WAY THATAPPEARED TO BE DISCOLORED BY CRUDE OIL. AN ON-GROUND INVESTIGATION CONFIRMEDA CRUDE OIL LEAK. BASED ON THE AREA AND DEPTH OF CONTAMINATION ESTABLISHED BYTHE INITIAL INVESTIGATION, THE TOTAL AMOUNT OF LEAKAGE WAS ESTIMATED ATAPPROXIMATELY 20 BARRELS. EQUIPMENT, MATERIALS AND PERSONNEL WERE IMMEDIATELYMOBILIZED TO REPAIR THE PIPELINE AND BEGIN CLEAN-UP OPERATIONS. THE LEAKRESULTED FROM APPROXIMATELY A 3/16-INCH DIAMETER PINHOLE CAUSED BY LOCALIZED,EXTERNAL CORROSION. THE CORROSION WAS IN AN AREA WHERE THE POLYKEN TAPECOATING APPEARED DEFECTIVE. A FULL ENCIRCLEMENT STEEL SLEEVE WAS WELDED ONTOTHE PIPELINE TO REPAIR THE CORROSION AREA. THE REPAIR WAS COMPLETED ONDECEMBER 14, 1997 AT APPROXIMATELY 1520 PST. AN EVALUATION OF INFORMATIONGATHERED DURING THE REPAIR OF THE PIPELINE PERFORMED MONDAY MORNING DECEMBER15, INDICATED THAT THE SIZE OF THE LEAK WAS IN EXCESS OF 50 BARRELS. BASEDON THE INFORMATION AVAILABLE AT THAT TIME, THE AMOUNT OF CRUDE OIL LEAKED WASESTIMATED AT 400 BARRELS. THE NRC WAS NOTIFIED AS SOON AS IT WAS DETERMINEDTHAT THE SPILL WAS REPORTABLE UNDER FEDERAL REGULATIONS. EXTENSIVEEXCAVATION TO DETERMINE THE TOTAL AREA AFFECTED BY THE LEAK CONDUCTEDSUBSEQUENT TO THE DATE THE LEAK WAS REPORTED TO THE NRC HAS RESULTED, AS OFJANUARY 6, 1998, IN THE RECOVERY OF 1605 BARRELS OF CRUDE OIL. EFFORTS TORECOVER CRUDE OIL THAT LEAKED WILL CONTINUE AS LONG AS THESE EFFORTS REMAINEFFECTIVE. BASED ON THE DATA AVAILABLE THE DATE OF THIS REPORT, IT ISESTIMATED THAT A TOTAL OF 5530 BARRELS OF CRUDE OIL LEAKED FROM THE PIPELINE.A FINAL ESTIMATE WILL NOT BE POSSIBLE UNTIL EFFORTS TO RECOVER AS MUCH OF THELEAKED OIL AS POSSIBLE ARE COMPLETE AND FINAL SITE CHARACTERIZATION DATA ISOBTAINED. A FINAL ESTIMATE OF THE AMOUNT OF OIL LEAKED AND THE TOTAL AMOUNTRECOVERED WILL BE PROVIDED IN A FOLLOW-UP REPORT WHEN THIS DATA IS AVAILABLE.ALL AMERICAN IS COORDINATING WITH CALIFORNIA STATE AUTHORITIES TO MITIGATE THEAREA THAT WAS IMPACTED BY THE LEAK.
2017-09-29 08:50 | YES | NO | 19980008 | 1998-01-02 | 26127 | CHEVRON PIPELINE CO | NO | 1997-12-04 | 1730 | CA | SAN JOAQUIN |  | NO |  | NO | .3 MILE SOUTH OF SOUTH BIRD ROAD, TRACY CA |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 70845.1066 | 142923.1955 | CRUDE OIL | 1 | 4 | 4 | NO | NO | 20 | 0.3 | 35 | WELDED |  | 714 | 450 | YES | 4 | 880 | 5 | 97 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL GARRETT, PIPELINER | 5107532007 | CORROSION LEAK AT 7:00 POSITION ON PIPE RELEASED A SMALL AMOUNT OF OIL (4BBLS) TO THE SOIL. THE SOIL WAS WET FROM THE RAIN CAUSING THE OIL TO SPREADOUT OVER A LARGER THAN NORMAL SURFACE AREA. NO IMPACT TO WATER OCCURED.
2017-09-29 08:50 | YES | NO | 19980009 | 1998-01-05 | 12470 | MID - VALLEY PIPELINE CO | YES | 1997-12-12 | 330 | OH | WOOD |  | NO |  | NO | 5152 ROCK RIDGE ROAD, CYGNET, OH - MVPL PUMPROOM |  | PUMPING STATION | OTHER | 1/2" SS BEARING LUBE LINE | 1997 | OTHER | STAINLESS STEEL FITTING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 28338.0426 | 57169.2782 | CRUDE OIL | 3 | 100 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDITH F. COEN, MGR. HES WESTERN AREA | 9185866942 | AT APPROXIMATELY 0330 EASTERN STANDARD TIME, A 1/2" STAINLESS STEEL FITTINGLOCATED IN A BEARING COOLING/LUBRICATION LINE ON A MAINLINE PUMP FAILED,ALLOWING CRUDE OIL TO ESCAPE FROM THE LINE.
2017-09-29 08:50 | YES | NO | 19980010 | 1998-01-02 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1997-12-17 | 1030 | TX | COLEMAN | COLEMAN | NO |  | NO | TAKE HWY 84 SOUTH OF COLEMAN, TX TO FM ROAD 568, GO EAST C. 6 MILES TO FM ROAD 1176, TURN NORTH C. 1 MILE LEAK LOCATED ON WEST SIDE OF ROAD. |  | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3542.2553 | 7146.1598 | CRUDE OIL | 1 | 200 | 0 | NO | NO | 8 | 0.32 | 25000 | WELDED |  | 741 | 250 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T. MACON, PIPELINE MANAGER | 9156748231 | SPILL WAS REPORTED ON 12-17-97 TO OUR HAWLEY OFFICE. PIPELINE WAS SHUT DOWNAND CREWS WERE DISPATCHED TO CLAMP LEAK AND BEGIN CLEAN UP. AREA WILL BECLEANED UP PER STATE WIDE RULE 91.
2017-09-29 08:50 | YES | NO | 19980011 | 1998-01-02 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 1997-12-02 | 857 | NJ | MIDDLESEX | PISCATAWAY | NO |  | NO | SEELEY AVENUE, CENTENNIAL SQUARE MALL CONSTUCTION SITE IN PISCATAWAY, NJ. C. 500 YARDS NORTHWEST OF THE SUNOCO MARKETING TERMINAL ON STELTON ROAD. |  | LINE PIPE | PIPE |  | 1956 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 291 | 170 | NO | NO | 14 | 0.25 | 42000 | WELDED |  | 1200 | 320 | YES | 50 | 1500 | 11 | 56 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | ALAN D. GILLIE, EASTERN AREA LOGISTICS HEALTH, ENVIRO SAFETY | 2159773344 | THE ACCIDENT WAS CAUSED BY A TRACKHOE OPERATOR EMPLOYED BY PELLARI BROS., ANEXCAVATION CONTRACTOR WORKING ON THE CENTENNIAL SQUARE MALL PROJECT. THECONTRACTOR'S TRACKHOE HIT THE PIPELINE WHILE DIGGING A TRENCH. AS A NORMALPREVENTATIVE ACTION, SUN PIPE LINE HAD PLACED HIGHLY VISIBLE PIPELINE MARKERSTO IDENTIFY THE LOCATION OF THE UNDERGROUND PIPE. ALSO IN PLACE WAS THE "ONECALL" SYSTEM. THIS COMMUNICATION GIVES ANY EXCAVATION CONTRACTOR PERTINENTINFORMATION ON THE LOCATION OF UNDERGROUND PIPELINES AND UTILITIES BEFOREDIGGING BEGINS.
2017-09-29 08:50 | YES | NO | 19980012 | 1997-12-15 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1997-11-26 | 1300 | KS | MORTON | ROLLA | NO |  | YES | SW 1/4, SECTION 27, TOWNSHIP 34 SOUTH, RANGE 40 WEST, IN MORTON COUNTY, KANSAS, 4 1/2 MILES SOUTH AND 2 MILES WEST OF ROLLA, KANSAS. |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2833.8043 | 5716.9278 | CRUDE OIL | 1 | 76 | 0 | NO | NO | 6.63 | 0.19 | 35000 | WELDED |  | 1000 | 160 | YES | 8 | 1430 | 0 | 58 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON, SUPERINTENDENT OF OPERATIONS | 3162419270 | AT 1300 HOURS ON NOVEMBER 26, 1997, JAYHAWK'S AIR PATROL REPORTED LEAK ONJAYHAWK'S 6-INCH GATHERING LINE. BY 1400 HOURS, BLOCK VALVES ON EACH SIDE OFLEAK HAD BEEN CLOSED AND SECURED. BY 1600 HOURS A TEMPORARY REPAIR WASCOMPLETED AND ON DECEMBER 5, 1997 AN 18-INCH FULL ENCIRCLEMENT WAS INSTALLEDFOR FINAL REPAIR. CLEAN UP WAS DONE BY BURNING AND SOIL REMEDIATION WITH THEAPPROVAL OF KANSAS HEALTH AND ENVIRONMENT AND USDA FOREST SERVICE.
2017-09-29 08:50 | YES | NO | 19980013 | 1997-12-23 | 443 | AMOCO PIPELINE CO | NO | 1997-11-29 | 1600 | OK | PAYNE |  | NO |  | NO | SW 1/4 SECTION 14, TOWNSHIP 17N, RANGE 5E CUSHING TO FREEMAN LINE SEGMENT, CUSHING TERMINAL MANIFOLD |  | PUMPING STATION | OTHER | 2" DRAIN PLUG ON 20" STRN | 1984 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 70845.1066 | 142923.1955 | CRUDE OIL | 1 | 6500 | 6400 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | TO BE DETERMINED | NO DATA |  | Null | NO DATA |  | Null | Null | TERRY HUTSON, TEAMLEADER- CUSHING CORE TEAM | 9182231101 | 2" PLUG IN 20" STRAINER BLEW OUT DUE TO INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19980014 | 1997-12-23 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1997-11-19 | 1015 | CA | CONTRA COSTA |  | NO |  | NO | MOCOCO ROAD AND WATER FRONT ROAD EAST OF 680 FREEWAY - IN MARSH LAND. |  | LINE PIPE | PIPE |  | 1983 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1416902.132 | 2858463.9096 | CRUDE OIL | 1 | 40 | 35 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 745 | 150 | YES | 4 | 934 | 3 | 94 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD E. KELLY | 8053270110 | ELL HAS EXTERNAL CORROSION AND DEVELOPED SMALL HOLE.
2017-09-29 08:50 | YES | YES | 19980015 | 1997-12-17 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1997-11-14 | 710 | LA | LINCOLN |  | NO |  | NO | T-19N, R-2W, SEC. T, 2 MILES N. OF HWY.33 NEAR PILOT ROAD |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 5000 | 3542.2553 | 7146.1598 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 10.75 | 0.25 | 42000 | WELDED |  | 1340 | 600 | YES | 32 | 1893 | 8 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | RON SLEN | 5734865488 | OPERATOR OF HYDRO-AXE MACHINGE DID NOT WAIT FOR OTHER EMPLOYEE TO SPOT HAZARDSDURING RIGHT OF WAY CLEARING AND HIT KOCH'S 10" AMMONIA LINE WHICH WASPARTIALLY EXPOSED IN A WASHED OUT AREA. MACHINE OPERATOR WAS EXPOSED TOAMMONIA VAPORS AND TAKEN TO HOSPITAL FOR OBSERVATION AND RELEASED ON11/15/97. APPROXIMATELY 250 PEOPLE WERE ASKED TO EVACUATE HOMES AS A SAFETYPRECAUTION. MOST FAMILIES WERE BACK IN THEIR HOMES LATER THE SAME DAY(11/14/97). ENVIRONMENTAL CLEAN-UP PERFORMED AND COMPLETED UNDER LA-DEQSPECIFICATIONS AND APPROVAL.
2017-09-29 08:50 | YES | NO | 19980016 | 1998-01-07 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1997-12-08 | 1455 | KS | MCPHERSON |  | NO |  | NO | MP 13.7 ON ELDORADO MAIN LINE, APPROXIMATELY 2.5 MILES SOUTHEAST OF ELYRIA, KANSAS, MCPHERSON COUNTY, TOWNSHIP 21S, RANGE 3W, SECTION 4 |  | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 29000 | 20545.0809 | 41447.7267 | BUTANE | 2 | 9 | 0 | NO | NO | 6 | 0.16 | 42000 | WELDED |  | 1420 | 500 | YES | 24 | 1736 | 5 | 64 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL C. PEARSON, P.E. MANAGER PIPELINE ENGINEERING | 9185994043 | A FROST BALL IN CLOSE PROXIMITY OF THE PIPELINE WAS DETECTED. THE PIPELINEWAS IMMEDIATELY SHUTDOWN, FIELD OPERATIONS PERSONNEL DISPATCHED TO THELOCATION, AND THE LINE SEGMENT WAS BLOCKED IN AND ISOLATED. MID-AMERICALPIPELINE COMPANY (MAPL) PERSONNEL SECURED THE LOCATION, CONFIRMED THAT THELEAK WAS ON MAPL'S PIPELINE, EXCAVATED THE PIPELINE, EVALUATED THE CORROSIONANOMALY, AND PERMANENTLY REPAIRED THE PIN HOLE LEAK WITH A WELDEDFULL-ENCIRCLEMENT SLEEVE.
2017-09-29 08:50 | YES | NO | 19980017 | 1997-12-15 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1997-12-07 | 535 | KS | MEADE |  | NO |  | NO | NE 1/4, SECTION 34-TOWNSHIP 33 SOUTH-RANGE 30 WEST, MEADE COUNTY, KANSAS 8 MILES SOUTH OF PLAINS, KANSAS |  | TANK FARM | PIPE |  | 1963 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1062.6766 | 2143.8479 | CRUDE OIL | 1 | 170 | 150 | NO | NO | 12.75 | 0.25 | 46 | WELDED |  | 150 | 20 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON, SUPERINTENDENT OF OPERATIONS | 3162419270 | LEAK ON TANK DISCHARGE LINE WAS NOTICED AT 0530 HOURS DECEMBER 7, 1997, ANDTANK WAS IMMEDIATELY SHUT DOWN AND BLOCKED IN. CRUDE OIL WAS CONTAINED ANDMOSTLY RECOVERED. CONTAMINATED SOIL WILL BE REMEDIATED AT LOCATION. NEWSECTION OF PIPE INSTALLED AND DISCHARGE LINE WILL BE PRESSURE TESTED BEFOREOPERATION RESUMES.
2017-09-29 08:50 | YES | NO | 19980018 | 1998-01-02 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1997-12-14 | 2335 | TX | ROBERTSON |  | NO |  | NO | 1.8 MILES SOUTH OF THE INTERSECTIONS OF SH79 & SH6 AT HEARNE, TX. STATION SITE IS ABOUT 300 YARDS EAST OF SH6 |  | TANK FARM | TANK |  | 1979 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 9800 | 6942.8204 | 14006.4732 | CRUDE OIL | 1 | 600 | 586 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID FRITSCHE | 4015354855 | THE TANK GUAGE STUCK AT ABOUT 10 FOOT. THE PUMPS WERE NOT GIVEN A RUN LEVELTHUS THE TANK OVERRAN WHEN THE INCOMING CRUDE FILLED THE TANK.
2017-09-29 08:50 | NO | NO | 19980019 | 1998-01-02 | 19226 | TEXACO PIPELINE INC | NO | 1997-11-30 | 1900 | TX | WHARTON |  | NO |  | NO | ADJACENT TO CNTY ROAD 444, APPROXIMATELY 5 MILES EAST OF THE INTERSECTION OF FM 1162 AND COUNTY ROAD 555 NEAR THE PIERCE RANCH ENTRANCE |  | LINE PIPE | NO DATA |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4250.7064 | 8575.3917 | CRUDE OIL | 1 | 8 | 8 | NO | NO | 6 | 0.28 | 24000 | WELDED |  | 30 | 0 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. LEDNICKY, DISTRICT MANAGER | 7137526514 | PART H - NEVER TESTED, RURAL GATHERING LINE (OPERATED BELOW 20% OF YIELDSTRENGTH. PART K - SMALL LEAK CAUSED BY INTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19980020 | 1998-01-27 | 2552 | COLONIAL PIPELINE CO | Null | 1997-12-09 | 1235 | NC | GUILFORD | GREENSBORO | NO |  | NO | GREENSBORO JUNCTION TANK NO.836 411 GALLIMORE DAIRY RD. GREENSBORO, NC 27409 |  | TANK FARM | TANK |  | 1963 | OTHER | CRACK IN TANK BOTTOM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 177112.7665 | 357307.9887 | GASOLINE | 3 | 100 | 46 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.A. COX, CODES AND STANDARDS LEADER | 4048412296 | AT APPROX. 12:35 ON DECEMBER 9, 1997, A GREENSBORO JUNCTION CONTRACTORDISCOVERED PETROLEUM PRODUCT IN AN OPEN PIT IN THE AREA BETWEEN THE LAGOON ANDTHE GASOLINE MANIFOLD. THE CONTRACTOR NOTIFIED ENVIRONMENTAL PERSONNELIMMEDIATELY. UPON INVESTIGATION, IT WAS DETERMINED THAT THERE WERE 6-8" OFGASOLINE ON TOP OF THE GROUNDWATER. ENVIROMENTAL PERSONNEL NOTIFIED PROJECTPERSONNEL TO BEGIN CLEAN-UP. FURTHER ASSESSMENT OF THE AREA INDICATED THATPRODUCT WAS COMING FROM TANK 836. OPERATION PERSONNEL BEGAN EMPTYING SUSPECTTANK. THE DISTRICT ENVIRONMENTAL PROJECT MANAGER WAS NOTIFIED AT APPOXIMATELY16:40. THE NC DEPARTMENT OF EMERGENCY MANAGEMENT WAS NOTIFIED AT 17:05.GUILFORD COUNTY EMERGENCY MANAGEMENT WAS CONTACTED BY STATE AND COUNTYPERSONNEL CALLED COLONIAL AT 18:15. THE NRC WAS NOTIFIED AT APPROX. 18:35.THE ORIGINAL VOLUME IN PIT WAS ESTIMATED TO BE AROUND 200 GALLONS. FURTHERINVESTIGATION DETERMINED LEAK TO BE GREATER THAN 55 BBLS. REMEDIATION ISONGOING.
2017-09-29 08:50 | YES | NO | 19980021 | 1998-01-20 | 2814 | FINA PIPE LINE CO | NO | 1997-11-16 | 1230 | TX | HOWARD |  | NO |  | NO | T&P RR SURVEY, BLOCK 32, T-2-N, SECTION 38, NORTHERN HOWARD COUNTY, TX. 17.4 MI. N-NE OF BIG SPRING AND 100 YDS. EAST OF FM-669 |  | PUMPING STATION | TANK |  | 1991 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4250.7064 | 8575.3917 | CRUDE OIL | 1 | 2480 | 2380 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED, SPECIALIST, ENV. & REGULATORY COMPLIANCE | 9152639256 | AT 12:30PM ON SUNDAY, NOVEMBER 16TH, FINA'S FIELD GAUGER ARRIVED AT THETEX-MEX TANK BATTERY FOR A ROUTINE CHECK OF THE FACILITY. UPON ARRIVAL, HEFOUND THE BATTERY'S SECOND CONTAINMENT (FIREWALL) FILLED WITH CRUDE OIL, THETANKS HAVING OVERFLOWED AFTER FILLING. THIS SITUATION WAS IMMEDIATELYREPORTED TO FINA'S CONTROL CENTER IN BIG SPRING. ACTIONS WERE IMMEDIATELYBEGUN TO RESPOND TO THIS RELEASE, WHICH WAS FULLY CONTAINED WITHIN THEFIREWALL SURROUNDING THIS BATTERY OF 5,500 BBL INTERCONNECTED TANKS. BY 8:00AMOF THE FOLLOWING DAY, NOV. 17TH, VACUUM TRUCKS HAD RECOVERED 2380 BBLS., WHICHWERE PUMPED BACK INTO STORAGE. APPROXIMATELY 100 C.Y. OF CONTAMINATED SOIL WASTAKEN OFF-SITE UNDER AUTHORITY OF RRC MINOR PERMIT NO 8-2945, TO A PERMITTEDLAND TREATMENT SITE OWNED BY FINA. AT THIS TIME, AN INVESTIGATION INTO THEEXACT CAUSE(S) OF THIS INCIDENT IS ON-GOING. IT IS KNOWN THAT THE COUPLER ONTHE TEXAS-NEW MEXICO PUMP FAILED. THE MOTOR ACTIVATED, BUT COULD NOT OPERATETHE PUMP TO PUMP-OUT THE TANK BATTERY. THE BATTERY'S HIGH LEVEL ALARM ALSOFAILED, WITH THE RESULT THAT THE TANKS OVERFLOWED. WE ATTRIBUTE THIS ACCIDENTTO "MULTIPLE FAILURE OF MECHANICAL AND ELECTRONIC DEVICES."
2017-09-29 08:50 | YES | NO | 19980022 | 1998-01-20 | 4906 | EXXON PIPELINE CO | YES | 1997-12-17 | 900 | TX |  | WEBSTER | NO |  | NO | 2004 HWY 3 WEBSTER 77598 (JUST SOUTH OF NASA RD. 1) |  | TANK FARM | TANK |  | 1958 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 9918.3149 | 20009.2474 | CRUDE OIL | 1 | 6500 | 6200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | NO | F.T. BRADSHAW, AREA MANAGER | 7136560649 | LEAK WAS CAUSED BY ROOF DRAIN HOSE FAILURE, CAUSING OIL TO DRAIN INTO THE HOSEINTO THE FIRE WALL.
2017-09-29 08:50 | NO | NO | 19980023 | 1998-01-20 | 4906 | EXXON PIPELINE CO | NO | 1997-12-15 | 1145 | TX |  | LA PORTE | NO |  | NO | 1/2 NORTH OF SPENCER HIGHWAY ON MYRTLE CREEK ROAD. |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 38964.8086 | 78607.7575 | GASOLINE | 1 | 3 | 1 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | OTHER |  | Null | YES | F.T. BRADSHAW | 7136560649 | AN ELECTROLITHIC SHORT IN THE CASING, CAUSING A CORROSION CELL TO FORM IN THEPIPE, THUS FILLING THE CASING. A LEAK THEN APPEARED IN THE CASING, ALLOWINGTHE PRODUCT IN THE CASING TO RELEASE.
2017-09-29 08:50 | YES | NO | 19980024 | 1998-03-04 | 12127 | MARATHON PIPE LINE CO | YES | 1997-08-24 | 1604 | IN | PARKE COUNTY |  | NO |  | NO | APPROXIMATELY ONE MILE NORTHEAST OF ROSEDALE,IN SECTION 27, T14N,R8W, PARKE CO.,IN |  | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1416902.132 | 2858463.9096 | CRUDE OIL | 1 | 11206 | 5655 | NO | NO | 22 | 0.34 | 46000 | WELDED |  | 970 | 1024 | YES | 4 | 1273 | 10 | 94 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | TAD A SCHELL | 4194213201 | AT 16:04 AGUST 24,1997, MARATHON PIPE LINE COMPANY'S (MPL'S) OPERATIONS CENTERLOCATED IN FINDLAY, OHIO DETECTED A SUDDEN PRESSURE DROP ON MPL"SMARTINSVILLE-LIMA 22" CRUDE OIL PIPELINE. THE PIPELINE WAS IMMEDIATELYSHUTDOWN, AND MPL FIELD PERSONNEL WERE CONTACTED AND BEGAN SEARCHING FOR THERELEASE LOCATION, WHICH WAS BELIEVED TO BE DOWN STREAM IN THE VICINITY OFMPL'S ROSEDALE,IN PUMP STATION. AT 18:35 THE SAME DAY, THE RELEASE LOCATIONWAS DISCOVERED APPROXIMATELY ONE MILE NORTHEAST OF ROSEDALE,IN. THE PIPE HADFAILED INSIDE A CASING UNDER AN ABANDONED RAILROAD GRADE. CRUDE OIL HAD LEFTTHE CASING. TRAVELED ACROSS A BEAN FIELD AND ENTERED A MARSHY AREA WHICHDRAINS TO A DITCH WHICH RUNS INTO BIG RACOON CREEK. INITIALLY IT WASESTIMATED THAT APPROXIMATELY 3000 BBL. OF CRUDE OIL WERE RELEASED. ONEHUNDRED AND THIRTY-TWO FEET OF LINE PIPE WAS REPLACED WITH NEW,HYDROSTATICALLY TESTED PIPE. THE PIPE LINE WAS RETURNED TO SERVICE AT 23:30AUGUST 26. THE ESTIMATE OF OIL RELEASED WAS REVISED TO 11206 BBL. UPONMERERING THE COMPLETED CRUDE OIL SHIIPMENT. THE FAILED SECTION OF THE PIPEWAS SENT TO KIEFNER & ASSOCIATES, INC IN WORTHINGTON, OH FOR ANALYSIS,PRELIMINARY RESULT OF THE INVESTIGATION FIND THE FAILURE WAS DUE TO EXTERNALCORROSION. CLEANUP EFFORTS ARE CONTINUING WITH 5,655BBL. OF OIL RECOVEREDAND AN ESTIMATED 2208 BBL. EVAPORATED AS OF SEPTEMBER 22. LONG TERM CLEANUPAND REMEDIATION PLANS ARE BEING DEVELOPED IN COOPERATION WITH THE INDIANADEPARTMENT OF ENVIRONMENTAL MANAGEMENT AND OTHER AFFECTED STATE AND FEDERALAGENCIES.
2017-09-29 08:50 | YES | NO | 19980025 | 1998-02-12 | 18519 | SANTA FE PACIFIC PIPELINE CO | NO | 1997-12-11 | 1028 | CA | PLACER |  | NO |  | NO | SFPP ROCKLIN STATION 6050 PACIFIC STREET ROCKLIN , CA 95677 |  | PUMPING STATION | SCRAPER TRAP |  | 1987 | OTHER | COBINATION OF OPERATOR ER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 177112.7665 | 357307.9887 | DIESEL FUEL | 3 | 60 | 30 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | J.M. ABBOUD | 714560472 | THE DOOR ON THE RO TO RE LINE WAS OPENED UNDER PRESSURE. DIESEL FLOWED OUTONTO THE GROUND. IT IS BELIEVED THAT THERE WAS FURTHER OF EQUIPMENTASSOCIATED WITH ASSOCIATED WITH THE TRAP. THE PIPELINE WAS DEPRESSURIZED ANDTHE SPILL STOPPED. SPILL STOPED. THE SPILL XLEANUP WAS STARTED THAT DAY,SOIL WAS ECAVATED AND PROTECTIVE MEASURES TAKEN TO ENSURE SPILLED DIESELREMAINED INSIDE SFPP PROPERTY. REPORT SENT TO DOT, >50BBL, & > $50K PROPERTYDAMAGE, CA OES RWQCB & PLACER COUNTY ENVIRONMENT HEALTH NOTIFIED
2017-09-29 08:50 | YES | NO | 19980027 | 1998-03-17 | 18273 | SHELL PIPELINE CORP | YES | 1998-02-14 | 1400 | CA | VENTURA COUNTY |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1044127 | 730703.4423 | 1474123.9858 | CRUDE OIL | 1 | 249 | 2 | NO | NO | 10 | 0.37 | 2377 | WELDED |  | 1440 | 750 | YES | 0 | 2040 | 12 | 93 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | ONE CALL |  | NO | NO | D F SHEAFFM SR. | 7132414381 | FOLLOWING DAYS OF HEAVY RAINS IN THE VENTURA AREA, SECTION OF HILLSIDE FAILEDAND CARRIED THE VENTURA CRUDE LINE WITH IT. THE PIPE RUPTURED AS A RESULT OFTHE MUDSLIDE.
2017-09-29 08:50 | YES | NO | 19980028 | 1998-03-16 | 25133 | TEXACO TRADING & TRANSPORTATION INC | NO | 1998-02-14 | 1430 | CA | VENTURA |  | NO |  | NO | HIGH POINT OF SAN JON BARRANCA |  | LINE PIPE | PIPE |  | 1952 | OTHER | LANDSLIDE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 1 | 111 | 5 | NO | NO | 8 | 0.28 | 35000 | NO DATA |  | 800 | 5 | Null | 4 | 1000 | 0 | 94 | NO DATA | Null | Null | NO DATA |  | LANDSLIDE |  | Null | NO DATA |  | NO | YES | G G HOHNSTEIN | 8053282329 | DUE TO EXCESSIVE "EL NINO" RAINS IN THE FOOTHILLS OF VENTURA, AN EARTHENLANDSLIDE OCCURRED WHICH OVER STRESSED AND RUPTURED SEVERAL PIPELINE. THEPIPELINES WERE IMMEDIATELY SHUTDOWN WITH MINIMAL LOSSES. THE CRUDE OIL,MUD,WATER, FLOWED DOWN SAN JOM BARRANCA, THROUGH A VENTRA CITY STORM DRAIN ANDINTO THE PACIFIC OCEAN, A UNIFIED COMMAND SYSTEM WAS ACTIVATED WITH FOUR (4)HOURS OF THE LEAK WITH US COAST GUARD. STATE OSPR (FISH AND GAME), SHELL OIL( R.P.) AND TEXACO TRADING AND TRANSPORTATION INC. ( R.P.). THE RESPONSE WASCONCLUDED IN FOUR (4) DAYS WITH THREE (3) WEEKS OF VISUAL MONITORING PLAN INPLACE. THERE WAS MINIMAL STAINING TO THE STORM DRAIN AND NO VISIBLESTAININGOF LOCAL BEACHES OR SCHEEN ON THE OCEAN WATERS.
2017-09-29 08:50 | YES | NO | 19980029 | 1998-03-16 | 18273 | SHELL PIPELINE CORP | YES | 1998-02-09 | 1800 | LA | PLAQUEMINES PARISH |  | NO |  | NO | 20" MAINLINE IN THE MARSH NORTH OF PORT SULPHUR |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 174955.595 | 352956.1025 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 832 | 400 | YES | 24 | 1040 | 0 | 59 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D F SHEAFF | 7132414381 | MECHANICAL DAMAGE BY OTHERS RESULTED IN A GOUGE IN THE PIPE APPROXIMATELY 1" X1-1/2" NEAR THE TOP OF THE PIPE.
2017-09-29 08:50 | YES | YES | 19980030 | 1998-03-12 | 30777 | STAR ENTERPRISE | NO | 1998-02-08 | 2015 | LA | ST. JAMES PARISH |  | NO |  | NO | STAR ENTERPRISE REFINERY |  | NO DATA | PIPE |  | 1994 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NOT GIVEN |  | 0 | 0 | NO | NO | 10 | 0.36 | 16000 | WELDED |  | 1000 | 35 | YES | 5 | 1200 | 0 | 96 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | K W BERGSEID | 5042963806 | OPERATOR DID NOT CLOSE VALVE TO FLARE LINE AS REQUIRED BY PLANT PROCEDUREWHICH ALLOWED GAS CONTAINING HYDROGEN SULFIDE TO ESCAPE FROM SCRAPER TRAP.
2017-09-29 08:50 | NO | NO | 19980031 | 1998-03-11 | 2190 | CENTRAL FLORIDA PIPELINE CORP | NO | 1998-02-25 | 2100 | FL | OSCEOLA | KISSIMEE | NO |  | NO | SEE ATTACHED |  | LINE PIPE | OTHER | GRAVITOMETER | 1998 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | GASOLINE | 1 | 10 | 8 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A PASTERNAK | 8132482148 | CFPL CONTROL ROOM-TAMPA WAS NOTIFIED BY FIRE CHIEF MEYERS IN KISSIMEE,FLORIDA, OF A SPRAY LEAK AT THE 16" PIPELINE STATION NEAR HIGHWAY 535 ANDPOLYNESIAN ISLE BLVD. AT APPROXIMATELY 2100 HOURS ON 2/25/1998. THE CFPL 16"PIPELINE WAS DOWN AT THAT TIME AND UNDER NORMAL SHUTDOWN PRESSURE. THEPRESSURE ON THE PIPELINE WAS IMMEDIATELY REDUCED GY OPENING VALVES INTO THEORLANDO TERMINAL RECEIVING FACILITY. THEN THE MAINLINE VALVES WERE CLOSED BYREMOTE CONTROOL TO ISOLATE THE SECTION. CFPL EMERGENCY FIRST RESPONDERS WEREDISPATCHED TO THE LEAKINAG SPILL SITE LOCATION ALONDG WITH EMERGENCY RESPONSECONTRACTORS. A GASKET WAS LEAKING ON THE GRAVITOMETER. UNLEADED GASOLINE HADPOOLED IN A GROUND DEPRESSION AT THE SITE. BOOMS AND OTHER EQUIPMENT WEREUSED TO CONTAIN THE SPILLAGE IN THE IMMEDIATE VICINITY OF THE PIPELINE.SPILLED PRODUCT AND SURFACE WATER WAS COLLECTED AT THE SPILL SITE BY USE OFVACUUM TRUCKS AND TANKERS. THE SPILL DID NOT ENTER ANY STREAMS OR WATERWAYS. BY 1800 HOURS ON 02/26/1998, ALL FREE PRODUCT HAD BEEN REMOVED FROMTHE SITE AND CONTAMINATED SOILS WERE LOADED ON TO TRUCKS AND DELIVERED FORINCINERATION ON 03/02/1998. ALL CONTAMINATED SOILS REGULATIONS. THE SITE WASINSPECTED BY AN OFFICIAL OF THE FLORIDA DEPARTMENT OF ENVIRONMENTALPROTECTION. THE LEAKING GRAVITOMETER SYSTEMS WAS DISCONNECTED AND ISOLATEDFROM THE PIPELINE SYSTEM. TESTS ARE UNDERWAY AT THE SPILL SITE TO ASSESS THECLEAN-UP TO INSURE THAT ALL CONTAINMENTS HAVE BEEN COLLECDSTED AND REMOVEDFROM THE SITE. FURTHER SITE MONITORING WILL BE ACCOMPLISHED TO ASSURECOMPLETE RESTORATION OF THE SPILL AREA.
2017-09-29 08:50 | YES | NO | 19980032 | 1998-03-10 | 12106 | MAPCO INC | YES | 1998-02-10 | 1000 | NM | LEA COUNTY |  | NO |  | NO | SECTION 17, TOWNSHIP 20 SOUTH, RANGE 39 EAST. MILE POST 15.75 ON MID-ATLANTIC PIPELINE COMPANY'S DOLLARHIDE BLUE PIPELINE |  | LINE PIPE | GIRTH |  | 1960 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 4898.7567 | 9882.7709 | NATURAL GAS LIQUID | 2 | 23 | 0 | NO | NO | 8.63 | 0.19 | 1830 | WELDED |  | 1318 | 570 | YES | 8 | 1706 | 6 | 87 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL C PEARSON | 9185994043 | PIPELINE CONTROL RECEIVED INDICATIONS OF A LEAK AND SHUTDOWM THE PIPELINELOCATION. THE PIPELINE WAS ECAVATED AND THE PINHOLE LEAK WAS PERMANENTLYREPAIRED WITH A FULL ENCIRCLEMENT WELDED SLEEVE.
2017-09-29 08:50 | YES | NO | 19980033 | 1998-03-03 | 15851 | PRIDE REFINING INC | NO | 1998-01-28 | 100 | TX | COMANCHE COUNTY |  | NO |  | NO | PRIDE PIPELINE'S COMYN STATION, APPROXIMATELY 5 MILES EAST OF DELEON, TX SOUTH OF HIGHWAY 6 ABOUT 3 MILES. |  | NO DATA | NO DATA |  | 1958 | OTHER | PUMP PACKING FAILURE. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | CRUDE OIL | 1 | 50 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON | 9156748231 | AT APPROXIMATELY 1:00 AM ON WEDNESDAY THE 20TH OF JANUARY THE PACKING FAILEDON THE MAINLINE GASO PUMP, RESULTING IN A SPILL OF APPROXIMATELY 50 BBLS OFCRUDE OIL.
2017-09-29 08:50 | YES | NO | 19980034 | 1998-03-03 | 15490 | PHILLIPS PIPE LINE CO | YES | 1998-01-30 | 1505 | KS | BUTLER |  | NO |  | NO | BORGER-E. CHICAGO "BLUE" LINE - MP 303-41+00 SEC.32, T24S,R6E - APPROXIMATELY 200' OFF EL DORADO, KS, ON HWY 177 |  | LINE PIPE | WELDING FITTING |  | 1985 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 524866.7851 | 1058868.3075 | PROPANE | 2 | 25 | 0 | NO | NO | 12.75 | 0.38 | 42000 | OTHER |  | 960 | 800 | YES | 8 | 1610 | 5 | 85 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J SCHMITZ | 9186614814 | POROSITY ON WELD+END SEAL WELDS RESULTED IN A SMALL LEAK.SITE IS UNDER 0 FT.OF WATER WHICH RESULTED IN VERY LARGE REPAIR COSTS.
2017-09-29 08:50 | YES | NO | 19980035 | 1998-02-26 | 2387 | CITGO PIPELINE CO | YES | 1998-02-10 | 1400 | TX | HARDIN | SOUR LAKE | NO |  | NO | HWY 326 N. |  | TANK FARM | OTHER | FIRE OCCURRED AT TANK ROO | 1975 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 11197.1581 | 22589.1906 | NOT GIVEN |  | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | ROBERT B BUTRAL | 3184976944 | ON FEB. 10, 1998 AT 1400 HOURS A FIRE OCCURRED TO THE EXTERNAL SEAL AREA OFTANK 389 AT CITGO PIPELINE COMPANY SOUR LAKE TANK FARM. CRUDE OIL WAS BEINGSTORED IN THIS TANK AT THE TIME OF THE INCIDENT. THIS FIRE WAS LIMITED TO APORTION OF THE SEAL AREA OF THE TANK. JANUARY 12, 1998, CITGO PIPELINECOMPANY NOTIFIEDTHE TNRCC OF A FAILED SEAL CONDITION TO THIS TANK. THISCONDITION WAS DISCOVERED DURING A ROUTINE TANK INSPECTION. REPLACEMENT OFTHIS SEAL WAS BEING ACCOMPLISHED JUST PRIOR TO THE INCIDENT. THE FIREOCCURRED DURING A SEVERE ELECTRICAL STORM THAT WAS AFFECTING THE HARDIN COUNTYAREA ON THIS DATE. THERE WERE NO INJURIES AS A RESULT OF THIS INCIDENT.
2017-09-29 08:50 | NO | NO | 19980036 | 1998-02-25 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1998-01-26 | 1245 | OK | CREEK COUNTY |  | NO |  | NO | SE/4 SECTION 7-T. 18N-R9E |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 24493.7833 | 49413.8544 | CRUDE OIL |  | 10 | 8 | NO | NO | 3 | 0.19 | 35000 | WELDED |  | 720 | 0 | YES | 8 | 1000 | 4 | 92 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A HENRY | 5803952377 | PIPELINE CONSTRUCTED ON TOP OF GROUND. RELEASE CAUSED BY LOCALIZED EXTERNALCORROSION WHERE PIPELINE WAS IN CONTACT WITH GROUND.
2017-09-29 08:50 | YES | NO | 19980037 | 1998-02-25 | 443 | AMOCO PIPELINE CO | YES | 1998-01-22 | 1914 |  |  |  | YES | LATITUDE28'32.1'LONGITUD | YES | THE LEAK OCCURRED IN HIGH ISLAND BOCK A - 164 APPROXIMATELY 57.3 MILES FROM GALVESTON BEACH AND 21.7 MILES FROM PLATFORM HIA-474 |  | LINE PIPE | PIPE |  | 1978 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 215944 | 151122.444 | 304875.0104 | CRUDE OIL | 1 | 956 | 287 | NO | NO | 14 | 0.38 | 42000 | WELDED |  | 1618 | 578 | YES | 24 | 2025 | 9 | 78 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | JERRY W NATIONS | 4099483407 | ON 1/22/1998 AT APPROXIMATELY 1914 HOURS THE TEXAS CITY OPERATIONS CONTROLCENTER EXPERIENCED AN ABRUPT LOSS OF FLOW AND PRESSURE. THE OPERATORIMMEDIATELY REVIEWED THE SYSTEM DATA AND BEGIN " SHUTTING IN" WHILE CALLINGTHE SUPERVISOR OPERATIONS. THE GO AHEAD TO SHUT THE ENTIRE SYSTEM IN WASGIVEN. AGENCIES WERE NOTIFIED AND THE RESPONSE PLAN ACTIVATED. THE SLICKWAS LOCATED AND SKIMMING OPERATIONS WERE STARTED. DISPERSANT WAS USED TO AIDIN THE CLEAN UP. THE DAMAGED AREA OF THE PIPE WAS LOCATED ON SATURDAYAFTERNOON IN HIGH ISLAND BLOCK A-164 IN 120 FEET OF WATER. THERE WAS ARUPTURE IN THE LINE AT THE 5'OCLOCK POSITION RUNNING LONGITUDINALLY FORAPPROXIMATELY 40 INCHES THEN RUNNING UP TO THE 10'OCLOCK POSITION LATERALLY.THE PIPE WAS CHECKED BACACK BOTH WAYS FROM THE DAMAGED AREA TO LOCATE GOODPIPE. APPROXIMATELY 110' OF PIPE WAS CUT OUT FOR REPLACEMENT. REPAIRS WEREMADE USING NEW PIPE FROM STOCK AND A SET OF GRIPPER SEALL REPAIR TOOLS. THESYSTEM WAS LEAKED CHECKED AND PUT INTO SERVICE ON 2/01/1998. THE PIPELINE HADSUSTAINED DAMAGE BY AN OUTSIDE FORCE. THERE WERE MECHANICAL SCORES AND GOUGESALONG THE PIPE THAT WERE PROMARILY IN THE LONGITUDINAL DIRECTION. THE BADSECTION OF PIPE IS CURRENTLY UNDER GOING FAILURE ANALYSIS AT METALLURGICALCONSULTANTS, INC. IN HOUSTON, TEXAS
2017-09-29 08:50 | YES | NO | 19980038 | 1998-02-19 | 12106 | MAPCO INC | YES | 1998-01-25 | 2229 | MO | RAY COUNTY |  | NO |  | NO | 18 MILES NE OF MID-AMERICA PIPELINE COMPANY'S KEARNEY STATION AT ARIAL MARKER 18. 1 MILE NORTH OF BOBWHITE ROAD & HWY BB INTERSECTION ON BOBWHITE RD. TOWNSP |  | LINE PIPE | GIRTH |  | 1972 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 86000 | 60184.7247 | 121416.8993 | PROPANE | 2 | 9 | 0 | YES | NO | 10 | 0.19 | 1310 | WELDED |  | 1300 | 832 | YES | 24 | 1726 | 8 | 72 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL C PEARSON | 9185994043 | PIPELINE CONTROL RECEIVED INDICATIONS OF A LEAK AND IMMEDIATELY SHUTDOWN THEPIPELINE SYSTEM. FIELD OPERATIONS PERSONNEL RESPONDED TO THE LEAK AND SECUREDTHE LOCATION. THE PIPELINE SEGMENT WAS ISOLATED, EVACUATED OF PRODUCT AND THEDEFECTIVE GIRTH WELD WAS REMOVED AND REPLACED WITH A SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19980039 | 1998-02-18 | 30918 | KINDER MORGEN GP, INC. | YES | 1998-01-13 | 851 | IA | POLK COUNTY |  | NO |  | YES | 1402 VANDALIA RD , DES MOINES IOWA, 1 MILE WEST OF 65/69 BYPASS HIGHWAY |  | LINE PIPE | GIRTH |  | 1965 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 349.9112 | 705.9122 | BUTANE | 2 | 15 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A FANT | 7138449526 | THE PROBABLE CAUSE OF THIS RELEASE IS THE OVERFILING OF THE BELOW GROUNDACCUMULATOR. THE OVER FILLING WAS DUE TO A MALFUNCTIONING LEVEL CONTROLLER ONA DEHYDRATION SEPERATOR. AT THE TIME OF THE RELEASE A MAINTENANCE CREW WASPURGING THE FLARE SYSTEM WHICH CREATED A CONDITION WHEREBY THE PRESSURE IN THEFLARE SYSTEM EXCEEDED THE RELIEF PRESSURE OF THE ACCUMULATOR, PREVENTING FLOWINTO FLARE SYSTEM PIPING. DUE TO THE MALFUNCTIONING CONTROLLER, THEACCUMULATOR FILLED WITHOUT ABILITY TO ENTER THE FLARE SYSTEM, THE LIQUIDSESCAPED THROUGH THE ACCUMULATOR PUMP GASKET INTO THE ATMOSPHERE. THE EVENINGBEFORE THE RELEASE, JANUARY 12TH AT APPROXIMATELY 1630 A "FLARE STACKACCUMULATOR TANK INTERMEDIATE ALARM" AND "FLARE STACK ACCUMULATOR TANK HIGHLEVEL ALARM" ENUNCIATED. THE OPERATOR ON DUTY, SUSPECTING A HIGH LEVEL IN THEACCUMULULATOR, INSPECTED THE ACCUMULATOR SYSTEM AND FOUND NO EVIDENCE OF AHIGH LIQUID LEVEL. HE DISCUSSED THE SUTUATION WITH THE ON-CALL MAINTANCEPERSON. GIVEN THE OPERATING CONDITIONS THEY AGREED TO WAIT UNTIL THEFOLLOWING MORNING. AT APPROXIMATELY . 0852 HRS., WHILE TRYING TO CLEAR THEFLARE SYSTEM AND TROUBLESHOOTING FOR THE CAUSE OF THE TWO ALARMS THE RELEASEOCCURRED. SUBSEQUENT INVESTIGATION INDECATED THAT THE LEVEL CONTROLLER WASOUT OF RANGE.
2017-09-29 08:50 | YES | NO | 19980040 | 1998-02-05 | 30903 | ARCO PIPE LINE COMPANY | YES | 1998-01-07 | 1500 | TX | MONTAGUE COUNTY |  | NO |  | NO | FOUR MILES WEST OF MONTAGUE,TX @ INTERSECTION OF FARM TO MARKET ROAD 1806 AND ARCO PIPELINE RIGHT OF WAY |  | LINE PIPE | PIPE |  | 1990 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | CRUDE OIL | 1 | 10 | 0 | NO | NO | 20 | 0.31 | 65000 | WELDED |  | 1270 | 300 | YES | 8 | 1918 | 3 | 91 | EXTERNAL | Null | YES | OTHER | IMPRESSED CURRENT ELECTRI | NO DATA |  | Null | NO DATA |  | Null | Null | MIKE SCHMIDT | 9182232980 | EVIDENCE OF A CRUDE OIL LEAK WAS DISCOVERED DURING SCHEDULED MAINTENANCE OF A20 INCH UNDERGROUND PIPELINE. IN PREPARATION FOR MAINTENANCE, THE PIPELINEWAS EXPOSED BY EXCAVATION. THE CAUSE IS BELIEVED TO BE EXTERNAL CORROSION ANDPERMANENT REPAIRS HAVE BEEN COMPLETED. THERE WERE NO INJURIES , FIRES, OREXPLOSIONS ASSICIATED WITH THIS RELEASE.
2017-09-29 08:50 | YES | NO | 19980041 | 1998-01-04 | 19226 | TEXACO PIPELINE INC | YES | 1998-01-02 | 1200 | TX | ORANGE COUNTY |  | NO |  | NO | AT COW BAYOU APPROX. 200 YDS. N OF THE FM 1442 BRIDGE, BRIDGE CITY, TX |  | LINE PIPE | PIPE |  | 1953 | OTHER | UNKNOWN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 454884.5471 | 917685.8665 | CRUDE OIL | 1 | 5 | 3 | Null | Null | 22 | 0.31 | 52000 | NO DATA |  | 1062 | 594 | YES | 8 | 1327 | 0 | 95 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | B.L. LEDNICKY | 7137526514 | THE PIPELINE CROSSING AT COW BAYOU DEVELOPED A SMALL LEAK BENEATH COW BAYOU.THE CAUSES OF THE LEAK WAS REPAIRED BY REPLACEMENT OF THE CROSSING BY THEDIRECTIONAL DRILLING METHOD. THE OLD PIPE WAS VOIDED, FILED WITH WATER, ANDABANDONED IN PLACE.
2017-09-29 08:50 | YES | NO | 19980042 | 1998-03-30 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1998-02-25 | 1120 | KS | BARTON |  | NO |  | NO | NW 1/4 SECTION 13, TOWNSHIP 16 SOUTH, RANGE 14 WEST, BARTON COUNTY, KANSAS APPROXIMATELY 2 MILES NORTH AND 2 1/4 MILES WEST OF SUSANK, KANSAS |  | LINE PIPE | PIPE |  | 1945 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1399.6448 | 2823.6488 | CRUDE OIL | 1 | 51 | 3 | NO | NO | 3 | 0.19 | 0 | WELDED |  | 20 | 0 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON, SUPERINTENDENT OF OPERATIONS | 3162419270 | THIS LEAK OCCURRED IN 3-INCH SUCTION LINE TO JAYHAWK'S GAUGER FOUND THE LEAKON THE MORNING OF FEBUARY 25, AND REPORTED 15 BARRELS OUT. THE LEAK WASCLAMPED AND 3 BARRELS WERE RECOVERED. WHEN PERSONNEL ARRIVED 2 DAYS LATER TOREPAIR THE LEAK, IT WAS FOUND THAT THE SOIL WAS CONTAMINATION.
2017-09-29 08:50 | YES | NO | 19980043 | 1998-03-17 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1998-02-26 | 1340 | KS | RENO COUNTY |  | NO |  | NO | NW 1/4, SECTION 21, TOWNSHIP 24 SOUTH, RANGE 4 WEST, RENO COUNTY, KANSAS 4 MILES NORTH AND 1/4 MILE EAST OF HAVEN, KANSAS |  | LINE PIPE | PIPE |  |  | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2449.3783 | 4941.3854 | CRUDE OIL | 1 | 126 | 12 | NO | NO | 2.5 | 0 | 0 | OTHER |  | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ALLEN R WILKERSON | 3162419270 | A CONTRACTOR DOING WORK FOR A PRODUCER CUT JAYHAWK'S PLASTIC GRAVITY FIELDLINE ON FEBUARY 25,1998. THE NEXT MORNING, JAYHAWK'S GAUGER OPENED FIELD TANKTO THE LINE, AND ON HIS RETURN THAT AFTERNOON TO SHUT OFF, OIL WAS ON TOP OFTHE GROUND AND ALSO RAN DOWN THE CONTRACTORS DITCH LINE. THE CONTRACTOR NEVERCALLED JAYHAWK OR ONE-CALL. THE LINE WAS REPAIRED AND CONTRACTOR DID ALLCLEANUP ACCORDING TO THE KANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19980044 | 1998-03-24 | 2552 | COLONIAL PIPELINE CO | YES | 1998-02-23 | 1135 | TX | HARRIS | CLOVERLEAF | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 349911.1901 | 705912.205 | FUEL OIL | 1 | 213 | 204 | NO | NO | 36 | 0.38 | 46000 | WELDED |  | 690 | 318 | YES | 24 | 737 | 0 | 62 | EXTERNAL | Null | YES | OTHER | PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | S.E. GILLIAM, | 4048412314 | AT 11:35 AM CENTRAL STANDARD TIME ON 2/23/1998 A CHEVRON REPRESENTATIVENOTIFIED COLONIAL OF A POSSIBLE LEAK AT INTERSTATE 10. CHEVRON'S AERIALPATRON PILOR HAD SPOTTED DEAD VEGETATION IN A DITCH NEAR COLONIAL'S 36"PIPELINE. CHEVRON, EXPLORER AND COLONIAL HAVE ADJACEMENT PIPELINES THATPARALLEL THE UNION PACIFIC RAILROAD TRACK UNDERNEATH AN INTERSTATE 10 BRIDGEAT A RAILROAD CROSSING. THE PIPELINE WAS SHUT DOWN AND ISOLATED BY CLOSINGBLOCK VALVES AT HOUSTON STATION AND SHELDON ROAD. EMERGENCY RESPONSE EFFORTSWERE INTIATED UTILIZING COLONIAL AND CONTRACTOR PERSONNEL. NOTIFICATIONS WEREMADE TO LOCAL, STATE AND FEDERAL AUTHORITIES. COLONIAL'S 36" PIPELINE ISCASED IN THIS AREA. THE LEAK WAS DETERMINED TO BE LOCATED INSIDE THE CASING.COLONIAL REMOVED 640' OF PIPE FROM THE CASING, AND FOUND THE LEAK WAS A RESULTOF A CORROSION PIT IN THE PIPE. THE 640 FEET PF PIPE WAS REP;ADED THE NRCREPORT NUMBER 427996.
2017-09-29 08:50 | YES | NO | 19980045 | 1998-03-19 | 18273 | SHELL PIPELINE CORP | YES | 1998-02-16 | 1235 |  |  |  | YES | X=27447549.8/Y=216657.00 | NO | COBIA 12" , MAIN PASS, BLOCK 70 |  | LINE PIPE | PIPE |  | 1968 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 349911.1901 | 705912.205 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 12 | 0.41 | 52000 | WELDED |  | 1400 | 455 | YES | 24 | 1800 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D.F. SHEAFF | 7132414381 | APPROXIMATELY 1 BL OF CRUDE OIL SEEPED FROM A POSSIBLE CRACK IN THE PIPE. THECAUSE OF THE RELEASE IS BEING INVESTIGATED.
2017-09-29 08:50 | YES | NO | 19980047 | 1998-03-31 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1998-03-22 | 1000 | OK | LINCOLN COUNTY |  | NO |  | NO | NW/4 SECTION 22 - T17N - R 5E |  | TANK FARM | TANK |  |  | OTHER | INSUFFICIENT PROCEDURES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 3 | 80 | 80 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A HENRY | 5803952377 | BBL TANK. OIL SUBSEQUENTLY RAN INTO ROOF DRAIN AND INTO SECONDARYCONTAINMENT WHERE IT WAS COLLECTED.
2017-09-29 08:50 | YES | NO | 19980048 | 1998-04-03 | 18386 | BP OIL PIPELINE CO | NO | 1998-03-28 | 1125 | OH | HANCOCK |  | NO |  | NO | 22782 STATE ROUTE 12 FOSTORIA, OH 44830 |  | PUMPING STATION | PUMP |  | 1978 | OTHER | PUMP CASE CRACKED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | GASOLINE | 1 | 230 | 132 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G.A. DEBROCK | 2165862003 | BOOSTER #1 PUMP CASE CRACKED CAUSING A RELEASE OF 230 BBLS. OF PREMIUM 93GASOLINE INTO TANK #6004 DIKE AREA.ALL PRODUCT WAS CINTAINED WITHIN THE DIKEAREA, FLOATING ON WAER. 132 BARRELS WERE RECOVERED AND A HIGH AMOUNTEVAPORATED DUE TO WARM WEATHER (80'F) AND HITH WIND CONDITIONS.
2017-09-29 08:50 | NO | NO | 19980049 | 1998-04-06 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1998-03-12 | 1545 | OK | LINCOLN |  | NO |  | NO | SW/4 SECTION 11-T 15N-R 5E |  | LINE PIPE | PIPE |  | 1927 | OTHER | INSUFFICIENT PROCEDURES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15500 | 10847.2469 | 21883.2784 | CRUDE OIL | 3 | 25 | 20 | NO | NO | 10 | 0.39 | 24000 | WELDED |  | 400 | 300 | YES | 8 | 500 | 5 | 94 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A HENRY | 5803952377 | PIPELINE RUPTURED DURING EVALUATION RESULTING IN RELEASE OF CRUDE OIL.
2017-09-29 08:50 | YES | NO | 19980051 | 1998-04-06 | 2733 | CHEVRON PIPELINE CO - MIDLAND DIV | YES | 1998-03-10 | 1600 | NM | LEA | MONUMENT | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1978 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 27992.8952 | 56472.9764 | L. P. G. | 2 | 518 | 0 | NO | NO | 4.5 | 0.16 | 35000 | WELDED |  | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JIM JOHNSON | 2813637156 | BOH CONSTRUCTION WAS EXCAVETING WEAR THE LINE WHEN THEY HIT THE LINE WITH ABACKHOE. THE LINE WAS MARKED.
2017-09-29 08:50 | YES | NO | 19980052 | 1998-04-09 | 2387 | CITGO PIPELINE CO | YES | 1998-03-17 | 1400 | TX | HARDIN |  | NO |  | NO | CITGO TANK FARM 530 HWY. 326 NORTH |  | TANK FARM | OTHER | EXPANSION SLEEVE | 1952 | OTHER | DRESSER COUPLING SLIPPED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1399.6448 | 2823.6488 | CRUDE OIL | 1 | 90 | 0 | NO | NO | 16 | 0.25 | 0 | NO DATA |  | 0 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M.D. MOSELEY | 4092873594 | EXPANSION SLEEVE FAILED CAUSING LINE TO SEPERATE
2017-09-29 08:50 | NO | NO | 19980053 | 1998-04-10 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1998-03-11 | 1438 | IL | COLES |  | NO |  | NO | T-11N. R-7E, SEC. 18, APPROX. 3 MILES WEST OF ETNA,IL COUNTY ROAD 11 |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 41989.3428 | 84709.4646 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 8.63 | 0.2 | 42000 | WELDED |  | 1340 | 300 | YES | 30 | 1994 | 12 | 69 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | MARC DEVARENNES | 5734865488 | CONTRACTOR FOR RURAL ELECTRIC COMPANY HIT THE PIPELINE WITH A POWER AUGERWHILE SETTING UTILITY POLES CAUSING A CRACK IN THE PIPELINE APPROX. 1/2" LONGAND 1/32 WIDE. PREVIOUS DISCUSSION WITH KOCH PERSONNEL AND UTILITY COMPANYCONCERNING WORK SCOPE INDICATED NO ACTIVICTIES WOULD TAKE PLACE ON THE NORTHSIDE OF THE ROAD WHERE THE INCIDENT OCCURRED. NO EVACUATIONS TOOK PLACE. ONEROAD CLOSED. NO IMMEDIATE DANGER TO PEOPLE OR THE ENVIRONMENT.
2017-09-29 08:50 | YES | NO | 19980054 | 1998-04-13 | 2552 | COLONIAL PIPELINE CO | YES | 1997-12-02 | 1200 | LA | ST HELENA |  | NO |  | NO | USGS MAP ATTACHED |  | LINE PIPE | PIPE |  | 1962 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 14137000 | 10015372.7203 | 20205052.1449 | GASOLINE | 1 | 10000 | 4389 | NO | NO | 36 | 0.28 | 52000 | WELDED |  | 584 | 345 | YES | 24 | 758 | 0 | 1962 | EXTERNAL | Null | YES | OTHER | PITTING |  |  | Null |  |  | Null | Null | S.E. GILLIAM | 404841231 | ON 12/2/1997 AT 12:00 CST THE LINE 1 COMTROLLER WAS CALLED BY INSPECTOR TOREPORT A SMALL PINHOLE LEAK AT M.P. 299. LINE 1 WAS SHUT DOWN BY 12:15. THEPRODUCT WAS CONTAINED IN THE PIPELINE BY USING A NYLON RATCHET STRAP ANDRUBBER SEAL UNTIL NECESSARY PIPELINE CLEANING WAS COMPLETE. PRODUCT THATESCAPED WHILE APPLYING TEMPERARY SEAL WAS CONTAINED IN A FIVE GALLON BUCKETAPPRONIMATELY 1 GALLON. FINAL REPAIR WAS ACHIEVED BY INSTALLLATION OF A 3FOOT FULL ENCIRCLEMENT SLEVE. AT FINAL CLEAN-UP, STARTED 3/12/1998. THEENVIRONMENTAL TECHNICIAN INSTALLED PIEZOMETER WELLS AND ESTIMATEDAPPROXIMATELY 860 BBLS HAD CONTAMINATED SOIL. A TELEPHONIC REPORT (REPORT NO.427996) WAS MADE ON 3/12/1998 AND A CALL TO DOT/OTS OFFICE IN HOUSTON WASMADE. ENVIRONMENTAL CLEAN-UP EFFORTS ARE CONTINUING. COLONIAL IS PROVIDING THIS SUPPLEMENTAL ACCIDENT REPORT TO NOTE CHANGES IN INFORMATION RELATED TO THIS EVENT SINCE THE LAST SUPPLEMENTAL REPORT DATE JUNE 12, 1998. AS OF MARCH 31, 2001, COLONIAL HAS RECOVERED APPROXIMATELY 10,134 BARRELS OF SEPARATE PHASE HYDROCARBONS (GASOLINE) FROM THE SITE. IN ADDITION, COLONIAL HAS RECOVERED APPROXIMATELY 4,389 BARRELS OF GASOLINE IN THE FORM OF EXTRACTED VAPOR FROM THE RECOVERY SYSTEM OPERATING ON SITE. COLONIAL IS CONTINUING TO CONDUCT REMEDIATION ACTIVITIES AT THE SITE UNDER THE OVERSIGHT OF THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY. THE CURRENT ESTIMATE OF TOTAL PROPERTY DAMAGE FOR THE SITE IS APPROXIMATELY $4,664.000. COLONIAL IS CONTINUING TO INVESTIGATE THE CAUSE OF THE RELEASE. COLONIAL WILL UPDATE THIS REPORT UPON THE DEVELOPMENT OF ANY SIGNIFICANT NEW INFORMATION RELATED TO THE RELEASE. 2/6/03 COLONIAL IS PROVIDING THIS SUPPLEMENTAL ACCIDENT REPORT TO NOTE CHANGES IN INFORMATION RELATED TO THIS EVENT SINCE THE LAST SUPPLEMENTAL REPORT DATED MAY 3, 2001. AS OF 12/31/2002, COLONIAL HAS RECOVERED APPROXIMATELY 17,405 BARRELS OF SEPARATE PHASE HYDROCARBONS (GASOLINE) FROM THE SITE. COLONIAL IS CONTINUING TO CONDUCT REMEDIATION ACTIVITIES AT THE SITE UNDER THE OVERSIGHT OF THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY. THE ESTIMATE OF TOTAL PROPERTY DAMAGE AS OF SEPTEMBER 2002 FOR THE SITE IS APPROXIMATELY $15,084,905. COLONIAL IS CONTINUING TO INVESTIGATE THE CAUSE OF THE RELEASE. COLONIAL WILL UPDATE THIS REPORT UPON THE DEVELOPMENT OF ANY SIGNIFICANT NEW INFORMATION RELATED TO THE RELEASE.
2017-09-29 08:50 | YES | NO | 19980055 | 1998-04-15 | 4805 | EXPLORER PIPELINE CO | YES | 1998-03-16 | 1035 | TX | FANNIN |  | NO |  | NO | WEST OF LEONARD, TEXAS ON HIGHWAY 78 1/4 MILE, THEN 1/4 MILE SOUTH |  | LINE PIPE | PIPE |  | 1971 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 139964.476 | 282364.882 | FUEL OIL | 3 | 15 | 1 | NO | NO | 28 | 0.28 | 52000 | WELDED |  | 751 | 325 | YES | 24 | 1030 | 12 | 71 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R.E. SANDS | 9184935106 | ON MARCH 16, 1998 AT 1035 HOURS EXPLORER'S PIPELINE CONTROL CENTER IN TULSA,OKLAHOMA RECEIVED A PHONE CALL FROM A LOCAL RESIDENT REPORTING A POSSIBLEPIPELINE LEAK NEAR LEONARD, TEXAS. COMPANY PERSONNEL ARIVED ON SITE AT 1145HOURS AND DISCOVERED FUEL OIL ON A 150' X 75' AREA OF GRASS OVER EXPLORER'S28" PIPELINE AND ON AN ADJACENT FARM POND. COMPANY PERSONNEL PLACED SORBENTBOOMS TO PREVENT FURTHER MIGRATION OF PRODUCT INTO THE POND. EXPLORER'S SPILLRESPONSE CONTRACTOR WAS CALLED TO ASSIST WITH CLEANUP AND A MAINTENANCECONTRACTOR WAS DISPATCHED TO THE SITE FOR EXCAVATION AND REPAIRS/ EXCAVATIONBEGAN ON MARCH 17, 1998 AND AT APPROXIMATELY 1600 HOURS THE SOURCE OF THERELEASE WAS LOCATED. IT DETERMINED TO BE A SMALL CRACK IN THE BOTTOM OF THE28" PIPE WHERE IT HAD BEEN RESTING ON ROCK. A FULL ENCIRCLEMENT BOLT ONPLIDCO SPLIT SLEEVE WAS INSTALLED AND THE LINE PLACED BACK INTO OPERATION AT2320 HURS ON MARCH 17,1998. CLEAN-UP ACTIVICTIES ARE BEING COORDINATED WITHTHE TNRCC.
2017-09-29 08:50 | NO | NO | 19980056 | 1998-04-17 | 30950 | EL PASO FIELD SERVICES | NO | 1998-03-23 | 1345 |  |  |  | YES | 96' 13.2" W 28' 25.6"N | NO | STATE LEASE MATAGORDA ISLAND AREA BLOCK 485 |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 24493.7833 | 49413.8544 | NATURAL GAS LIQUID | 2 | 1 | 0 | NO | NO | 6 | 0.42 | 35000 | WELDED |  | 1440 | 500 | YES | 24 | 2162 | 9 | 79 | INTERNAL | Null | YES | OTHER | INTRNL CORR FROM LIQUID | NO DATA |  | Null | NO DATA |  | Null | Null |  | 7137573534 | 1:45PM D.J LAMB OF PETROLEUM HELICOPTERS, INC. CALLED. HE SPOTTED A SHEEN ATCOORDINATES 2825.6 9613.2 NORTHWEST OF MI 520. ROBERT TOLD D.J. TO FLY TOINVESTIGATE. 1:50 ROBERT CALLED MONTE TO DISPATCH HIM TO CATCH THE HELICOPTERAT OYSTER LAKE. 2:20 MONTE CALLED - THERE WAS A VISIBLE SHEEN AT COORDINATESREPORTED BY D.J. EARLIER. THERE WERE VERY FEW BUBBLES AND A SHEEN OF ABOUT 60YARDS BY 6 MILES IN LENGTH. SEAS WERE CALM WITH SHEEN MOVING EAST INTO THEGULF AND AWAY FROM LAND. IT WAS ALSO DISSIPATING RAPIDLY DUE TO THE BRIGHTSUN AND CLEAR SKYS. 2:30 ROBERT CALLED AMERICAN OILFIELD DRIVERS TO CHECK ONTHE AVAILABILITY OF A DIVE BOAT AND CREW TO BEGIN MOBILIZATION TO THELOCATION. JOHN SKINNER SAID HE WOULD CALL HHIM BACK ON STATUS. 3:00 ROBERTCALLED RANDY WEST TO INFORM HIM OF REPORT. 4:30 JOHN SKINNER CALLED ROBERT -THEY WILL BE MOBILIZING A BOAT AT MIDNIGHT TONIGHT (3/23) FOR ARRIVAL AT PORTO'CONNER ON WEDNESDAY 3/25 BETWEEN 3 AND 6 PM. 5:45 I CALLED THE US COSTGUARD IN PORT LAVACA AND LEFT A MESSAGE FOR EITHER SCOTT CLINGENPEEL OR MARTYPRITCHARD. 5:50 I CALLED THE NATIONAL RESPONSE CENTER TO INFORM THEM THAT WEARE INVESTIGATING A REPORT OF POSSIBLE LEAK AND RELAYED ALL DETAILS THUS FAR.I SPOKE TO CHRIS SAVAGE AND RECEIVED REPORT NUMBER OF 429532. 6:10 I CALLEDTHE TEXAS GENERAL LAND OFFICE AND INFORMED THEM OF DETAILS- RECEIVED REPORTNUMBER OF 980535 BY WORSLEY. 6:30 I E-MAILED PATTY MILLER AND DICK SUMNERRELAYING ALL INFORMATION KNOWN UP TO THIS POINT. 7:45 RECEIVED A PAGE FROMNEIL IRVIN WITH THE GENERAL LAND OFFICE - HE WAS CONCERNED THAT IT WAS CRUDEOIL LEAKING. I TOLD HIM THAT WE BELIEVED IT TO BE A NATURAL GAS CONDENSATEBECAUSE OF THE VARIOUS LINES IN THAT SAME VICINITY. I TOLD HIM I WOULD KEEPHIM UPDATE AS SOON AS I RECEIVED MORE INFORMATION. 8:30 PETTY OFFICER SCOTTCLINGENPEEL WITH THE U.S. COAST GUARD PAGED ME - HE HAD BEEN SPEAKING TO HISSUPERVISOR IN CORPUS CHRISTI AND HIS SUPERVISOR WAS CONCERNED AND WANTING MORE
2017-09-29 08:50 | YES | NO | 19980057 | 1998-04-24 | 443 | AMOCO PIPELINE CO | YES | 1998-03-21 | 930 | OK | CREEK |  | NO |  | NO | SE/4 SEC 33, T18N R7E CUSHING-FREEMAN LINE SEGMENT-DRUM RIGHT STATION TANK 0045 |  | NO DATA | NO DATA |  |  | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | CRUDE OIL | 1 | 8500 | 8400 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TERRY L HUTSON | 9182231101 | TANK VALVE ON TANK 0045 WAS OPENED WHILE TANK VALVE ON TANK 6929 WAS OPEN,ALLOWING TANK 0045 TO OVERFLOW DUE TO 26-FOOT ELEVATION DIFFERENCE. CAUSE WASFAULTY COMMUNICATIONS CABLE ALLOWING INCORRECT VALVE STATUSES TO BETRANSMITTED TO THE TULSA CONTROL CENTER.
2017-09-29 08:50 | NO | NO | 19980058 | 1998-04-23 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1998-02-05 | 1510 | OH | MAHONING |  | NO |  | NO | SEE ATTACHED DRAWING NO. 11792-A |  | LINE PIPE | PIPE |  | 1968 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 45488.4547 | 91768.5867 | GASOLINE | 3 | 10 | 5 | NO | NO | 10 | 0.2 | 1970 | WELDED |  | 1115 | 360 | YES | 24 | 1548 | 9 | 97 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | CARL A OSTACH | 6107704495 | ON THURSDAY, FEBRUARY 5, 1998, A PROPERTY OWNER CALLED BUCKEYE PIPE LINECOMPANY'S MANTUA STATION AND REPORTED THE SMELL OF GASOLINE. A BUCKEYE PIPELINE COMPANY EMPLOYEE WAS DISPATCHED TO THE SITE AND DISCOVERED PETROLEUMPRODUCT IN A FARMER'S FIELD NEAR BUCKEYE'S 10" MANTUA OHIO, TO CORAOPOLIS,PENNSYLVANIA PIPELINE SYSTEM. AFTER FURTHER INVESTIGATION, A SMALL CORROSIONPIT WAS FOUND IN THE MAINLINE PIPE. TEMPORARY REPAIRS WERE COMPLETED ONFEBRUARY 5, 1998, AND PERMANENT REPAIRS WERE COMPLETED ON FEBRUARY 11, 1998.ALL APPLICABLE REGULATORY AGENCIES WERE NOTIFIED AND RECOVERY AND CLEANUPACTIVIES ARE BEING COMPLETED UNDER THE SUPERVISION OF THE OHIO ENVIRONMENTALPROTECTION AGENCY.
2017-09-29 08:50 | YES | NO | 19980059 | 1998-04-27 | 12106 | MAPCO INC | YES | 1998-03-31 | 1230 | WY | SWEETWATER |  | NO |  | YES | APPROXIMATELY A.M. 76 ON MID-AMERICA'S EAST LEG SYSTEM, LOCATED 1 MILE EAST OF WAMSUTTER, WYOMING ON I-80 SECTION 26, TOWNSHIP 20 NORTH, RANGE 94 WEST |  | LINE PIPE | PIPE |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 62310 | 43605.9325 | 87970.779 | NATURAL GAS LIQUID | 2 | 3358 | 0 | NO | NO | 6.63 | 0.13 | 52000 | WELDED |  | 1440 | 1260 | YES | 24 | 1977 | 8 | 82 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | MICHAEL C PEARSON | 9185994043 | PIPELINE CONTROL RECEIVED INDICATIONS OF A LEAK AND SHUTDOWN THE PIPELINESYSTEM. FIELD OPERATIONS PERSONNEL RESPONDED TO THE LEAK AND SECURED THELOCATION. THE PIPELINE WAS EXCAVATED AND THE SECTION OF FAILED PIPE WAS CUTOUT AND REPLACED. THE FAILED PIPE COMPONENT SHOWED EVIDENCE OF PRIORMECHANICAL DAMAGE. THE CUT OUT SECTION HAS BEEN SENT TO A THIRD PARTY FIRM TODETERMINE THE CONTRIBUTING CAUSE OF FAILURE.
2017-09-29 08:50 | YES | NO | 19980060 |  | 2552 | COLONIAL PIPELINE CO | YES | 1998-03-30 | 1605 | GA | FULTON | ATLANTA | NO |  | NO | USGS MAP ATTACHED |  | LINE PIPE | PIPE |  | 1978 | OTHER | BUCKLE WITH CRACK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4041136 | 2828077.4139 | 5705374.4491 | GASOLINE | 3 | 920 | 413 | NO | NO | 40 | 0.34 | 743 | WELDED |  | 594 | 375 | YES | 24 | 1032 | 1 | 1978 |  | Null | YES |  |  |  |  | Null |  |  | Null | Null | S E GILLIAM |  | THE FAILURE RESULTED FROM A BUCKLE ON THE TOP HALF OF THE PIPE. A 10-FOOTSECTION OF PIPE CONTAINING THE BUCKLE WAS CUT FROM THE LINE AND PRE-TESTEDSECTION OF 40" 0.500 W.T. API 5L-X52 PIPE WAS INSTALLED. THE PIPELINE WASRETURNED TO SERVICE AT 1607 ON 4/4/98.
2017-09-29 08:50 | YES | YES | 19980062 | 1998-06-09 | 31067 | AERA ENERGY, LLC. | NO | 1998-05-15 | 850 | CA | LOS ANGELES | LONG BEACH | NO |  | NO | 100 NO PICO AVE (AT OCEAN BLVD) |  | PUMPING STATION | PIPE |  | 1998 | OTHER | CLAMPING MECHANISM FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 20000 | 13996.4476 | 28236.4882 |  |  | 10 | 10 | NO | NO | 8 | 0.5 | 0 | FLANGED |  | 1350 | 1200 | YES | 0 | 1200 | 5 | 98 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN R LIMOUSIN | 7149693533 | AT 0850 HOURS ON 5/15/98, INJURED WAS WALKING BETWEEN THE #2 AND #3 METER RUNSWHEN THE WALKER SAMPLER FOR THE #2 RUN WORKED LOOSE FROM ITS MOUNT AND BLEWOUT, STRIKING THE INJURED IN THE LEFT HAND AND CHEST. THE INJURED, WHO WASWORKING ALONE AT THE FACILITY, IMMEDIATELY CLOSED THE METER #2 DISCHARGEISOLATION VALVE, STOPPING THE RELEASE OF CRUDE OIL FROM THE SAMPLER MOUNT.THE #2 METER RUN WAS NOT ACTIVE (NO FLOW) AT THE TIME, BUT HAD APPROXIMATELY1200 PSIG BECAUSE THE #3 METER RUN WAS ACTIVE AND BECAUSE OF THE COMMONDISCHARGE HEADER PIPING CONFIGURATION. AFTER STOPPING THE RELEASE, THEINJURED NOTIFIED THE SHELL OIL HOUSTON CONTROL CENTER FOR A SHUT DOWN, THENNOTIFIED THE AERA ENGERY SUPERVISOR ON THE BETA PLATFORMS TO ARRANGE FORPROPER AGENCY NOTIFICATIONS.
2017-09-29 08:50 | YES | NO | 19980063 | 1998-05-11 | 10012 | KANEB PIPELINE CO | YES | 1998-04-04 | 1445 | SD | UNION |  | NO |  | NO | RURAL LOCATION - FARMLAND: SW 1/4, SECTION 2, T-93-N, R-49-W |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 27992.8952 | 56472.9764 | FUEL OIL | 3 | 195 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | LEROY ANDERSON | 3162621408 | IN ACCORDANCE WITH SOUTH DAKOTA STATE LAW, I CONTACTED THE ONE-CALL CENTER ONMARCH 27, 1998 AND REQUESTED LOCATES FOR WORK TO TAKE PLACE IN UNION COUNTY,SD, TWP 93N, 49W, SECTIONS 2-S1/2, 11-NE AND 12-NW. AS YOU KNOW AN ERROR WASMADE ON TICKET 980860093 AND CONSEQUENTLY, KANEB PIPELINE COMPANY WAS NOTNOTIFIED OF THE WORK AND DID NOT MARK A PIPELINE THEY HAD IN THE S1/2 OFSECTION 2. ON THE AFTERNOON OF APRIL 4 A CONTRACTOR WORKING FOR CLAY RURALWATER SYSTEM HIT THE PIPELINE AND RUPTURED IT. WE PHONED KANEB OFFICIAL INYANKTON, SD IMMEDIATELY AND REPORTED THE INCIDENT. ATTACHED IS A COPY OFKANEB'S INTERNAL EMERGENCY NOTIFICATION SHEET. KANEB'S ENVIRONMENTAL CHIEF,LEROY ANDERSON OF KANEB'S WICHITA OFFICE CONTACTED THE SOUTH DAKOTA DEPT OFENVIRONMENT AND NATURAL RESOURCES (DENR) AND REPORTED THE INCIDENT. ATTACHEDIS A COPY OF DENR'S SPILL REPORT FORM.
2017-09-29 08:50 | YES | NO | 19980064 | 1998-04-30 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1998-03-31 | 1240 | KS | SUMNER |  | NO |  | NO | NW 1/4, SECTION 17, TOWNSHIP 32 SOUTH, RANGE 2 EAST, SUMNER COUNTY, KANSAS APPROXIMATELY 3 1/2 MILE SOUTH OF OXFORD, KANSAS |  | LINE PIPE | PIPE |  |  | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 1749.556 | 3529.561 | CRUDE OIL | 1 | 55 | 45 | NO | NO | 4 | 0.25 | 0 | WELDED |  | 20 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | YES | ALLEN R WILKERSON | 3162419270 | FARMER WAS CHISELING FIELD 18 INCHES DEEP AND HIT THE PIPELINE, BUT DID NOTCALL JAYHAWK. THIS LINE IS A GRAVITY LINE SO THE PIPELINE WAS EMPTY WHENFARMER PUNCTURED THE LINE. THE NEXT DAY, JAYHAWK GAUGER TURNED OIL ON FROMLEASE AND THE LEAK OCCURRED. NEW TESTED PIPE WAS INSTALLED AND LOWERED TO 36INCHES.
2017-09-29 08:50 | YES | NO | 19980066 | 1998-05-20 | 18273 | SHELL PIPELINE CORP | YES | 1998-04-18 | 2030 | LA | ST JAMES | ST JAMES | NO |  | NO | CAPLINE TANK FARM, ST JAMES TERMINAL, TANK 519 FILL LINE |  | TANK FARM | OTHER | DRESSER COUPLING | 1976 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 128287 | 89778.1137 | 181118.7181 | CRUDE OIL | 1 | 17806 | 14600 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF | 7132414381 | 48" DRESSER COUPLING INSTALLED IN THE FILL/SUCTION LINE FAILED WHEN THELONGITUDINAL SUPPORT RODS WERE OVERSTRESSED. ONE END OF THE DRESSER COUPLINGWAS LEFT UNSUPPORTED, FOLLOWING THE PREVIOUS REMOVAL OF A TANK VALVE FORREPAIR.
2017-09-29 08:50 | YES | NO | 19980067 | 1998-05-12 | 30903 | ARCO PIPE LINE COMPANY | YES | 1998-03-24 | 1130 | CA |  | LONG BEACH | NO |  | NO | INTERSECTION OF FASHION AND BURNETT STREETS IN THE CITY OF LONG BEACH, CA. TWP 4S RANGE 13W. LONG BEACH QUADRANGLE, CA LOS ANGELES CO 7.5 MIN 15 SERIES |  | LINE PIPE | PIPE |  | 1952 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 87477.7975 | 176478.0513 | CRUDE OIL | 1 | 3 | 0 | NO | NO | 12 | 0.25 | 42000 | OTHER |  | 720 | 0 | YES | 4 | 900 | 9 | 83 | NO DATA | Null | Null | NO DATA |  | OTHER | BROKEN WATER LINE | Null | ONE CALL |  | YES | YES | MICHAEL VAN LEEUWEN | 5627282221 | OUR CONTRACTORS WERE IN THE PROCESS OF REMOVING A SECTION OF LINE 71 WHEN ANEARBY 6" TRANSITE WATER MAIN BROKE. THE REMOVAL WAS PART OF AN UPGRADE TOTHE PIPELINE. PRIOR TO THE REMOVAL, THE LINE HAD FIRST BEEN PURGED WITHNITROGEN, THEN VACUUM TRUCK DRAINED WITH EACH END OF THE CUT (NORTH & SOUTH)PLUGGED. ADDITIONALLY, THE SEGMENT WAS ISLOATED WITH BLIND FLANGES AT THENEARBY VAULT BOX (SOUTH OF THE EXCAVATION). ONCE THE WATER MAIN HAD RUPTURED,WATER FILLED THE EXCAVATION AREA WASHING OUT APPROXIMATELY 3 BARRELS OF OIL INTHE LINE, NORTH OF THE CUT SECTION (THE PLUG HAD BEEN WASHED OUT ALLOWINGWATER INTO THE LINE). THE PIPELINE WAS NOT OPERATING AT THE TIME.(ATTACHED) THIS INCIDENT OCCURRED DURING AND UPGRADE TO A PORTION OF APL'SLINE 71. A 6" TRANSITE WATER LINE BROKE IN THE EXCAVETION AREA WASHING OUTAPPRX. 3 BARRELS OF CRUDE OIL INTO THE STREET. PRIOR TO THE WATER LINEBREAK, LINE 71 HAD BEEN NITROGEN PURGED, VACUMN TRUCK DRAINED AND ISOLATED ATTHE BLOCK VALVE. AFTER THE LINE WAS CUT FOR THE UPGRADE, EACH CUT SECTION WASSECURED WITH A PLUMBERS PLUG. AFTER THE WATER LINE BROKE, ONE OF THE PLUGSCAME LOOSE, AND WATER CAUSE OIL THAT WAS IN THE EXCAVATION AND THE SECTIONOFPIPE TO WASH INTO THE STREET. APL IMMEDIATELY IMPLEMENTED ITS EMERGENCYRESPONSE PROCEDURES AND NOTIFIED THE NRC. PROPERTY DAMAGE DUE TO THE INCIDENTWAS GREATER THAN $50,000.
2017-09-29 08:50 | YES | NO | 19980068 | 1998-05-12 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1998-04-07 | 1415 | OH | WARREN | LEBANON | NO |  | NO | TEPPCO'S LEBANON TERMINAL ON STATE HIGHWAY 122 APPROXIMATELY 0.3 MILES EAST OF RED LION, OH |  | TANK FARM | TANK |  |  | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 4898.7567 | 9882.7709 | TRANSMIX (PART.REFINED PETRO) | 1 | 149 | 125 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ERNEST P HAGAN | 7137593845 | A FAILURE TO FOLLOW WRITTEN OPERATING PROCEDURES RESULTED IN THE OVERFILLINGOF A TRANSMIX TANK TEPPCO'S LEBANON, OHIO TERMINAL. UPON DISCOVERY, THEOPERATOR IMMEDIATELY SHUT OFF FLOW TO THE TANK AND STOPPED THE OVERFLOW OFPRODUCT. THERE WAS APPROXIMATELY 24 BARRELS LOST TO ATMOSPHERIC EVAPORATIONAND GROUND ABSORPTION. TEPPCO IS CURRENTLY WORKING WITH APPROPRIATE STATEAGENCY FOR REMEDIATION PLAN IN THE CONTAINMENT AREA.
2017-09-29 08:50 | YES | NO | 19980069 | 1998-05-15 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1998-04-09 | 730 | OK | LOGAN |  | NO |  | NO | SE/4 SECTION 8, TOWNSHIP 19 NORTH, RANGE 2 WEST - FROM HWY 51 & 74 JCT 8 MILES EAST, 1 1/4 MILE NORTH, WEST INTO |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2099.4671 | 4235.4732 | CRUDE OIL | 1 | 50 | 40 | NO | NO | 8 | 0.19 | 52000 | WELDED |  | 1632 | 560 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | BACTERIAL | NO DATA |  | Null | NO DATA |  | Null | Null | VANCE WEBB | 5807674845 | THIS LETTER SERVES AS THE REQUIRED WRITTEN FOLLOW UP REGARDING THE CRUDE OILRELEASE WHICH OCCURRED ON CONOCO PIPE LINE'S (CPL) KINGFISHER, OK TO COLORADO,OK 8" CRUDE OIL PIPELINE. THE RELEASE WAS REPORTED TO PETTY OFFICER TURMAN OFTHE NRC ON APRIL 9, 1999 @ 11:20 HRS BY MYSELF, VANCE WEBB OF CPL AND WASASSIGNED AN INCIDENT NUMBER OF (431811). THIS RELEASE WAS ALSO REPORTED TOTONY CUPP OF THE OKLAHOMA CORP COMM @ 09:00 ON THAT SAME DAY. ADDITIONALLY,PLEASE FIND ENCLOSED THE REQUIRED 7000-1 REPORT FOR THE INCIDENT. METHOD OFCLEAN UP:VACUUM TRUCKS AND ABSORBENT PADS WERE USED TO RECOVER THE RELEASEDMATERIAL. AFFECTED SOIL WAS AERATED ON LOCATION. CREEK AND BANKS WERE WATERWASHED AND FREE PRODUCT WAS REMOVED. THE EFFECTED AREA AROUND THE LEAK SITEAND THE CREEK BANKS WERE THEN BURNED AFTER RECEIVING PERMISSION FROM THEOKLAHOMA DEPT OF ENVIRONMENTAL QUALITY.
2017-09-29 08:50 | YES | NO | 19980070 | 1998-05-22 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1998-05-01 | 318 | TX | MATAGORDA | DANEVANG | NO |  | NO | PIPELINE PUMP STATE LOCATED IMMEDIATELY NORTHWEST OF INTERSECTIN OF COUNTY ROADS 401 & 434 |  | PUMPING STATION | PUMP |  | 1991 | OTHER | PUMP SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 139964.476 | 282364.882 | BUTANE |  | 0 | 0 | NO | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | REX J PROSSER | 7138777370 | ON 5/1/98 AT APPROXIMATELY 0318, POWER AND REMOTE COMMUNICATION WAS LOST ATTHE DANEVANG PUMP STATION. SUBSEQUENT INVESTIGATION DETERMINED THAT LPGLEAKING FROM A PUMP (INTRINSICALLY SAFEY PUMP & MOTOR) BUILT UP OVER NIGHT ANDDETONATED WHEN A REMOTE START WAS ATTEMPTED. THE DETONATION CAUSED SEVERESTRUCTURAL DAMAGE TO THE 16' X 20' CONTROL BUILDING. PROPERTY DAMAGE ONLY.
2017-09-29 08:50 | YES | NO | 19980071 | 1998-05-28 | 4906 | EXXON PIPELINE CO | NO | 1998-04-20 | 1015 | TX | ANDERSON |  | NO |  | NO | THE RELEASE OCCURRED IN ANDERSON COUNTY, TX. WHEN HEADING OUT OF NECHES ON HIGHWAY 19 WEST GO TILL YOU COME TO COUNTY ROAD 747. TURN RIGHT ON 747 TO SPILL |  | LINE PIPE | NO DATA | DMG BY OUTSIDE FORCES | 1977 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 52486.6785 | 105886.8308 | CRUDE OIL | 1 | 100 | 100 | NO | NO | 8 | 0 | 42000 | WELDED |  | 619 | 450 | YES | 8 | 774 | 7 | 95 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | J B BACON | 7136560649 | THIRD PARTY DAMAGE TO EPC'C ARP NECHES JUNCTION PIPELINE THAT WENT UNREPORTEDAT THE TIME OF DAMAGE. THE DAMAGE TO THE PIPELINE LATER RESULTED IN A RELEASEOF 100 BARRELLS OF CRUDE OIL TO LAND AND WATER ON BRUSHY CREEK.
2017-09-29 08:50 | YES | NO | 19980072 | 1998-06-02 | 30903 | ARCO PIPE LINE COMPANY | NO | 1998-05-08 | 931 | CA |  | LONG BEACH | NO |  | NO | 5884 ELM STREET, LONG BEACH. BETWEEN HULLETT AND 59TH STREETS (GRID D2, PAGE 765 OF 1997 LOS ANGELES THOMAS GUIDE) |  | LINE PIPE | LONGITUDINAL WELD |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 699822.3801 | 1411824.41 | CRUDE OIL | 1 | 750 | 672 | NO | NO | 14 | 0.25 | 35000 | WELDED |  | 668 | 675 | YES | 4 | 865 | 6 | 95 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ART DIEFENBACH | 5627282719 | DURING A SHIPMENT OF CRUDE OIL PUMPING FROM ARCO PIPE LINE COMPANY'S (APL)WEST HYNES PUMP STATION TO EQUILLON'S REFINERY IN WILMINGTON, CA THE PIPELINERUPUTURED ALONG A LONGITUDINAL SEAM. THE PRESSURE AT THE TIME OF THE BREAKWAS WITHIN 110% OF MOP. THE SUPERVISORY CONTROL AND DATA AQUISTTION SYSTEMDETECTED ABNORMALITIES WHICH INDICATED THE BREAK. THE PIPELINE OPERATOR TOOKACTION TO SHUT DOWN THE PIPELINE. THE OPERATOR THEN RECEIVED A CALL FROM THELONG BEACH FIRE DEPARTMENT (LBFD) ADVISING OF A CRUDE OIL LEAK ALONG THE ROUTEOF THIS PIPELINE. APL PERSONNEL WERE DISPATCHED TO THE AREA. EXCAVATION OFTHE PIPELINE REVEALED A FAILURE OF A LONGITUDINAL SINGLE SIDED SUBMERGED ARCWELD. THE RUPTURE WAS APPROXIMATELY 14 INCHES IN LENGTH OF 0.75" WIDE AT THECENTER OF THE BREAK. APL'S INCIDENT COMMAND SYSTEM WAS IMMEDIATELYIMPLEMENTED WITH NOTIFICATION TO THE NRC.
2017-09-29 08:50 | YES | NO | 19980073 | 1998-06-01 | 15490 | PHILLIPS PIPE LINE CO | YES | 1998-05-01 | 1900 | IL |  | KANKAKEE | NO |  | NO | BORGER-E, CHICAGO "BLUE" LINE - MP 899-33+52 SEC 3, T30N, R11E 2 MILES WEST OF KANKAKEE, IL ON STATE RT #17 |  | LINE PIPE | OTHER | MUELLER FITTING | 1959 | OTHER | FAILED GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | BUTANE | 2 | 250 | 0 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 960 | 400 | YES | 24 | 1470 | 5 | 82 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | L J SCHMITZ | 9186614814 | THE SHERIFF'S DEPT CALLED THE CONTROLLER TO REPORT A POSSIBLE LEAK. THEPIPELINE WAS DOWN AND BLOCKED AT THE TIME. PPL PERSONNEL DISCOVERED EVIDENCEOF A LEAK, AND AN ADDITIONAL BLOCK VALVE AT MP 897 WAS CLOSED. SEVERALRESIDENTS WERE ASKED TO LEAVE THEIR HOMES BY THE FIRE CHIEF AS A PRECAUTIONAYMEASURE. AN OLD MUELLER STOPPLE FITTING GASKET WAS THE SOURCE OF THE LEAK.THE FITTING WAS REMOVED.
2017-09-29 08:50 | YES | NO | 19980074 | 1998-06-01 | 2330 | CHEVRON PIPELINE CO | YES | 1998-04-28 | 1054 | UT | WEBER | WEST HAVEN | NO |  | NO | 2500 SOUTH 1900 WEST OGDEN, UT |  | LINE PIPE | PIPE |  | 1948 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | GASOLINE | 1 | 200 | 100 | NO | NO | 8 | 0.25 | 45000 | WELDED |  | 1880 | 1180 | YES | 8 | 2160 | 9 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | JOHN R MOON | 8015397293 | CPL WAS PREPARING TO DO A PIPE REPLACEMENT IN THE AREA. DURING THE EXCAVATIONOF THE PIPELINE, AN UNKNOWN 3/4" VALVE WAS HIT BY THE BACKHOE BUCKET. THEPIPELINE WAS SHIPPING UNDER HIGH PRESSURE WHEN THE VALVE WAS BROKEN OFF. THEADJOINING HIGHWAY WAS IMMEDIATELY SHUT DOWN AND BUSINESSES IN A 300-YARD AREAWERE EVACUATED.
2017-09-29 08:50 | YES | NO | 19980075 | 1998-06-09 | 15851 | PRIDE REFINING INC | NO | 1998-05-13 | 1010 | TX |  | CALLAHAN | NO |  | NO | 6 MILES NORTH OF BAIRD, TX ON HWY 283 TURN EAST APPROXIMATELY 4 MILES |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10497.3357 | 21177.3662 | CRUDE OIL | 1 | 1470 | 370 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 828 | 100 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | AIR PATROL & PL SIGNS | NO | NO | JOHN T MACON | 9156748231 | AT APPROXIMATELY ON 5/13/98 WE RECEIVED A CALL TO OUR 24 HOUR MANNED NUMBERTHAT OUR LINE HAD BEEN HIT AND OIL WAS LEAKING OUT. WE IMMEDIATELY SHUT OURLINES DOWN AND DISPATCHED CREWS TO THE LEAK SITE. VALVES WERE CLOSED ON BOTHSIDES OF LEAK. UPON ARRIVING IT WAS DISCOVERED THAT WHILE DIGGING POST HOLESWITH A DRILLING MACHINE OUR LINE WAS STRUCK RESULTING IN APPROXIMATELY 11/2-2" HOLE IN OUR LINE. A CONTAINMENT DITCH WAS DUG AND AREA WAS SECURED.AT 8:30 PM LINE WAS THEN ABLE TO BE CLAMPED. LEAK #436649.
2017-09-29 08:50 | YES | NO | 19980076 | 1998-06-11 | 18273 | SHELL PIPELINE CORP | NO | 1998-05-07 | 1015 | MI |  | KALKASKA | NO |  | NO | MICHIGAN CRUDE PIPELINE, MANISTEE 12" (DORMAN RD & US 131) |  | LINE PIPE | PIPE |  | 1973 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 80479.5737 | 162359.8072 | CRUDE OIL | 1 | 75 | 35 | NO | NO | 12.75 | 0.25 | 52000 | WELDED |  | 1400 | 768 | YES | 24 | 1900 | 0 | 73 | INTERNAL | Null | YES | OTHER | BACTERIAL | NO DATA |  | Null | NO DATA |  | Null | Null | D F SHEAFF | 7132414381 | THE PIPELINE STREAM WAS REROUTED TO CONTINGENCY STORAGE AT JUNCTION STATIONFROM LEWISTON TANKAGE. A VALVE AT JUNCTION STATION WAS INADVERTENTLY CLOSED.THIS PRESSURED UP THE MAIN LINE TO APPROXIMATELY 768 PSI, CAUSING THEFAILURE. THE OPERATING PRESSURE WAS WELL BELOW THE MOP OF 1400 AT THE TIME OFTHE RELEASE.
2017-09-29 08:50 | NO | NO | 19980077 | 1998-06-11 | 18273 | SHELL PIPELINE CORP | NO | 1998-05-07 | 900 | MI | KALKASKA |  | NO |  | NO | MICHIGAN CRUDE PIPE LINE SYSTEM - MAINSTEE 12-INCH (WOOD RD & US 131) |  | LINE PIPE | PIPE |  | 1973 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 48987.5666 | 98827.7087 | CRUDE OIL | 1 | 28 | 20 | NO | NO | 12.75 | 0.25 | 52000 | NO DATA |  | 1440 | 768 | YES | 24 | 1900 | 1 | 73 | INTERNAL | Null | YES | OTHER | BACTERIAL | NO DATA |  | Null | NO DATA |  | Null | Null | D F SHEAFF | 7132414381 | FAILURE. THE OPERATING PRESSURE WAS WELL BELOW THE MOP OF 1400 PSI AT THETIME OF THE RELEASE.
2017-09-29 08:50 | YES | NO | 19980078 | 1998-06-11 | 4805 | EXPLORER PIPELINE CO | YES | 1998-05-12 | 1407 | OK | HUGHES |  | NO |  | NO | 2 MILES WEST & 1 MILE SOUTH OF INTERSECTION OF STATE HIGHWAYS 270 & 75, APPROXIMATELY 6 MILES EAST OF HOLDENVILLE, OK. SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1970 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 209946.714 | 423547.323 | JET FUEL | 3 | 5893 | 5565 | NO | NO | 28 | 0.28 | 52000 | WELDED |  | 751 | 773 | YES | 24 | 955 | 2 | 71 | NO DATA | Null | Null | NO DATA |  | OTHER | SOURCE UNKNOWN | Null | NO DATA |  | Null | Null | R E SANDS | 9184935106 | AT 1407 HOURS MAY 12, 1998 A MALFUNCTION OF A RTU AT MP 493.1 REMOTECONTROLLED BLOCK VALVE SITE CAUSED THE BLOCK VALVE TO CLOSE ON EXPLORER'S 28"OPERATING PIPELINE. THE CENTRAL CONTROL TECHNICIANS AT EXPLORER'S PIPELINECONTROL CENTER IN TULSA, OKLAHOMA INTIATED AN EMERGENCY SHUTDOWN AND ISOLATIONOF THE 28" SYSTEM FROM PT. ARTHUR, TEXAS TO GLENPOOL, OKLAHOMA. AN INDIVIDUALNEAR THE LEAK SITE CALLED TO REPORT THE LEAK AT 1410 HOURS. THE PRESSURESRESULTING FROM THE CLOSURE CAUSED THE 28" PIPE TO RUPTURE APPROXIMATELY 0.8MILE UPSTREAM (MP 455.8) OF HOLDENVILLE BOOSTER STATION. EXPLORER'S EMERGENCYRESPONSE TEAM WAS ACTIVATED. A HELICOPTER WAS DISPATCHED TO FLY COMPANYPERSONNEL TO THE RELEASE SITE. COMPANY EMPLOYEES FROM THE GLENPOOL, OKLAHOMAAREA OFFICE RESPONDED WITH SPILL CONTAINMENT BOOMS AND CLEANUP EQUIPMENT.EXPLORER'S SPILL RESPONSE AND MAINTENANCE CONTRACTORS WERE ALSO NOTIFIED TORESPOND WITH PERSONNEL, SPILL RESPONSE EQUIPMENT, AND EXCAVATION/EARTH MOVINGEQUIPMENT. THE JET FUEL WAS CONTAINED ON A LARGE POND SOUTH OF THE LEAKSITE. VACUUM TRUCKS AND TANK TRUCKS WERE DISPATCHED TO THE SITE TO BEGINRECOVERY OF JET FUEL AND TRANSPORT IT TO EXPLORER'S GLENPOOL FACILITY.EXCAVATION OF THE PIPE REVEALED A 47 INCH LONGITUDINAL TEAR IN THE PIPE BODYAT AN EXTERNAL GOUGE AREA. IT APPEARS THE EXTERNAL DAMAGE MAY HAVE OCCURREDDURING ORIGINAL CONSTRUCTION. A METALLURGICAL ANALYSIS OF THE FAILED SECTIONIS IN PROGRESS. MR. LARRY ATWELL, P.E. WITH THE SOUTHWEST REGION, OFFICE OFPIPELINE SAFETY, ARRIVED TO INVESTIGATE THE ACCIDENT AT 1600 HOURS, MAY 13,1998. A TEN FOOT SECTION OF THE 28" PIPE WAS REMOVED AND REPLACED. THEPIPELINE WAS SLOWLY REFILLED AND PRESSURED TESTED FOR 30 MINUTES PRIOR TORESUMING NORMAL OPERATIONS ON MAY 14, 1997. CLEANUP OF THE AREA IS NEARCOMPLETION.
2017-09-29 08:50 | YES | NO | 19980079 | 1998-06-11 | 18162 | SEAWAY PIPELINE INC | YES | 1998-05-24 | 2315 | TX | HARRIS |  | NO |  | NO | 901 CLINTON DRIVE, GALENA PARK, TEXAS EZEKIAL THOMAS SURVEY A-73, HARRIS COUNTY, TX. LATTITUDE N 29 44' 01.6', LONGITUDE W 95 13' 38" |  | PUMPING STATION | PUMP |  | 1991 | OTHER | MECHANICAL FATIGUE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 62984.0142 | 127064.1969 | GASOLINE | 1 | 25 | 5 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MIKE A SCHMIDT | 9182232957 | AT 2315 HOURS ON MAY 24, 1998 SEAWAY PIPELINE EXPERIENCE A PETROLEUM PRODUCTSSPILL OF #2 FUEL OIL AND UNLEADED GASOLINE AT THE GALENA PARK PUMP STATION,LOCATED AT 901 CLINTON DRIVE, GALENA PARK, TX. THE EXTENT OF THE SPILL WASCONFINED ENTIRELY TO COMPANY PROPERTY. ARCO PIPE LINE COMPANY IS THE OPERATOROF SEAWAY PIPELINE, WHICH EXTENDS FROM GALENA PARK, TX TO CUSHING, OKLAHOMA.THERE WERE NO INJURIES, FIRES, OR EXPLOSION RESULTING FROM THIS INCIDENT ANDTHE RELEASED PRODUCT DID NOT REACH ANY WATERWAYS. AS A RESULT OF THEACTIVATION OF AN AUTOMATED DETECTION SYSTEM, COMPANY EMPLOYEES WERE DISPATCHEDTO THE GALENA PARK TANK FARM AND PUMP STATION FACILITY. THE SOURCE OF THERELEASE WAS IDENTIFIED AS A BROKEN 1/2 O.D. STAINLESS STEEL TUBING ON THENUMBER THREE PUMP UNIT, WHICH WAS IN OPERATION AT THE TIME OF THE INCIDENT.THE FAILED TUBING IS A COMPONENT OF THE ANCILLARY PIPING WHICH FACILITIESPRODUCT FLOW THROUGH THE UNIT'S SEAL FLUSH SYSTEM. IMMEDIATELY AFTERDISCOVERY OF THE RELEASE, THE PUMP UNIT WAS SHUT DOWN AND ISOLATED WHICHSTOPPED THE FLOW OF PRODUCT. EMERGENCY RESPONSE AND CLEANUP PERSONNEL WERECALLED IN THE SITE TO UNDERTAKE CONTAINMENT, CLEANUP AND REPAIR ACTIVITIES.APPROXIMATELY 90 CUBIC YARDS OF SOIL AND GRAVEL AFFECTED BY THE PRODUCTRELEASE. THIS AFFECTED MATERIAL HAS BEEN COLLECTED AND STAGED ON SITE INROLL-OF BINS UNTIL SUCH TIME THAT IT WILL BE SAMPLED FOR CHARACTERIZATION ANDPROPER DISPOSAL. CLEAN UP OF THE SPILL IS BEING COORDINATED BYREPRESENTATIVES OF APL'S ENVIRONMENTAL HEALTH, AND SAFETY GROUP, WITHASSISTANCE FROM GARPER ENVIRONMENTAL SERVICES.
2017-09-29 08:50 | YES | NO | 19980080 | 1998-06-11 | 30072 | EXXON CO USA - SANTA YNEZ UNIT | NO | 1998-05-18 | 1415 | CA |  | MARTINEZ | NO |  | NO | N 38" 01.046" W 122 05.830" WEST SIDE OF INTERSTATE 680 UNDERCROSSING ADJACENT TO MOUNTAIN VIEW SANITARY DISTRICT TREATING PLANT |  | LINE PIPE | PIPE |  | 1968 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 104973.357 | 211773.6615 | CRUDE OIL | 1 | 16 | 16 | NO | NO | 20 | 0.28 | 52000 | WELDED |  | 335 | 28 | YES | 8 | 420 | 7 | 97 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | LAUREN K BIRD | 7077457570 | EMPLOYEES OF THE MOUNTAIN VIEW SANITARY DISTRICT SAW OIL IN THE SOIL BY ANACCESS ROAD. THEY PHONED THE EXXON EMERGENCY NUMBER ON THE PIPELINE MARKER.EXXON EMPLOYEES RESPONDED IMMEDIATELY AND ISOLATED THE SHORE SEGMENT OF PIPE(125 FEET) USING LINE VALVES. THE LINE WAS REMOVED FROM SERVICE,NOTIFICATIONS MADE AND CLEANUP OPERATIONS STARTED. IT WAS DECIDED TO REPLACETHE ENTIRE SEGMENT OF LINE BETWEEN LINE VALVES. THE LEAK WAS DUE TO SEPARTIONOF THE PROTECTIVE COATING AND GENERALIZED EXTERNAL CORROSION.
2017-09-29 08:50 | YES | NO | 19980081 | 1998-06-11 | 18162 | SEAWAY PIPELINE INC | YES | 1998-05-20 | 800 | OK | POTTAWATOMIE |  | NO |  | NO | FROM THE TOWN OF PURCELL, OKLAHOMA 14 MILES EAST IN SECTION 8. TOWNSHIP 6N, RANGE 2E. LATTITUDE N35 00' 51.9 LONGITUDE W97 08' 32.6' |  | PUMPING STATION | PUMP |  | 1993 | OTHER | MECHANICAL FATIGUE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 279928.952 | 564729.764 | GASOLINE | 1 | 600 | 250 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MIKE A SCHMIDT | 9182232957 | AT 0845 ON MAY 20,1998 ARCO PIPE LINE COMPANY (APL) MADE A TELEPHONIC REPORTTO THE NRC (REPORT NO. 437732) OF A #2-FUEL OIL SPILL AT SEAWAY PIPELINECOMPANY'S PURCELL STATION, LOCATED APPROXIMATELY 13 MILES EAST OF PURCELL,OKLAHOMA ON SR-39. APL IS THE OPERATOR OF SEAWAY PIPELINE, WHICH EXTENDS FROMGALENA PARK, TEXAS, TO CUSHING OKLAHOMA. AT APPROXIMATELY 0800 ON MAY 20,1998, A LEAK WAS DISCOVERED BY A COMPANY EMPLOYEE PERFORMING A ROUTINE STATIONINSPECTION. THE SOURCE OF THE RELEASE WAS IDENTIFIED AS A BROKEN 1/2 INCH O.D.STAINLESS TUBING ON THE NUMBER TWO PUMP UNIT, WHICH WAS IN OPERATION AT THETIME OF THE INCIDENT. THE FAILED TUBING IS A COMPONENT OF THE ANCILLARYPIPING WHICH FACILITATES PRODUCT FLOWN THROUGH THE UNITS' BEARING OIL COOLINGSYSTEM. IMMEDIATELY AFTER DISCOVERY OF THE RELEASE, THE PUMP UNIT WAS SHUTDOWN AND ISOLATED, STOPPING THE FLOW OF PRODUCT, AND EMERGENCY RESPONSE ANDCLEANUP PERSONNEL WERE CALLED TO THE SITE TO UNDERTAKE CONTAINMENT, CLEANUPAND REPAIR ACTIVITIES. ALTHOUGH NO WATERWAYS WERE AFFECTED, THE AREA AFFECTEDBY THE RELEASE INCLUDED APPROXIMATELY 1/4 MILE OF A DRY CREEK, LOCATED ONPRIVATE PROPERTY TO THE SOUTH OF THE SEAWAY FACILITY. METERED VOLUMES INDICATEA TOTAL RELEASE VOLUME OF APPROXIMATELY 600 BARRELS OF #2 FUEL OIL.APPROXIMATELY 250 BARRELS OF LIQUID HAS BEEN RECOVERED FROM THE RELEASE SITEAND TRANSPORTED TOT ANOTHER COMPANY FACILITY FOR RE-INJECTION INTO THESYSTEM. FUEL OIL AFFECTED SOIL WAS REMOVED AND STOCKPILED ON SHEET PLASTICFOR FUTURE REMEDIATION. CLEAN UP OF THE SPILL SITE IS BEING COORDINATED BYREPRESENTATIVES OF APL'S ENVIRONMENTAL, HEALTH AND SAFETY GROUP, WITHASSISTANCE FROM GARNER ENVIRONMENTAL SERVICES.
2017-09-29 08:50 | YES | NO | 19980082 | 1998-06-09 | 25133 | TEXACO TRADING & TRANSPORTATION INC | Null | 1998-05-18 | 540 | CA | SAN JOAQUIN |  | NO |  | NO |  |  | PUMPING STATION | OTHER | INSULATING FLANGE GASKET | 1989 | OTHER | INSULATING FLANGE GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 24493.7833 | 49413.8544 | CRUDE OIL | 1 | 960 | 860 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PAUL W SMITH | 8053282358 | INSULATING FLANGE GASKET FAILED.
2017-09-29 08:50 | YES | NO | 19980083 | 1998-06-12 | 12626 | MOBIL PIPELINE CO - EMPIRE | YES | 1998-05-15 | 845 | TX | WINKLER |  | NO |  | NO | MOBIL PIPE LINE COMPANY HALLEY STATION, APPROX 8 MILES SOUTH OF KERMIT, TEXAS |  | TANK FARM | PIPE |  | 1940 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 1 | 130 | 105 | NO | NO | 8 | 0.25 | 35000 | WELDED |  | 35 | 20 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D G SCOTT | 2146585914 | LEAK OCCURRED ON 8" FILL LINE TO TANK #2315. OIL CONTAINED INSIDE TANKFIREWALL DIKE. PERMANENT REPAIRS MADE. OILY SOIL WAS BLENDED TO LESS THAN1%. LINE WAS TAKEN OUT OF SERVICE.
2017-09-29 08:50 | YES | NO | 19980084 | 1998-05-19 | 31128 | STOLTHAVEN PERTH AMBOY INC | NO | 1998-04-20 | 1553 | NJ | MIDDLESEX | WOODBRIDGE | NO |  | NO | WEST OF STATE STREET IN THE SEWAREN SECTION OF WOODBRIDGE, NJ AND WEST OF THE CONRAIL RAIL LINE RUNNING PARALLEL TO STATE ST. THE PIPELINE LEAK IS APPROX 300 |  | LINE PIPE | PIPE |  | 1982 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 349911.1901 | 705912.205 | GASOLINE | 1 | 184 | 53 | NO | NO | 12.75 | 0.33 | 1806 | WELDED |  | 360 | 60 | YES | 25 | 1812 | 2 | 82 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A BUCE | 7328261144 | ACCIDENT DISCOVERED ON APRIL 20, 1998, WHEN IT OCCURRED IS UNCLEAR. ACCIDENTREPORTED TO NJDEP ON 1553.
2017-09-29 08:50 | YES | NO | 19980085 | 1998-05-06 | 10318 | KOCH REFINING CO | NO | 1998-02-11 | 1800 | TX | FALLS |  | NO |  | NO | EAST OF TEMPLE FM 438 AND BOTTOM ROAD |  | LINE PIPE | PIPE |  | 1984 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 174955.595 | 352956.1025 | DIESEL FUEL | 3 | 100 | 81 | NO | NO | 4.5 | 0.14 | 2193 | WELDED |  | 1440 | 130 | YES | 8 | 2075 | 5 | 84 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | NO | NO | TIM LARSEN | 2547565442 | WE MET WITH SAUNDERS CONSTRUCTION ON 1-13-98 WHILE THE CROSSED OUR CHAPARRALPIPELINE. OUR REPRESENTATIVE LEFT HIS BUSINESS CARD WITH SHELBY SAUNDERS TOGIVE HIM A CONTACT NUMBER BECAUSE WE HAVE FOUR PIPELINES IN THE AREA. HE SAIDHE WOULD CALL IF HE SAW ANY MORE KOCH RIGHT OF WAY SIGNS. HE DID SEE OURSOUTHWEST PIPELINE SIGNS, BUT ASSUMED OUR PIPELINE RAN IN A STRAIGHT LINE FROMONE SIGN TO THE OTHER. THE TENANT STOPPED BY WHILE THEY WERE AROUND WITH ABACKHOE AND WARNED THEM OF THE PIPELINE. HE DID NOT CALL US. OUR PIPELINE WASCOLLAPSED, WHILE THEY WERE LAYING FIBER OPTIC CABLE CASTING.
2017-09-29 08:50 | YES | NO | 19980086 | 1998-04-30 | 2337 | CHEVRON PIPELINE CO | YES | 1998-04-06 | 630 | TX | EASTLAND | RANGER | NO |  | NO | SEE ATTACHED MAP |  | PUMPING STATION | VALVE |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | CRUDE OIL | 1 | 993 | 555 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BILL JASPER | 2813635422 | THE LEAK OCCURRED WHEN A 3/4" NIPPLE, LOCATED AT THE BOTTOM OF A 10' STATIONMANIFOLD VALVE, BROKE OFF. THE NIPPLE HAD CORRODED INTERNALLY AND SHOWED NOOUTWARD SIGNS THAT A PROBLEM EXISTED. THIS THREADED NIPPLE WAS SCREWED INTOTHE BODY OF THE 10" MANIFOLD VALVE, WITH A 3/4" BALL VALVE ATTACHED TO IT.THE VALVE IS USED TO DRAIN THE PRODUCT FROM THE BODY OF THE 10" GATE VALVE.THE STATION WAS DOWN, SO THE LEAK OCCURRED UNDER VERY LOW PRESSURE (STATICHEAD PRESSURE). THE STATION WAS NOT MANNED AT THE TIME AND THE LEAK WAS NOTDISCOVERED UNTIL THE OPERATOR ARRIVED THE NEXT MORNING AT 0630. WE HAVEINCREASED OUR INITIAL COST ESTIMATES DUE TO SHALLOW ROCK FORMATIONS, WHICHPROLONGED EXCAVATION AND REMOVAL OF SOIL. HAVING ROCK IN THE MIXTURE WILLALSO INCREASE THE COST OF REMEDIATION.
2017-09-29 08:50 | YES | NO | 19980087 |  | 15774 | PORTAL PIPELINE CO | YES | 1998-04-21 | 820 | ND | WILLIAMS |  | NO |  | NO | PORTAL PIPELINE COMPANY'S TRENTON STATION LOCATED 7 MILES WEST AND 1 MILE SOUTH OF WILLISTON, ND |  | PUMPING STATION | PUMP |  | 1983 | OTHER | PUMP PACKING GLAND BLEW | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 1 | 175 | 170 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD C SANDAHL | 2187250102 | ON APRIL 21, 1998, AT 8:20 AM, THE WILLISTON GAUGER (WHILE DOING ROUTINEDUTIES AT TRENTON STATION) FOUND 175 BARRELS OF OIL ON THE GROUND SURROUNDINGTHE PUMP AND DRAINING OUT ON PORTAL'S PROPERTY. ALL OF THE OIL WAS CONTAINEDON PORTAL PROPERTY. THE OIL WAS RECOVERED AND THE AREA CLEANED UP. NEWPACKING WAS INSTALLED.
2017-09-29 08:50 | YES | YES | 19980088 | 1998-06-18 | 443 | AMOCO PIPELINE CO | YES | 1998-06-02 | 1300 | MO | NODAWAY | BURLINGTON JUNCTION | NO |  | NO | 3 MILES WEST OF BURLINGTON JUNCTION, MO ON HWY 136, 3 1/2 MILES NORTH ON COUNTY RD. YY AS ROAD TURNS NORTH CONTINUE EAST ON GRAVEL ROAD TO LEAK SITE. |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 12000000 | 8397868.5613 | 16941892.9206 | GASOLINE | 1 | 100 | 10 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1648 | 345 | YES | 24 | 1890 | 1 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MIKE BROZOVICH | 8162523357 | TOWNSHIP ROAD GRADER WAS GRADING A DIRT ROAD, IN VERY RURAL AREA. THE ROAD ISONE LANE DIRT WITH NO GRAVEL OR ROAD BASE. EACH CONSECUTIVE GRADING PLUSNATURAL EROSION FROM RAIN WIND AND TRAFFIC CAUSED THE COVER TO BE REMOVED FROMTHE PIPELINE OVER TIME. AS THE OPERATOR WAS GRADING AND PULLING SIDES OF ROADTO CENTER OF ROAD TO CREATE A CROWN FOR RUNOFF, END OF GRADER BLADE STRUCKPIPELINE CAUSING A 6" TO 8" PUNCTURE IN THE TOP QUARTER OF THE LINE. THISCAUSED THE DISCHARGE OF GASOLINE INTO THE ROADWAY AND DITCH. ROAD GRADEROPERATOR SUFFERED A BROKEN NOSE DURING THE INCIDENT.
2017-09-29 08:50 | YES | NO | 19980089 | 1998-06-19 | 2371 | CINIZA PIPELINE INC | NO | 1998-05-28 | 830 | NM | SAN JUAN |  | NO |  | YES | CINIZA'S BISTI STATION, SEC 17, T 26N, R12W. 10 MILES WEST OF JUNCTION OF COUNTY ROAD 7100 AND HIGHWAY 44 |  | PUMPING STATION | PIPE |  | 1978 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 9152 | 6404.7744 | 12921.017 | CRUDE OIL | 1 | 187 | 91 | NO | NO | 12 | 0.25 | 42000 | WELDED |  | 375 | 45 | YES | 24 | 410 | 5 | 78 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY ARMENTA | 5056328006 | THE LEAK WAS CAUSED BY INTERNAL CORROSION ON THE BOTTOM OF A 12" TANK FILLLINE. APPROXIMATELY 187 BARRELS OF OIL LEAKED INTO THE BERMED AREA. 91BARRELS WERE RECOVERED BY THE TRUCK. THE STAINED SOIL WAS TAKEN TO THELANDFARM.
2017-09-29 08:50 | YES | NO | 19980090 | 1998-06-16 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1998-05-21 | 1100 | PA | BERKS |  | NO |  | NO | SEE ATTACHED DRAWING NUMBER 11800-A |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 102000 | 71381.8828 | 144006.0898 | GASOLINE | 1 | 1 | 0 | NO | NO | 24 | 0.28 | 1220 | WELDED |  | 850 | 571 | YES | 24 | 1069 | 5 | 94 | NO DATA | Null | Null | NO DATA |  | OTHER | STRESS CONCENTRATOR/ROCK | Null | ONE CALL |  | Null | Null | CARL A OSTACH | 6107704495 | CUMRU TOWNSHIP, BERKS COUNTY PENNSYLVANIA, CALLED BUCKEYE'S MACUNGIE CONTROLCENTER AND REPORTED A SMELL OF PETROLEUM PRODUCT IN THE AREA OF THE 24' LAURELPIPELINE A THE 6 O'CLOCK POSITION. A REPAIR SLEEVE WAS INSTALLED AND THEPIPELINE WAS RESTARTED ON MAY 22, 1998, AT APPROXIMATELY 1000 HOURS, WITH THEMAXIMUM OPERATIONG PRESSURE REDUCED TO 80% OF NORMAL MAXIMUM OPERATINGPRESSURE. PERMANENT REPAIRS WILL BE COMPLETED THIS SUMMER. ALL APPLICABLEAGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE PERFORMED UNDERSUPERVISION OF THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL PROTECTION AND THEPENNSYLVANIA FISH AND BOAT COMMISSION.
2017-09-29 08:50 | YES | NO | 19980091 | 1998-06-29 | 10012 | KANEB PIPELINE CO | YES | 1998-05-28 | 1751 | CO | DOUGLAS |  | NO |  | NO | N 1/2, SECTION 12, RANGE 66 WEST, TOWNSHIP 8 SOUTH, DOUGLAS COUNTY, COLORADO. SEE ENCLOSED MAP |  | LINE PIPE | NO DATA |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 209946.714 | 423547.323 | OIL AND GASOLINE | 3 | 1057 | 35 | NO | NO | 6 | 0.19 | 42000 | WELDED |  | 1440 | 1100 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | NO DATA |  | Null | Null | LEROY ANDERSON | 3162621408 | THE PIPELINE FAILED AT APPROXIMATELY 17:51 MDT. KANEB'S CONTROL CENTERPERSONNEL WERE ABLE TO SHUT DOWN PUMPING OPERATIONS WITHIN APPROXIMATELY 1MINUTE 15 SECONDS. KANEB WAS NOTIFIED AT APPROXIMATELY 18:00 MDT BY THEDOUGLAS COUNTY SHERIFF'S DEPARTMENT THAT THE LOCATION OF THE FAILURE WASADJACENT TO THE RUSSELLVILLE ROAD, APPROXIMATELY 4 MILES SOUTHEAST OFFRANKTOWN, COLORADO. KANEB PERSONNEL BASED IN DUPONT, COLORADO WERE MOBILIZEDOVER THE COURSE OF THE FOLLOWING 3O MINUTES. KANEB ALSO MOBILIZED 2 EMERGENCYCONTRACTORS TO ASSIST WITH THE EMERGENCY RESPONSE ACTIVITIES. KANEB ALSOMOBILIZED COLORADO GROUNDWATER RESOURCES SERVICES, AN ENVIRONMENTAL CONSULTINGFIRM, TO OVERSEE AND DIRECT THE RESPONSE AND REMEDIATION EFFORTS. TESTPERFORMED BY METALLURGICAL CONSULTANTS, INC OF HOUSTON, TEXAS HAVE ESTABLISHEDTHE PIPELINE FAILED DUE TO EXTERNAL DAMAGE. THE DAMAGE WAS THE RESULT OF THEA TELEPHONE CALBE INSTALLATION A NUMBER OF YEARS AGO. OUR INVESTIGATIONCONTINUES TO DETERMINE THE AGE OF THE DAMAGE. SOIL AND GROUND WATERREMEDIATION EFFORTS ARE UNDERWAY AND ARE LIKELY TO CONTINUE FOR THEFORESEEABLE FUTURE.
2017-09-29 08:50 | YES | NO | 19980092 | 1998-06-26 | 22610 | WILLIAMS PIPELINE CO | Null | 1998-05-16 | 1330 | KS | MONTGOMERY |  | NO |  | NO | RELEASE OCCURRED AT WPL PUMP STATION LOCATED IN SECTION 36 TOWNSHIP 34 SOUTH - RANGE 16 EAST |  | PUMPING STATION | OTHER | FLANGE ON MANIFOLD | 1997 | OTHER | INSUFFICIENT CLAMPING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13996.4476 | 28236.4882 | FUEL OIL | 3 | 50 | 50 | NO | NO | 12 | 0 | 0 | FLANGED |  | 0 | 90 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH L LAYBARGER | 9185735774 | THE PUMP STATION IS ON PROPERTY LEASED FROM AND ADJACENT TO FARMLANDINDUSTRIES COFFEYVILLE, KANSAS REFINERY. FARMLAND HAD RECENTLY INSTALLED ANEW 12' PIPELINE FROM ITS TANKS UP TO AND TYING INTO THE MANIFOLD AT THEWILLIAMS STATION. AT 13:30 FARMLAND EMPLOYEES DETECTED PRODUCT LEAKING AT THEFLANGE CONNECTION AND NOTIFIED THE WPL DISPATCH CENTER IN TULSA. AT 13:45OPERATING EMPLOYEES WERE CALLED TO THE SITE. THE SUPERINTENDENT AND CREWARRIVED AT THE SCENE AT 15:00 WHERE IT WAS DISCOVERED THE PRODUCT WASPOOLING. THE LINE WAS SHUTDOWN AND A VACCUM TRUCK ORDERED TO THE SCENE. THEVACCUM TRUCK ARRIVED AT 15:35 AND BEGAN RECOVERING PRODUCT. THE COORDINATOROF OPERATIONS ARRIVED AT 17:00. IT WAS DETERMINED THAT THE LEAK OCCURREDWHERE THE 12' GATE VALVE ATTACHED TO THE MANIFOLD HEADER. THE CAUSE WASTHOUGHT TO BE EITHER A LEAKING GASKET OR IMPROPER ALIGNMENT OF THE LINE PIPEAND VALVE TO THE HEADER BY FARMLAND'S CONTRACTOR. REPAIR WAS MADE BYINSTALLING A NEW GASKET AND RECONNECTING THE VALVE FLANGE TO THE HEADER.PRODUCT RECOVERY HAD BEEN COMPLETED WITH THE RECOVERY DATE IN EXCESS OF 50BBL. CONTAMINANTED SOIL WAS REMOVED TO ANOTHER LOCATION WHERE IT WAS SPREADAND AERATED IN ACCORDANCE WITH THE KDHE PRACTICES. SAND WAS PLACED IN THEEXCAVATED AREAS.
2017-09-29 08:50 | YES | NO | 19980093 | 1998-06-29 | 443 | AMOCO PIPELINE CO | Null | 1998-06-09 | 1500 | OK | PAYNE |  | NO |  | NO | SW 1/4 OF SW 1/4, SECTION 12, R17N, T5E 2.5 MILES SOUTH OF OKLAHOMA HIGHWAY 33 ON HARMONY ROAD, THEN 1/8 MILE EAST ON ESECO ROAD. TANK 1372 |  | TANK FARM | TANK |  | 1923 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 2000 | 1900 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TERRY L HUTSON | 9182231101 | AUTOMATIC TANK GAUGE HUNG UP AND WAS NOT ACCURATELY TRACKING INCREASING LEVELIN TANK. ESTIMATED FILL TIME WAS OFF, CAUSING TANK TO OVERFLOW INTO DIKEDAREA.
2017-09-29 08:50 | YES | NO | 19980095 |  | 18214 | THE SHAMROCK PIPE LINE CORP | NO | 1998-05-14 | 1100 | TX | HUTCHINSON | PHILLIPS | NO |  | NO | FROM BORGER, TEXAS TAKEY HWY 119 NORT 1 MI TO PHILLIPS TEXAS. TURN RIGHT AND FOLLOW BLACKTOP ST 3/4 MI EAST, THEN PROCEED ON GRAVELED ROAD 1/4 MI N OF DIXON |  | NO DATA | PIPE |  | 1979 | OTHER | MALFUNCTION OF MIXER UNIT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9212 | 6446.7638 | 13005.7265 | CRUDE OIL | 1 | 32903 | 32606 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BILL THOMPSON | 2105924692 | AT APPROXIMATELY 1100 HOURS ON MAY 14, 1998, DURING A MAINTENANCE PROCEDURE ONTHE TANK MIXER CONNECTED TO TANK 80M-1, THERE WAS A COMPLETE FAILURE OF THEMIXER SEAL WHICH RESULTED IN SPILLING THE CONTENTS OF THE TANK INTO THE DIKECONTAINMENT AREA. IGNITION SOURCES WERE ELIMINATED, EMERGENCY RESPONSENOTIFICATIONS WERE MADE, AND RECOVERED ACTIVITIES WERE BEGUN IMMEDIATELY.AFTER RECOVERY OF THE SPILLED CRUDE OIL, THE MIXER HATCH WAS SEALED AND THETANK WAS RETURNED TO SERVICE. BIOREMEDIATION OF THE SPILL AREA HAS BEGUN ANDIS ONGOING.
2017-09-29 08:50 | YES | NO | 19980096 | 1998-06-30 | 2731 | CHEVRON PIPELINE CO | NO | 1998-05-28 | 1850 | TX | HARRIS | HOUSTON | NO |  | NO | 1/4 MILE EAST OF THE 8700 BLOCK OF 1-45 SOUTH, NEAR BERRY HILL STREET |  | LINE PIPE | PIPE |  | 1940 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1650000 | 1154706.9272 | 2329510.2766 | CRUDE OIL | 1 | 45 | 44 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 675 | 248 | YES | 8 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | PHILLIP C DEPRANG, W. M OUTLAW | 2813635422 | REPORTED BY RESIDENTS OF BERRY HILL STREET, CITY OF HOUSTON. CHEVRONOPERATIONS PERSONNEL ISOLATED THIS SEGMENT OF PIPELINE. BLOCKED IN MAINLINEAND JUMP OVER VALVES. CONTACTED CONSTRUCTION AND ENVIRONMENTAL CONTRACTOR.REPORTED TO CITY OF HOUSTON HAZMAT, FIRE DEPARTMENT (BOTH RESPONDED).NOTIFIED TEXAS RAILROAD COMMISSION, HOUSTON EPA (BOTH ARRIVED ON-SITE). 8INCH LINE WAS ALLOWED TO DRAIN DOWN, CUT-OUT BAD SEGMENT OF PIPE, INSTALLED A40 FOOT SECTION OF NEW PIPE. RECOVERED CRUDE OIL AND CONTAMINATED SOIL WASTRANSPORTED TO CHEVRON'S ALMEDA STATION TANK FARM FOR REMEDIATION. 45 BBLS OFCRUDE OIL WERE RECOVERED. USE 8 5/8 X .322 W. T. SEAMLESS PIPE AS REPLACEMENT.
2017-09-29 08:50 | YES | NO | 19980097 | 1998-06-30 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1998-06-09 | 615 | WY | PLATTE |  | NO |  | NO | CONOCO PIPE LINE CO GUERNSEY, WY. PUMP STATION AND TANK FARM, T 26N, R 65W, SECTION 17. |  | TANK FARM | PUMP |  | 1997 | OTHER | SEAL FAILURE ON MAINLINE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 3639.0764 | 7341.4869 | CRUDE OIL | 1 | 265 | 255 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W BEGGS | 3036494090 | SEAL FAILURE ON TANK 1158 MAINLINE BOOSTER PUMP. THE RESULT WAS RELEASE OF265 BBLS OF SOUR CRUDE INTO THE TANK DIKE. CRUDE WAS CONTAINED AND RECOVEREDFROM THE TANK DIKE. CONTAMINATED SOIL WAS REMOVED AND PUT ON PLASTIC,AWAITING PROPER DISPOSAL.
2017-09-29 08:50 | YES | NO | 19980098 | 1998-06-30 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1998-05-28 | 1128 | IL | COOK |  | NO |  | NO | WEST HALF OF SOUTHWEST QUARTER OF SECTION 32, TOWNSHIP 36 NORTH, RANGE 12 EAST OF THE THIRD PRINCIPAL MERIDIAN. |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 174955.595 | 352956.1025 | CRUDE OIL | 1 | 300 | 250 | NO | NO | 20 | 0.25 | 35000 | WELDED |  | 220 | 176 | YES | 24 | 808 | 11 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | RICHARD C SANDAHL | 2187250102 | A 2" FITTING LOCATED ON THE MOKENA 20" DELIVERY LINE WAS DAMAGED BY ACONTRACTOR DURING EXCAVATION FOR MEASUREMENT OF FARICATION FOR A TIE-IN,CAUSING CRUDE OIL RELEASE. THE CONTROL CENTER IMMEDIATELY SHUTDOWN THE LINEAND THE 20" VALVE AT THE MAINLINE TAKE OFF WAS CLOSED TO ISOLATE THE LINE.THE SITE WAS SECURED AND CRUDE RECOVERY WAS PERFORMED WITH VACCUM TRUCKS. THEEXCAVATION WAS THEN CLEANED TO ALLOW PERSONNEL TO PLACE A SPLIT REPAIR SLEEVEOVER THE DAMAGED AREA. SUBSEQUENTLY, SOIL WAS REMOVED AND TRANSPORTED TO ALANDFILL. AN EARTHEN BERM WAS CONSTRUCTED AROUND THE AREA TO CONTAIN ANYPRODUCT RUNOFF AND SORBENT BOOMS WERE PLACED IN A DITCH APPROXIMATELY 2,000'FROM THE SPILL SITE TO CONTAIN SMALL AMOUNTS OF CRUDE THAT SEEPED INTO ANUNDERGROUND DRAIN TILE SYSTEM THAT ORIGINATED NEAR THE SPILL SITE.
2017-09-29 08:50 | YES | NO | 19980099 |  | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1998-02-26 | 1100 | TX | LASALLA |  | NO |  | NO | ROBERTSON RANCH OFF OF STATE HIGHWAY 97 11 MILES EAST OF CATULLA TX |  | LINE PIPE | PIPE |  | 1938 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4198.9343 | 8470.9465 | CRUDE OIL | 1 | 367 | 171 | NO | NO | 6 | 0.19 | 500 | WELDED |  | 1200 | 500 | Null | 8 | 1500 | 5 | 91 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | REX J PROSSER | 7138777370 | EXTERNAL CORROSION ON THE PIPELINE CAUSING A RELEASE OF 367 BBLS OF CRUDEOIL. THE OIL FLOWED ALONG THE GROUND AND ENTERED A STOCK POND APPROX 300 FTFROM THE SPILL FIRE SITE. THE STOCK POND AND SPILL SITE WERE CLEANED UP. ALINE SECTION OF 6" PIPE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 19980100 | 1998-07-10 | 26145 | TOSCO CORP | NO | 1998-07-02 | 1115 | CA | KERN |  | NO |  | NO | D2A FOR PUMP STATION IS 117, THE INCIDENT WAS LOCATED AT THE SW CORNER OF SW 1/4 SECTION 10 TOWNSHIP 28 SOUTH, RANGE 20 EAST. |  | LINE PIPE | PIPE |  | 1994 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1399.6448 | 2823.6488 | CRUDE OIL | 3 | 55 | 50 | NO | NO | 6 | 0.25 | 0 | WELDED |  | 750 | 20 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENT J. PENNINGROTH | 8055477251 | AT 11:15 ON JULY 2, 1998 THE PUMP STATION MECHANIC OBSERVED A CRUDE OIL LEAKWITHIN THE FACILITY IN THE VICINITY OF THE E&B NATURAL RESOURCES GATHERINGLINE. ALL OPERATIONS WERE THEN SHUT DOWN. THE ESTIMATED VOLUME ON THE GROUNDAT THAT TIME WAS 10 BARRELS. THE COES, NRC AND 911 WERE NOTIFIED BY12:00. THE 6" DIAMETER GATHERING LINE IS OWNED AND OPERATED BY E&B NATURALRESOURCES OF BAKERSFIELD, CALIFORNIA. THE PIPELINE OWNER WAS NOTIFIED. TOSCOEMERGENCY RESPONSE PERSONNEL ARRIVED AT THE SITE WITHIN 1 HOUR TO ISOLATEAFFECTED SYSTEMS, ASSESS THE SPILL, AND IMPLEMENT CLEAN-UP MEASURES. BY 15:00HOURS THE LOCATION OF THE LEAK WAS FOUND IN THE 6" DIAMETER PIPE. A HOLIDAYIN THE X-TRU-COAT PROTECTIVE WRAP WAS FOUND THAT HAD HASTENED CORROSION ATTHAT POINT. A SECTION OF HALF SOLE WAS WELDED OVER THE CORRODED AREA AND THEPIPE WAS RETURNED TO SERVICE AT APPROXIMATELY 19:00 HOURS. APPROXIMATELY 50BARRELS OF CRUDE OIL WAS RECOVERED IN A VACUUM TRUCK AND TRANSPORTED T ANOTHERPUMP STATION. APPROXIMATELY 20 CUBIC YARDS OF SOIL IMPACTED BY THE RELEASEWAS STOCKPILED AT THE SITE FOR LATER DISPOSITION.
2017-09-29 08:50 | YES | NO | 19980101 | 1998-07-06 | 10318 | KOCH REFINING CO | NO | 1998-02-21 | 845 | TX | WEBB |  | NO |  | NO | 1.5 MILES NE OF OF MILTON, TX DOWN WELLHAVEN RD |  | LINE PIPE | OTHER | 4" TAP W/ VALVE OFF MAIN | 1926 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 559.8579 | 1129.4595 | CRUDE OIL | 1 | 200 | 135 | NO | NO | 4 | 0.25 | 0 | THREADED |  | 500 | 80 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | KOCH PIPELINE CONTROL CTR | NO | YES | JASON HILL | 5123947961 | WHILE EXCAVATNG MIRANDO DUVAL 8" PIPELINE TRACKHOE BUCKET SCRAPPED ACROSS 4"TAP WITH VALVE WHICH WAS THREADED INTO THE SIDE OF THE 8" MAINLINE. WHEN THISACTION OCCURRED THE 4" TAP BLEW OUT AT THE THREADS EXPOSING A 4" OPENING INTOTHE 8" LINE. LINE HAD BEEN EXPOSED AND LOCATED WHEN 4" TAP WAS HIT.
2017-09-29 08:50 | YES | NO | 19980102 | 1998-07-15 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1998-05-21 | 1315 | TX |  | PANOLA | NO |  | NO | EAST OF COUNTY ROAD 326, SOUTH OF STATE HIGHWAY 79 |  | LINE PIPE | OTHER | 1/2' NIPPLE ON PIPELINE |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 3849.0231 | 7765.0343 | DIESEL FUEL | 3 | 74 | 74 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | ERNEST P HAGAN | 7137593845 | AT APPROXIMATELY 0845 HOURS ON THE MORNING OF MAY 21, 1998, A TEPPCOMAINTENANCE CREW WAS INVOLVED IN DIGGING OUT A VALVE. THE BACKHOE OPERATOR,IN THE PROCESS OF CLEANING OUT THE EXCAVATION, STRUCK A 1/2' NIPPLE ON THEPIPELINE, RESULTING IN A RELEASE OF DIESEL FUEL. THE PIPELINE WAS NOTOPERATING AT THE TIME OF THE INCIDENT. BY APPROXIMATELY 1315 HOURS, PERSONNELON-SITE DETERMINED A QUANTITY OF GREATER THAN 50 BARRELS HAD BEEN RELEASED.TEPPCO MADE MANDATORY NOTIFICATION TO THE NATIONAL RESPONSE CENTER AT THISTIME. THE RELEASED PRODUCT HAD BEEN CONTAINED IN THE EXCAVATED AREA. SOILTESTING IS CURRENTLY BEING PERFORMED TO DETERMINE PROPER METHODS FOR ANYCONTAMINATED SOIL.
2017-09-29 08:50 | YES | NO | 19980103 | 1998-07-16 | 15774 | PORTAL PIPELINE CO | YES | 1998-06-23 | 1115 | MT | SHERIDAN |  | NO |  | NO | PORTAL PIPE LINE COMPANY'S RESERVE STATION, MT FROM RESERVE, MT - 1 MILE EAST ON COUNTY ROAD 258 THEN 1 MILE SOUTH ON HWY 16. |  | PUMPING STATION | PUMP |  | 1971 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 4898.7567 | 9882.7709 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD C SANDAHL | 2187250102 | THE CAUSE OF THE SPILL WAS AN ABOVE GROUND STORAGE TANK, WHICH WASINADVERTENTLY OVERFILLED WHEN COMMUNICATIONS BETWEEN THE STATION AND CONTROLCENTER WERE LOST DUE TO ELECTRICAL STORMS. ATTEMPTS TO LOCKOUT THE SHIPPERLACT UNITS AT THE SITE WERE UNSUCCESSFUL IN PREVENTING THE RECEIPT TANK FROMBEING OVER FILLED.
2017-09-29 08:50 | YES | NO | 19980104 | 1998-07-22 | 25133 | TEXACO TRADING & TRANSPORTATION INC | Null | 1998-06-06 | 235 | CA | ALAMEDA |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1989 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 279928.952 | 564729.764 | CRUDE OIL | 1 | 300 | 0 | NO | NO | 24 | 0.26 | 936 | WELDED |  | 936 | 0 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | PAUL W SMITH | 8053262358 | SPLIT IN PIPELINE.
2017-09-29 08:50 | YES | NO | 19980105 | 1998-08-17 | 10318 | KOCH REFINING CO | YES | 1998-05-10 | 1600 | WI |  | MCFARLAND | NO |  | NO | THIS OCCURRED INSIDE TERMINAL PROPERTY AT 4505 TERMINAL DRIVE |  | TANK FARM | TANK |  | 1989 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OIL AND GASOLINE | 1 | 60 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROY GENEVICH | 6514381261 | CHECK VALVES IN LINE FROM TRANSMIX TANK TO OIL WATER SEPARATOR FAILED ALLOWINGPRODUCT TO FLOW BACK INTO THE OWS CREATING PRODUCT TO OVERFILL THE OWS.PRODUCT THEN ESCAPED TO A RAINWATER DRAIN WHICH LED TO A CREEK.
2017-09-29 08:50 | YES | YES | 19980106 | 1998-07-28 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1998-07-14 | 1000 | TX | VICTORIA |  | NO |  | NO | THREE MILES NORTH EAST OF GAHLKE STATION ON STATE HIGHWAY 616 AND ABOUT 1/4 MILE SOUTH OF GARCITAS CREEK. |  | LINE PIPE | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 1 | 0 | 1 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | NATURAL GAS LIQUID | 2 | 1000 | 0 | YES | YES | 8.63 | 0.36 | 24000 | WELDED |  | 750 | 400 | YES | 8 | 968 | 1 | 92 | NO DATA | Null | Null | NO DATA |  | OTHER | DAMAGE BY 3RD PARTY | Null | OTHER | PIPELINE MARKERS/PUBLIC | NO | YES | REX J. PROSSER | 7138777370 | ON JULY 14, 1998 WORK CREWS FROM PATE AND PATE ENTERPRISES, INC. (GENERALON A 64 INCH FROM LAKE TEXANA (NEAR EDNA) TEXAS TO CORPUS CHRISTI, TEXAS. ANOPERATOR FOR PATE AND PATE WAS OPERATING A ROAD GRADER PERPENDICULAR TO THETHE PIPELINE ALONG A RANCH FENCE LINE. IT APPEARED THE OPERATOR WAS GRADING AROAD ALONG THE FENCE LINE. THE GENERAL AREA OF THE PIPELINE HAD BEENEXCAVATED AND RECOVERED AS PART OF THE 64 INCH WATERLINE PROJECT. PIPELINEMARKERS WERE WITHIN 12 FEET OF THE ACCIDENT LOCATION. PATE AND PATE FAILED TOCONTACT COASTAL STATES CRUDE GATHERING CO. CONCERNING THE ROAD GRADINGOPERATIONS ON JULY 14, 1998. HOWEVER, PRIOR TO THE AFOREMENTIONED EVENT PATEAND PATE HAD CONTACTED COASTAL STATES CRUDE GATHERING COMPANY REGARDING OTHERCONSTRUCTION ACTIVITIES ALONG OUR PIPELINE RIGHT OF WAY.
2017-09-29 08:50 | YES | NO | 19980109 | 1998-08-11 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1998-07-14 | 1715 | TX | JACKSON |  | NO |  | NO | 0.5 MILE NORTHWEST OF VANDERBILT, TEXAS ALONG HIGHWAY 234 AND 1000 YARDS WEST OF HIGHWAY 234 IN A CULTIVATED FIELD. |  | LINE PIPE | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 24000 | 16795.7371 | 33883.7858 | NATURAL GAS LIQUID |  | 1000 | 0 | NO | NO | 8.63 | 0.36 | 0 | WELDED |  | 750 | 300 | YES | 8 | 968 | 1 | 92 | NO DATA | Null | Null | NO DATA |  | OTHER | DAMAGE BY THIRD PARTY | Null | OTHER | PUBLIC EDUCATION | NO | YES | REX J. PROSSER | 7138777370 | LOADER CLEANING OUT OF A DRAINAGE DITCH THAT WAS LOCATED ON THE SOUTHWESTERNSTAKES. IT APPEARS THE OPERATOR STRUCK THE 8" LPG PIPELINE WITH A STEEL TOOTHON THE BUCKET OF THE FRONT END LOADER. THERE WAS A RELEASE OF LPG. PATEAND PATE AGAIN FAILED TO NOTIFY COASTAL STATES CRUDE GATHERING COMPANYCONCERNING THE SCOPE OF WORK BEING CONDUCTED NEAR THE 8" LPG PIPELINE ON JULY14, 1998.
2017-09-29 08:50 | YES | NO | 19980110 | 1998-07-29 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 1998-06-30 | 2100 | LA | ASCENSION | GONZALES | NO |  | NO | APPROXIMATELY 500 YARDS EAST OF HWY 935 AT A POINT ROUGHLY 1.5 MILES SOUTH OF HIGHWAY 44. LANDOWER ADDRESS: 42252 BAYOU NARCISSE RD (HWY 935) |  | LINE PIPE | PIPE |  | 1977 | OTHER | ARC BURN/METAL LURGICAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 59484.9023 | 120005.0749 | GASOLINE | 3 | 1 | 0 | NO | NO | 20 | 0.31 | 65000 | WELDED |  | 875 | 339 | YES | 24 | 1917 | 1 | 78 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G. L. WIELAND | 7132962426 | A STAIN WAS OBSERVED BY THE LANDOWNER ON THE GROUND OVER THE PIPELINE. UPONEXCAVATION, AN ANOMALY WAS FOUND AT THE 3:00 POSITION ON THE PIPE. THEANOMALY APPEARS TO BE DUE TO AN ARC BURN DURING CONSTRUCTION OF THE LINE.ASSOCIATED GALVANIC CELL CORROSION UNDER THE PIPE COATING AT THE ANOMALYRESULTED IN A PINHOLE LEAK OF AN ESTIMATED 1 BARREL OF GASOLINE.
2017-09-29 08:50 | YES | NO | 19980111 | 1998-08-04 | 22610 | WILLIAMS PIPELINE CO | YES | 1998-06-28 | 100 | OK | TULSA |  | NO |  | NO | EXPLORER TANK FARM OPERATED BY WILLIAMS PIPE LINE COMPANY AT ITS WEST TULSA TERMINAL, 2120 S 33RD WEST AVENUE, TULSA OK 74107 |  | TANK FARM | TANK |  | 1977 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 55279 | 38685.4813 | 78044.2416 | JET FUEL | 3 | 275 | 200 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | MICROBIOLOGICAL | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH L LYBARGER | 9185735774 | 1:00-THE LEAK WAS DISCOVERED BY STATION OPERATOR DURING A ROUTINE INSPECTIONOF THE TANK FARM. 1:15-VISUAL INSPECTION OF THE TANK (#1504) CONFIRMED THATTHE TANK WAS LEAKING JET FUEL. THE IMPACT AREA WAS APPROXIMATELY 20 FEET WIDEWITH 3 SMALL STREAMS OF FUEL RUNNING OUT TO LOWER GROUND. STATION MANAGER WASNOTIFIED AT HOME AND LEFT TO COME TO THE STATION. 1:45- STATION MANAGERARRIVED AT THE STATION AND INSPECTED THE LEAK SITE. 2:00 PIPELINE OPERATIONSCONTROL (DISPATCH) WAS CONTACTED AND REQUESTED THAT THE TANK BE EMPTIED ASSOON AS POSSIBLE. 2:15-REGIONAL DIRECTOR IN KANSAS CITY WAS INFORMED OF THELEAK. 2:20 OPERATIONS CONTROL INSTRUCTED STATION PERSONNEL TO BEGIN PUMPING50,000 BARRELS BATCH OF JP-8 TO THE #1 NORTH MAINLINE. 2:30-THE REGIONALENVIRONMENTAL ENGINEER WAS NOTIFIED OF THE LEAK AND GIVEN NECESSARYINFORMATION TO NOTIFY THE NRC AND OTHER REGULATORY AGENCIES. 2:58- REGIONALENVIRONMENTAL ENGINEER MADE TELEPHONIC NOTIFICATION. 3:00-STATIONCOORDINATOR OF OPERATIONS & MAINTENANCE CALLED IN TO ASSIST IN SUPERVISINGVACUUM TRUCK AND CONTRACTOR PERSONNEL. 4:00-REPRESENTATIVE OF THE OKLAHOMADEQ CALLED FOR A STATUS CHECK OF THE LEAK AND DETERMINED IT WASN'TSIGNIFICANT ENOUGH TO REQUIRE HIS PRESENCE. 4:45-VACUUM TRUCK ARRIVED ANDBEGAN RECOVERING PRODUCT. IT REMAINED UNTIL 1504 WAS EMPTY AND PRODUCTCEASED RUNNING OUT. 5:00-CONTRACTOR WAS CONTACTED AND INSTRUCTED TO PROVIDEEXCAVATION EQUIPMENT, INCLUDING A DUMP TRUCK AND PERSONNEL. 7:00-CONTRACTORCREW ARRIVED AND BEGAN REMEDIATION. A TRENCH 20 FEET LONG WAS EXCAVATEDNEAR THE TANK BASE AND LINED WITH VISQUEEN AND A 500 GALLON TANK STOCK TANKSET INSIDE THE TRENCH TO COLLECT THE PRODUCT STILL RUNNING INTO THE TRENCHIN ORDER TO MINIMIZE CONTACT OF THE PRODUCT WITH THE SOIL. 13:55-TANK 1207WAS EMPTIED AND TRANSFER OF PRODUCT FROM TANK 1504 INTO TANK 1207 WASSTARTED. JUNE 29, 1998 - 6:00-THE TRANSFER FROM TANK 1504 WAS SHUTDOWN ONLOW LEVEL SETTING AND THE SUMP PUMPS WERE STARTED TO REMOVE THE REMAININGFUEL FROM THE TANK'S SUMP AND FILL LINES. 10:00-TANK 1504 WAS COMPLETELYEMPTY OF PRODUCT. TANK 1504 HAS SUBSEQUENTLY BEEN CLEANED AND SAND-BLASTEDAT WHICH TIME INTERNAL CORROSION WAS DISCOVERED, AND IS CURRENTLY BEINGREPAIRED.
2017-09-29 08:50 | YES | NO | 19980112 | 1998-08-05 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 1998-07-09 | 639 | KS | SEDGWICK | WICHITA | NO |  | NO | 2360 EAST 37TH STREET NORTH WICHITA, KS 67219-3536 |  | TANK FARM | OTHER | RELIEF VALVE ON TANK | 1962 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10497.3357 | 21177.3662 | BUTANE | 2 | 2 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | EDWARD A. (BUZZ) FANT | 7138449526 | ON THURSDAY, JULY 9TH, AT 0639 HRS HOUSTON CONTROL CENTER RECEIVED AN ESDALARM INDICATING A PROBLEM AT OUR WICHITA KS FACILITY. THE CONTROL CENTERCONTACTED THE WICHITA FIRE DEPT AND COMPANY PERSONAL. A COMPANY TECHNICIANARRIVED ON SITE AT 0645 HRS. THERE WERE STORMS IN THE AREA AND IT APPEARSTHAT LIGHTING STRUCK A RELIEF VALVE ON AN ABOVE GROUND SPHERE (TANK #201B) ANDIGNITED VAPORS. THE FIRE DEPT ARRIVED ON SITE AT 0655 HRS. FIRE DEPARTMENTPERSONNEL EXTINGUISHED THE FIRE AT 0716 HRS UTLIZING A HAND HELD DRY CHEMICALFIRE EXTINGUISHER. DISCHAGE FROM THE TANK'S PRESSURE SAFETY VALVE (PSV)LASTED FOR 2 HOURS UNTIL THE PSV BLOCK VALVE WAS CLOSED. THE PRODUCT LOSSCOULD NOT BE DETECTED BY TANK GAUGING, THEREFORE THE AMOUNT OF COMMODITYINVOLVED IS ESTIMATED BASED ON "EYE WITNESSES" DESCPRITION OF THE SOUND OFESCAPING VAPORS. THE TANK PRESSURE WAS 22 PSIG AT THE TIME OF THE ACCIDENT.THE PILOT VALVE WAS SET TO BEGIN RELIEVING AT 38 PSIG WITH FULL OPEN AT 40PSIG. THE PRODUCT WAS REMOVED FROM THE TANK AND THE TANK WAS OUT OF SERVICEUNTIL THE PROPER REPAIRS AND CALIBRATION WAS PERFORMED ON THE DAMAGED RELIEFVALVE. A DAMAGED "O" RING WAS FOUND IN THE RELIEF VALVE. THE TANK WAS PLACEDBACK IN SERVICE ON 7-10-98.
2017-09-29 08:50 | YES | NO | 19980113 | 1998-08-05 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 1998-07-11 | 521 | IA | POLK | DES MOINES | NO |  | NO | 4401 VALDALIA ROAD, DES MOINES, IA |  | TANK FARM | VALVE |  | 1980 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 349.9112 | 705.9122 | BUTANE | 2 | 14 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A. "BUZZ" FANT | 7138449526 | ON SATURDAY JULY 11, AT 0521 HRS DURING NORMAL OPERATIONS, KINDER MORGANENERGY PARTNERS EXPERIENCED A RELEASE OF REFINERY GRADE BUTANE, A HVL AT OURDES MOINES IOWA STORAGE FACILITY. THE RELEASE WAS DUE TO A MALFUNCTION OF ALEVEL CONTROL VALVE ON A WATER KNOCKOUT TANK IN OUR DEHYDRATION SYSTEM. THEMALFUNCTION WAS CAUSED BY FILTER MATERIAL (A CLOTH LIKE SUBSTANCE) BEINGWEDGED INTO THE LEVEL CONTROL VALVE PREVENTING THE VALVE TO SEAT. THEMALFUNCTION OF THE CONTROL VALVE ALLOWED WATER AND BUTANE TO FLOW INTO THEACCUMULATOR SYSTEM OVER-FILLING THE UNDERGROUND ACCUMULATOR, ALLOWING BUTANETO ESCAPE TO THE ATMOSPHERE THROUGH THE UNDERGROUND ACCUMULATOR PUMP BASEGASKET AND EVAPORATION POND.
2017-09-29 08:50 | NO | NO | 19980114 | 1998-08-05 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | NO | 1998-07-07 | 900 | CA | PLACER | ROCKLIN | NO |  | NO | 6050 PACIFIC ST ROCKLIN, CA |  | TANK FARM | PIPE |  | 1961 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 51000 | 35690.9414 | 72003.0449 | DIESEL FUEL | 1 | 0 | 0 | NO | NO | 10 | 0.32 | 35000 | FLANGED |  | 275 | 26 | YES | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL PITTING | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A. "BUZZ" FANT | 7138449526 | ON TUESDAY, JULY 7, 1998 AT APPROXIMATELY 1000 HRS, DURING ROUTINE FACILITYROUNDS, EMPLOYEES OF KINDER MORGAN ENGERY PARTNERS' ROCKLIN TANK FARMDISCOVERED A "STAIN" IN THE BOOSTER PUMP AREA. THE LOCAL EMERGENCY PLAN WASACTIVATED AND ENVIRONMENTAL CLEAN UP CONTRACTORS WERE CALLED TO SITE.EXCAVATION TO DETERMINE SOURCE OF LEAK BEGAN AT 1400 HRS. AT APPROXIMATELY1940 HRS A LEAK WAS DISCOVERED ON THE BOTTOM OF THE PIPE, APPROXIMATELY 2 FTFROM A FLANGE.
2017-09-29 08:50 | YES | NO | 19980115 | 1998-08-21 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 1998-07-24 | 705 | CA | LOS ANGELES | CARSON | NO |  | NO | 20410 S WILMINGTON AVE CARSON, CA 90810 |  | TANK FARM | TANK |  | 1955 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 377100 | 263903.0195 | 532398.985 | TURBINE FUEL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A. "BUZZ" FANT | 7138449526 | ON FRIDAY JULY 24, 1998 AT APPROXIMATELY 0705 HRS, DURING ROUTINE FACILITYROUNDS, EMPLOYEES OF KINDER MORGAN ENERGY PARTNERS' WATSON STATION TANK FARMDISCOVERED 3 "STAINS", ALL APPROXIMATELY 1' X 3" AROUND TANK W-2 IN THEBREAKOUT TANK AREA. THE LOCAL EMERGENCY PLAN WAS ACTIVATED AND ENVIRONMENTALCLEAN-UP CONTRACTORS WERE CALLED TO SITE. A LEAK WAS DISCOVERED IN TANK W-2.
2017-09-29 08:50 | YES | NO | 19980116 | 1998-08-21 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 1998-07-22 | 915 | CA | LOS ANGELES | CARSON | NO |  | NO | 20410 S WILMINGTON AVE CARSON, CA 90810 |  | TANK FARM | TANK |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 627000 | 438788.6323 | 885213.9051 | GASOLINE | 1 | 0 | 150 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | EDWARD A. "BUZZ" FANT | 7138449526 | ON WEDNESDAY JULY 22, 1998 AT APPROXIMATELY 0905 HRS, DURING ROUTINE FACILITYROUNDS, EMPLOYEES OF KINDER MORGAN ENERGY PARTNERS' WATSON STATION FARMDISCOVERED A "STAIN" IN THE BREAKOUT TANK AREA ON THE NORTH SIDE OF TANK W-7.THE LOCAL EMERGENCY PLAN WAS ACTIVATED, TANK W-7 WAS EMPTIED AND ENVIRONMENTALCLEAN-UP CONTRACTORS WERE CALLED TO SITE. A LEAK WAS DISCOVERED IN TANK W-7.THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19980117 | 1998-08-31 | 31146 | EQUISTAR PIPELINE OPERATIONS | NO | 1998-07-21 | 115 | TX | NUECES |  | NO |  | NO | VALVE STATION 0, NEAR EQUISTAR CORPUS CHRISTI PLANT, 1501 MCKENZIE ROAD, CORPUS CHRISTI, TX |  | NO DATA | OTHER | ORIFICE FITTING | 1997 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 174955.595 | 352956.1025 | BENZENE/BENZOL | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICHARD ESKCHEN | 7138446915 | ON TUESDAY, JULY 21, 1998, THE CORPUS CHRISTI PLANT OPERATOR WAS MAKING HISMIDNIGHT ROUNDS. AT ABOUT 1:15 AM, HE SMELLED BENZENE WHILE DRIVING AROUNDTHE PIPELINE METER AT THE PIG TRAP AREA. HE CALLED HIS SUPERVISOR, WHO CAMEOUT TO ASSIST. THEY FOUND THE ORIFICE FITTING ON THE BENZENE PIPELINE METERLEAKING AND IMMEDIATELY BLOCKED THE METER IN. THERE WERE NO INJURIES.PRODUCTION WAS NOT IMPACTED BECAUSE THE METER WAS BLOCKED IN AND BYPASSED.HOWEVER, A SIGNIFICANT AMOUNT OF SOIL WAS CONTAMINATED WITH BENZENE RUN-OFFFROM THE LEAK.
2017-09-29 08:50 | YES | NO | 19980118 | 1998-08-31 | 18718 | SUN PIPE LINE CO | NO | 1998-08-17 | 1455 | OK | OKLAHOMA | OKLAHOMA | NO |  | NO | BETWEEN SANTA FE AND WESTER SECTION 16-13N-13W OKLAHOMA CITY, OKLAHOMA |  | LINE PIPE | VALVE |  |  | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2050 | 1434.6359 | 2894.24 | CRUDE OIL | 1 | 145 | 140 | Null | NO | 8 | 0.28 | 308 | WELDED |  | 500 | 160 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | EDITH F. COEN | 9185866942 | TRACKHOE OPERATOR WAS IN THE PROCESS OF EXCAVATING AN 8" LINE FOR REPLACEMENTWHEN HE HIT AN UNKNOWN 3" BURIED VALVE. THE 3" VALVE WAS INSTALLED ON THEPIPELINE AT AN ANGLE AND UPON IMPACT BROKE ALONG THE WELD ALLOWING OIL TOESCAPE FROM THE LINE.
2017-09-29 08:50 | YES | NO | 19980119 | 1998-08-28 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | NO | 1998-07-27 | 1000 | CA | ORANGE | IRVINE | NO |  | NO | 15000 CULVER DR AND RAILROAD TRACKS, IRVINE, CA |  | LINE PIPE | BOLTED FITTING |  | 1995 | OTHER | LEAKING STOPPLE TEE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | GASOLINE | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A. "BUZZ" FANT | 7138449526 | A HYDROCARBON SHEEN WAS DISCOVERED IN A STORM WATER SEWER SUMP IN IRVINE, CABY LOCAL OFFICIALS AND REPORTED TO KINDER MORGAN ENGERY. ON JULY 27, A CREWWAS DISPATCHED TO "POT HOLE" AND PHYSICALLY INSPECTS THE PIPELINE EVERY 50FEET FOR 1/4 MILE IN BOTH DIRECTIONS FROM THE STORM WATER SEWER SUMP. AT 0930HOURS CONTAMINATED SOIL WAS DISCOVERED AT A STOPPLE EXCAVATION SITE ONPIPELINE NUMBER LS 126. IT WAS DETERMINED THAT THE STOPPLE FLANGE GASKET WASLEAKING AT 1000 HOURS. THE PIPELINE WAS SHUTDOWN AND THE EMERGENCY PLAN WASACTIVATED AND ENVIRONMENTAL CLEAN-UP CONTRACTORS WERE CALLED TO THE SITE.
2017-09-29 08:50 | YES | NO | 19980120 | 1998-08-17 | 31147 | DYNEGY MIDSTREAM SERVICES INC | YES | 1998-08-06 | 1223 | LA | PLAQUEMINES |  | NO |  | NO | MARINE TERMINAL MASTER MANIFOLD AREA |  | LINE PIPE | BOLTED FITTING |  | 1998 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 69.9822 | 141.1824 | BUTANE | 2 | 55 | 0 | Null | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TODD E YOUNG | 5045344070 | WELL #1 HAD BEEN WORKED OVER AND WAS N PROCESS OF BEING PUT BACK IN SERVICE.THE PRODUCT LINE FROM THE MASTER MANIFOLD TO THE WELL HEAD WAS BEING PRESSUREDUP ON THE WELL SIDE OF THE MASTER MANIFOLD. THE FLANGE ON THE WELL SIDE OFTHE MASTER MAINFOLD DEVELOPED A LEAK CAUSING A RELEASE.
2017-09-29 08:50 | YES | NO | 19980121 |  | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1998-07-31 | 2100 | TX | ORANGE |  | NO |  | NO |  |  | TANK FARM | TANK |  |  | OTHER | MALFUNCTION OF ELECTRICAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5598.579 | 11294.5953 | KEROSENE | 3 | 246 | 236 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | WILLIAM J HOFF | 7133593710 | TEPPCO PERSONNEL HAD TAKEN A BREAKOUT STORAGE TANK OUT OF SERVICE FOR A CHANGEIN SERVICE. THE MANWAY TO THE TANK HAD BEEN REMOVED AND REPLACED AS PART OFTHIS WORK. AN ELECTRICAL MALFUNCTION AT THE FACILITY INADVERTENTLY OPENED ANISOLATION VALVE ON THE BREAKOUT TANK WHILE A PRODUCT DELIVERLY WAS IN PROGRESSTO AN ADJACENT BREAKOUT STORAGE TANK ON THE SAME TANK LINE, THUS ALLOWINGPRODUCT TO GRAVITY FROM ONE TANK INTO THE OTHER. THIS RAISED THE LEVEL OFPRODUCT IN THE OUT OF SERVICE TANK ALLOWING IT TO ESCAPE FROM THE LOOSENEDMANWAY. UPON DISCOVERY, TEPPCO'S EMERGENCY PROCEDURE WAS IMMEDIATELYINITIATED. FLOW WAS STOPPED AND REMAINING PRODUCT WAS TRANSFERED FROM THE OUTOF SERVICE TANK TO OTHER STORAGE TANKS. ALL RELEASED PRODUCT WAS CONTAINEDINSIDE THE SECONDARY CONTAINMENT AREA AROUND THE TANK. 236 BARRELS OF PRODUCTWAS RECOVERED. SAMPLES HAVE BEEN COLLECTED FROM THE SPILL AREA TO DETERMINEIF ANY REMEDIATION ACTIONS ARE NECESSARY.
2017-09-29 08:50 | NO | NO | 19980122 |  | 22430 | WEST SHORE PIPELINE CO | YES | 1998-08-18 | 630 | IL | COOK | RIVERDALE | NO |  | NO | NEAR AN APARTMENT BUILDING. SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | GASOLINE | 1 | 5 | 5 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 1165 | 550 | YES | 8 | 1500 | 0 | 0 | EXTERNAL | Null | YES | OTHER | CREVICE CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | DANIEL PALLO | 6302573742 | 2" NICOR LINE WAS LAYING AT 90 DEGREE ANGLE ON TOP OF WEST SHORE 16' PIPE.EXTERNAL CORROSION RESULTED AFTER APPARENT THIRD PARTY COATING DAMAGE OCCURREDTO THE WEST SHORE LINE.
2017-09-29 08:50 | YES | NO | 19980123 |  | 2387 | CITGO PIPELINE CO | YES | 1998-08-03 | 700 | TX | HARDIN |  | NO |  | NO | CITGO PIPELINE CO 530 HWY 326 NORTH SOUR LAKE, TX |  | TANK FARM | PIPE |  | 1952 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2799.2895 | 5647.2976 | CRUDE OIL | 1 | 597 | 505 | NO | NO | 20 | 0.22 | 24000 | WELDED |  | 275 | 15 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M. D. MOSELEY | 4092873594 | TANK RECEIVING VALVE WAS OPEN WAITING FOR DELIVERY, OPERATOR NOTICED VOLUME INTANK WAS DECREASING AND CALLED GAUGER TO CHECK. HE FOUND OIL OUT IN TANK 378FIREWALL. LINE WAS EXCAVATED AND LEAK FOUND AND LINE PATCHED. OIL CLEAN UPBEGAN. LINE CHECKED WITH U/T THICKNESS METER FOR OTHER CORROSION. FULL SOLEWELDED ON LEAK SITE.
2017-09-29 08:50 | YES | NO | 19980124 |  | 30755 | CITGO PRODUCTS PIPELINE CO | YES | 1998-08-05 | 1100 | TX | DENTON | CORINTH | NO |  | NO | 1900 SOUTH OF 2181 IN CORINTH, TEXAS, DENTON COUNTY |  | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 209946.714 | 423547.323 | GASOLINE | 3 | 105 | 42 | NO | NO | 8.63 | 0.32 | 35000 | WELDED |  | 720 | 300 | YES | 8 | 1000 | 11 | 96 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JIM SANDERS | 9184954786 | CONTRACTOR STRUCK LINE WHEN EXCAVATING FOR NEW SEWER LINE.
2017-09-29 08:50 | YES | NO | 19980125 |  | 2325 | CHEVRON USA INC | NO | 1998-08-02 | 630 | LA | PLAQUEMINES | EMPIRE | NO |  | YES | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000000 | 10497335.7016 | 21177366.1507 | CRUDE OIL | 3 | 100 | 90 | NO | NO | 16 | 0 | 35000 | WELDED |  | 0 | 60 | NO | 0 | 0 | 1 | 84 | INTERNAL | Null | NO | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEPHEN J MOLLEY | 5043642133 | THE LEAK WAS DISCOVERED BY CHEVRON PIPE LINE, EMPIRE TERMINAL PERSONNEL WHILEMAKING GAUGING REPORTS AT 0630 HRS ON 8/2/98. A HOLE, CAUSED BY INTERNALCORROSION OCCURRED IN THE 16' PIPELINE, ALLOWING 100 BARRELS TO LEAK WITHINTHE CONTAINMENT LEVEE WALLS IN THE CHEVRON PIPE LINE OSTRICA TERMINAL. THEVALVES WERE IMMEDIATELY CLOSED BY THE CHEVRON PIPE LINE SERVICE CENTER TO STOPTHE FLOW OF OIL. THE SECTION OF 16' LINE WAS ISOLATED AND THE DEAD LEGREMOVED AND REPLACED WITH A 12 FOOT SECTION OF FLANGED PIPE. THE FREE FLOWINGOILS WERE REMOVED FROM THE SURROUNDING SHELL AND GRASS AREAS WITH SITEREMEDIATION OF THE CONTAMINATED AREA TO FOLLOW.
2017-09-29 08:50 | YES | NO | 19980126 | 1998-09-08 | 30950 | EL PASO FIELD SERVICES | NO | 1998-08-05 | 1130 |  |  |  | YES | 2825.58 X 9613.32 | NO | THIS LEAK WAS IN THE VICINITY OF MI 520 PLATFORM IN THE MATAGORDA ISLAND AREA |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 105000 | 73481.3499 | 148241.5631 | CONDENSATE | 1 | 1 | 0 | NO | NO | 6 | 0.42 | 35000 | WELDED |  | 1440 | 0 | YES | 24 | 2162 | 9 | 79 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | E R WEST | 7134203534 | 11:30 A.M- J.D. CALLED JACK BREWER HAD INFORMED HIM THAT A PILOT WITHSHUT IN DUE TO MI 520 DOING SOME REPAIRS TO A LEAKING VALVE. 11:40 A.M. -J.D.PAGED MONTE TO FLY OVER THE COORDINATES AND REPORT BACK. 12:10 P.M.- MONTEWIDE. IT IS DISSPATING RAPIDLY. THE BUBBLES ARE 3 MILES OFF OF THE BEACH.12:15 P.M.- J. D. CALLING DIVE BOATS AND VARIOUS COMPANIES TO CHECK ON THEAVAILABILITY OF BOAT AND DIVERS. 2:15 P.M. J.D. SECURED A BOAT AND DIVERSWITH AMERICAN OILFIELD DIVERS. THE BOAT WILL BE IN PORT O'CONNOR DOCK TONIGHTBY 5:OO P.M. DIVERS WILL BE MOBILED TO BOARD THE BOAT AT THAT TIME AND THEY2:30 PM- RONDA CALLED THE NATIONAL RESPONSE CENTER AND SPOKE TO "FLETCHER".GIVEN REPORT #449186. 2:40PM- RONDA CALLED THE COAST GUARD AND SPOKE TO PETTYOFFICER MARTY PRITCHARD. 2:50PM-RONDA CALLED GABE MACIAS WITH THE TEXASRAILROAD COMMISSION OFFICE IN HOUSTON, TX. 2:55 PM RONDA CALLED IN AUSTIN, TX-REPORTED POSSIBLE LEAK TO "CARRIER". 2:58PM- RONDA CALLED KIM AT THE GENERALLAND OFFICE IN PORT LAVACA AND REPORTED INCIDENTS. 3:00 PM- RONDA CALLED THEGENERAL LAND OFFICE FOR SPILL REPORTS AND REPORTED ALL INCIDENTS TO "MOORER".RECEIVED REPORT NUMBER 981523. 3:15 PM- ROBERT CALLED EL PASO FIELD SERVICESMANAGEMENT AND CODES COMPLIANCE DEPARTMENT TO LET THEM KNOW OF INCIDENT. 4:30PM- MONTE FLEW OVER THE REPORTED SITE AGAIN. EVERYTHING REMAINED AS THEY WEREEARLIER IN THE DAY WHEN EVERYTHING WAS REPORTED. 5:30PM- AMERICAN OILFIELDDIVERS ARRIVED AT PORT O'CONNOR. THEY SECURED THE CLAMPS THAT WOULD BE NEEDEDIN CASE IT WAS FOUND TO BE OUR LINE. JOHN DORNAK WITH EL PASO ALSO BOARDEDTHE BOAT. THURSDAY, AUGUST 6, 1998 7:00 AM- THEY ARE NOT ABLE TO FIND THEBUBBLES NOW. THERE IS NOT ENOUGH PRESSURE ON THE LINE TO CAUSE BUBBLES TOFORM. JOHN WILL CALL MI 520 TO ASK THEM IF THEY CAN POSSIBLY PUT SOME GASINTO THE LINE IN ORDER TO HELP THEM LOCATE THE LEAK. JOE AND MONTE WILL DO AFLY OVER TO ALSO ASSIST IN LOCATING ANY SIGNS. 8AM- THE SHEEN AND BUBBLESHAVE BEEN LOCATED. THE BOAT ARRIVED IN POSITION. COORDINATES GIVEN YESTERDAYARE ACTUALLY APPORXIMATELY 900 YARDS OFF OF THE ACTUAL SHEEN AND BUBBLES.8:30AM- ANCHORS ARE BEING SET. 9:30AM SAFETY MEETING IS BEING HELD- DIVERS AREPREPARING TO DIVE ON LOCATION. 12PM- DIVERS HAVE BEEN DIVING ON LOCATION ANDJETTING OUT LINE. IT HAS BEEN DETERMINED TO BE THE 6' CAVALLO LIQUID LINE.THE BUBBLES WERE TRAVELING ALONG THE LINE MAKING IT HARD FOR THEM TO DETERMINEEXACTLY WHERE THE LEAK WAS. 1:15PM- RONDA CALLED ALL THE GOVERNMENT AGENCIESTO UPDATE THEM WHERE REPAIRS WERE AT ON THE LEAK AND TO LET THEM KNOW IT WASOUR LINE. 2PM THE DIVERS ARE CONTINUING TO JET OUT ALONG THE LINE. IT ISDIFFICULT TO DETERMINE WHERE THE ACTUAL LEAK IS. THE LINE HAD TWO TYPE OFCOATINGS, A MASTIC TYPE OF TAPE AND THEN ANOTHER COATING. THEY ARE PEELINGSOME OF THE MASTIC COATING OFF TO SEE THE BUBBLES BETTER. SEE REPORT FOR MOREDETAILS..
2017-09-29 08:50 | YES | NO | 19980127 | 1998-09-08 | 30950 | EL PASO FIELD SERVICES | NO | 1998-08-08 | 1205 |  |  |  | YES | 2825.58 X 9613.32 | NO | THIS LEAK WAS IN THE VICINITY OF MI 520 PLATFORM IN THE MATAGORDA ISLAND AREA. |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | CONDENSATE | 1 | 1 | 0 | NO | NO | 6 | 0.42 | 35000 | WELDED |  | 1440 | 0 | YES | 24 | 2162 | 9 | 79 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION | NO DATA |  | Null | NO DATA |  | Null | Null | E R WEST | 7134203534 | SATURDAY, AUGUST 8, 1998 - 12:05PM- JD CALLED ROBERT SHIMEK UPON FLYING OUT TOMI 520 TO CONTINUE WORK ON VALVE, HE SPOTTED A SHEEN IN THE SAME VICINITY ASTHE NEWLY COMPLETED REPAIRS ON A LEAK SITE. 12:15PM- ROBERT BEGAN MAKINGCALLS TO ACQUIRE A DIVE BOAT. THE BOAT WE JUST RELEASED HAS ALREADY RETURNEDTO GALVESTON AND CANNOT ASSIST ON THIS REPORT. THERE ARE TWO BOATS INCAMERON, LA. 1:30PM- ROBERT CALLED POWER OFFSHORE AND WAS ABLE TO ACQUIRE ALIFT BOAT, BUT THEY DO NOT HAVE ANY DIVERS TO ASSIST. 2:50PM- ROBERT CALLEDCEANIC (AMERICAN OILFIELD DIVERS) AND ARRANGED FOR DIVERS TO MEET THE BOAT ATTHE PORT O'CONNOR DOCK. THE BOAT WILL ARRIVE ON MONDAY MORNING ATAPPROXIMATELY 5AM J.D. RAMOS WITH EL PASO WILL BE ON BOARD. 2:55PM ROBERTCALLED RONDA TO NOTIFY HER OF SITUATION AND TO MAKE REGULATORY CALLS. 3PM-GUARD ANSWEREING SERVICES TO REPORT INCIDENT. 3:08PM- RON GASPARD WITH THEGLO CALLED. RONDA UPDATED HIM AS TO ALL INCIDENTS. 3:09PM- JIM MALEER WITHTHE RAILROAD COMMISSION OF TEXAS CALLED. RONDA UPDATED HIM. HE WILL NOTIFYTHE LOCAL HOUSTON OFFICE OF THE RAILROAD COMMISSION IN ORDER FOR THEM TOCONTACT RONDA. 3:15PM- GREG ROLLIN WITH THE RAILROAD COMMISSION OFFICE INHOUSTON CALLED. RONDA UPDATED HIM AS TO ALL EVENTS. 3:15PM- PETTY OFFICERSCOTT CLIGENPEEL CALLED. RONDA UPDATED HIM AS TO ALL INFORMATION. SUNDAY,AUGUST 9, 1998 7AM- ROBERT CALLED. REPAIRS ON MI 520 CONTINUE. LINE IS STILLSHUT-IN. LIFT BOAT HAS ALREADY ARRIVED AT THE PORT O'CONNOR DOCK AND ISSTANDING BY WAITING TO GO OUT TO THE REPORTED LOCATION. A FLY OVER WASCOMPLETED AND NO BUBBLES OR A SHEEN IS VISIBLE AT THIS TIME. 2PM- A FLY OVERWAS COMPLETED. STILL NO SHEEN OR BUBBLES. MONDAY, AUGUST 10, 1998 8AM-REPAIRS ON MI 520 ARE NOT COMPLETED AS OF YET. REPAIRS TO LINE WILL WAITUNTIL PLATFORM IS COMPLETED. THERE IS NO MORE EVIDENCE OF SHEEN OR BUBBLES ATLOCATION. 8:30AM RONDA CALLED ALL GOVERNMENT AGENCIES TO NOTIFY THEM OFACTIVITIES. 10AM- A FLY OVER WAS DONE STILL NO SHEEN OF BUBBLES. SEE REPORTFOR MORE DETAILS.
2017-09-29 08:50 | YES | NO | 19980129 | 1998-09-08 | 3012 | PRIDE TEXAS PLAINS L.P. | NO | 1998-08-13 | 1600 | TX | GRAY | ALANREED | NO |  | NO | APPROXIMATELY 24 MILES WEST OF ALANREED, TX ON INTERSTATE 40 TO FM RD. 2477 TURN NORTH GO APPROXIMATELY 13 MILES. LEAK ON WEST SIDE OF FM 2477. |  | LINE PIPE | NO DATA |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | CRUDE OIL | 3 | 477 | 185 | NO | NO | 10.75 | 0.37 | 25000 | WELDED |  | 600 | 300 | YES | 8 | 0 | 1 | 76 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | JOHN T MACON | 9156748231 | LEAK WAS REPORTED BY TENANT, AT APPROXIMATELY 4PM ON 8/13/98. PIPELINE WASSHUTDOWN, CREWS WERE DISPATCHED. WHILE IN PROCESS OF MAKING TEMPORARY REPAIRSTO THE LINE, A 2" NIPPLE WAS BROKE OFF RESULTING IN ADDITIONAL CRUDE BEINGLOST OUT OF THE LINE. THE LINE WAS THEN UNCOVERED AND NEW PIPE WAS INSTALLED.
2017-09-29 08:50 | NO | NO | 19980130 | 1998-09-08 | 2325 | CHEVRON USA INC | NO | 1998-04-28 | 2300 |  |  |  | YES | X=2278342 Y=71559 | YES | SOUTH TIMBALIER BLOCK 52- 10" CRUDE OIL PIPELINE FROM ST 52 "A" TO ST 35 "D". NOTE SOUT TIMBALIER BLK 52 -8" CRUDE OIL PIPELINE IS DOCUMENTED ON SEPARATE RPT. |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 1 | 0 | NO | NO | 10 | 0.5 | 35000 | WELDED |  | 1440 | 500 | YES | 8 | 2214 | 10 | 84 | NO DATA | Null | Null | NO DATA |  | SHIP ANCHOR |  | Null | NO DATA |  | Null | Null | STEPHEN J. MOLLOY | 5043642133 | ON APRIL 28TH, 1998, WHILE OPERATING IN THE SOUTH TIMBALIER 52 FIELD, AMCDERMOTT VESSELL (MV101) LOSS POWER AND BEGAN DRIFTING IN HEAVY SEAS (8' TODROPPED. THE ANCHORS HOOKED AND SEVERED THE ABOVE REFERENCE PIPELINES CAUSINGTHE LINES TO BE RUPTURED. THE CHEVRON PRODUCTION OPERATOR AT ST 52-PRODUCTIONWITH ASSISTANCE FROM THE CHEVRON PIPELINE OPERATOR AT FOURCHON. NO SIGNS OFPIPELINE LEAKS WERE NOTICED IMMEDIATELY DUE TO DARKNESS AND WEATHERCONDITIONS. ON APRIL 30, 0645 HRS, AN AERIAL FLY-OVER BY CHEVRON OBSERVED ASHEEN 2" MILES LONG, 15 FEET WIDE WITH FAINT COLORS, WHICH WAS ESTIMATED TO BELESS THAN A 1 GALLON RELEASE. THE SHEET WAS SEEN MOVING SSW. THE M/V SEACATDIVE BOAT, WITH DIVERS WAS ON LOCATION NEAR THE 10" LINE. AN FRU (M/V DIXIE)WAS DISPATCHED AT 7:34AM, WITH AN ETA OF 2 HRS. IN ADDITION, LAY BARGE, M/VGP37, WAS IN ROUTE, WITH AN ETA OF 2400 HRS, 4/30. THE MSRC WAS ALERTED TOTHE POSSIBLE USE OF THEIR 37' SKIMMING VESSEL AND CREW, AND ADDITIONAL FRU WASPUT ON STANDBY AND A CLASS 150' JACKUP WAS ON STANDBY AT THE LEEVILLESHOREBASE TO BE USED WITH ADDITIONAL DIVERS AS NEEDED. NOTIFICATIONS INCLUDETHE NATIONAL RESPONSE CENTER (NRC REPORT #434469), COAST GUARD (MSO JASONMARINEAU), LOUISANA STATE POLICE AND THE LOUISANA DEPARTMENT OF ENVIRONMENTALQUALITY. THE CHEVRON INCIDENT COMMAND STRUCTURE WAS SETUP, WITH SOURCECONTROL AND REPAIR OPERATIONS TO BE MANAGED IN 6 TASK FORCES. FRU M/V DIXIEON STANDBY AT LOCATION READY TO RESPOND AS WARRANTED AND REPAIRS TO PIPELINESSUBJECT TO INSPECTION BY DIVERS AND WILL BEGIN AS APPROPRIATE. SEE ATTACHEDMAP OVERVIEW.
2017-09-29 08:50 | NO | NO | 19980131 | 1998-08-09 | 2325 | CHEVRON USA INC | NO | 1998-04-28 | 2300 |  |  |  | YES | X=2278342 Y=71559 | YES | SOUTH TIMBALIER BLOCK 52-8' CRUDE OIL PIPELINE FROM ST 52 "A" TO ST 63 "A". NOTE S. TIMBALIER BLOCK 52-10" CRUDE OIL PIPELINE IS DOCUMENTED IN SEPARATE RPT. |  | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 1 | 0 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 1440 | 500 | YES | 4 | 1900 | 3 | 91 | NO DATA | Null | Null | NO DATA |  | SHIP ANCHOR |  | Null | NO DATA |  | Null | Null | STEPHEN J MOLLOY | 5043642133 | ON APRIL 28, 1998, WHILE OPERATING IN THE SOUTH TIMBALIER 52 FIELD, AMCDERMOTT VESSEL (MV101) LOSS POWER AND BEGAN DRIFTING IN HEAVY SEAS (8' TO10') AND HIGH WINDS. TO PREVENT THE VESSEL FROM DRIFTING, THE ANCHORS WEREDROPPED. THE ANCHORS HOOKED AND SEVERED THE ABOVE REFERENCED PIPELINE CAUSINGTHE LINE TO BE RUPTURED. THE CHEVRON PRODUCTION OPERATOR AT ST 52-PRODUCTIONSTRUCTURE NOTICED A PRESSURE DROP IN THE PIPELINE AND SHUT DOWN THE SYSTEMWITH ASSISTANCE FROM THE CHEVRON PIPE LINE OPERATOR AT FOURCHON. NO SIGNS OFPIPELINE IMMEDIATELY DUE TO DARKNESS AND WEATHER CONDITIONS. ON APRIL 30,0645 HRS, AN AERIAL FLY OVER BY CHEVRON OBSERVED SHEEN 2 MILES LONG, 15 FEETWIDE WITH FAINT COLORS, WHICH WAS ESTIMATED TO BE LESS THAN A 1 GALLONRELEASE. THE SHEEN WAS SEEN MOVING SSW. THE M/V SEACAT DIVE BOAT, WITHDIVERS, WAS ON LOCATION NEAR THE 8" LINE. A FRU (M/V DIXIE) WAS DISPATCHED AT7:34AM, WITH AN ETA OF 2 HRS. IN ADDITION, A LAY BARGE, M/V GP37, WAS INROUTE, WITH AN ETA OF 2400 HRS, 4/30. THE MSRC WAS ALERTED TO THE POSSIBLEUSE OF THEIR 37' SKIMMING VESSEL AND CREW, AN ADDITIONAL FRU WAS PUT ONSTANDBY AND A CLASS 150' JACKUP WAS ON STAND BY AT THE LEEVILLE SHOREBASE TOBE USED WITH ADDITIONAL DIVERS AS NEEDED. NOTIFICATIONS INCLUDE THE NATIONALRESPONSE CENTER (NRC REPORT #434469), COAST GUARD (MSO JASON MARINEAU),LOUISIANA STATE POLICE AND LOUISANA DEPARTMENT OF ENVIRONMENTAL QUALITY. THECHEVRON INCIDENT COMMAND STRUCTURE WAS SET UP, WITH SOURCE CONTROL AND REPAIROPERATIONS DIVISION TO MANAGED IN 6 TASK FORCES. FRU M/V DIXIE ON STAND BY ATLOCATION READY TO RESPOND AS WARRANTED AND REPAIRS TO PIPELINES SUBJECT TOINSPECTION BY DIVERS AND WILL BEGIN AS APPROPRIATE. SEE ATTACHED MAP OVERVIEW.
2017-09-29 08:50 | YES | NO | 19980132 | 1998-09-08 | 2325 | CHEVRON USA INC | NO | 1998-01-07 | 1445 |  |  |  | YES | LAT 29 4'6" N LONG 90 11' | YES | SOUTH TIMBALIER 131, 0.5 MILES SOUTH OF THE JETTIES OF BELLE PASS, LA |  | LINE PIPE | PIPE |  | 1978 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 793 | 150 | NO | NO | 12 | 0.5 | 35000 | WELDED |  | 1440 | 50 | YES | 0 | 2205 | 7 | 76 | NO DATA | Null | Null | NO DATA |  | OTHER | TUGBOAT SINKING | Null | NO DATA |  | Null | Null | STEPHEN J. MOLLOY | 5043642133 | AT 1740 HRS ON JANUARY 6, 1998, THE M/V STONE FUELER SANK AT SOUTH TIMBALIER131, 0.5 MILES SOUTH OF THE BELLE PASS JETTIES. AN OIL RELEASE WAS OBSERVEDDURING AN OVERFLIGHT BY THE USCG AT 1420 HRS ON JANUARY 7, 1998. THE USCGNOTIFIED ALL PIPELINE OWNERS IN THE VICINITY OF THE SINKING, AT WHICH TIME,CHEVRON PIPE LINE SHUT IN THE PIPELINE NEAR ST 131. AN OVERFLIGHT WASPERFORMED IMMEDIATELY BY CHEVRON PIPE LINE TO VERIFY THAT THE TUGBOAT WAS NEARTHE PIPELINE. AT 1700 HRS ON JANUARY 7, 1998 A PRESSURE TEST VERIFIED THECHEVRON OWNED 12 INCH CRUDE OIL LINE HAD BEEN DAMAGED. CHEVRON PIPE LINEDISPATCHED A DIVE BOAT WITH DIVERS TO THE INCIDENT SCENE IN SUPPORT OF THEUNIFIED COMMAND, WHICH HAD ALREADY BEEN ESTABLISHED BY THE USCG AND JOHN W.STONE OIL DISTRIBUTORS LLC. APPROPRIATE CONTRACTORS AND EQUIPMENT WERE PLACEDON LOCATION TO INITIATE REPAIRS AS SOON AS THE USCG, STONE OIL DISTRIBUTORS,AND CHEVRON PIPE LINE AGREED WITHIN THE UNIFIED COMMAND THAT DIVERS COULD MOVEINTO THE AREA TO MAKE THE NEEDED REPAIRS. NOTIFICATIONS INCLUDE THE NATIONALRESPONSE CNETER (NCR REPORT #418581)
2017-09-29 08:50 | YES | NO | 19980133 | 1998-09-10 | 26303 | UNOCAL PIPELINE CO | NO | 1998-08-11 | 830 | IL | WILL |  | NO |  | NO | CHICAP'S METERING STATION LOCATED 1/2 MILES SOUTHWEST OF MANHATTAN, IL |  | NO DATA | OTHER | 1/2 HP ELECTRIC PUMP | 1991 | OTHER | EQUIPMENT FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | CRUDE OIL | 3 | 50 | 48 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID T HOCKING | 7084799260 | CHICAP PIPELINE COMPANY IS A JOINT VENTURE PIPELINE OPERATED BY UNOCALPIPELINE COMPANY. THE 202 MILE 26" DIAMETER PIPELINE ORIGINATES IN PATOKA,ILLINOIS AND TERMINATES IN MOKENA, ILLINOIS. THE PIPELINE BATCHES VARIOUSTYPES OF CRUDE OIL FROM PATOKA FOR DELIVERY AT BOTH MANHATTAN AND MOKENA. ACOMBINED GRAVITOMETER AND SULFUR ANALYZER IS CONNECTED TO THE 26" PIPELINE ATMANHATTAN STATION TO DETERMINE BATCH DELIVERIES AT MANHATTAN AND MOKENA. THISUNIT ASSISTS THE OPERATORS AT UNOCAL'S 24-HOUR CONTROL CENTER LOCATED INPATOKA, ILLINOIS, TO HELP DETERMINE THE BEGINNING AND END OF BATCHES DELIVEREDTO MANHATTAN AND MOKENA. FLOW IS SIPHONED OFF THE 26" PIPELINE. THIS UNITOPERATES 24-HOURS PER DAY 7 DAYS PER WEEK. THE SULFUR ANALYZER AND PUMP WEREINSTALLED IN 1991. CHICAP'S MANHATTAN STATION IS LOCATED ON AMOCO PIPELINECOMPANY'S PROPERTY, WHICH IS LOCATED 1/2 MILE SOUTHWEST OF MANHATTAN,ILLINOIS. AT APPROXIMATELY 8AM ON AUGUST 11, 1998 TOM BOSCO, AN AMOCOEMPLOYEE, ENTERED THE AMOCO FACILITY AND DETECTED THE ODOR OF CRUDE OIL. UPONINVESTIGATION, TOM IDENTIFIED THE SOURCE OF THE RELEASE AS COMING FROMCHICAP'S GRAVITOMETER PUMP. THE PUMP OPERATES A 7-10 GALLONS PER MINUTE. TOMSHUT OFF THE PUMP AND THE RELEASE COMING FROM THE PUMP STOPPED. TOMIMMEDIATELY RECOGNIZED THAT THE RELEASE FLOW WOULD END UP IN THE FACILITIESRETENTION PONDS AND THEN DISCHARGE FROM THESE PONDS INTO DRAINAGE, WHICHEMPTIES INTO PRAIRIE CREEK. TO IMMEDIATELY SHUT OFF THE VALVE ON THERETENTION POND TO ELIMINATE ANY ADDITIONAL OIL LEAVING THE AMOCO FACILITY.TOM THEN BUILT AN EARTHEN DAM NEAR THE SITE OF THE RELEASE TO CONTAIN THE OILAND PREVENT ADDITIONAL OIL FROM ENTERING THE FACILITIES DRAINAGE SYSTEM, WHICHEMPTIES INTO THE RETENTION PONDS. AMOCO THEN NOTIFIED CHICAP OF THE RELEASE.THE CALL WAS RECEIVED AT THE PATOKA CONTROL CENTER AT APPROXIMATELY 8:30 AM.AL HINDERLITER, A CHICAP DISPATCHER, RECEIVED THE CALL AND TRANSFERRED IT TODAVE HOCKING, CHICAP'S UTILITY TECHNICIAN. DAVE WAS AT THE CONTROL CENTER ASA RELIEF SCHEDULER AND IS TRAINED TO BE AN INCIDENT COMMANDER/QUALIFIEDPERSON. DAVE IMMEDIATELY NOTIFIED ROGER MORRIS, CHICAP'S OPERATIONS FOREMANWHO IS ALSO TRAINED AS AN INCIDENT COMMANDER. TYPICALLY ROGER WOULD ACT ASTHE OPERATIONS CHIEF IN AN INCIDENT. ROGER WAS IN THE MOKENA OFFICE WHEN HERECEIVED THE NOTIFICATION AND IMMEDIATELY DROVE TO MANHATTAN STATION TO ASSESSTHE SITUATION. ROGER ARRIVED AND AT THE RELEASE SITE AT 8:50 AM ANDIMMEDIATELY BEGAN HELPING AMOCO PERSONNEL CONTAIN THE RELEASE. AT 9:25 AM,AFTER ASSESSING THE EXTENT OF THE RELEASE, ROGER NOTIFIED DAVE TO INFORM HIMOF THE DETAILS AND THAT THE RELEASED AMOUNT WAS APPROXIMATELY 50 BARRELS.DAVE THEN NOTIFIED THE NATIONAL RESPONSE CENTER AND THE ILLINOIS EMERGENCYMANAGEMENT AGENCY. DAVE ALSO NOTIFIED HERITAGE, CHICAP'S CONTRACTED EMERGENCYRESPONSE CONTRACTOR, THAT A RELEASE HAD OCCURRED AND WE WOULD REQUIREPERSONNEL AND EQUIPMENT AS SOON AS THEY COULD GET THERE. UPON ARRIVAL ON THESCENE ROGER MORRIS BEGAN TO ASSESS THE SITUATION. AMOCO HAD PERFORMED INITIALATMOSPHERIC MONITORING AND DETERMINED THE AREA WAS NON-HAZARDOUS ANDRESPONDERS COULD WEAR CLASS D PROTECTION. AMOCO'S READINGS WERE LATERCONFIRMED BY KARL LOHRMANN, CHICAP'S HESS SPECIALIST. AMOCO'S INSPECTED OFPRAIRIE CREEK HAD DETERMINE THAT OIL REACHED THE CREEK. ABSORBENT BOOM WASINSTALLED IN 2 PLACES ON PRAIRIE CREEK TO PREVENT THE SPREAD OF THE RELEASE.THE FIRST BOOM WAS PLACED 100 YARDS DOWN STREAM FROM THE TILE INLET AND INFRONT OF THE LEADING EDGE OF THE OIL SHEEN. THE SECON ABSORBENT BOOM WAS
2017-09-29 08:50 | YES | NO | 19980134 | 1998-09-11 | 25133 | TEXACO TRADING & TRANSPORTATION INC | Null | 1998-08-11 | 1130 | CA | MERCED |  | NO |  | YES | APPROX 1 MILE WEST OF INTERSTATE 5 IN FRONT OF LOS BANOS DETENTION DAM. |  | LINE PIPE | OTHER | 2' HOT TAP CONNECTION |  | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 800000 | 559857.9041 | 1129459.528 | CRUDE OIL | 1 | 1412 | 1112 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | YES | PAUL W. SMITH | 8053282358 | CONTRACT OPERATOR HIT 2" HOT TOP CONNECTION ON EXISTING 20" PIPELINE WHILEEXCAVATING FOR NEW PIPE INSTALLATION.
2017-09-29 08:50 | YES | NO | 19980135 | 1998-09-09 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1998-08-28 | 820 | KS | RICE |  | NO |  | NO | NW 1/4, SECTION 30, TOWNSHIP 18 SOUTH, RANGE 7 WEST, RICE COUNTY, KANSAS 3 MILES SOUTH AND 1/2 MILE EAST OF GENESEO, KANSAS |  | PUMPING STATION | TANK |  | 1943 | OTHER | ROOF DRAIN LINE FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 1 | 1098 | 1085 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R. WILKERSON | 3162419270 | THE TANK IN QUESTION, LOCATED AT JAYHAWK'S GENESEO PUMP STATION, HAS ANEXTERNAL FLOATING ROOF AND THE ROOF DRAIN LINE PARTED INSIDE THE TANK, WHICHIN TURN LET OIL RUN OUT THE DRAIN LINE INTO DIKE. ALL OIL WAS CONTAINEDINSIDE DIKE. 1,085 BARRELS WERE RECOVERED AND SOIL REMEDIATION WILL BE DONEINSIDE DIKE FOR FINAL CLEAN UP. ALL CRUDE OIL WILL BE REMOVED FROM TANK ANDNEW DRAIN LINE WILL BE INSTALLED.
2017-09-29 08:50 | YES | NO | 19980136 | 1998-09-17 | 30903 | ARCO PIPE LINE COMPANY | YES | 1998-08-27 | 920 | TX | FREESTONE |  | NO |  | NO | FROM THE TOWN OF TEAGUE, TX WEST ON FM 1365 1.5 MILES, THEN .25 MILES SOUTH ON PRIVATE DRIVE. LAT N31 37' 11.9", LONG W96 18' 35.6 INN THE G BREWER LEAGUE,A-5 |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 349911.1901 | 705912.205 | GASOLINE | 1 | 3000 | 695 | NO | NO | 16 | 0.28 | 52000 | WELDED |  | 1118 | 447 | YES | 8 | 1449 | 2 | 88 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | MIKE A SCHMIDT | 9182232957 | AT 11:00 ON AUGUST 27, 1998 ARCO PIPELINE COMPANY (APL) MADE A TELEPHONICREPORT TO NRC (REPORT NO. 452574) OF AN UNLEADED GASOLINE SPILL ON SEAWAYPIPELINE COMPANY'S TEAGUE TO JACKSBORO 18-INCH PIPELINE, AT A LOCATIONAPPROXIMATELY 1.5 MILES WEST OF THE TOWN OF TEAGUE, TX AND .25 MILES SOUTH OFFM 1365. APL IS THE OPERATOR OF THE SEAWAY PRODUCTS PIPELINE, WHICH EXTENDSFROM GALENA PARK, TX TO CUSHING, OK. AT APPROXIMATELY 9:00 ON AUGUST 27, THEAPL OPERATIONS CENTER RECEIVED NOTIFICATION FROM THE APL AERIAL PATROL PILOTCONCERNING WHAT APPEARED TO BE A POSSIBLE LEAK DURING A ROUTINE FLY-OVER OFTHE PIPELINE. AT APPROXIMATELY 09:20 THE LEAK WAS CONFIRMED BY APL EMPLOYEESDISPATCHED TO THE SITE TO INVESTIGATE THE REPORT. THE AFFECTED LINE SEGMENTWAS ISOLATED BY CLOSING BLOCK VALVES ON EITHER SIDE OF THE LEAK LOCATION ANDEMERGENCY RESPONSE AND CLEANUP PERSONNEL WERE IMMEDIATELY CALLED TO THE SITETO UNDERTAKE CONTAINMENT, REPAIR AND CLEANUP ACTIVITIES. THE SOURCE OF THERELEASE WAS IDENTIFIED AS CORROSION PIT ON THE UNDERSIDE OF THE PIPELINE ANDWAS REPAIRED BY THE INSTALLATION OF A MECHANCIAL REPAIR SLEEVE. THERE WERE NOINJURIES, FIRES, OR EXPLOSIONS RESULTING FROM THIS INCIDENT AND THE RELEASEDPRODUCT DID NOT REACH ANY WATERWAYS. THE AREA AFFECTED BY THE RELEASE ISLOCATED ON PRIVATE PROPERTY. RECONCILED VOLUMES INDICATE A TOTAL RELEASEVOLUME OF APPROXIMATELY 3,000 BARRELS OF UNLEADED GASOLINE. APPROXIMATELY 695BARRELS OF LIQUIDS WERE IMMEDIATELY RECOVERED FROM THE RELEASE SITE ANDTRANSPORTED TO ANOTHER COMPANY FACILITY FOR REINJECTION INTO THE SYSTEM.APPROXIMATELY ANOTHER 600 BARRELS OF LIQUID HAVE BEEN RECOVERED FROM POSTINCIDENT RECOVERY ACTIVITIES. EXCAVATED SOIL HAS BEEN COLLECTED AND STAGEDONSITE IN ROLL OFF BOXES UNTIL SUCH TIME THAT SAMPLING AND CHARACTERIZATIONCAN BE COMPLETED FOR PROPER DISPOSAL. CLEAN CUP OF THE SPILL SITE IS BEINGCOORDINATED BY REPRESENTATIVES OF APL'S ENVIRONMENTAL, HEALTH AND SAFETYGROUP, WITH ASSISTANCE FROM GARNER ENVIRONMENTAL SERVICES.
2017-09-29 08:50 | YES | NO | 19980137 | 1998-09-14 | 10012 | KANEB PIPELINE CO | YES | 1998-08-10 | 1950 | SD | CUSTER |  | NO |  | NO | SW 1/4, SW 1/4, SECTION 27, TOWNSHIP 6 SOUTH, RANGE 7 EAST |  | PUMPING STATION | PUMP |  | 1990 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 20994.6714 | 42354.7323 | JET FUEL | 3 | 123 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | UNDER INVESTIGATION | NO DATA |  | Null | NO DATA |  | Null | Null | LEROY ANDERSON | 3162621408 | THE QUENCH LINE THAT COOLS THE PUMP SEAL BROKE. AN IDENTIFIED PERSON NOTIFIEDKANEB BY TELEPHONE THAT THERE WAS A PROBLEM AT OUR FACILITY. THE PIPELINE WASSHUT DOWN IMMEDIATELY. RESPONSE PERSONNEL FOUND BROKEN QUENCH LINE WHEN THEYARRIVED AT THE FACILITY.
2017-09-29 08:50 | YES | NO | 19980138 | 1998-09-11 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1998-08-20 | 1900 | TX | SAN PAT |  | NO |  | NO | FLORKE FARM- BETWEEN CO ROAD 98 & 100 |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | L. P. G. | 2 | 2761 | 0 | NO | NO | 8 | 0.32 | 0 | WELDED |  | 740 | 559 | YES | 4 | 1025 | 6 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | SIGNS | NO | NO | DE HUNT JR | 5128662190 | TENANT FARMER MONTY FLOKE EMPLOYEE PULLING CHISEL PLOW ACROSS COASTAL 8"
2017-09-29 08:50 | YES | NO | 19980139 | 1998-09-11 | 30991 | MOBIL OIL CORPORATION | YES | 1998-08-14 | 400 | TX | NAVARRO | CORSICANA | NO |  | NO | 1604 SOUTH 15TH ST, CORSICANA, TX -APPROX. 1 MILE NORTH OF DOWNTOWN CORISCANA AT THE MOBIL OIL CORP, TANK FARM - TANK #2709 |  | TANK FARM | TANK |  | 1953 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | NOT GIVEN |  | 0 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | D G SCOTT | 2146585914 | AT APPROXIMATELY 0400 HRS, AUGUST 14, DURING A SEVERE LIGHTNING ANDTHUNDERSTORM, TANK #2709 WAS STRUCK BY LIGHTNING. OPERATING PERSONNEL ON SITEAT THE TIME IMMEDIATELY NOTIFIED THE CORSICANA FIRE DEPT. WHO PROMPTLYRESPONDED AND EXTINGUISHED THE FIRE IN ITS ENTIRETY AT 0500 HRS. OTHERPERTINENT MOBIL PERSONNEL DISPATCHED TO THE AREA IMMEDIATELY FOLLOWING THEFIRE DEPT NOTIFICATION. ALL REQUIRED NOTIFICATIONS WERE MADE TO APPROPRIATEGOVERNMENTAL AGENCIES BY MOBIL CONST PERSONNEL. TANK #2709 IS AN EXTERNALFLOATING ROOF TANK. THERE WERE NO INJURIES OR DEATHS ASSOCIATED WITH THISINCIDENT.
2017-09-29 08:50 | YES | NO | 19980140 | 1998-09-29 | 12555 | MINNESOTA PIPELINE CO | YES | 1998-08-25 | 715 | MN | MORRISON | LITTLE FALLS | NO |  | NO | SPILL OCCURRED WITHIN THE PUMP STATION. SEE ATTACHED MAP |  | PUMPING STATION | OTHER | CORROSION COUPON HOLDER | 1995 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | CRUDE OIL | 1 | 200 | 133 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | ROY GENEVICH | 6514381261 | THE 2" VALVE BETWEEN THE COUPON HOLDER AND THE ACTIVE LINE WAS NOT PROPERLYCLOSED PRIOR TO REMOVING THE 2" COUPON HOLDER. THE 2" VALVE WAS FOUND OPENAFTER SHUTTING DOWN THE STATION PIPING. THE PROPER LOCKOUT TAGOUT PROCEDURESWERE NOT FOLLOWED BY THE CONTRACTOR. THE 2" VALVE WAS TESTED IN THE CLOSEPOSITION AND IT WAS FOUND TO BE OPERATING PROPERLY. THE INCIDENTINVESTIGATION CONCLUDE THAT IT WAS OPERATOR ERROR ON THE PART OF THECONTRACTOR WHO WAS REMOVING AND INSTALLING COUPONS.
2017-09-29 08:50 | YES | NO | 19980141 | 1998-09-23 | 443 | AMOCO PIPELINE CO | YES | 1998-08-19 | 1236 | MN | WILKIN |  | NO |  | NO | NEAR BARNSVILLE, MN IN WILKIN COUNTY, TOWNSHIP 136 (PRAIRIEVIEW), RANGE 46, SECTION 30 |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 1300 | 700 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1440 | 650 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DALE NEILAN | 6124254201 | WHILE ATTEMPTING TO REGRADE A DRAINAGE DITCH AREA WITH A EARTHMOVER THE LANDOWNER HIT AND GOUGED THE AMOCO PIPELINE RESULTING IN A 12" GASH. THIS GASHRESULTED IN COMMODITY BEING SPILLED INTO THE DRAINAGE DITCH AREA.
2017-09-29 08:50 | YES | NO | 19980143 | 1998-10-08 | 1044 | WESTTEX 66 PIPELINE CO | YES | 1998-09-11 | 2300 | TX |  | UPTON | NO |  | NO | BENEDUM PUMP STATION- BENEDUM-SWEENY PIPELINE-SRW 417-1-1-MP O SEC. 46, BLOCK Y, M.K. & T.R.R. SURVEY UPTON CO. TX, 7 MILES N OF RANKIN ON 349 AND 10 MILES E |  | PUMPING STATION | OTHER | THERMAL RELIEF VALVE |  | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 699.8224 | 1411.8244 | NATURAL GAS LIQUID | 2 | 63 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J SCHMITZ | 9186614814 | APPROXIMATELY 2-3 YEARS AGO, THE PIPING MOP WAS UPGRADED FROM 720 PSIG TO PSIG1440 PSIG. THE SET POINT ON THE RELIEF VALVE HAD BEEN SET AT 720 PSIG, ANDWAS NOT CHANGED WHEN THE PIPING UPGRADE WAS MADE. THIRD PERSONNEL OBSERVEDTHE VAPOR RELEASE AND NOTIFIED THE PPL CONTROL CENTER WHO THEN NOTIFIED THEAPPROPRIATE FIELD PERSONNEL. THE RELIEF VALVE WAS REPLACED AND THE PROPERPRESSURE SET.
2017-09-29 08:50 | YES | NO | 19980144 | 1998-10-07 | 30991 | MOBIL OIL CORPORATION | NO | 1998-09-08 | 900 | IL |  | LOCKPORT | NO |  | NO | INCIDENT ACCRUED INSIDE OF TERMINAL. |  | TANK FARM | PIPE |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | GASOLINE | 1 | 3900 | 2100 | NO | NO | 16 | 0.5 | 24000 | WELDED |  | 275 | 40 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | FACILITY PLAN | NO | YES | DALE A MAY | 8154237760 | ON SEPTEMBER 8, 1998 MOBIL OIL CONTRACTED A COMPANY TO REPLACE A RETENTIONWALL THAT SURROUNDS THE MANIFOLD SYSTEM. WHILE EXCAVATING AROUND THE WALL THECONTRACTOR WAS PLACING THE DIRT ON THE ROAD WAY (ROAD WAY IS DIRT ANDGRAVEL). ANOTHER TRACTOR WAS PICKING THE DIRT UP OFF THE ROAD WAY AND SCRAPEDTHE TOP OF THE 16" PRODUCT LINE. THE TRACTOR OPERATOR NOTICED THE LEAK ANDIMMEDIATELY CONTACTED THE MOBIL OPERATOR TO SHUTDOWN THE LINE BOTH 911 AND THEMOBIL FIRE DEPARTMENT WERE CALLED. BOTH THE LEMONT AND MOBIL FIRE DEPARTMENTSARRIVED ON SCENE AND APPLIED FOAM TO DISPERSE THE VAPORS. NO EVACUATIONS WEREMADE AND NO PRODUCT LEFT THE SITE. PRODUCT WAS ABLE TO BE CONTAINED IN THEPUMP MANIFOLD AREA AND THE FACILITY RETENTION POND. VACUUM TRUCKS WEREBROUGHT IN TO RECOVER THE PRODUCT AND ENVIRONMENTAL SAMPLES WILL BE TAKEN TOCLEAN ANY ADDITIONAL SOIL.
2017-09-29 08:50 | YES | NO | 19980145 | 1998-09-30 | 30991 | MOBIL OIL CORPORATION | YES | 1998-08-31 | 1140 | TX | TARRANT | ARLINGTON | NO |  | NO | 3300 BLOCK OF SUNSET LANE AND PARK AVE. DALWORTHINGTON GARDENS- ARLINGTON, TX. MOBIL PIPE LINE COMPANY MILE POST MARKER 93.8 |  | LINE PIPE | PIPE |  | 1954 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 244937.833 | 494138.5435 | CRUDE OIL | 1 | 150 | 115 | NO | NO | 16 | 0.25 | 42000 | WELDED |  | 800 | 200 | YES | 8 | 1004 | 2 | 94 | NO DATA | Null | YES | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | PUBLIC AWARENESS PROGRAM | NO | YES | D G SCOTT | 2146585914 | ON AUGUST 31, 1998 AT APPROXIMATELY 1140 HOURS AN INDEPENDENT EXCAVATINGCONTRACTOR WAS WORKING FOR A HOMEOWNER IN THE AREA OF MOBIL PIPE LINE COMPANYS16" CORSICANA TO RINGGOLD CRUDE OIL PIPELINE AT MILE POST 93.8 IN THEDALWORTHINGTON GARDENS AREA OF ARLINGTON, TEXAS HIT THE 16" PIPELINE WITH HISFRONT END LOADER CAUSING THE PIPELINE TO RUPTURE AND 150 BBLS OF CRUDE OILESCAPED. MOBIL PIPE LINE COMPANY OPERATIONS CONTROL CENTER IN DALLAS, TX WASNOTIFIED OF THE ACCIDENT AND THE PIPELINE WAS IMMEDIATELY SHUTDOWN ANDEMERGENCY RESPONSE PROCEDURE IMPLEMENTED. MOBIL MAINTENANCE CREWS DISPATCHEDTO AREA. RECOVERY AND CLEANUP PROCEDURES INITIATED. PERMANENT REPAIRS MADEBY REPLACING 12 FEET OF TESTED 16" PIPE. ALL FEDERAL AND STATE AGENCIESNOTIFIED WITHIN 2 HOURS OF ACCIDENT. NATIONAL RESPONSE CENTER ASSIGNED CASE#453216 TO THIS INCIDENT. NO CRUDE OIL REACHED ANY CREEKS, STREAMS, PONDS ORLAKES. NO CALLS WERE MADE TO MOBIL PIPE LINE COMPANY BY THE CONTRACTOR PRIORTO DOING ANY WORK IN THE AREA.
2017-09-29 08:50 | YES | NO | 19980147 | 1998-10-19 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1998-09-16 | 1840 | MN |  |  | NO |  | NO | PIPELINE AT MP 0878.1, TOWNSHIP 151 N, SECTION 14, SOUTHWEST QUARTER, RANGE 42 WEST, TRACT #803 |  | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | CRUDE OIL | 1 | 5700 | 5415 | NO | NO | 26 | 0.28 | 52000 | WELDED |  | 652 | 350 | YES | 25 | 820 | 1 | 74 | NO DATA | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R C SANDAHL | 2187250102 | IN THE EARLY EVENING OF SEPTEMBER 16, 1998, THE EDMONTON CONTROL CENTER WAS INTHE PROCESS OF STARTING UP THE 26" LINE 2. WHEN THE DISCHARGE PRESSURE AT THE5,700 BBLS. (CRUDE TYPE "SOUR 109") INTO AN AGRICULTURAL FIELD. THE EDMONTONCONTROL CENTER IMMEDIATELY SHUTDOWN THE PIPELINE AS A RESULT OF LINE PRESSUREABNORMALITIES. CALLS TO THE SUPERIOR CONTROL CENTER FROM THE LOCAL LANDOWNERSREPORTING STRONG ODORS CONFIRMED THE RUPTURE. LAKEHEAD PERSONNEL WEREIMMEDIATELY PERSONNEL WERE IMMEDIATELY CONTACTED AND LOCAL STAFF WEREDISPATCHED TO THE SITE. COUNTY AUTHORITIES WERE ALSO IMMEDIATELY CONTACTED.ONCE ON SITE, THE COMPANY AND LOCAL AGENCIES QUICKLY INFORMED THE PUBLIC INTHE AREA ABOUT THE INCIDENT, AND AS A PRECOUTIONARY MEASURE, SUGGESTED THEYEVACUATE THE TOWN OF PLUMMER, THE OIL HAD FLOWED NORTH THROUGH THEAGRICULTURAL FIELD VIA TWO MAIN DITCHES. THESE DITCHES DRAINED INTO ANOTHERDITCH ALONG COUNTY ROAD 1, THAT PHYSICALLY RAN EAST AND WEST. THE OIL FLOWEDEAST IN THIS DITCH ALONG THE COUNTY ROAD. EMERGENCY RESPONSE PERSONNEL HADQUICKLY BUILT EARTHERN DYKES ACROSS THE DITCHES WHICH KEPT THE OIL CONTAINEDWITHIN THE AGRICULTURAL FIELD AND ROADSIDE DITCH. FREE PRODUCT WAS COLLECTEDBY VACUUM TRUCKS AND TANKER TRUCKS, AND WAS SHIPPED TO TANKAGE AT LAKEHEAD'SCLEARBROOK TERMINAL FACILITY. THE PIPELINE WAS REPAIRED AND PUT BACK INTOSERVICE IN THE MORNING OF SEPTEMBER 18. THE COMPANY RECOVERED ALL FREEPRODUCT BY SUNDAY, SEPTEMBER 20, AND COMMENCED IMPLEMENTATION OF REMEDIATIONPLANS AGREED UPON WITH STATE AGENCIES.
2017-09-29 08:50 | YES | NO | 19980148 | 1998-10-19 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1998-09-19 | 2041 | WY | NATRONA |  | NO |  | NO | CONOCO PIPE LINE CO. CASPER, WY. PUMP STATION AND TANK FARM, 133N, R78W, SECTION 6 |  | TANK FARM | TANK |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | GASOLINE | 3 | 75 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDY W. BEGGS | 3036494090 | 9/19/98 15:30, CASPER GAUGE ON TANK 1083 "HUNG UP" AT 34' 9". OPERATIONSCOORDINATOR DID NOT REALIZE TANK GAUGE HAD "HUNG UP". OPERATION COORDINATORCONTINUED TO UPDATE R&D WITH TANK VOLUME FROM "HUNG" GAUGE. THIS INDICATEDROOM WAS AVAILABLE IN THE TANK. 17:41, CASPER RECEIVED HIGH TANK LEVEL ALARMON TANK 1083. OPERATIONS COORDINATOR MISTAKENLY THOUGHT THE ALARM WAS THE"HIGH TANK LIMIT ALARM" WHICH IS A SOFTWARE ALARM GENERATED WHEN THE VOLUME INTHE TANK REACHES A LEVEL THAT IS SET IN THE SCADA FOR INDIVIDUAL TANKS. THIS"HIGH TANK LIMIT ALARM" IS SET AT A VOLUME LESS THAT THE "HIGH TANK LEVELALARM" VOLUME. BECAUSE THE GAUGE HAD "HUNG UP" THERE WAS NOT A "HIGH TANKLIMIT ALARM" GENERATED. 20:41, ESTIMATED TIME TANK BEGAN TO OVERFLOW. 20:45,OPERATIONS COORDINATOR SWITCHED FROM TANK 1083 TO TANK 1079. PRODUCT WASCONTAINED IN THE TANK DIKE AND SOAKED INTO THE GROUND. CONTAMINATED SOIL WILLBE REMOVED AND DISPOSED OF PROPERLY.
2017-09-29 08:50 | NO | NO | 19980150 | 1998-10-14 | 30991 | MOBIL OIL CORPORATION | YES | 1998-09-17 | 1035 | AR | LITTLE RIVER | FOREMAN | NO |  | NO | 1 MILE SOUTH OF FOREMAN, ARKANSAS ON STATE HWY 41 AT MOBIL PIPELINE COMPANY FACILITY- FOREMAN STATION |  | PUMPING STATION | VALVE |  | 1947 | OTHER | CHECK VALVE GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 31492.0071 | 63532.0985 | CRUDE OIL | 1 | 25 | 20 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D G SCOTT | 2146585914 | GASKET FAILURE ON 16" CHECK VALVE. VALVE WAS LOCATED UNDERGROUND ON THEDISCHARGE SIDE OF THE #3 PUMP UNIT. STATION IMMEDIATELY SHUTDOWN ANDNOTIFICATION WAS MADE TO OPERATIONS CONTROL CENTER IN DALLAS, TEXAS.EMERGENCY RESPONSE PROCEDURES IMPLEMENTED. MOBIL MAINTENANCE CREWS DISPATCHEDTO LOCATION. RECOVERY AND CLEAN UP PROCEDURES INITIATED. PERMANENT REPAIRSMADE BY REPLACING FAULTY GASKET. ALL FEDERAL AND STATE AGENCIES PROPERLYNOTIFIED. NRC ASSIGNED CASE #455958. NO CRUDE OIL REACHED ANY CREEKS,STREAMS, PONDS OR LAKES. NO INJURIES OR DEATHS ASSOCIATED WITH THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 19980151 | 1998-10-26 | 4805 | EXPLORER PIPELINE CO | YES | 1998-09-23 | 1015 | TX | FANNIN |  | NO |  | NO | 2 MILES NORTH AND 1/2 MILE WEST OF INTERSECTION OF HIGHWAY 69 AND COUNTY ROAD 896, NEAR LEONARD, TEXAS. |  | LINE PIPE | PIPE |  | 1971 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 83978.6856 | 169418.9292 | OIL AND GASOLINE | 3 | 20 | 10 | NO | NO | 28 | 0.28 | 52000 | WELDED |  | 751 | 415 | YES | 24 | 1030 | 12 | 71 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | R E SANDS | 9184935106 | ON SEPTEMBER 23, 1998 EXPLORER'S MAINTENANCE CONTRACTOR BEGAN EXCAVATION ALONGTHE 28" PIPELINE FOLLOWING DISCOVERY OF REFINED PRODUCT IN AN OLD ABANDONEDHAND-DUG WATER WELL LOCATED 75 FEET EAST OF THE PIPELINE NEAR LEONARD, TEXAS.THERE WERE NO OTHER VISIBLE SIGNS OF RELEASED PRODUCT IN THE VICINITY, SOEXCAVATION ALONG THE PIPELINE RIGHT-OF-WAY WAS STARTED TO LOCATE A POSSIBLELEAK. AT APPROXIMATELY 1015 HOURS ON SEPTEMBER 23, 1998 PRODUCT WASDISCOVERED AT A LOCATION 150 FEET SOUTH OF THE ABANDONED WATER WELL SIT.VACUUM TRUCKS WERE ON SITE WHILE EXCAVATION CONTINUED UNTIL THE SOURCE OF THELEAK WAS DETERMINED TO BE A SMALL CRACK ON THE BOTTOM OF THE 28" PIPE WHERE ITWAS RESTING ON ROCK. THE LINE WAS SHUT DOWN AT 1040 HOURS SEPTEMBER 24, 1998,A FULL ENCIRCLEMENT BOLT-ON PLIDCO SPLIT SLEEVE INSTALLED AND THE LINE PLACEDBACK IN OPERATION AT 1412 HOURS THE SAME DAY. AT 24-FOOT SECTION OF THEDEFECTIVE PIPE WAS REMOVED AND REPLACED ON OCTOBER 15, 1998. CLEANUPACTIVITIES ARE BEING COORDINATED WITH THE TNRCC.
2017-09-29 08:50 | YES | NO | 19980152 | 1998-10-23 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 1998-09-11 | 1145 | NJ | CAMDEN | RUNNEMEDE | NO |  | NO | END OF ROSE AVENUE IN RUNNEMEDE, NJ |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 55985.7904 | 112945.9528 | GASOLINE | 1 | 20 | 13 | NO | NO | 16 | 0.28 | 0 | NO DATA |  | 850 | 600 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | CHARLES MASER | 2159376240 | GASOLINE WAS DISCOVERED ON THE GROUND ABOVE THE PIPELINE RIGHT OF WAY. LOCALAUTHORITIES CALLED SUN PIPE LINE. SUN PIPE RESPONDED AND UNCOVERED THE LINE.A SMALL HOLE WAS DISCOVERED. A FIELD REPAIR WAS MADE. INITIAL INSPECTIONDISCOVERED PREVIOUS DAMAGE FROM AN UNKNOWN SOURCE.
2017-09-29 08:50 | YES | NO | 19980153 | 1998-10-08 | 30755 | CITGO PRODUCTS PIPELINE CO | YES | 1998-09-30 | 715 | TX |  | MONT BELVIEU | NO |  | NO | 11140 HWY 146 |  | PUMPING STATION | OTHER | VISUAL FLOW MONITOR | 1994 | OTHER | FLOW INDICATION DEVICE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NATURAL GAS LIQUID | 2 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | M D MOSELY | 4092873594 | DEVICE THAT ALLOWS VISUAL MONITORING OF RELIEF VALVE ACTIVITY FAILED. LEAKWAS REPORTED BY TEPCO EMPLOYEE. CREW WAS DISPATCHED, ISOLATED LEAKING DEVICEAND REPAIRED.
2017-09-29 08:50 | YES | NO | 19980154 | 1998-11-07 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1998-10-07 | 1123 | KS | MCPHERSON |  | NO |  | NO | 1426 5TH AVENUE, MCPHERSON, KANSAS (SECTION 20--T 19 SOUTH-RANGE 5 WEST) |  | PUMPING STATION | OTHER | REGENERATION HEATER | 1991 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | PROPANE | 2 | 628 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH L LYBARGER | 9185735774 | AT APPROXIMATELY 11:23 (A.M) STATION PERSONNEL OBSERVED A FIRE COMING FROM THESTACK OF THE #2 REGENERATOR HEATER. HEATER PRODUCT (PROPANE) AND NATURAL GAS(FUEL) LINES TO THE HEATER WERE BLOCKED IN AND THE AREA WAS SECURED. PIPELINECONTROL (DISPATCHERS) WAS NOTIFIED. CONTROLLERS WERE KEPT INFORMED OF THESITUATION THROUGHOUT. AT 13:35 PIPELINE CONTROL TELEPHONED THE NATIONALRESPONSE CENTER WHO ASSIGNED CASE NUMBER 458914 TO THE INCIDENT. SUBSEQUENTTELEPHONE CALLS WERE MADE TO. AT 14:23 THE RELEASE WAS BROUGHT UNDER CONTROLAND AN INVESTIGATION STARTED TO DETERMINE THE CAUSE AND THE EXTENT OF THEDAMAGE TO THE HEATER. IT WAS SUBSEQUENTLY DETERMINED THAT THE ACCIDENT WASCAUSED BY OPERATOR ERROR. PRODUCT WAS INTRODUCED INTO THE HEATER UNDERPRESSURE WITH THE OUTLET VALVE CLOSED, RESULTING IN OVER-PRESSURING THEINTERNAL TUBING CAUSING IT TO BURST RELEASING HOT PROPANE INSIDE THE HEATERWHICH IGNITED. THE DAMAGE WAS CONFINED TO THE HEATER UNIT. (THE UNIT WILLNOT BE RETURNED TO SERVICE, BUT WILL BE USED AS A SOURCE OF PARTS FOR THREEOTHER REGENERATORS).
2017-09-29 08:50 | YES | NO | 19980155 | 1998-11-10 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1998-10-19 | 755 | MN |  |  | NO |  | NO | MP 0878.1, TOWNSHIP 151 N., SECTION 14, SOUTHWEST QUATER, RANGE 42 WEST, TRACT #803 |  | LINE PIPE | PIPE |  | 1994 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69982.238 | 141182.441 | NATURAL GAS LIQUID | 2 | 950 | 0 | NO | NO | 20 | 0.31 | 2028 | WELDED |  | 1460 | 596 | YES | 8 | 2122 | 10 | 94 | NO DATA | Null | YES | GALVANIC |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R C SANDAHL | 2187250102 | AT APPROXIMATELY 0755 MST ON 10/19/1998, A LANDOWNER OBSERVED A VAPOR CLOUD INHIS FIELD, DOWNSTREAM OF PLUMMER STATION. FIELD VERIFICATION WAS IMMEDIATE,AND LINE 1 WAS SHUTDOWN. THE LOCAL AUTHORITIES SECURED THE SITE. DOWNSTREAMAND NEARBY LANDOWNERS WERE EVACUATED. AT 0955 MST, THE NGL CLOUD WASIGNITED. IT BURNED THROUGH THE NIGHT UNTIL A SYNTHETIC CRUDE BATCH ARRIVED.THE SITE WAS EXCAVATED AND CONFIRMED THAT THE LEAK WAS CAUSED BY THIRD PARTYDAMAGE. REPAIRS TO THE PIPELINE WERE COMPLETED BY INSTALLING A PLIDCO REPAIRSLEEVE OVER THE LEAKING CRACK IN A GOUGE, AND FULL ENCIRCLEMENT SLEEVES OVEROTHER DENTS CAUSED BY THE EXCAVATOR. ALL SLEEVES WERE MADE PERMANENTY BYFULLY WELDING.
2017-09-29 08:50 | YES | NO | 19980156 | 1998-11-03 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1998-09-30 | 1510 |  |  |  | YES | X=274580.86 & Y=216682.40 | NO | ODYSSEY 12", MAIN PASS, BLOCK 70 |  | LINE PIPE | PIPE |  | 1968 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 280000 | 195950.2664 | 395310.8348 | CRUDE OIL | 1 | 3 | 0 | NO | NO | 12.75 | 0.41 | 52000 | WELDED |  | 1440 | 1440 | YES | 12 | 1800 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | G L ZIMMERMAN | 7132415334 | UNKNOWN STRESSES DURING HURRICANE GEORGES CAUSED REPAIR FITTING TO LEAK.
2017-09-29 08:50 | YES | NO | 19980157 | 1998-11-03 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1998-10-02 | 1510 | LA | PLAQUEMINES |  | NO |  | NO | ADAMS BAY, PLAQUEMINES PARISH, LOUISIANA |  | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 104973.357 | 211773.6615 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 12.75 | 0.25 | 52000 | WELDED |  | 720 | 111 | YES | 12 | 1600 | 0 | 62 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | G L ZIMMERMAN | 7132415334 | CONTRACTOR WORKING ON RIGHT OF WAY SPOTTED SHEEN IN WATER. PRODUCERS WERENOTIFIED IMMEDIATELY AND PIPELINE WAS SHUTDOWN. AREA OF RELEASE IS IN MARSHYAREA OF ADAMS BAY. HYDRO-TECH CLAMP INSTALLED.
2017-09-29 08:50 | YES | NO | 19980158 | 1998-11-02 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1998-10-06 | 1355 | KS | OSBORNE |  | NO |  | NO | SW 1/4, SECTION 17, TOWNSHIP 9 SOUTH, RANGE 15 WEST, OSBORNE COUNTY, KANSAS 5 MILES NORTH AND 1/2 MILE EAST OF NATOMA, KANSAS |  | PUMPING STATION | PIPE |  | 1971 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 6500 | 4548.8455 | 9176.8587 | CRUDE OIL | 1 | 275 | 0 | NO | NO | 16 | 0.25 | 46 | WELDED |  | 50 | 0 | YES | 4 | 275 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R WILKERSON | 3162419270 | THE LEAK OCCURRED IN AN ABANDONED LINE THAT CONNECTED JAYHAWK'S TWO BREAK-OUTTANKS LOCATED AT JAYHAWK'S LATON STATION. THE LINE WAS PURGED ANDDISCONNECTED FROM THE TANKS. THIS WAS CONTAINED INSIDE THE TANK DIKE AND ALLCONTAMINATED SOIL IS BEING REMEDIATED ON SITE.
2017-09-29 08:50 | NO | NO | 19980159 | 1998-11-03 | 26041 | GATX TERMINALS CORP | NO | 1998-09-30 | 415 | NJ | MIDDLESEX | CARTERET | NO |  | NO | GATX TERMINALS CORPORATION PLANT SITE, SUN PIPELINE, NEAR TANK 260-2. |  | TANK FARM | WELDING FITTING |  |  | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 36 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | CHRISTOPHER D CARY | 7329695719 | OPERATOR SWITCHED VALVES TO PUMP PRODUCT INTO TANK 260-2. VALVE AT TANK WASCLOSED, THIS CAUSED LINE TO OVERPRESSURIZE. TWO GASKETED BOLTED FLANGES BLEWTHEIR GASKETS AND OIL SPRAYED ONTO ADJACENT AREAS.
2017-09-29 08:50 | YES | NO | 19980160 | 1998-11-10 | 2331 | CHEVRON USA INC - EASTERN REGION | NO | 1998-10-01 | 1630 |  |  |  | YES | X=2,617,220 Y=64,947 | YES | SOUTH PASS BLOCK 77; OCS G-2940 AT A LOCATION 50' SOUTH OF SOUTH PASS 77 "A" PLATFOR (SEE ATTACHED SKETCH) |  | LINE PIPE | OTHER | PRESSURE BALANCE SAFETY | 1992 | OUTSIDE FORCE DAMAGE | MUDSLIDE | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 3000000 | 2099467.1403 | 4235473.2301 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 10 | 0.5 | 42000 | OTHER |  | 1440 | 0 | YES | 8 | 2160 | 9 | 92 | NO DATA | Null | Null | NO DATA |  | MUDSLIDE |  | Null | ONE CALL |  | Null | Null | PAUL JOHNSTON | 5045926317 | OPERATIONS PUT SMALL AMOUNT OF NATURAL GAS INTO PIPELINE DURING DAMAGEASSESSMENT AFTER HURRICANE GEORGES. OPERATIONS SAW GAS BUBBLES ON SURFACE OFWATER ABOUT 50 FEET SOUTH OF SP 77 "A" PLATFORM. ASSUME THAT PIPELINE WASDAMAGED BY A MUDSLIDE EVENT THAT OCCURRED DURING HURRICANE GEORGES.INVESTIGATION OF SITE REVEALED THAT PIPELINE SEPARATED AT THE PBSJ LOCATEDABOUT 50' FROM THE RISER. SINCE UNABLE TO FIND THE PIPELINE SIDE OF THEBREAK, INSTALLED NEW PIPELINE SECTION FROM RISER AT SP 77 "A" OUTAPPROXIMATELY 2,000' AND TIED INTO THE EXISTING PIPELINE.
2017-09-29 08:50 | YES | NO | 19980161 | 1998-11-16 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1998-10-07 | 315 | OK | TULSA | OKLAHOMA | NO |  | NO | NW/4 SECTION 30, TOWNSHIP 18 NORTH, RANGE 13 EAST TULSA COUNTY, OKLAHOMA (POLE CAT CREEK) MILE POST 87.3 |  | LINE PIPE | NO DATA |  | 1970 | OUTSIDE FORCE DAMAGE | WASHOUT | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 139964.476 | 282364.882 | PROPANE | 2 | 1500 | 0 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 899 | 368 | YES | 8 | 1124 | 8 | 84 | NO DATA | Null | Null | NO DATA |  | WASHOUT |  | Null | NO DATA |  | Null | Null | VANCE WEBB | 5807674845 | ON OCTOBER 6, 1998, CONOCO PIPELINE (CPL) OIL MOVEMENTS GROUP LOCATED INHOUSTON, TEXAS, RECEIVED A DEVIATION ALARM ON ITS SCADA SYSTEM. THE ALARMINDIATED A PRESSURE DEVIATION ON THE NO. 2 GLENPOOL, OKLAHOMA TO WOOD RIVER,ILLINOIS 10" PIPELINE, NEAR GLENPOOL STATION. UPON RECEIVING THE ALARM, OILMOVEMENTS INITATED EMERGENCY SHUT DOWN PROCEDURES FOR THE SYSTEM, WHICHINCLUDES LINE ISOLATION BY REMOTELY OPERATED BLOCK VALVE. DURING THE SHUTDOWNPROCEDURE EMERGENCY RESPONSE PERSONNEL WERE NOTIFIED OF THE POSSIBILITY OF ARELEASE AND DISPATCHED TO THE SUSPECT LOCATION. RESPONSE PERSONNEL BEGANSYSTEMATIC SEARCH FOR THE ACTUAL RELEASE LOCATION BY CLOSING MANUALLY OPERATEDBLOCK VALVES AND WALKING THE PIPELINE. AFTER SEVERAL SWEEPS OF THE SUSPECTLINE SEGMENT, DETECTION EQUIPMENT CONTINUALLY PICKED UP FAINT SIGNALS THATINDICATED THE PRESENCE OF A HYDROCARBON AROUND THE POLE CAT CREEK SUBSURFACELINE CROSSING. AT PRESENCE OF A HYDROCARBON AROUND THE POLE CAT CREEKSUBSURFACE LINE CROSSING. AT 6:03 A.M. EMERGENCY RESPONSE PERSONNEL CONFIRMEDTHE RELEASE LOCATION AS THE POLE CAT CREEK CROSSING. THIS WAS EVIDENCED BYOCCASIONAL BUBBLES ON THE WATER SURFACE NEAR THE APPROXIMATE LOCATION OF THEPIPELINE CROSSING. THIS DETERMINATION WAS DIFFICULT AS THE CREEK WAS ABOVEFLOOD STAGE AND THE WATER EXTREMELY FAST AND TURBULENT, DUE TO RECENTTORRENTIAL RAINS IN THE AREA. THE FAILURE LOCATION WAS FURTHER CONFIRMED BYDISPLACING THE LINE WITH NITROGEN AND WATCHING FOR ADDITIONAL BUBBLES. THEFAILURE WAS DISPLACING THE LINE WITH NITROGEN AND WATCHING FOR ADDITIONALBUBBLES. THE FAILURE WAS DETERMINED TO BE THE RESULT OF EXCESSIVE EXTERNALFORCES BROUGHT ABOUT THE FLOODWATERS AND DEBRIS IMPACT UPON PIPELINE AFTER THEERROSIONAL FORCES OF THE WATER EXPOSED IT. TO PREVENT FUTURE OCCURENCES OFTHIS TYPE OF FAILURE, THE CROSSING WAS REPLACED BY DIRECTIONALLY DRILLING ANDINSTALLING NEW PIPE 30 FEET BELOW THE FLUIDIZED BED OF THE CREEK.
2017-09-29 08:50 | YES | NO | 19980162 | 1998-12-01 | 443 | AMOCO PIPELINE CO | YES | 1998-10-28 | 1234 | MO | SALINE |  | NO |  | NO | MISSOURI, SALINE COUNTY, HWY EE & COUNTY ROAD 328 |  | LINE PIPE | PIPE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | CRUDE OIL | 1 | 200 | 200 | NO | NO | 24 | 0.28 | 52000 | NO DATA |  | 1070 | 350 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | FRED WILLIAMSON | 8168995600 | CONTRACTOR, INSTALLING FIELD TILE FOR LANDOWNER, HIT PIPELINE WITH ATRENCHING/DITCHING MACHINE. APL HAD PREVIOUSLY LOCATED PIPELINE IN ADIFFERENT LOCATION AND WAS ON SITE FOR TILE CROSSING. CONTRACTOR INFORMED APLEMPLOYEE THAT HIS WORK WAS COMPLETED. AFTER APL EMPLOYEE LEFT, CONTRACTORINDEPENDENTLY STARTED TO MAKE A SECOND CROSSING APPROXIMATELY A QUARTER OF AMILE AWAY IN THE SAME FIELD. AT WHICH TIME, THE PIPELINE WAS DAMAGED. DAMAGECONSISTED OF A 3" GOUGE AT THE 2 O'CLOCK POSITION, PENETRATING THE PIPE WALL.
2017-09-29 08:50 | YES | NO | 19980163 | 1998-11-23 | 2331 | CHEVRON USA INC - EASTERN REGION | YES | 1998-10-05 | 1700 |  |  |  | YES | 28.56.44.4(LAT)89.16.47.9 | YES | ORIGINAL SPILL AREA ENCOMPASSES AN AREA FROM PASS TANTE PHONE (MS DELTA AREA) TO BLIND BAY FROM LAT. 28.53 LONG 89.08 TO LAT. 28.38 LONG 89.35 IN LENGTH |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | MUDSLIDE | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | 0 | 0 | 0 | 0 | 0 | 0 | 6500000 | 4548845.4707 | 9176858.6653 | CRUDE OIL | 1 | 8212 | 65 | NO | NO | 10 | 0.5 | 35000 | WELDED |  | 1440 | 139 | YES | 24 | 2203 | 6 | 80 | NO DATA | Null | Null | NO DATA |  | MUDSLIDE |  | Null | NO DATA |  | Null | Null | STEPHEN J MOLLOY | 5045927688 | AFTER THE PASSAGE OF HURRICANE GEORGES INTO THE GULF OF MEXICO AND INLAND ONSEPTEMBER 28TH, 1998, CHEVRON PIPE LINE BEGAN ONSHORE/OFFSHORE PIPELINE ANDCOMMUNICATIONS CHECK ON SEPTEMBER 29TH ON THE SOUTH PASS 49 OFFSHORE (MC109,MC20, SP49A AND SP45) AND SOUTH PASS 49 ONSHORE SYSTEMS. DURING PUMPINGOPERATIONS TO THE 10" SOUTH PASS 49 PIPELINE SYSTEM, WHICH BEGAN ON SEPTEMBER30TH, MC109, BRITISH PETROLEUM'S (BP) OFFSHORE PLATFORM, WAS TOLD TO SHUTDOWNPUMPING OPERATIONS AT APPROXIMATELY 2000 HRS IN ORDER TO INVESTIGATE APOSSIBLE PROBLEM ON THE SYSTEM. ON OCTOBER 1ST, 1030 HRS, BRITISH PETROLEUMREPORTED AN OIL RELEASE INTO THE GULF OF MEXICO FROM THEIR MC109 LATERALPIPELINE, WHICH WAS SPOTTED BY AN USCG OVERFLIGHT IN THE WD 143 BLOCK AREA.BP, IN COORDINATION WITH USCG AND MMS, BEGAN OIL SPILL EMERGENCY OPERATIONS,INCLUDING SPILL CONTAINMENT, RECOVERY AND AREA PROTECTION OF THE SHORELINE INRESPONSE TO THE SPILL OF CRUDE OIL REPORTED TO THE USCG AND NATIONAL RESPONSECENTER ON OCTOBER 1. SPILL RESPONSE OPERATIONS INCLUDED THE USE OF A CONTRACTAIRCRAFT (DC 3 AND DC 4) FOR COREXIT 9550 OIL SPILL DISPERSENT OPERATIONS (ASAPPROVED BY USCG MSO IN MORGAN CITY, LA), AND MSRC AND NRC SKIMMING ANDBOOMING OFFSHORE, AND NEAR SHORE SHORELINE PROTECTION OPERATIONS. ON OCTOBER4TH, AFTER NO VISUAL DAMAGE TO BP'S PIPELINE SEGMENT COULD BE FOUND, BP ANDCHEVRON PIPE LINE DEVELOPED PROCEDURES FOR PERFORMING A PIPELINE PRESSURE TESTOF THE 10" PIPELINE FROM SP49A PLATFORM TO THE SP49 ONSHORE FACILITY. TESTWAS OBSERVED IN SP BLOCK 38, WHICH WAS IMMEDIATELY RESPONDED TO BY BP AND WASESTIMATED AT APPROXIMATELY 85 BARRELS. SKIMMING OPERATION CONTINUED UNTILDARK, CONCLUDING WITH APPROXIMATELY 65 BARRELS OF OIL RECOVERED. (NOTE: TOTALSPILL VOLUME IS ESTIMATED TO BE 8212 BARRELS WITH 65 BARRELS RECOVERED)
2017-09-29 08:50 | YES | NO | 19980164 | 1998-11-25 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1998-10-30 | 1200 | NY | MONROE |  | NO |  | NO | SEE ATTACHED DRAWING NUMBER 11815-A | 461832 | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | CORROSION, EXTERNAL | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 104973.357 | 211773.6615 | KEROSENE | 1 | 30 | 19 | NO | NO | 8 | 0.2 | 2170 | WELDED |  | 275 | 0 | YES | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | CARL A OSTACH | 6107704495 | ON OCTOBER 28, 1998, A BUCKEYE CORROSION TECHNICIAN WAS TAKING ROUTINEPIPE-TO-SOIL READINGS ON THE ROCHESTER TERMINAL DELIVERY LINES WHEN HE NOTICEDCASING GREASE COMING OUT OF A CASING VENT PIPE. THE CORROSION TECHNICIANCALLED BUCKEYE'S AREA SUPERVISOR TO REPORT THE CONDITION. ON OCTOBER 29,1998, THE BUCKEYE'S MAINTENANCE CREW BEGAN ON-SITE INVESTIGATION ANDEXCAVATION ACTIVITY. ON OCTOBER 30, 1998, IT WAS DETERMINED THAT A PIPEFAILURE OCCURRED ON BUCKEYE'S 8" DELIVERY LINE TO A LOCAL SHIPPER BULKTERMINAL. THE 8" DELIVERY LINE WAS CUT AND PULLED FROM ITS CASING. A BOLTFROM A "THINSULATOR" WAS FOUND TO BE IN CONTACT WITH THE CARRIER PIPE,RESULTING IN A HOLE CAUSING BY CORROSION AT THE POINT OF CONTACT. THE FAILEDSECTION OF CARRIER PIPE WAS CUT OUT AND THEN REPLACED WITH A CERTIFIEDHYDROSTATICALLY TESTED PIPE SECTION. THE REMAINING ORIGINAL CARRIER PIPEINSIDE THE CASING WAS HYDROSTATICALLY PRESSURE TESTED ANF FOUND TO BE IN GOODCONDITION. BUCKEYE HAS FIVE PIPELINES WHICH CROSS UNDER THE RAILROAD TRACKSAT THIS LOCATION. THE FIVE PIPELINES ARE IN INDIVIDUAL CASINGS SURROUNDED BYA 42-INCH OUTER CASING. BEFORE RETURNING TO SERVICE, HIGH DIELECTRIC FILLERWAS INJECTED INTO ALL FIVE INDIVDUAL CASINGS, AS WELL AS THE 42-INCH OUTERCASING. THE DELIVERY LINE WAS PUT BACK INTO SERVICE ON NOVEMBER 10, 1998.ALL APPLICABLE AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WEREPERFORMED UNDER THE SUPERVISION OF THE NEW YORK DEPARTMENT OF ENVIRONMENTALCONSERVATION AND THE NEW YORK PUBLIC SERVICE COMMISSION.
2017-09-29 08:50 | YES | NO | 19980165 | 1998-12-02 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1998-11-06 | 1230 | TX | HARRIS |  | NO |  | NO |  |  | TANK FARM | PUMP |  |  | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIESEL FUEL | 1 | 160 | 160 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D F SHEAFF SR | 7132414381 | DURING VALVE MAINTENANCE ON PLANT PIPING, A SECTION OF THE LINE WAS ISOLATEDWITHOUT THERMAL RELIEF. THERMAL EXPANSION CAUSED THE CASING ON THE BOOSTERPUMP TO FAIL. PRODUCT WAS RELEASED AND A COUPLE OF GALLONS FOUND ITS WAY INTOHUNTING BAYOU, WHICH RUNS THROUGH THE MIDDLE OF EAST HOUSTION TANK FARM. THEPRODUCT WAS PICKED UP AND THE BAYOU WAS CLEANED UP IMMEDIATELY.
2017-09-29 08:50 | YES | NO | 19980166 | 1998-12-02 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 1998-10-26 | 630 | CA | KERN |  | NO |  | NO | SEC 6 T12N-R22W, 1/2 MI NORTH OF THE HWY 166 & 2.5 MILES EAST OF BASIC SCHOOL ROAD |  | LINE PIPE | PIPE |  | 1952 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | CRUDE OIL | 1 | 1959 | 400 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | G L ZIMMERMAN | 7132415334 | FARMING OPERATION STRUCK AND PUNCTURED PIPELINE WITH DEEP (0R CHISEL) PLOWMANAGER OF FARMING OPERATION UTILIZED ONE-CALL SYSTEM (USA). PIPELINETEMPORARILY MARKED AND LOCATION COMMUNICATED, FACE-TO-FACE, TO MANAGER BYEQPL. PLOW OPERATOR WAS AWARE OF LOCATION OF PIPELINE IN FIELD (A PORTION OFFIELD ALREADY PLOWED ON THE PREVIOUS DAY(S), WITH PIPELINE SAFELY TRAVERSED.IT WAS PRE-DAWN(DARK) WHEN PLOW OPERATOR INADVERTENTLY STRUCK PIPELINE. PLOWOPERATOR DID NOT REALIZE PIPELINE HAD BEEN STRUCK (RELEASE), HOWEVER, SAMEMANAGER WAS NEARBY AND IMMEDIATELY CALLED EQPL, USING PHONE NUMBER PROVIDEDWHEN PIPELINE WAS MARKED.
2017-09-29 08:50 | YES | NO | 19980167 | 1998-12-03 | 31193 | PRIDE PIPELINE CO | YES | 1998-11-12 | 1230 | TX | JONES |  | NO |  | NO | APPROXIMATELY 5 MILES NORTH OF TRENT, TX ON FM RD 1085 TO COUNTY RD 401 APPROXIMATELY 2 MILES ON EAST SIDE OF ROAD. |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 1 | 165 | 0 | NO | NO | 4.25 | 0.25 | 0 | NO DATA |  | 50 | 50 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON | 9156748231 | AT APPROXIMATELY 12:30 PM SPILL WAS DISCOVERED. THE LINE WAS SHUT DOWN ANDCREWS WERE DISPATCHED TO CLAMP THE LEAK AND BEGIN CLEAN=UP. SITE WILL BECLEANED TO MEET STATE WIDE RULEE #91.
2017-09-29 08:50 | YES | NO | 19980168 | 1998-12-03 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1998-11-15 | 1105 | TX | WEBB |  | NO |  | NO | 2 1/2 MILES NE OF OILTON, TX. LOCATED ON KOCH R.O.W. |  | LINE PIPE | PIPE |  | 1940 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 126 | 5 | NO | NO | 8 | 0.32 | 0 | WELDED |  | 720 | 100 | YES | 0 | 0 | 0 | 0 | INTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null
2017-09-29 08:50 | YES | NO | 19980169 | 1998-12-03 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1998-10-30 | 410 | TX | DUVAL |  | NO |  | NO | KOCH DUVAL STATION LOCATED 1/2 MILE W HWY 59 FREER, TX |  | PUMPING STATION | PIPE |  | 1960 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 405 | 35 | NO | NO | 6 | 0.25 | 2641 | WELDED |  | 0 | 80 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JASON HILL | 5123947961 | LEAK WAS A RESULT OF TWO EXTERNAL CORROSION PITS ON UNDERSIDE OF 6" STATIONTRUCK LINE.
2017-09-29 08:50 | YES | NO | 19980170 | 1998-12-03 | 30991 | MOBIL OIL CORPORATION | YES | 1998-11-08 | 530 | TX | GAINES |  | NO |  | NO | MOBIL PIPELINE COMPANY-SEMINOLE STATION FACILITY-APPROX 3 MILES SOUTH OF SEMINOLE TEXAS ON STATE HWY 385. FACILITY IS LOCATED ON THE WEST SIDE OF HWY. |  | TANK FARM | PIPE |  | 1940 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 1 | 150 | 100 | NO | NO | 16 | 0.25 | 35000 | WELDED |  | 25 | 25 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D G SCOTT | 2146585914 | LEAK OCCURRED ON 16" SUCTION FILL LINE TO TANK NUMBER 1878. INTERNALCORROSION. OIL CONTAINED ON STATION FACILITY. TEMPORARY REPAIRS MADE. LEAKCLAMP INSTALLED. OILY SOIL BLENDED TO LESS THE 1%. ALL NOTIFICATIONS MADE TO
2017-09-29 08:50 | YES | NO | 19980173 | 1998-12-16 | 30991 | MOBIL OIL CORPORATION | YES | 1998-11-10 | 800 | TX | MIDLAND |  | NO |  | NO | 2200 COUNTY ROAD 90 EAST, APPROXIMATELY 2 MILES EAST OF MIDLAND, TEXAS. MOBIL PIPE LINE COMPANY TANK FARM FACILITY |  | TANK FARM | OTHER | 10" TEX-MEX DELIVERY LINE | 1940 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | CRUDE OIL | 1 | 50 | 35 | NO | NO | 10 | 0.25 | 35000 | WELDED |  | 25 | 25 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D G SCOTT | 2146585914 | ON NOVEMBER 10, 1998 THE PIPELINE PATROL PILOT REPORTED A LEAK ON THE MIDLANDTANK FARM. STATION PERSONNEL DETERMINED THAT THE LEAK WAS ON THE 10" TEX-MEXDELIVERY LINE. THE TEX-MEX DISPATCHER WAS NOTIFIED TO IMMEDIATELY SHUT DOWNTHEIR DELIVERY. OIL CONTAINED ON STATION FACILITY. TEMPORARY REPAIRS MADEUSING LEAK CLAMP. OILY SOIL BLENDED TO LESS THAN 1%. ALL NOTIFICATIONS MADETO REGULATORY AGENCIES.
2017-09-29 08:50 | YES | NO | 19980174 | 1998-12-07 | 5083 | FARMLAND INDUSTRIES INC | YES | 1998-11-17 | 2000 | KS | MONTGOMERY | COFFEYVILLE | NO |  | NO | SECTION 30, TOWNSHIP 34, RANGE 17 OF MONTGOMERY COUNTY KANSAS | 601861 | LINE PIPE | PIPE |  | 1977 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 699.8224 | 1411.8244 | CRUDE OIL | 1 | 5000 | 780 | NO | NO | 12 | 0.25 | 1186 | WELDED |  | 220 | 28 | YES | 24 | 394 | 1 | 1975 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES SCOTT THOMPSON | 9183334111
2017-09-29 08:50 | YES | NO | 19990002 | 1998-12-16 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1998-11-17 | 900 | KS | RICE |  | YES | N | NO | NE 1/4, SECTION 4, TOWNSHIP 20 SOUTH, RANGE 9 WEST, RICE COUNTY, KANSAS 6 MILES WEST AND 1/4 MILE SOUTH OF LYONS, KANSAS |  | PUMPING STATION | PIPE |  | 1943 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5598.579 | 11294.5953 | CRUDE OIL | 1 | 1303 | 1233 | NO | NO | 12 | 0.31 | 35000 | WELDED |  | 200 | 0 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R WILKERSON | 3162419270 | THE COMMON LINE (BEING SUCTION AND DISCHARGE) TO TANK C-7 AT JAYHAWK'S CHASEII PUMP STATION LEAKED INTERNAL CORROSION. ALL OIL EXCEPT 5 BARRELS (WHICHLEAKED OUT DIKE DRAIN) WAS CONTAINED INSIDE THE TANK DIKE. MOST OF THE OILWAS RECOVERED AND SOIL REMEDIATION WILL BE DONE INSIDE DIKE FOR FINALCLEANUP. FIVE FEET OF NEW PRESSURE TESTED PIPE WAS INSTALLED AND A PRESSURETEST WILL BE DONE ON THE REST OF THE PIPE BEFORE BEING PUT BACK INTO SERVICE.
2017-09-29 08:50 | YES | NO | 19990003 | 1998-12-23 | 3012 | PRIDE TEXAS PLAINS L.P. | NO | 1998-11-02 | 1030 | TX |  | JONES | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | CRUDE OIL | 3 | 1000 | 0 | NO | NO | 10.75 | 0.37 | 25000 | THREADED |  | 600 | 350 | YES | 8 | 0 | 0 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON | 9156748231 | LEAK WAS FIRST DISCOVERED ON 11/2/98 AND THOUGHT TO BE LESS THAN 5 BBLS.WHILE PREPARING FOR PERMANENT REPAIRS BY REPLACING 420' OF PIPE ON 12-7-98 ITWAS DISCOVERED THAT THE CONTAMINATION AREA WAS MUCH GREATER THAN EXPECTED.THEREFORE, WE CONTACTED THE LOCAL TEXAS RAILROAD COMMISSION OFFICE ANDREPORTED THE SPILL ON 12/8/98. SOIL SAMPLES ARE BEING TAKEN TO DETERMINE THECONTAMINATION AREA, AND ALSO TO DETERMINE IF THIS IS A SITE OF A PAST LEAK.WE ARE NOW IN THE PROCESS OF IDENTIFYING AND TESTING THE AREA FORCONTAMINATION AND BEGINNING CLEAN UP OF THE AREA.
2017-09-29 08:50 | YES | NO | 19990004 | 1998-12-23 | 3012 | PRIDE TEXAS PLAINS L.P. | NO | 1998-11-26 |  | TX |  | KING | NO |  | NO | SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | CRUDE OIL | 3 | 790 | 400 | NO | NO | 10.75 | 0.37 | 25000 | WELDED |  | 600 | 300 | YES | 8 | 0 | 0 | 76 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JOHN T MACON | 9156748231 | LEAK WAS DISCOVERED AT APPROXIMATELY 2:30 PM ON 11-26-98. TEMPORARY REPAIRSWERE MADE 11-27-98, PERMANENT REPAIRS WILL BE SCHEDULED AT A LATER DATE.CLEAN UP IN UNDERWAY.
2017-09-29 08:50 | YES | NO | 19990005 | 1998-12-31 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1998-11-25 | 1141 | TX | GONZALES |  | NO |  | NO | 4 MILES NORTH OF NIXON, TX ON SH 80, 0.35 MILES EAST ON CR131, 200 YARDS SOUTH OF COUNTY ROAD |  | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 17495.5595 | 35295.6103 | CRUDE OIL | 1 | 199 | 0 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1440 | 600 | YES | 0 | 0 | 0 | 0 | EXTERNAL | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID FRITSCHE | 4095354855 | KOCH'S PATROL PILOT SPOTTED STAINED VEGTATION WHILE PATROLING THE SECTION OFPIPE. KOCH'S PERSONNEL RESPONDED TO THE SITE AND CONFIRMED THE OIL SPILL.THE PIPE WAS EXCAVATED AND REPAIRED.
2017-09-29 08:50 | YES | NO | 19990006 | 1999-01-04 | 26145 | TOSCO CORP | NO | 1998-12-23 | 1030 | CA | KERN |  | NO |  | NO | SECTION 22 TR23E MDM; APPROXIMATELY 1.5 MILES SW/TAFT, CALIFORNIA IS UNINCORPORATED AREA OF KERN COUNTY | 605569 | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 27992.8952 | 56472.9764 | CRUDE OIL | 1 | 142 | 142 | NO | NO | 0 | 0.32 | 35000 | WELDED |  | 750 | 45 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | PETER SCHNIEDERS | 8055477200 | AT APPROXIMATELY 1030 ON 12-23-98, THE TOSCO PIPELINE CONTROLLER THE TOSCOTAFT DISTRICT OFFICE THAT A CRUDE OIL RELEASE HAD BEEN REPORTED IN THE TAFT,CA AREA. THE REPORT WAS IMMEDIATELY INVESTIGATED BY THE TOSCO HEAD GAUGER.THE TOSCO TAFT DISTRICT FOREMAN ORDERED THE MIDWAY GATHERING PIPELINE(PIPELINE WITH THE POTENTIAL RELEASE) TO BE IMMEDIATELY SHUTDOWN, LOCKED-OUTAND TAGGED-OUT. THE RELEASE WAS LOCATED AT APPROXIMATELY 1200 AND ITAPPEARED TO HAVE ORIGINATED FROM THE UNOCAP GATHERING LINE #155, OPERATED BYTOSCO. APPROXIMATLEY ONE HUNDRED (100) BARRELS OF SAN JOAQUIN HEAVY CRUDE OILWAS RELEASED TO SOIL. NO WATER WAS IMPACTED OR THREATENED. TOSCO ANDCONTRACT PERSONNEL WERE NOTIFIED AND DIRECTED TO REPORT TO THE SITE. ALLREQUIRED AGENCY NOTIFICATIONS WERE MADE. AN EMERGENCY EXCAVATION NOTICE WASFILED. A QUALIFIED BIOLOGIST, DR. DIANNE MITCHELL, WAS CALLED TO THE SITE TOCONSULT ON ENVIRONMENTAL ISSUES AND PROVIDE CLEANUP ADVICE. THE RESPONDERSEXCAVATED THE PIPELINE AND REPLACED APPROXIMATELY 21 FEET OF PIPE.
2017-09-29 08:50 | YES | NO | 19990007 | 1999-01-13 | 2552 | COLONIAL PIPELINE CO | Null | 1998-11-18 | 916 | NC |  |  | NO |  | NO | COLONIAL PIPELINE CO. 411 GALLIMORE DAIRY RD, GREENSBORO, NC 27409 |  | TANK FARM | TANK |  | 1962 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 98000 | 68582.5933 | 138358.7922 | GASOLINE | 1 | 34 | 34 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | OTHER | TANK FLOOR DAMAGE | Null |  |  | Null | Null | STEPHEN E GILLIAM | 4048412314 | DURING ROUTINE TANK VISUAL INSPECTION, PRODUCT WAS DISCOVERED LEAKING AT BASEOF TANK. THE LEAK WAS DISCOVERED AT APPROXIMATELY 0916. THE LOCAL OPERATORIMMEDIATELY STARTED GRAVITATING PRODUCT TO ANOTHER TANK (TANK NO. 811). THEOPERATOR CONTACTED THE ATLANTA CONTROL CENTER ADVISED HIS/HER OF THESITUATION. SWITCHED INTO TANK 811 IN ORDER TO EXPEDITE EMPTYING OF TANK 815.TANK 815 WAS EMPTY AT 1500 HOURS. REMEDIATION OF TANK BEGAN ON 11/19/1998 ANDTANK 815 IS OUT OF SERVICE UNTIL REPAIRS ARE COMPLETED DUE TO THE ESTIMATE OF REPAIRS EXCEEDING $50,000 THE TELEPHONE REPORT WAS MADE ON 12/14/98 REPORT NO. 467511..
2017-09-29 08:50 | YES | NO | 19990008 | 1999-01-12 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1998-12-29 | 830 | TX | NUECUES |  | NO |  | NO | SW OF CC INTERNATIONAL AIRPORT ON MCGLOIN ROAD |  | LINE PIPE | VALVE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13996.4476 | 28236.4882 | L. P. G. | 2 | 1000 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | DEHUNT JR | 5128662190 | CONTRACTOR DIGGING OUT 6' VALVE AND HIT 1/2 VALVE ON SIDE OF PIPE.
2017-09-29 08:50 | YES | NO | 19990009 | 1999-01-11 | 443 | AMOCO PIPELINE CO | YES | 1998-12-02 | 958 | IL | COOK | LEMONT | NO |  | NO | APPROXIMATELY 1000 FEET NORTHEAST OF INTERSECTION OF ARCHER AVE AND STATE STREET OFF ARCHER. |  | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 104973.357 | 211773.6615 | FUEL OIL | 1 | 520 | 261 | NO | NO | 8 | 0.22 | 35000 | WELDED |  | 1219 | 527 | YES | 8 | 1556 | 0 | 95 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | FRANK STAAB | 8154786121 | THIRD PARTY SEWER CONTRACTOR INSTALLING SANITARY SEWER SYSTEM IN DEVELOPINGRESIDENTIAL AREA STRUCK AND PUNCTURED PIPELINE WITH TRACKHOE EXCAVATOR DURINGEXCAVATION. AMOCO REPRESENTATIVE MET WITH FOREMAN OF THIRD PARTY CONTRACTORAT SITE PREVIOUS TO RELEASE. AT THAT TIME THE CONTRACTOR INDICATED THAT HEWOULD NOT BE EXCAVATING TOWARD AMOCO'S PIPELINE THAT DAY. AMOCO PERSONNELLEFT THE SITE AND MINUTES LATER THE CONTRACTOR BEGAN EXCAVATING NEAR AMOCOPIPELINE. UPON RUPTURE, PIPELINE PRODUCT WAS RELEASED TO SEWER EXCAVATIONTRENCH AND TO THE SANITARY SEWER SYSTEM WHICH WAS PARTIALLY INSTALLED ANDCONNECTED TO EXISTING ACTIVE SANITARY SEWER SYSTEM.
2017-09-29 08:50 | YES | NO | 19990010 | 1999-02-02 | 22610 | WILLIAMS PIPELINE CO | YES | 1998-12-31 | 1530 | OK | TULSA |  | NO |  | NO | WILLIAMS PIPELINE COMPANY WEST TULSA TERMINAL, 2120 SOUTH 33RD WEST AVENUE, TULSA OK 74107 |  | TANK FARM | TANK |  | 1937 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY NATURAL FORCES | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 3950 | 2764.2984 | 5576.7064 | GASOLINE | 1 | 94 | 94 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | KENNETH L LYBARGER | 9185735774 | APPROXIMATELY ONE WEEK PRIOR TO THE RELEASE THE GAUGE ASSEMBLY FROZE DUE TOCOLD TEMPERTURES. OPERATORS ON DUTY THAWED THE ASSEMBLY, ADJUSTED THE LINEAND HAND-LINED THE TANK, BUT FAILED TO NOTICE THE COVER ON THE FLOAT WELLINSIDE THE TANK HAD COME OFF. ON DECEMBER 31 THE TANK WAS BEING FILLED WITHUNLEADED GASOLINE. DURING THE FILLING OPERATION, THE OPERATORS REALIZED THEFLOW RATE INTO THE TANK WAS EXCEEDING THE READING INDICATED ON THE GAUGE, ANDTHAT THE TANK GAUGE WAS FAILING TO RISE WITH THE LEVEL OF THE PRODUCT.REALIZING THE TANK WAS NEARING ITS CAPACITY, THE OPERATORS SHUT DOWN THE PUMPSDELIVERING PRODUCT INTO THE TANK. AN OPERATOR DROVE TO THE TANK TO MAKE AVISUAL ASSESSMENT. AS THE OPERATOR ARRIVED AT THE TANK, HE NOTICED PRODUCTBEGINNING TO FLOW FROM THE VENTS ON TOP OF THE TANK. A VACUUM TRUCK WASIMMEDIATELY DISPATCHED AND INITIATED RECOVERY OF PRODUCT. APPROXIMATELY 80BARRELS OF PRODUCT WAS RECOVERED BY THE VACUUM TRUCK, AND ANOTHER 14 BARRELSWAS RECOVERED THROUGH SOIL EXCAVATION, BRINGING THE TOTAL AMOUNT OF PRODUCTRECOVERED TO 94 BARRELS.
2017-09-29 08:50 | YES | NO | 19990011 | 1999-02-02 | 15490 | PHILLIPS PIPE LINE CO | YES | 1998-12-26 | 1330 | TX | LAMB |  | NO |  | NO | OLTON PUMP STATION- MEXTEX LINE 80 PIPELINE-SRW 37-22- MP 169-11+60 SEC. 21, BLOCK T-1,T.A. THOMPSON SURVEY, LAMB CO, TX 4 M SOUTH AND 1 MILE EAST/SPRINGLAKE |  | PUMPING STATION | VALVE |  | 1988 | OTHER | FAILURE OF BONNET ON 8" | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 33500 | 23444.0497 | 47296.1177 | NATURAL GAS LIQUID | 2 | 2500 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J SCHMITZ | 9186614814 | A NEIGHBOR CALLED TO ADVISE THAT SOMETHING WAS BEING RELEASED AT THE PUMPSTATION. THE PIPELINE WAS NOT OPERATING AT THE TIME AND WAS BLOCKED IN.PERSONNEL DISCOVERED THAT THE BONNET, HAND WHEEL AND GATE SLABS OF AN 8' 600"WKM MODEL D VALVE HAD BEEN EXPELLED FROM THE VALVE BODY ALLOWING PRODUCT TOVENT. NO POSITIVE DETERMINATION OF FAILURE MODE HAS BEEN MADE, BUT THEPRESENCE OF A GAP BETWEEN THE VALVE BODY AND TOPWORKS IS A VISBLE PRECURSOR.
2017-09-29 08:50 | YES | NO | 19990012 | 1999-02-09 | 400 | AMERICAN PETROFINA PIPELINE CO | NO | 1999-01-01 | 2230 | TX | ROBERTSON |  | NO |  | NO | APPROX 1.25 MI WEST OF OSR (OLD SAN ANTONIO RD), HWY IN ROBERTSON COUNTY, 7.25 MI NE OF OSR/190 & 6 HWY INTERSECTION, AT BENCHLEY |  | LINE PIPE | PIPE |  | 1928 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 475000 | 328251.0649 | 662214.9837 | CRUDE OIL | 1 | 50 | 3 | NO | NO | 10 | 0.31 | 35000 | WELDED |  | 1050 | 809 | YES | 8 | 1347 | 3 | 89 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB REED | 9152639256 | AT 1030PM, ON JAN. 1, WANDA TODD, A LANDOWNER THROUGH WHOSE PROPERTY THISPIPELINE IS ROUTED, CALLED FINA'S "800" PHONE NUMBER, WHICH IS THE PIPELINE'SBIG SPRING, TX, CONTROL CENTER NUMBER, AND REPORTED PETROLEUM ODOR. THERE WASNO INDICATION OF A PROBLEM ON THIS PIPELINE, EITHER BY PRESSURE DROP OR BY"SHORTAGE" OF RECEIPTS VS. DELIVERIES. FINA'S NEAREST EMPLOYEE, GARY BARKLEY,WAS CONTACTED IN THE BEAUMONT AREA, AND HE ARRIVED ON-SITE AT 0230 ON JAN2ND. AT 0305, OIL WAS FOUND ON CREEK AT THE OSR HWY, CROSSING, BUT WASBELIEVED TO HAVE ORIGINATED FROM A SOURCE OTHER THANK THIS PIPELINE. AT350AM, AS A PRECAUTIONARY MEASURE, THE PIPELINE WAS SHUTDOWN WHILE THEINVESTIGATION OF THE SOURCE WAS CONTINUING. AT 0615, FINA'S MAINTENANCE CREW,WITH SPILL RESPONSE EQUIPMENT, WAS ORDERED OUT OF THE BROWNWOOD AREA, AGAIN ASA PRECAUTIONARY MEASURE IN THE EVENT THAT THE LEAK WAS DISCOVERED TO HAVEORIGINATED FROM THE FINA PIPELINE. AT 0805 ON JANUARY 2ND, THE SOURCE OF THELEAK WAS CONFIRMED AS BEING FROM THIS PIPELINE, AND FURTHER CALL OUTS WEREMADE. AT 0930 THE LEADING EDGE OF THE OIL WAS FOUND, APPROX 1.5 MI EAST OFTHE OSR HWY, IN BRAZOS COUNTY, AND BOMMS WERE PLACED TO PREVENT FURTHERPROGRESS OF THE LEAK. THE ADVANCE OF THE OIL ALONG BEE CREEK (A NORMALLYINTERMITTENT WATER BODY) WAS EXPEDITED BY HEAVY RAINS HAVING OCCURRED IN THEAREA DURING THE NIGHT OF THE 1ST. LEAK CLEAN UP WAS BEGUN THE AFTERNOON OFTHE 2ND, AND WAS ESSENTIALLY COMPLETED BY THE 27TH OF JANUARY.
2017-09-29 08:50 | NO | NO | 19990013 | 1999-01-27 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1999-01-03 | 1050 | AR | JEFFERSON |  | NO |  | NO | T-5S, R-11W, SEC 4 APPROXIMATELY 12 MILES WEST OF PINE BLUFF, AR ON HIGHWAY 270 |  | PUMPING STATION | VALVE |  | 1969 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 1 | 0 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | OTHER | VANDALISM | Null |  |  | Null | Null | MARC DEVARENNES | 5734865488 | AT APPROXIMATELY 1050AM ON 1/3/99, KOCHS PIPELINE CONTROL CENTER IN WICHITA,KANSAS RECEIVED A "SECURITY ALARM" FROM THE PINE BLUFF, AR PUMPING STATION.NO ACTIVITY COULD BEEN SEEN BY THE PIPELINE CONTROL CENTER FROM THE REMOTESECURITY CAMERA AT THE STATION. A KOCH EMPLOYEE WAS DISPATCHED TO THE SITE.THE EMPLOYEE ARRIVED AT APPROXIMATELY 1140 AND FOUND A VAPOR CLOUD OFANHYDROUS AMMONIA INSIDE THE STATION FENCE. A 1/2 PLUG HAD BEEN REMOVED FROMA BLOW DOWN VALVE ON THE STATION PIPING. THE EMPLOYEE WAS SAFELY ABLE TO TURNTHE VALVE HANDLE, STOPPING THE RELEASE. THE PRODUCT WAS RELEASED INTO THEATMOSPHERE WITH NO IMMEDIATE DANGER TO PERSONNEL OR THE ENVIRONMENT. THEREWERE NO INJURIES OR EVACUATIONS. AN UNKNOWN QUANTITY GREATER THAN THE RQ OF100 LBS WAS RELEASED. DUE TO UNKNOWN VARIABLES SUCH AS HOW FAR THE 1/2 VALVEWAS OPENED AT THE TIME WHEN THE PIPING PLUG WAS REMOVED AND THE PRESSURE DROPACROSS AN UPSTREAM CONTROL VALVE, AN ACCURATE ENGINEERING ESTIMATE OF THEQUANTITY RELEASE COULD NOT BE MADE. SUBSEQUENT ENGINEERING INVESTIGATION OF FLOW SIMULATIONS AND CONDITIONS PERFORMED ON 6/1/00 HAS SHOWN THAT AN ESTIMATED 240LBS WAS RELEASED DURING THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 19990016 | 1999-01-26 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1998-12-31 | 645 | TN |  | PIPERTON | NO |  | NO | 1/2 MILE NORTH OF THE WOLF RIVER APPROX 25-30 MILES EAST OF MEMPHIS, TN. THE SITE IS A RIVER BOTTOM/MARSHY AREA. | 469311 | LINE PIPE | PIPE |  | 1968 | FAILED PIPE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 2035276 | 1424331.6945 | 2873452.338 | CRUDE OIL | 1 | 20 | 0 | NO | NO | 40 | 0.31 | 52000 | WELDED |  | 585 | 0 | YES | 24 | 752 | 0 | 1968 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | D F SHEAFF | 7132414381 | FAILURE POINT WAS A 5 1/8 LONG CRACK IN A SLIGHTLY DENTED AREA APPROXIMATELY2 1/2" IN RADIUS AND 3/8" DEEP. THE DENTED AREA WAS AT THE END OF A 22" LONGSCRATCH. ALTHOUGH THE CAUSE OF THE DENT/SCRATCH IS UNKNOWN, IT IS BELIEVED TOHAVE OCCURRED DURING INITAL CONSTRUCTION-EITHER DURING THE PIPE PLACEMENTOPERATIONS OR DURING BACKFILLING. REPAIR: BECAUSE THE CRACK WAS IN THELONGITUDINAL DIRECTION, 1/4" HOLES WERE DRILLED ON THE ENDS OF THE CRACK TOPREVENT PROPAGATION OF THE CRACK. A 36"X40" PLIDCO MECHANICAL SPLIT SLEEVEWAS THEN INSTALLED OVER THE AREA, BOLTED, AND WELDED. BOTH MAGNETIC PARTICLEAND LIQUID PENETRANT INSPECTION NDT WAS PERFORMED ON ALL WELDS.
2017-09-29 08:50 | YES | NO | 19990017 | 1999-01-26 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1998-12-28 | 835 | MT |  | ALZADA | NO |  | NO |  |  | PUMPING STATION | OTHER | THREAD FITTING | 1952 | OUTSIDE FORCE DAMAGE | FROSTHEAVE | NATURAL FORCE DAMAGE | TEMPERATURE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 41989.3428 | 84709.4646 | CRUDE OIL | 1 | 190 | 160 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | FROSTHEAVE |  | Null | NO DATA |  | Null | Null | D F SHEAFF | 7132414381 | SECONDARY PIPE NIPPLE FAILURE DUE TO FROSTHEAVE. TO CORRECT THE PROBLEM, THISSECONDARY PIPING WAS REPLACED WITH STAINLESS STEEL TUBING AND TIED INABOVEGROUND.
2017-09-29 08:50 | YES | NO | 19990018 | 1999-01-26 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1998-12-21 | 100 | TX | SCURRY |  | NO |  | NO | BLK 3 SEC 4 H&GRNY SURVEY - 12 MI NORTH OF COLORADO CITY ON HWY 208 2 MI EAST ON CR 4156 |  | TANK FARM | PIPE |  |  | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3499.1119 | 7059.1221 | CRUDE OIL | 1 | 415 | 405 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D F SHEAF | 7132414381 | PIPING FAILURE NEAR WELD. CONTENTS OF TANK HAVE BEEN TRANSFERRED TO ANOTHERTANK.
2017-09-29 08:50 | YES | NO | 19990019 | 1999-01-25 | 30991 | MOBIL OIL CORPORATION | YES | 1998-12-14 | 1300 | TX | WINKLER |  | NO |  | NO | APPROX 5 MILES SOUTH OF MONAHANS, TEXAS 4 MILES EAST OF STATE HIGHWAY 18 MITCHELL RANCH 4.5 MILES EAST OF MOBIL PIPELINE COMPANY'S HALLEY STATION |  | LINE PIPE | GIRTH |  | 1929 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34991.119 | 70591.2205 | CRUDE OIL | 1 | 1390 | 800 | NO | NO | 10 | 0.37 | 35000 | WELDED |  | 652 | 600 | YES | 19 | 815 | 8 | 90 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D G SCOTT | 2146585914 | A WELD AT MILE POST 4.5 (4.5 MILES EAST OF MOBIL PIPE LINE COMPANY'S HALLEYSTATION) "PARTED" DUE TO STRESS AT AN OVERBEND LOCATION. THE LINE WASCONSTRUCTED IN 1929 AND ACETYLENE WELDED. LINE WAS SHUT DOWN BY PIPELINEOPERATIONS CONTROL CENTER AND CREWS DISPATCHED TO THE AREA TO BEGIN CLEAN UPAND TO MAKE PERMANENT REPAIRS. REMEDIATION EFFORTS ARE UNDERWAY TO BLEND OILYSOIL TO LESS THAN 1%. NO DEATHS OR INJURIES WERE ASSOCIATED WITH THISINCIDENT. LEAK OCCURRED IN A RURAL AREA. ALL NOTIFICATIONS WERE MADE TOREGULATORY AGENCIES.
2017-09-29 08:50 | YES | NO | 19990020 | 1999-01-26 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1998-12-22 | 1030 | OK | GARVIN |  | NO |  | NO | N/2 SW/4 SECTION 18-T4N-R2W |  | PUMPING STATION | PIPE |  | 1954 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6998.2238 | 14118.2441 | NOT GIVEN | 1 | 320 | 300 | NO | NO | 6 | 0.16 | 42000 | WELDED |  | 80 | 25 | NO | 0 | 0 | 1 | 99 | INTERNAL | Null | YES | OTHER | BACTERIA | NO DATA |  | Null | NO DATA |  | Null | Null | JAMES A HENRY | 5802557151 | RELEASE CAUSED BY INTERNAL CORROSION ON FILL LINE TO TANK. PRODUCT CONTAINEDWITH SECONDARY CONTAINMENT.
2017-09-29 08:50 | YES | NO | 19990021 | 1999-02-17 | 26041 | GATX TERMINALS CORP | NO | 1999-01-11 | 1500 | CA | LOS ANGELES | CARSON | NO |  | NO | ALONG UNION PACIFIC RAILROAD TRACKS, 500 FEET WEST OF ALAMEDA STREET AND 2000 FEET SOUTH OF SEPULVEDA BOULEVARD. |  | NO DATA | GIRTH |  | 1929 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 38008.018 | 76677.5244 | TRANSMIX (PART.REFINED PETRO) | 1 | 60 | 46 | NO | NO | 6 | 0.22 | 2160 | WELDED |  | 450 | 125 | YES | 4 | 577 | 7 | 97 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DAVID J KINGSTON | 3105187705 | RECEIVED A TELEPHONE CALL FROM TOSCO INFORMING THAT PRODUCT WAS SEEPING FROMTHE GROUND EAST OF THE FENCE AT THE WEST BOUNDRY OF THEIR REFINERY IN UNIONPACIFIC RAILROAD PROPERTY. GATX RESPONDED AND HAD OPERATIONS PUT A SLIGHTPRESSURE PACK ON THE PIPELINE TO DETERMINE IF THE RELEASE WAS GATX'S. AS SOONAS THE PRESSURE PACK WAS APPLIED, PRODUCT BEGAN SURFACING. GATX CLAIMEDRESPONSIBILITY FOR THE RELEASE AND BEGAN IMMEDIATE EMERGENCY RESPONSEACTIVITIES. THE LEAK AREA WAS EXPOSED AND A TEMPORARY LEAK CLAMP WASINSTALLED THE EVENING OF 1/11/99. GATX CONTRACTORS RETURNED ON 1/12/99 ANDREMOVED A 12-FOOT SECTION OF PIPE AND REPLACED IT WITH NEW PRETESTED PIPE.
2017-09-29 08:50 | YES | NO | 19990022 | 1999-02-17 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1999-01-16 | 1800 | WI | DOUGLAS | SUPERIOR | NO |  | NO | MP 1097.6 TOWNSHIP 49N SECTION 36 NORTHERN PART OF SW 1/4 RANGE 14W |  | LINE PIPE | OTHER | INSTRUMENTATION PIPE | 1972 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 365000 | 252235.0288 | 508859.9349 | NATURAL GAS LIQUID | 2 | 130 | 30 | YES | NO | 0.75 | 0.15 | 10267 | THREADED |  | 820 | 130 | YES | 24 | 1031 | 0 | 1974 | EXTERNAL | Null | YES | GALVANIC |  | FROSTHEAVE |  | Null |  |  | Null | Null | RC SANDAHL | 2187250102 | DURING NORMAL INSPECTION OF THE DENSITOMETER BUILDING IN THE PLM YARD, THEGAUGER 2 NOTICED A SMALL AMOUNT OF VAPOR BUBBLING UP THROUGH STANDING WATER INTHE WHISTLE AROUND THE INSTRUMENT TAP ON LINE 1. SINCE THE VOLUME OF NGLBEING RELEASED WAS MINIMAL AND VAPORS WERE NOT ACCUMULATING, IT WAS DECIDED TOCONTINUOUSLY MONITOR THE SITE AND WAIT FOR THE FOLLOWING CRUDE BATCH TODISPLACE THE NGL SO THAT THE REPAIR COULD BE SAFELY PERFORMED. AT 0500 MSTON 1/19/99, THE SAFETY WATCH NOTICED AN INCREASE IN THE VOLUME AND THEACCUMULATION OF CONDENSATE IN THE LEAK AREA. FOLLOWING A REVIEW OF THE SITE,IT WAS DETERMINED THAT A PLANNED INGITION WAS THE MOST PRUDENT METHOD TOCONTROL RELEASE. PRIOR TO THE IGNITION, THE SUPERIOR FIRE DEPARTMENT PUMPEDFOAM INTO AND AROUND THE DENSITOMETER BUILDING. FOLLOWING NOTIFICATION TOTHE PUBLIC, AND CLOSURE OF BARDON AND STINSON AVENUES BY THE SUPERIOR POLICEDEPARTMENT, THE RELEASE WAS FLARED AT 1100 MST ON 1/19/99. THE FIRE WASEXTINGUISHED AT 2000 MST ONCE CRUDE OIL ARRIVED AT THE LEAK SITE.
2017-09-29 08:50 | YES | NO | 19990023 | 1999-02-12 | 22430 | WEST SHORE PIPELINE CO | YES | 1999-01-23 | 1500 | WI | WASHINGTON | GERMANTOWN | NO |  | NO | SEE ATTACHED SKETCH. |  | LINE PIPE | PIPE |  | 1961 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 276421.9494 | 557654.7231 | GASOLINE | 1 | 660 | 620 | NO | NO | 10 | 0.2 | 1964 | WELDED |  | 1414 | 138 | YES | 8 | 1830 | 1 | 91 | NO DATA | Null | Null | NO DATA |  | OTHER | STRESS | Null | ONE CALL |  | Null | Null | JAY ANDREWS | 8474390270 | OUTSIDE PARTY REPORTED GAS SMELL; SHUT DOWN PIPELINE; INVESTIGATED AREA OF GASODOR; FOUND DITCH CONTAINING GASOLINE/FUEL OIL MIXTURE; EXPOSED PIPELINE ANDFOUND A STRESS CRACK IN A DENT CAUSED BY THIRD PARTY DAMAGE (SOURCE AND TIMEOF DAMAGE UNKNOWN); INSTALLED A NEW SECTION OF PIPE TO REPLACE DAMAGE;RETURNED PIPELINE TO SERVICE; SPILL CLEANUP CONTINUES.
2017-09-29 08:50 | YES | NO | 19990024 | 1999-03-01 | 2731 | CHEVRON PIPELINE CO | YES | 1999-01-21 | 1545 | LA |  | EMPIRE | NO |  | NO | SEE ATTACHED FACILITY DRAWING |  | LINE PIPE | PIPE |  | 1958 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 103658.231 | 209120.5212 | CRUDE OIL | 1 | 5000 | 4980 | NO | NO | 26 | 0.32 | 0 | WELDED |  | 275 | 30 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEPHEN J MOLLOY | 5045927688 | ON 1/21/99 AT 3:45 PM, PIPE LINE EMPLOYEE MAKING A VISUAL INSPECTION AROUNDTHE FACILITY OBSERVED OIL INSIDE THE FIRE WALL OF THE OSTRICA TERMINAL PUMPSTATION. THE RELEASE, ORIGINATING FROM AN UNDERGROUNDD 26" PIPELINE LEAK,WAS LOCATED AT THE TRANSFER PIPING RUNNING FROM THE UPPER PART OF OSTRICASUPER STATION. THE LINE WAS ISOLATED AND SECURED FROM THE T-2 MANIFOLD TO THEOSTRICA TANKS. THE AMOUNT OF THE RELEASE, AS REPORTED TO THE NRC (#471377)WAS 2,000 BARRELS. AN UPDATED RELEASE VOLUME ESTIMATE ISSUED THE FOLLOWINGDAY WAS REVISED TO 5,000 BARRELS. THE ADDITIONAL COLUME WAS DUE PRIMARILY TOADDITIONAL DRAINAGE OF THE PIPELINE INTO THE SPILL AREA AND DIFFICULTYDETERMINING THE ORIGINAL THICKNESS OF OIL ACROSS THE SITE. ALL THE OIL WASTRAPPED AND CONTAINED INSIDE OF TWO BERMS WITHIN THE CHEVRON FACILITY ANDPOSED NO THREAT TO WATER. CHEVRON PIPE LINE'S OIL SPILL CONTRACTOR WASNOTIFIED AND BEGAN ON-SITE AIR TESTING AND INITIAL CLEANUP. THE RECOVERY ANDSTORAGE OF FREE OIL WAS ACCOMPLISHED BY PUMPING THE OIL BACCK INTO ON-SITETANKAGE. IMPACTED AREAS WERE FLUSHED WITH WATER TO AID IN OIL RECOVERY, ASOUTLINED IN THE JOB SITE SAFETY PLAN. A 12" BYPASS FROM THE ORIGINAL 26" WASINSTALLED ON SUNDAY, JANUARY 24TH, AND THE LINE WAS PUT BACK INTO SERVICE.SITE REMEDIATION IS CURRENTLY ONGOING.
2017-09-29 08:50 | YES | NO | 19990025 | 1999-02-04 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1998-10-19 | 330 | TX | KAINES | FALL | NO |  | NO | FACILITY LOCATED AT INTERSECTION (NE QUADRANT) OF TEXAS HIGHWAY 181 AND FARM TO MARKET (FM) 887. |  | PUMPING STATION | PIPE |  | 1945 | OUTSIDE FORCE DAMAGE | OTHER | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2500000 | 1749555.9503 | 3529561.0251 | CRUDE OIL | 1 | 963 | 770 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | OTHER | SEVERE WEATHER/RAIN/FLOOD | Null | NO DATA |  | Null | Null | GABRIEL LUGO | 5122423524 | DURING A RAIN STORM (FLOODING AREA RIVERS), THE ROOF BEGAN HOLDING WATER. THEWEIGHT CAUSED THE ROOF TO PARTIALLY COLLAPSE. THE MOVEMENT CAUSED BY THE ROOFRUPTURED THE SIDE TANK CONNECTION OF THE STATION PIPING AND THE TANK MATERIALFLOWED INTO FIREWALL FROM THE DISCONNECTION (PARTIAL SEPARATIONS). CRUDEOIL ESCAPED FROM THE FIREWALL THROUGH AN OLD SECTION OF PIPE WHICH HAD BEENCUT AND NO KNOWN TO EXIST.
2017-09-29 08:50 | YES | NO | 19990026 | 1999-02-16 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1999-01-08 | 1130 | TX | DUVAL | BENAVIDES | NO |  | NO | BENAVIDES STATION 1.5 MILES NORTH BENAVIDES, TEXAS. |  | TANK FARM | PIPE |  | 1940 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 10500 | 70 | NO | NO | 12 | 0.25 | 794 | WELDED |  | 275 | 10 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | NO DATA |  | OTHER | N/A | Null | NO DATA |  | Null | Null | JASON HILL | 5123947961 | INTERNAL CORROSION ON 12" SECTION LINE AT BENAVIDES STATION CAUSING REPORTED10500 BBL RELEASE.
2017-09-29 08:50 | NO | NO | 19990027 | 1999-03-04 | 30950 | EL PASO FIELD SERVICES | NO | 1999-01-28 | 1400 |  |  |  | YES | 2823.73 X 9616.08 | NO | THIS LEAK WAS IN THE VICINITY OF MI 520 PLATFORM IN THE MATAGORDA ISLAND AREA. |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 41463.2924 | 83648.2085 | CONDENSATE | 1 | 1 | 0 | NO | NO | 6 | 0.42 | 35000 | WELDED |  | 1440 | 400 | YES | 24 | 2162 | 9 | 79 | INTERNAL | Null | YES | OTHER | CORROSION FROM LIQUID | NO DATA |  | Null | NO DATA |  | Null | Null |  | 7134203534 | SEE ATTACHED LOG OF THE INCIDENT.
2017-09-29 08:50 | YES | NO | 19990028 | 1999-03-04 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1999-02-17 | 1300 | KS | MCPHERSON |  | NO |  | NO | E 1/2 SECTION 19, TOWNSHIP 21 SOUTH, RANGE 5 WEST, MCPHERSON COUNTY, KANSAS 7 MILES WEST AND 1 1/2 MILES SOUTH OF INMAN, KANSAS |  | LINE PIPE | PIPE |  | 1937 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9500 | 6565.0213 | 13244.2997 | CRUDE OIL | 1 | 100 | 65 | NO | NO | 10.75 | 0.31 | 30000 | WELDED |  | 700 | 423 | YES | 4 | 880 | 11 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ALLEN R WILKERSON | 3162419270 | TOWNSHIP ROAD MAINTAINER WAS DIGGING OUT THE ROAD DITCHES AND GOUGED THEPIPE. NO ONE-CALLS WERE MADE AND THE PIPELINE MARKERS WERE ON EACH SIDE OFTHE ROAD. THE OPERATOR OF THE MAINTAINER CALLED THE NUMBER ON THE SIGN ANDJAYHAWK CREW RESPONDED BY SHUTTING DOWN THE LINE AND CLOSING BLOCK VALVESWITHIN 4O MINUTES. THE PIPELINE WAS REPAIRED AND BACK IN SERVICE WITHIN 6HOURS.
2017-09-29 08:50 | NO | NO | 19990029 | 1999-03-08 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 1999-02-10 | 1445 | IA | HANCOCK |  | NO |  | NO | APPROXIMATELY 4 MILES EAST OF GARNER IOWA NEAR THE INTERSECTION OF VALE AVE AND HWY 18. GARNER FARMLAND AMMONIA TERMINAL |  | NO DATA | BOLTED FITTING |  | 1999 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROYCE HOEMANN | 5734865488 | EMPLOYESS HAD DE-PRESSURED PROVER TO REMOVE INACTIVE DETECTOR SWITCHES, WHICHHAD BEEN REPLACED PREVIOUSLY, AND INSTALL BLIND PLATES. DURING RE-PRESSURINGOF THE PROVER, A SMALL LEAK FROM THE NEWLY INSTALLED BLIND PLATE WAS VISUALLYDETECTED. EMPLOYEE TRIED TO TIGHTEN BOLTS AND FOUND THE FIRST TWO BOLTSLOOSE. EMPLOYEE BEGAN TO DE-PRESSURE PROVER TO PROPERLY TIGHTEN THE BOLTSWHEN THE BLIND PLATE CAME OFF OF THE PROVER CAUSING A RELEASE OF PRODUCT TOTHE ATMOSPHERE. EMPLOYEES ALREADY HAD NECESSARY VALVES CLOSED, SO WAITED FORLINE SECTION TO COMPLETE DE-PRESSURING AND MADE NECESSARY REPAIRS.APPROXIMATELY 185 LBS WAS RELEASED DURING THIS TIME.
2017-09-29 08:50 | NO | NO | 19990031 | 1999-03-15 | 31128 | STOLTHAVEN PERTH AMBOY INC | NO | 1999-02-08 | 1145 | NJ | MIDDLESEX | WOODBRIDGE | NO |  | NO | WEST OF STATE STREET IN THE SEWAREN SECTION OF WOODBRIDGE, NJ AND WEST OF THE CONRAIL RAIL LINE RUNNING PARALLEL TO STATE ST. THE PIPELINE RUNS PARALLEL |  | LINE PIPE | PIPE |  | 1982 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | FUEL OIL | 1 | 2 | 0 | NO | NO | 12.75 | 0.22 | 1806 | WELDED |  | 360 | 0 | YES | 8 | 540 | 6 | 98 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | GLENN E RIKER | 7328261144 | A VERBAL REPORT WAS GIVEN TO THE NATIONAL RESPONSE CENTER 2/8/99 AT 1211HOURS. THE CONFIRMATION NUMBER IS 473252. WE DISCOVERED A HOLE IN THELINE ON 2/8/99 AT 1145 HOURS. WE RAN AN INTELLIGENT PIG THROUGH THE LINEON 1/28/99 AND RECEIVED AN INITIAL REPORT ON THE LOCATION OF ANOMALIES.THE LINE WAS EVACUATED ON 1/29/99. WHEN THE HOLE WAS DISCOVERED THE LINEWAS EMPTY OF ALL PRODUCT, AS WE WERE PROCEEDING TO LOCATE AND INVESTIGATETHE ANOMALIES IDENTIFIED. ALL SECTIONS OF THE LINE THAT WERE REMOVED, WEREREPLACED WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 19990032 | 1999-03-15 | 2325 | CHEVRON USA INC | YES | 1999-02-16 | 1745 |  |  |  | YES | LAT 2912.26 LONG 8902.04 | YES | MAIN PASS 69 PIPELINE TERMINAL - NEAR ROMERE PASS WEST SIDE OF TERMINAL NEAR HELIPAD AND BUNKHOUSE 10" CRUDE OIL PIPELINE NEAR PIG LAUNCHER |  | LINE PIPE | PIPE |  | 1964 | OTHER | RETAINER RING (WELDED TO | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 345527.4367 | 697068.4039 | CRUDE OIL | 1 | 125 | 50 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1236 | 550 | YES | 8 | 1545 | 0 | 91 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | STEPHEN J MOLLOY | 5045927688 | AT 1745 HRS ON 2/16/99, SHORTLY AFTER THE START-UP OF PIPELINE PUMPS ON THE10" MP 69 TO EMPIRE TERMINAL PIPELINE, CHEVRON PIPELINE MP69 OPERATORS CRUDEOIL FLOWING ABOVE THE WATERLINE FROM THE 10" PIPELINE, LOCATED IN SHALLOWWATER AND NEAR THE MP69 TERMINAL HELIPAD AND BUNKHOUSE. THE 10" LINE WASIMMEDIATELY SHUTDOWN AND BOOM (BOTH HARD AND ABSORBENT BOOM USED) WASDEPLOYED TO CONFINE THE MAJORITY OF THE OIL TO THE IMPACT AREA AND MINIMIZEIMPACT TO THE SURROUNDING TALL CANES. NOTIFICATIONS WERE MADE TO THE NRC(474144), EPA, LA STATE POLICE/LOSCO (#990903), PLAQUEMINES LEPC (#990028),LA FISH AND WILDLIFE AND THE USCG TO REPORT THE ORIGINAL ESTIMATED RELEASEVOLUME OF 20 BARRELS. (ESTIMATION OF SPILL VOLUME LIMITED DUE TO NIGHTTIMEVISIBILITY.) SPILL RESPONSE CLEAN-UP CREWS AND EQUIPMENT CONSISTING OF MSRCSHALLOW WATER SKIMMERS, AIR BOATS AND FLATBOATS WERE DISPATCHED TO THE SPILLSITE TO BEGIN OIL RECOVERY OPERATIONS. A DEEP WATER SKIMMER WAS PLACED ONSTANDBY AT THE FURTHEST EXTENTION OF THE SHEEN SHOULD RECOVERABLE OIL BEENCOUNTERED. A NIGHT FLIGHT DISPATCHED ON THE EVENING OF 2/16/99 TO PROVIDETHERMAL IMAGING DATA RESULTED IN A REVISION TO THE ESTIMATED RELEASE VOLUMETO 75-125 BBLS. THE SITE WAS VISITED BY THE USCG AND LA FISH AND WILDLIFEAGENCY. NO IMPACT TO SHORELINE OR WILDLIFE WAS OBSERVED OR EXPECTED. ALLFREE LIQUIDS RECOVERED WAS STORED IN FACILITY TANKAGE. PIPELINE REPAIRPROCEDURES CALLED FOR THE REMOVAL OF THE BROKEN 10" SECTION AND THEINSTALLATION OF A TEMPORARY 8" BYPASS SECTION. THE LINE WAS PRESSURE TESTEDON 2/21/99 AND BROUGHT BACK IN SERVICE ON 2/22/99. AERIAL SURVEILLANCE WASAGAIN PERFORMED WITH NO VISUAL OIL SIGHTINGS. SKIMMERS WERE DEMOBED,DECONTAMINATED AND RELEASED ON THE AFTERNOON OF 2/22/99. PASSIVE REMEDIATIONIS ONGOING.
2017-09-29 08:50 | YES | NO | 19990033 | 1999-03-19 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1999-02-15 | 1400 | KS | RENO |  | NO |  | NO | MID-AMERICA PIPELINE COMPANY PARTRIDGE PUMP STATION LOCATED IN SECTION 14- TOWNSHIP 23 SOUTH - RANGE 7 WEST, RENO COUNTY, KANSAS |  | PUMPING STATION | BOLTED FITTING |  | 1968 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 69.1055 | 139.4137 | ANHYDROUS AMMONIA | 2 | 5 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | NO DATA |  | Null | Null | KENNETH L LYBARGER | 9185735774 | 13:30- FIELD TECHNICIANS WERE INSTALLING A MOTOR OPERATOR ON THE NORTH BOUNDFIRE-GATE VALVE AT THE MID-AMERICA PIPELINE COMPANY PARTRIDGE STATION. ASTHEY ATTEMPTED TO ATTACH A HOIST TO THE OPERATOR WHICH WAS IN THE BED OF APICKUP TRUCK, THE OPERATOR BECAME UNSTABLE AND FELL INTO THE VALVE, CRACKINGTHE 1/2 INCH BODY BLEED VALVE AND NIPPLE ASSEMBLY. THE CRACK WASAPPROXIMATELY .0029 BY .0394. PRODUCT ESCAPED THROUGH THE CRACK. 14:02 -DISPATCH CONTROL CENTER WAS NOTIFIED AND THE UNIT SHUT DOWN. 14:02-15:00-TECHNICIANS ATTEMPT TO STOP THE FLOW OF ESCAPING PRODUCT. 15:01-THE NATIONALRESPONSE CENTER WAS NOTIFIED THAT A RELEASE HAD OCCURRED THAT MOST LIKELY WILLEXCEED 5 BBL OF HVL. 15:10-DISPATCH WAS INSTRUCTED TO BLOCK IN THE LINE ANDATTEMPT TO PULL THE PRODUCT BACK DOWNSTREAM. SUBSEQUENT TELEPHONIC NOTICEWAS MADE TO: 15:12-THE LEPC & 15:15-THE SERC. 15:30- NEAREST OFFISITE VALVEWAS CLOSED TO BLOCK IN A SMALLER LINE SEGMENT. 16:05-DECISION WAS MADE TO SETSTOPPLE IN LINE NEAR VALVE SITE AND ORDERS PLACED FOR ASSISTANCE FROM EXTERNALCONTRACTORS. 16:05-23:00-PIPELINE WAS MADE READY FOR PLACEMENT OF STOPPLE.23:30-STOPPLE SET AND REMAINING PRODUCT IN THE LINE SEGMENT WAS EVACUATED.CRACKED NIPPLE REMOVED AND REPLACED.
2017-09-29 08:50 | NO | NO | 19990034 | 1999-03-19 | 15156 | SINCLAIR PIPELINE CO | YES | 1999-02-17 | 1540 | MO | SCOTLAND |  | NO |  | NO | 1 1/2 MILES NE OF THE TOWN OF RUTLEDGE, MO ALONG BNSF RAILROAD: NE 1/4 OF THE SW 1/4 OF SECTION 25, T64N, R11W, SCOTLAND COUNTY, MISSOURI |  | LINE PIPE | PIPE |  | 1905 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6910.5487 | 13941.3681 | GASOLINE | 1 | 12 | 8 | NO | NO | 8 | 0.32 | 0 | COUPLED |  | 400 | 100 | YES | 24 | 830 | 10 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | BARRY BLUTH | 6605420206 | RECEIVED CALL FROM CONTROL CENTER AT 3:40 PM ON WEDNESDAY, 2/17/1999, THATGARY YOAKUM, OF THE BNSF RAILROAD HAD REPORTED A GAS LEAK ON THE GROUND 1 1/2MILES NE OF THE TOWN OF RUTLEDGE, MO. PERSONNEL FROM FT. MADISON, IADISPATCHED TO THE SITE. UPON CONFIRMATION OF A LEAK, DISTRICT MANAGER ANDOTHER PERSONNEL DISPATCHED TO SCENE ALONG WITH A VACUUM TRUCK AND OTHEREMERGENCY EQUIPMENT. LINE WAS CLAMPED OFF AT 1:10 AM BY COMPANY PERSONNEL.BEGAN PICKING UP PRODUCT WITH VAC TRUCK AND ABSORBENT PADS.
2017-09-29 08:50 | YES | NO | 19990035 | 1999-03-17 | 22610 | WILLIAMS PIPELINE CO | YES | 1999-02-13 | 1153 | IA | FRANKLIN |  | NO |  | NO | LATIMER STATION (SOUTHWEST QUARTER OF SECTION 1 - T 92 NORTH - RANGE 22 WEST) |  | PUMPING STATION | OTHER | INSULATING FLANGE GASKET | 1984 | OTHER | GASKET AT FLANGE BLEW OUT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 55284.3899 | 111530.9446 | FUEL OIL | 1 | 670 | 528 | NO | NO | 12 | 0.31 | 0 | FLANGED |  | 1050 | 890 | YES | 8 | 1852 | 5 | 84 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH L LYBARGER | 9185735774 | 11:53- THE PIPELINE DISPATCHER OBSERVED A DROP IN THE PRESSURE ON THE LINE ASINDICATED ON THE SCADA MONITOR IN THE DISPATCH CONTROL CENTER IN TULSA.12:09-THE DISPATCHER SHUT DOWN THE LINE AS A RESULT OF DROPPING PRESSURE.12:20-THE DISPATCHER NOTIFIED THE AREA SUPERVISOR BY TELEPHONE OF THEPOSSIBILITY OF A POTENTIAL LOSS OF PRODUCT BETWEEN ROLAND AND MASON CITY,IOWA. THE AREA MANAGER NOTIFIED MAINTENANCE SUPERVISORS OF THE POTENTIALLOSS, AND THEY BEGAN SEARCHING DIFFERENT SEGMENTS OF THE LINE SECTION LOOKINGFOR INDICATIONS OF A RELEASE. 12:42-THE AERIAL PATROL SERVICE WAS INSTRUCTEDTO DISPATCH AN AIRCRAFT TO PATROL THE PIPELINE SECTION. 13:45-A COORDINATOROF MAINTENANCE ARRIVED AT LATIMER STATION AND SAW FUEL OIL ON THE GROUNDINSIDE THE STATION. 13:52-FRANKLIN COUNTY SHERIFF'S DEPARTMENT WAS NOTIFIEDPRIOR TO BLOCKADING THE ROAD BY THE STATION. 13:57-ENVIRONMENTAL CONTRACTORWAS INSTRUCTED TO DEPLOY EMERGENCY RESPONSE PERSONNEL, EQUIPMENT ANDSUPPLIES. 14:00-THE IOWA DEPARTMENT OF NATURAL RESOURCES WAS NOTIFIED BYTELEPHONE. 14:34-THE NATIONAL RESPONSE CENTER WAS NOTFIED BY TELEPHONE. (CASENUMBER 473903) 14:52-ROAD ADJACENT TO STATION WAS BARRICADED TO KEEP TRAFFICOUT OF THE AREA DURING PRODUCT RECOVER AND CLEAN UP. 15:15-CONTAINMENT BOOMDEPLOYED TO CONTAIN RELEASED PRODUCT. 16:45-BEGAN RECOVERING PRODUCT INTOTRANSPORT TRUCKS.
2017-09-29 08:50 | YES | NO | 19990036 | 1999-03-16 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1999-02-22 | 1025 | MN |  |  | NO |  | NO | MP 0834.5, TOWNSHIP 156N, SECTION 1, SE QUARTER, RANGE 47W. |  | LINE PIPE | BOLTED FITTING |  | 1999 | OTHER | LOOSE BOLTS ON THE FLANGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 400 | 385 | NO | NO | 48 | 0.41 | 0 | FLANGED |  | 618 | 185 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | ONE CALL |  | Null | Null | R C SANDAHL | 2187250102 | PATROL PILOT WITNESSED A POOL OF OIL IN AN EXISTING EXCAVATION AT THE 36"VALVE SITE AT MP 834.5. THESE FACILITIES HAD BEEN EXCAVATED IN CONJUNCTIONWITH NEW MAINLINE EXTENSION CONSTRUCTION. THIEF RIVER FALLS PLM STAFF WEREIMMEDIATELY NOTIFIED AND IN TURN NOTIFIED THE EDMONTON CONTROL CENTER. ALLLINES WERE SHUT DOWN AND THE THIEF RIVER FALLS PLM STAFF WERE DISPATCHED TOTHE SITE. THE 48" MAILINE VALVE WAS LEAKING OIL FROM IT'S FLANGE. THISFLANGE WAS NEW DUE TO MAINLINE CONSTRUCTION LATE IN 1998. IT IS SUSPECTED THECONTRACTOR MAY HAVE DAMAGED THE GASKET OR IMPROPERLY TIGHTENED THE FLANGEBOLTS. BOLTS WERE TIGHTENED ON THE 48" FLANGE. OIL MIGRATED UPSTREAM INTOTHE EXCAVATION AROUND THE 36" VALVE AND ALL OF THE CRUDE WAS CONTAINED WITHINGTHE EXCAVATION. FREE OIL WAS COLLECTED INTO VACUUM AND TANKER TRUCKS ANDHAULED TO CLEARBROOK TERMINAL. CONTAMINATED SOIL WAS BEING TEMPORARILYSTOCKPILED ON SITE, AND TRANSPORTED TO A LANDFARM. THE MPCA APPROVED LPL'SMETHODS FOR REMEDIATION.
2017-09-29 08:50 | YES | NO | 19990037 | 1998-02-23 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 1999-01-24 | 1030 | CA | PLACER | ROCKLIN | NO |  | NO | 6050 PACIFIC ST ROCKLIN, CA |  | TANK FARM | TANK |  | 1977 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 138210.9747 | 278827.3616 | DIESEL FUEL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A FANT | 7138449526 | ON MONDAY JANUARY 24, 1999 AT APPROXIMATELY 1030 HRS EMPLOYEES OF KINDERMORGAN ENERGY PARTNERS' ROCKLIN TANK FARM DISCOVERED LEAK IN THE VICINITY OFBREAKOUT TANK, RO-10. THE LOCAL EMERGENCY PLAN WAS ACTIVATED ANDENVIRONMENTAL CLEAN UP CONTRACTORS WERE CALLED TO SITE. AT APPROXIMATELY 1100HOURS ON JANUARY 25, 1999 RO-10 WAS CONFIRMED AS THE SOURCE OF THE LEAK.SUBSEQUENT INVESTIGATION DISCLOSED A CRACK IN A WELD WHERE THE 14-INCH FILLLINE PIPE IS WELDED TO THE SUMP ON THE UNDER SIDE OF THE TANK.
2017-09-29 08:50 | YES | NO | 19990038 | 1999-03-17 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 1999-02-09 | 1450 | CA | KERN |  | NO |  | NO | SEC 30, T28S-R27E, WEST SIDE OF CHESTER AVENUE |  | LINE PIPE | PIPE |  | 1980 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 345527.4367 | 697068.4039 | CRUDE OIL | 1 | 15 | 0 | NO | NO | 12.75 | 0.25 | 52000 | WELDED |  | 1036 | 698 | YES | 4 | 1295 | 6 | 95 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | D F SHEAFF | 7132414381 | THE CONTAMINATION FROM THIS RELEASE OCCURRED UNDERNEATH THE ROADWAY. TRAFFICHAS BEEN REROUTED AS THE CONTAMINATED SOIL IS REMOVED AND NEW PIPING INSTALLED.
2017-09-29 08:50 | YES | NO | 19990039 | 1999-03-22 | 30909 | TRANSMONTAIGNE PIPELINE INC | YES | 1999-02-17 | 930 | IL | LASALLE | STREATOR | NO |  | NO | ONE MILE SOUTH AND ONE MILE WEST OF KERNAN - SOUTH 1/4 MILE FROM INTERSECTION OF RTE 18 & E 21ST ST IN BARROW DITCH NE 1/4 SECTION 33 T31N-R4E |  | LINE PIPE | PIPE |  | 1905 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 138210.9747 | 278827.3616 | DIESEL FUEL | 3 | 0 | 92 | NO | NO | 8 | 0.32 | 24000 | THREADED |  | 650 | 185 | YES | 0 | 880 | 7 | 70 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | RICK H HOOD | 5015716903 | AT 9:30AM DEBBIE LALONDE RECEIVED A CALL FROM BOB ROY OF AMOCO WHO HADRECEIVED A CALL FROM ED BEDEKER, OTTER CREEK TWP ROAD SUPERVISOR, THAT THEREWAS RED PRODUCT COMING FROM A TILE AND FLOWING INTO A DRAINAGE DITCH, SAYS ITSMELLS LIKE DIESEL. RANDY GREEN LEFT FOR SITE, LINE WAS SHUT DOWN AT 9:42AFTER PHONE CALL TO ED BEDEKER BY RANDY GREEN CONFIRMING LEAK. CONTRACTORSHAD LEFT FOR SCENE WITH RANDY, LINE WAS EXPOSED TO LOCATE LEAK. VAC TRUCKSWERE CALLED, BLOCK VALVES SHUT, BOOMS AND PADS WERE PLACED AT VARIOUS SITES ONCREEK. PIPE WAS REPLACED. TIME LINE ATTACHED.
2017-09-29 08:50 | YES | NO | 19990040 | 1999-03-19 | 12622 | MOBIL EXPLORATION & PRODUCING US INC | NO | 1999-03-06 | 1345 |  |  |  | YES | N 3015.7 W 8801.4 | Null | SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1986 | OTHER | UKNOWN AT THIS TIME | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 120934.6029 | 243973.9414 | TRANSMIX (PART.REFINED PETRO) | 3 | 6 | 0 | NO | NO | 6 | 0 | 52000 | WELDED |  | 2100 | 1300 | YES | 33 | 2700 | 7 | 86 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | TONI COLLIER | 3348732113 | BOAT CAPTAIN FROM JANIECE G. NOTICED SHEEN ON WATER. AS HE PROCEEDED CLOSER,HE SAW BUBBLING ON WATER. BOTH ENDS OF LINE WERE ISOLATED AND PIPELINE WASDEPRESSURED. DIVERS DISCOVERED A 1/4 HOLE AT 6 O'CLOCK POSITION, 600 FT FROM77B PLATFORM.
2017-09-29 08:50 | YES | NO | 19990042 | 1999-03-06 | 22610 | WILLIAMS PIPELINE CO | YES | 1999-03-01 | 1400 | OK | PONTOTOC |  | NO |  | NO | ALLEN STATION, 107 SOUTH CAMPER ROAD, ALLEN, OK 74017 |  | PUMPING STATION | OTHER | FILTER | 1998 | OTHER | INCORRECT TYPE OF O-RING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4040 | 2791.8617 | 5632.3127 | NATURAL GAS LIQUID | 2 | 204 | 66 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH L LYBARGER | 9185735774 | 14:15-AERIAL PATROL PILOT CONTACTED THE OKLAHOMA CITY COORDINATOR OFMAINTENANCE FOR THE AREA AND REPORTED THAT HE SAW PRODUCT SPRAYING FROM AFILTER VESSEL AT ALLEN STATION DURING HIS AERIAL PATROL. THE COM IMMEDIATELYCONTACTED STATION PERSONNEL AND INSTRUCTED THEM TO INVESTIGATE. 14:15 TO14:30- STATION PERSONNEL INVESTIGATED AND CONFIRMED PRODUCT WAS SPRAYING FROMTHE FILTER LOCATED BETWEEN TANKS #114 AND #875. 14:30- VALVE AT TANK 114 WASCLOSED TO ISOLATE THE FILTER, WHERE UPON PRODUCT STOPPED SPRAYING OUT OF THEFILTER. THE LEAK SITE WAS ASSESSED AND PILOT HOLES WERE DUG TO COLLECTPRODUCT. 14:33-STATION PERSONNEL NOTIFIED THE OKLAHOMA AREA SUPERINTENDENTAND GAVE HIM A VERBAL ASSESSMENT. AMOUNT OF PRODUCT LOST WAS INTIALLYREPORTED AS ONE-HALF TO ONE BARREL. THEY ALSO REPORTED THAT A FROST BALL HADFORMED ON THE GROUND AROUND THE FILTER VESSEL. 14:45- A VACUUM TRUCK WASDEPLOYED TO THE STATION TO ASSIST IN COLLECTING PRODUCT. 14:45-16:00-SUPERINTENDENT OF OPERATIONS CONTACTED THE REGION ENVIRONMENTAL SPECIALIST ANDDIRECTOR OF OPERATIONS. SITE ASSESSMENT CONTINUED. STATION PERSONNEL CHECKEDLOCATION INVENTORY REPORTS AND DISCOVERED THAT TANK 114 INVENTORY INDICATED ASHORTAGE OF 204 BARRELS OVER THE THREE DAY PERIOD PRECEDING DISCOVERY OF THERELEASE. 15:30-REGION ENVIRONMENTAL SPECIALIST WAS UPDATED WITH THE MOSTCURRENT INFORMATION. 16:00- A LOCAL CONTRACTOR WAS CONTACTED AND DEPLOYED ATEAM TO ASSIST IN CLEAN-UP OPERATIONS. 16:00 - OKC AREA SUPERINTENDENT ANDCOORDINATOR OR MAINTENANCE DEPARTED FOR ALLEN STATION. 16:14-REGIONALENVIRONMENTAL SPECIALIST MADE TELEPHONIC NOTIFICATION TO: NRC-16:12 OKLAHOMACORPORATION COMMISSION - 16:05 LEPC-16:20 OKLAHOMA DEPARTMENT OF ENVIRONMENTALQUALITY -16:10 MARCH 29, 1999 ALL CONTAMINATED GRAVEL AND SOIL WAS REMOVED ANDLAND-FARMED ON SITE. NEW GRAVEL AND SOIL WERE BROUGHT IN TO COMPLETE THEREMEDIATION PROCESS. AN INVESTIGATION WAS CONDUCTED OF THE FILTER AND THESECONCLUSIONS REACHED: THE CAUSE OF THE RELEASE WAS FAILED O-RING BRACKETLOCATED INSIDE THE FILTER VESSEL. THE FAILURE CAUSED THE O-RING TO SHIFT DOWNAND IN CREATING AN AIR GAP BETWEEN THE LID AND VESSEL BODY PROVIDING ALOCATION FOR PRODUCT TO ESCAPE OUT OF THE FILTER VESSEL. UPON FURTHERINVESTIGATION IT WAS DISCOVERED THAT THE MANUFACTURER SENT THE INCORRECT TYPEOF O-RING CAUSING IT TO SWELL AND FIT IMPROPERLY IN USE, RESULTING IN THE GAPWHICH ALLOWED THE PRODUCT TO ESCAPE. THE FILTER MANUFACTURE HAD BEENCONTACTED REGARDING DESIGN AND MANUFACTURING SPECIFICATIONS.
2017-09-29 08:50 | YES | NO | 19990043 | 1999-04-06 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1999-03-12 | 943 | OK | GARVIN |  | NO |  | NO | NW/4 SECTION 7-T4N-R2W |  | NO DATA | VALVE |  |  | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6600 | 4560.9622 | 9201.3029 | CRUDE OIL | 3 | 75 | 70 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | JAMES A HENRY | 5802557151 | BACKHOE OPERATOR TRENCHING BESIDE PIPELINE HIT AN UNMARKED AND UNMAPPED BRANCHCONNECTION WELDED TO SIDE OF PIPELINE BEING LOWERED IN PLACE, BREAKING BRANCHCONNECTION.
2017-09-29 08:50 | NO | NO | 19990044 | 1999-04-06 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1999-03-05 | 1605 | OK | NOBEL |  | NO |  | NO | NW 1/4 SECTION 33 RANGE 20N TOWNSHIP 2W |  | LINE PIPE | PIPE |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 4 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB AEBI | 5803956294 | VINCE EITZEN, A KOCH EMPLOYEE WAS DRIVING BY AND SPOTTED THE LEAK. WESCHRISTENSEN WAS NOTIFIED AT 16:05. WES CALLED BOB AEBI CONCERNING THERELEASE. SINCE THE RELEASE INVOLVED WATER, A REPORT WAS CALLED INTO THE NRCAT 16:50. REPORT NUMBER 476010 AND TALKED TO PETTY OFFICER MATT ROBERSTON.THE OCC WAS CALLED AT 16:40. A MESSAGE WS LEFT ON THE RECORDER. AT 16:55 THEOKLAHOMA DEQ WAS NOTIFIED.
2017-09-29 08:50 | YES | NO | 19990045 | 1999-04-06 | 22855 | KOCH PIPELINE COMPANY, L.P. | YES | 1999-03-09 | 1015 | KS |  | DANVILLE | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1935 | OTHER | EROSION/CHANNELING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 24186.9206 | 48794.7883 | BUTANE | 2 | 5 | 0 | NO | NO | 6 | 0.22 | 0 | WELDED |  | 1440 | 800 | YES | 0 | 1815 | 11 | 94 | NO DATA | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | BOB AEBI | 5803956294 | A FARMER SPOTTED THE VAPOR CLOUD AND CALLED THE EMERGENCY NUMBER ON THE RIGHTOF WAY SIGN. THE RELEASE AS CONFIRMED TO BE KOCH PROPERTY. THE LOCAL SHERIFFDEPARTMENT AND LEPC WAS NOTIFIED. THE LINE WAS REPAIRED AND RETURNED TOSERVICE. AGENCIES NOTIFIED: COUNTY SHERIFF, LEPC, NRC, KANSAS CORPORATIONCOMMISSION AND KANSAS DEQ.
2017-09-29 08:50 | NO | NO | 19990046 | 1999-04-07 | 30991 | MOBIL OIL CORPORATION | YES | 1999-03-02 | 540 | IL | MARION | PATOKA | NO |  | NO | PATOKA CRUDE OIL TANK FARM FACILITY IS LOCATED 1 MILE NORTH OF THE CITY OF PATOKA, IL ON IL STATE HWY 51. THE FACILITY IS ON THE EAST SIDE OF THE HWY. |  | TANK FARM | VALVE |  | 1998 | OTHER | NEEDLE VALVE OPENED/VIBR. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 5 | 4 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D G SCOTT | 2146585914 | A LEAK OF 5 BARRELS OR LESS OF OMEGA CRUDE OIL WAS DISCOVERED AT PATOKATERMINAL AT 5:30AM, TUESDAY MORNING, MARCH 2, 1999. THE LEAK OCCURRED FROM ANOPEN 1/4" NEEDLE VALVE ON A SAMPLE POINT OFF THE 8" CONTROL LOOP, DOWNSTREAMOF THE 8" CONTROL VALVE ON THE #1-20" CRUDE PIPELINE INSIDE THE PATOKATERMINAL FENCELINE. THE OIL LEAKED THROUGH AN OPEN DRAIN IN THE SECONDARYCONTAINMENT, DOWN THROUGH A WASH AND INTO THE NORTH FORK CREEK, A DRINKINGWATER SUPPLY FOR THE CITY OF PATOKA. THE NORTH FORK CREEK IS LOCATED ABOUT400 YARDS SOUTH OF THE PATOKA TERMINAL AND AT THE LOCATION RUNS EAST TO WEST.THE LEAK WAS DISCOVERED BY STEVE COX, OPERATOR, AT ABOUT 5:40AM. STEVESMELLED CRUDE OIL UPON ARRIVING FOR WORK AND TOGETHER WITH THE OPERATOR ONSHIFT, INVESTIGATED TO DISCOVER THE LEAK. STEVE QUICKLY DETERMINED THAT OILHAD ENTERED THE CREEK, NOTIFIED THE ACTING FACILITY SUPERVISOR, WHO RESPONDEDTO PERFORM RECONNAISANCE AND BEGIN CLEANUP OPERATIONS. CRUDE OIL WAS OBSERVEDAT THIS TIME TO BE SPREAD IN "RIBBONS" OVER APPROXIMATE 1/2 MILE DOWN THECREEK. WITHIN AN HOUR AFTER DISCOVERY, BOOM WAS BEING APPROPRIATELY DEPLOYEDON THE CREEK AND THE CITY OF PATOKA HAD BEEN NOTIFIED TO SHUT IN THEIR WATERINTAKE FROM THE CREEK, WHICH IS LOCATED ABOUT 600 YARDS DOWNSTREAM OF WHERETHE OIL ENTERED THE CREEK. CLEANUP OPERATIONS CONTINUED THROUGHOUT THE DAY.AS OF NIGHTFALL, MARCH 2ND, APPROXIMATELY 95% OF THE OIL IN THE WATER HAD BEENREMOVED; CLEANUP OF REMAINING OIL CONTINUES MARCH 3RD. IT IS EXPECTED THATTHE CLEANUP OF THE CREEK MAY BE ENTIRELY COMPLETED AS EARLY AS NIGHTFALL MARCH3RD. A SHEEN WAS OBSERVED NEAR THE PATOKA DRINKING WATER INTAKE CAUSING MOBILTO ALERT THE CITY TO SHUT IN ITS INTAKE AND DEPLOY BOOM AROUND THE INTAKE.MOBIL REQUISTIONED THE SERVICES OF GEO-TECH, AN ENVIRONMENTAL CONSULTING FIRM,TO MEET WITH THE PATOKA WATER COMMISSIONER AND TAKE WATER SAMPLES FROM THEDRINKING WATER SUPPLY. THESE SAMPLES CONFIRMED THAT THER WAS NO IMPACT TO THEPATOKA WATER SUPPLY. SAMPLE RESULTS WERE REPORTED TO THE CITY OF PATOKA ANDTHE STATE OF ILLINOIS UPON RECEIPT. PUBLIC AFFAIRS ADVISOR DERRICK HINMON, ISON SITE AT PATOKA AND WILL ASSIST IN THIS REPORT TO THE CITY. THE LEAK WASREPORTED TO THE NATIONAL RESPONSE CENTER, THE ILLINOIS ENVIRONMENTALPROTECTION AGENCY, AND THE ILLINOIS COMMERCE COMMISSION. STATE AND FEDERALAGENCIES RESPONDING TO THE SPILL INCLUDE THE ILLINOIS STATE ENVIRONMENTALPROTECTION AGENCY, THE U. S. ENVIRONMENTAL PROTECTION AGENCY, AND THE U. S.ARMY CORPS OF ENGINEERS. ALL THE ABOVE AGENCIES RESPONDED MARCH 2ND TOOBSERVE CLEANUP OPERATIONS THEN UNDERWAY.
2017-09-29 08:50 | YES | NO | 19990047 | 1999-02-23 | 31241 | DUKE ENERGY PIPELINE CO | NO | 1998-10-18 | 1745 | TX | COLORADO | SEALY | NO |  | NO | 1 MILE NORTH OF THE I-10. SAN BERNARD RIVER BRIDGE |  | LINE PIPE | PIPE |  | 1924 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 524866.7851 | 1058868.3075 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 8 | 0.32 | 2260 | WELDED |  | 630 | 100 | YES | 8 | 806 | 0 | 68 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | KENNETH D PATTERSON | 4052397191 | TRIBUTARY OF THE SAN BERNARD RIVER FLOODED. FORCE OF WATER WASHED OUT PIPEAND DAMAGED. DAMAGED OCCURRED 25' FROM WATERS EDGE. CROSSING REBOARDED AND1000' OF PIPE REPLACED.
2017-09-29 08:50 | YES | NO | 19990048 | 1999-04-09 | 4906 | EXXON PIPELINE CO | NO | 1999-03-06 | 142 | TX | ELLIS | MILFORD | NO |  | NO | GO 45 MILES NORTH OF WACO ON HWY 35 NORTH AND TAKE MILFORD EXIT, TURN RIGHT AND GO 1 MILE, TURN RIGHT ONTO HWY 77; GO 1/4 MILE TURN LEFT ONTO HWY 78, THENO |  | PUMPING STATION | OTHER | OUTBOARD BEARING/PUMP | 1968 | OTHER | EQUIPMENT FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 65300 | 45125.8832 | 91037.1336 | DIESEL FUEL | 3 | 0 | 0 | YES | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | F T BRADSHAW | 7136562232 | A DISPATCHER AT EPC HOUSTON OIL CONTROL CENTER RECEIVED ALARMS OF SYSTEMSTATUS AT THE MILFORD BOOSTER PUMP STATION ON EPC'S BAYTOWN TO IRVING REFINEDPRODUCTS PIPELINE SYSTEM ON 3/6/99. A FIELD PERSONNEL WAS CONTACTED AND ANDEPC EMPLOYEE WAS SENT TO THE STATION TO INVESTIGATE. ON ARRIVING AT THESTATION, HE FOUND THE PUMP ON FIRE AT THE OUTBOARD BEARING END OF THE PUMP.THE FIRE WAS EXTINGUISHED. A MECHANICAL FAILURE IN THE PUMP CAUSED THEBEARING TO OVERHEAT AND FAIL, WHICH ALLOWED THE OVERHEATED SHAFT TO LOOSENTHE PUMP SEALS AND COME IN CONTACT WITH THE DIESEL PRODUCTS AT THE OUTBOARDEND OF PUMP. THIS RESULTED IN A FIRE. THE PUMP WAS REPAIRED AND PUT BACK INSERVICE.
2017-09-29 08:50 | YES | NO | 19990049 | 1999-03-16 | 31288 | KOCH PETROLEUM GROUP LP | Null | 1998-11-22 | 1810 | TX | TARRANT | FORT WORTH | NO |  | NO | LEAK WAS LOCATED AT 12550 TRINITY BLVD EULESS TX 76040. LOCATED WITHIN THE CITY LIMITS OF FORT WORTH. |  | PUMPING STATION | OTHER | FILTER VESSEL | 1989 | OTHER | GASKET FAILE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 44000 | 30792.1847 | 62120.274 | JET FUEL | 3 | 50 | 36 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LANCE BALLES | 8176853425 | GASKET FAILED ON FILTER VESSEL. THE RELEASED FUEL MIGRATED OVERLAND IN A PATHAPPROXIMATELY 320 FEET LONG AND 6 FEET WIDE. APPROXIMATELY 50 BARRELS OF JETFUEL WAS RELEASED REMEDIATION INCLUDED THE RECOVERY OF 36 BARRELS OF JET FUELAND THE REMOVAL OF APPROXIMATELY 280 CUBIC YARDS OF JET FUEL CONTAMINATED SOIL.
2017-09-29 08:50 | YES | YES | 19990050 | 1999-04-15 | 30909 | TRANSMONTAIGNE PIPELINE INC | YES | 1999-03-19 | 915 | IN | LAKE | SCHERERVILLE | NO |  | NO | AT TANK 1613 PIPING MANIFOLD |  | TANK FARM | TANK |  | 1957 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 1 | 1 | 0 | 517000 | 357275.3696 | 720768.7296 | GASOLINE | 1 | 285 | 100 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JERRY S PATTEN | 2193224913 | PUMPING OUT TANK 1613 BOTTOMS, USING PORTABLE 3" AIR PUMP AND HOSES AND AIRCOMPRESSOR. WHILE PUMPING, THE HOSE CONNECTION TO THE PUMP DISCHARGE FITTINGCAME LOOSE, CAUSING THE DISCHARGE HOSE TO COME OFF THE PUMP, ALLOWING GASOLINETO BE PUMPED ON THE GROUND. THE GASOLINE VAPORS CAME IN CONTACT WITH AIRCOMPRESSOR EXHAUST MANIFOLD, CREATING THE SOURCE OF IGNITION.
2017-09-29 08:50 | YES | NO | 19990051 | 1999-04-16 | 1683 | BP PIPELINES INC | YES | 1999-03-16 | 1110 | MI | BRANCH | SHERWOOD | NO |  | NO | ONE QUARTER MILE NORTH OF THE INTERSECTION OF DIVISION & FARRAND ROADS, APPROX 1 MILE EAST OF SHERWOOD, MI NORTHWEST QUARTER SECTION 35, TOWNSHIP 5S, RANGE 8W |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 280000 | 193495.3646 | 390358.3062 | GASOLINE | 1 | 80 | 75 | NO | NO | 10 | 0.28 | 42000 | WELDED |  | 1440 | 600 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GERALD J LAUER | 8154786100 | 16 MARCH 1999 AT APPROXIMATELY 1030 CST, A THIRD PARTY AGRICULTURAL DRAIN TILECONTRACTOR STRUCK AND CRACKED BP AMOCO PIPELINE 10" PETROLEUM PRODUCTSPIPELINE. THE INCIDENT OCCURRED IN AN AGRICULTURAL FIELD APPROXIMATELY ONEQUARTER MILE NORTH OF THE INTERSECTION OF DIVISION AND FARRANDS RD; ONE MILEEAST OF SHERWOOD, MI. UNLEADED GASOLINE PRODUCT ESCAPED FROM THE PIPELINE ANDFLOWED INTO NEWLY INSTALLED DRAIN TILE SYSTEM AND SUBSEQUENTLY INTO COUNTRYDRAINAGE DITCH SYSTEM. CONTRACTOR CALLED BPAMOCO PIPELINE PERSONNELIMMEDIATELY AFTER THE PIPELINE WAS STRUCK AND PRODUCT WAS NOTICED ESCAPING.BPAMOCO IMMEDIATELY SHUT THE PIPELINE DOWN AND INITIATED EMERGENCY RESPONSEPROCEDURES. EMERGENCY RESPONSE EQUIPMENT WAS DEPLOYED INTO THE COUNTRY DITCHAND AT THE LEAK SIGHT. CONTAINMENT AND SORBANT BOOM WERE DEPLOYED IN COUNTYDRAINAGE DITCH AND WATER SKIMMING/PRODUCT RECOVERY OPERATIONS CONDUCTED. THELEAK SIGHT WAS EXCAVATED AND VACUUM TRUCK PRODUCT RECOVERY OPERATIONSIMPLEMENTED. PIPELINE SYSTEM WAS DRAINED, DAMAGED SECTION REMOVED ANDREPLACEMENT PIPE INSTALLED. THE PIPELINE SYSTEM WAS AVAILABLE FOR RETURN TOSERVICE AT APPROXIMATELY 1830, 17 MARCH 1999. ENVIRONMENTAL RECOVERY ANDREMEDIATION EFFORTS WERE INITIATED AND CONTINUED. APPROXIMATELY 80 BARRELS OFPRODUCT WERE RELEASED AND 75 BARRELS RECOVERED WITHIN SEVEN DAYS AFTER THEINCIDENT. THE STATE OF MICHIGAN "ONE CALL" SYSTEM, "MISS DIG," WAS NOT USEDIN THIS INSTANCE BY THE CONTRACTOR THAT STRUCK THE PIPELINE AND CAUSED THERELEASE.
2017-09-29 08:50 | YES | NO | 19990052 | 1999-04-16 | 15156 | SINCLAIR PIPELINE CO | NO | 1999-03-19 | 1147 | WY | PLATTE |  | NO |  | NO |  |  | PUMPING STATION | VALVE |  | 1993 | OTHER | BLOWN GASKET ON VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 103658.231 | 209120.5212 | CRUDE OIL | 1 | 3370 | 2019 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | DON K NEUWERTH | 3073283549 | ON 3/19/99, THE CHEYENNE TO BN JUNCTION SEGMENT OF THE CHEYENNE TO CASPERSTATION 10" WAS SHUT DOWN AND BLOCKED IN. THERMAL EXPANSION BETWEEN A CLOSEDBLOCK VALVE AND A CHECK VALVE (SEE ATTACHED DRAWING) CAUSED AN UNUSUALLY HIGHPRESSURE WHICH RUPTURED A FLANGE GASKET. AT 11:47 A LOW ALARM WAS RECEIVED ONSCADA AT THE SINCLAIR CONTROL CENTER (SCC) FROM A TRANSMITTER AT BN JUNCTION.AT THIS POINT THE PRESSURE UP STREAM OF THE VALVE WAS 989 PSI. THE OPERATORAT SCC CHANGED THE LOW ALARM POINT FROM 990 TO 900 PSI. AT 13:01 ANOTHER LOWALARM WAS RECEIVED, THE PRESSURE NOW AT 893 PSI. FOLLOWING THIS THE OPERATORCHANGED THE LOW ALARM POINT TWICE AND GOT TWO MORE ALARMS, THE LAST AT 14:57,WITH THE PRESSURE AT 499 PSI. IN ADDITION TO THESE INDICATIONS, THE OPERATORWROTE DOWN A LINE PRESSURE AT THE CHEYENNE STATION OF 368 PSI FOR HIS ONEO'CLOCK READINGS IN THE DAILY LOGS. A PRESSURE OF 43 PSI WAS ENTERED FOR THETWO O'CLOCK READINGS. NORMALLY THESE PRESSURES STAY RELATIVELY CONSTANT WHENTHIS LINE IS BLOCKED IN. DESPITE THESE INDICATIONS NO ACTION WAS TAKEN. ON3/20/99 AT 07:49 THE MOTOR OPERATED VALVE WAS OPENED AND THE PUMP AT CHEYENNEWAS STARTED. AT 08:47 A CALL WAS RECEIVED FROM FARMER BEN LYMAN WHO REPORTEDOIL RUNNING OFF THE HILL AND "OIL SPRAYING OUT OF THE GROUND." THE PUMPS ATGUERNSEY, CHEYENNE, AND BEAR CREEK WERE SHUT DOWN. MR. LYMAN REPORTED THATTHE OIL QUIT SPRAYING. PIPELINE PERSONNEL WERE DISPATCHED TO THE SCENE ANDTHE SUBSEQUENT CLEAN UP AND REPAIR WERE INITIATED.
2017-09-29 08:50 | YES | NO | 19990053 | 1999-04-20 | 15674 | PLANTATION PIPE LINE CO | YES | 1999-03-24 | 840 | GA | HARRIS | HAMILTON | NO |  | NO | THE RELEASE ON THE 8" COLUMBUS LATERAL WAS IN THE SW QUADRANT OF HARRIS COUNTY GA, OFF HOODY HOUSTON RD. FROM HOODY HOUSTON RD TRAVEL IN NW DIRECTION ALONG THE |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69105.4873 | 139413.6808 | GASOLINE | 1 | 30 | 5 | NO | NO | 8.63 | 0.19 | 52000 | WELDED |  | 1225 | 70 | YES | 24 | 2034 | 11 | 71 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | JACQUE L WILLIAMS JR | 7707514095 | PLANTATION'S OPERATIONS CONTROL CENTER (OCC) WAS NOTIFIED BY A CONTRACTORMOWING THE ROW FOR GEORGIA POWER THAT HE HAD DISCOVERED GASOLINE ON OUR ROW.THE CONTRACTOR CALLED PLANTATION USING OUR 1-800 TELEPHONE NUMBER. THEPIPELINE WAS REPAIRED BY WELDING A 3 FOOT "TYPE B" FULL ENCIRLEMENT SLEEVEAROUND THE CORROSION PIT AREA.
2017-09-29 08:50 | YES | NO | 19990055 | 1999-04-21 | 22430 | WEST SHORE PIPELINE CO | YES | 1999-03-25 | 735 | IL | COOK |  | NO |  | NO | 12920 BELL ROAD, LEMONT, IL |  | PUMPING STATION | VALVE |  | 1974 | OTHER | CLOSED STOP ON VALVE WORN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FUEL OIL | 1 | 340 | 336 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | JAY ANDREWS | 8474390270 | INVESTIGATION INTO THE INCIDENT REVEALED THAT A TWO (2) INCH 600# BALL VALVECONNECTED TO THE DRAIN DOWN PIPING HAD MALFUNCTIONED. THE OPEN/CLOSEINDICATOR ON THE VALVE WAS NOT PROPERLY INDICATING THE CLOSED PORTION. THEVALVE WAS SLIGHTLY OPEN ALLOWING PRODUCT TO PASS THROUGH THE VALVE AND FLOWINTO THE DRAIN DOWN SYSTEM. THE PRODUCT PASSING BY THE DRAIN VALVE QUICKLYFILLED THE DRAIN SYSTEM AND SUMP TANK. THE PIPELINE CONTROL SYSTEMAUTOMATICALLY SHUT DOWN THE PIPELINE WHEN THE HIGH-HIGH LEVEL ALARM WASACTIVATED IN THE SUMP TANK. PRODUCT OVERFILLED THE SUMP TANK AND SPILLED ONTOTHE GROUND. STATION VALVES WERE CLOSED, ISOLATING THE STATION, AND STOPPINGTHE PRODUCT OVERFLOW. A SPILL RESPONSE CONTRACTOR WAS IMMEDIATELY AVAILABLEAND ON SITE WITHIN MINUTES TO BEGIN PRODUCT RECOVERY.
2017-09-29 08:50 | YES | NO | 19990056 | 1999-04-27 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 1999-03-23 | 815 | CA | KINGS |  | NO |  | NO | SEC. 29, T23S-R18E, 250' WEST OF HWY 33 IN NW CORNER OF STA |  | PUMPING STATION | NO DATA |  |  | OTHER | INSULATING GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 17276.3718 | 34853.4202 | CRUDE OIL | 1 | 200 | 185 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D F SHEAFF | 7132414381 | INSULATING GASKET FAILED DURING NORMAL OPERATIONS. REPLACED INSULATING GASKETIN FLANGE.
2017-09-29 08:50 | YES | NO | 19990057 | 1999-04-27 | 22610 | WILLIAMS PIPELINE CO | YES | 1999-03-24 | 1030 | IL | WILL |  | NO |  | NO | 2.5 MILES SOUTH OF HIGHWAY 113 ON WEST RIVER ROAD (SECTION 26-TOWNSHIP 32 NORTH- RANGE EAST) |  | NO DATA | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 345527.4367 | 697068.4039 | GASOLINE | 1 | 2693 | 1362 | NO | NO | 12 | 0.25 | 0 | NO DATA |  | 550 | 471 | YES | 8 | 1022 | 5 | 92 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | KENNETH L LYBARGER SR | 9185735774 | 10:21-SCADA ALARM SOUNDED IN WILLIAMS PIPELINE COMPANY DISPATCH CENTER INTULSA, AND LINE PRESSURE DROPPED FROM 477 PSIG TO 67 PSIG. THE LINE WAS SHUTIN AT THE TIME. 10:30-EMPLOYEE OF TENANT FARMING THE LAND CALLED THE TULSADISPATCH CENTER AND REPORTED HITTING THE PIPELINE WHILE ATTEMPTING TO DIG UPTREE STUMPS AND SMALL BRUSH NEAR THE LINE. HE ADMITTED THAT HE DID NOT THINKHE NEED TO CALL THE ILLINOIS ONE-CALL AGENCY TO HAVE THE LINE LOCATED,ALTHOUGH HE KNEW THE PIPELINE WAS IN THE VICINITY. DISPATCH IMMEDIATELY BEGANDRAINING LINE PRESSURE BACK INTO THE HEYWORTH TERMINAL TO MINIMIZE THE SIZE OFANY POTENTIAL RELEASE. (SUBSEQUENT INVESTIGATION BY WPL MAINTENANCE CREWDISCOVERED 11 FRESH DOZER BLADE MARKS ON THE PIPELINE SURFACE IN ADDITION TOTHE HIT FROM THE BLADE THAT PUNCTURED THE LINE). 11:05-NEAREST MAINTENANCECREW DISPATCHED TO SITE. 11:15-AREA OPERATIONS SUPERVISOR NOTIFIED ANDDISPATCHED TO THE SITE. 11:45-AREA ENVIRONMENTAL SPECIALISTS NOTIFIED ANDLOCAL ENVIRONMENTAL CONTRACT CREWS AND EQUIPMENT, INCLUDING VACUUM TRUCKSDISPATCHED TO THE SITE. 12:00-ILLINOIS ENVIRONMENTAL PROTECTION AGNECYNOTIFIED. 12:15-NATIONAL RESPOSE CENTER NOTIFIED (CASE #473977) 12:30-WILLCOUNTY SHERIFF NOTIFIED. 12:45-INCIDENT COMMAND SYSTEM INSTITUTED BY WPLPERSONNEL TO MANAGE THE INCIDENT. 12:45-CLEANUP OPERATIONS COMMENCED. FREEPRODUCT RECOVERED FROM SITE AND TRANSPORTED TO THE WPL HEYWORTH TERMINAL.CONTINUED UNTIL ALL FREE STANDING PRODUCT WAS RECOVERED. 12:46-WILL COUNTYEMERGENCY MANAGEMENT OFFICE (LEPC) NOTIFIED. MARCH 26, 1999 6:00_-18:00- LINEREPAIRED BY CUTTING OUT THE DAMAGED SECTION AND REPLACING WITH 20-PLUS FEET OFNEW X-42 GRADE PRE-TESTED PIPE WITH FUSION BONDED EPOXY COATING. ALL WELDSWERE X-RAYED. 19:45-BEGAN FILLING LINE WITH PRODUCT. REMOVAL OF PRODUCTSATURATED SOIL CONTINUED WITH OVERVIEW BY THE ILLINOIS EPA UNTIL COMPLETED.
2017-09-29 08:50 | NO | NO | 19990059 | 1999-04-26 | 31314 | DYNAIR FUELING INC | NO | 1997-05-18 | 330 | AZ | MARICOPA | PHOENIX | NO |  | NO | HIGH POINT VENT PIPE LOCATED ON AIRCRAFT HYDRANT FUELING SYSTEM PIPE LOCATED ON ROADWAY MEDIUM OF SKY HARBOR BLVD TERMINAL THREE ACCESS ROAD. |  | LINE PIPE | PIPE |  | 1980 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 35422.5533 | 71461.5977 | JET FUEL | 1 | 0 | 0 | NO | NO | 2 | 0.22 | 1884 | WELDED |  | 400 | 180 | YES | 72 | 500 | 2 | 99 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC | NO DATA |  | Null | NO DATA |  | Null | Null | RONALD FAVERO | 6022733662
2017-09-29 08:50 | YES | NO | 19990060 | 1999-04-30 | 18162 | SEAWAY PIPELINE INC | YES | 1999-03-23 | 940 | OK | GARVIN |  | NO |  | NO | THREE MILES EAST AND ONE MILE SOUTH OF THE TOWN OF PAOLI, OK SECTION 16, T4N R1E LATITUDE N34 49' 2.5', LONGITUDE W97 12' 32.1 |  | LINE PIPE | PUMP |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 103658.231 | 209120.5212 | GASOLINE | 1 | 13 | 10 | NO | NO | 16 | 0.25 | 52000 | WELDED |  | 903 | 300 | YES | 24 | 1129 | 3 | 64 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | MIKE A SCHMIDT | 9182232957 | AT 9:40 HOURS ON MARCH 24, 1999 SEAWAY PIPELINE EXPERIENCED A PETROLEUMPRODUCTS SPILL OF UNLEADED GASOLINE IN SECTION 16, T4N, R1E, GARVIN COUNTY,OK, APPROXIMATELY FIVE MILES NORTH OF THE TOWN OF PAULS VALLEY AND THREE MILESEAST OF THE TOWN OF PAOLI. THE EXTENT OF THE SPILL WAS CONFINED ENTIRELY TOTHE PIPELINE R-O-W. ARCO PIPELINE COMPANY (APL) IS THE OPERATOR OF SEAWAYPIPELINE, WHICH EXTENDS FROM GALENA PARK, TEXAS TO CUSHING, OKLAHOMA. THEREWERE NO INJURIES, FIRES, OR EXPLOSIONS RESULTING FROM THIS INCIDENT AND THERELEASED PRODUCT DID NOT REACH ANY WATERWAYS. THE RELEASE WAS A RESULT OFDAMAGE BY OUTSIDE PARTIES, CAUSED BY EXCAVATION ACTIVITIES ASSOCIATED WITH THEREMOVAL FOR SALVAGE OF AN IDLE 12-INCH PIPELINE. THE IDLE 12-INCH LINE BEINGREMOVED IS IN A PARALLEL R-O-W, SIXTEEN FEET TO THE EAST OF THE SEAWAYPIPELINE. IN AN ATTEMPT TO LOCATE THE LINE BEING SALVAGED, THE TRACKHOEOPERATOR MISTAKENLY LOCATED HIMSELF OVER THE SEAWAY LINE. ATTEMPTING TOLOCATE THE IDLE LINE, CONTACT WAS MADE WITH THE OPERATING LINE CAUSING A GOUGEWHICH PENETRATED THE PIPE. AN APL INSPECTOR WAS ASSIGNED TO CONTINUOUSLYMONITOR THE FOREIGN CONSTRUCTION ACTIVITY; HOWEVER, HE WAS LOCATING THE LINEAT A WORKSITE APPROXIMATELY 1/2 MILE AWAY AT THE TIME OF THE INCIDENT.IMMEDIATELY AFTER DISCOVERY OF THE RELEASE, THE PIPELINE WAS SHUT DOWN ANDMAINLINE ISOLATION VALVES ON EITHER SIDE OF THE LEAK WAS CLOSED. EMERGENCYRESPONSE AND CLEANUP PERSONNEL WERE CALLED TO THE SITE TO UNDERTAKECONTAINMENT, CLEANUP AND REPAIR ACTIVITIES. PRODUCT FLOW WAS STOPPED BY THEAPPLICATION OF A MECHANICAL REPAIR SLEEVE. APPROXIMATELY 60 CUBIC YARDS OFSOIL WAS AFFECTED BY THE PRODUCT RELEASE. THIS AFFECTED MATERIAL HAS BEENCOLLECTED AND STAGED ON SITE UNTIL SUCH TIME THAT IT CAN BE SAMPLED FORCHARACTERIZATION AND PROPER DISPOSAL. CLEAN UP OF THE SPILL SITE IS BEINGCOORDINATED BY REPRESENTATIVES OF APL'S ENVIROMENTAL, HEALTH AND SAFETY GROUP,WITH ASSISTANCE FROM WOODWARD CLYDE ENVIRONMENTAL SERVICES.
2017-09-29 08:50 | YES | NO | 19990061 | 1999-04-27 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 1999-03-30 | 1615 | IN | PARKE |  | NO |  | NO | 2 MILES NE OF CATLIN, PARKE COUNTY, IN. SECTION 32, RANGE 15N TOWNSHIP 7W |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 410000 | 283332.4981 | 571596.0912 | DIESEL FUEL | 3 | 1487 | 1437 | NO | NO | 10 | 0.31 | 0 | WELDED |  | 1200 | 750 | YES | 8 | 1668 | 0 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | TAD A SCHELL | 4194213201 | AT 16:15 CST ON MARCH 30, 1999, MARATHON ASHLAND PIPE LINE (MAPL) WAS NOTIFIEDBY A FARMER THAT HE HAD STRUCK AND PUNCTURED MAPL'S #1-10 PRODUCTS WITH ATILING MACHING. THE FARMER HAD NOT CALLED THE INDIANA ONE-CALL SYSTEM AND HADCROSSED THE PIPELINE SEVERAL TIMES THAT DAY BEFORE STRIKING IT. THE PRODUCTRELEASED WAS HIGH SULFUR DIESEL. THE PIPELINE WAS IMMEDIATELY SHUTDOWN ANDMAPL PERSONNEL MOBILIZED TO THE SCENE. THE CLOSET UPSTREAM AND DOWNSTREAMBLOCK VALVES ON THE PIPELINE WERE CLOSED. THE DIESEL ENTERED THE TILE SYSTEMAND RAN INTO A SMALL NO-NAME DITCH WHICH IS A TRIBUTARY TO LITTLE RACCOONCREEK. THE FARMER BUILT A DAM ACROSS THE DITCH WHICH CONTAINED MOST OF THEDIESEL UNTIL MAPL PERSONNEL AND CONTRACTORS ARRIVED ONSITE. A SMALL AMOUNT,ESTIMATED A 5 BBL ENTERED LITTLE RACCOON CREEK. MAPL PERSONNEL CONSTRUCTEDFLUME DAMS IN THE DITCH AND RECOVERED THE DIESEL BY VACUUM TRUCK. THEAFFECTED TILES WERE PLUGGED TO PREVENT FURTHER MIGRATION OF PRODUCT, THENREMOVED. CLEANUP CREWS REMOVED ACCESSIBLE SMALL POCKETS OF DIESEL IN LITTLERACCOON CREEK WITH SORBENTS. AT THE PRESENT TIME, MINOR RECOVERY OF PRODUCTTRACES IN THE AFFECTED DITCH, AND REMEDIATION OF THE AFFECTED SOIL ISCONTINUING.
2017-09-29 08:50 | YES | NO | 19990062 | 1999-05-10 | 18162 | SEAWAY PIPELINE INC | YES | 1999-04-05 | 1415 | TX | PARKER |  | NO |  | NO | LOT 26 DEER CREEK SUBDIVISION, PHASE VII, BLOCK 17 IN THE TOWN OF ANNETA SOUTH |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1036582.3102 | 2091205.2117 | GASOLINE | 1 | 1516 | 900 | NO | NO | 18 | 0.28 | 52000 | WELDED |  | 1118 | 317 | YES | 8 | 1449 | 1 | 88 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GLENN W HOFFMEYER | 9182232952 | BACKHOE WAS WORKING FOR A HOME DEVELOPER AND WAS DIGGING DIRECTLY ABOVEPIPELINE. THE BACKHOE STRUCK THE PIPELINE AND GASOLINE WAS RELEASED INTO THEAIR AND ONTO THE SURROUNDING SOIL AND VEGETATION. THE PIPELINE WAS NOTRUNNING AT THE TIME OF THE RELEASE. THE RELEASE OCCURRED IN A RESIDENTIALNEIGHBORHOOD AND NEARBY RESIDENTS WERE EVACUATED AS A PRECAUTIONARY MEASURE.RECOVERY OPERATIONS FOR RELEASED GASOLINE ARE CURRENTLY UNDERWAY AND GASOLINECONTINUES TO BE REMOVED FROM THE LEAK AREA. THE PIPELINE HAS BEEN PERMANENTLYREPAIRED AND IS BACK IN SERVICE.
2017-09-29 08:50 | YES | NO | 19990063 | 1999-05-11 | 19326 | TEXAS - NEW MEXICO PIPELINE CO | YES | 1999-04-06 | 1215 | NM | SANDOVAL |  | NO |  | NO | 2 MI NORTH OF BERNALILO, NM 1-25 |  | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 138210.9747 | 278827.3616 | CRUDE OIL | 1 | 505 | 420 | NO | NO | 16 | 0.31 | 46000 | WELDED |  | 850 | 669 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | GARY L ZIMMERMAN | 7132415334 | OPERATORS CONTRACT CREW WAS PREPARING TO REMOVE A CHECK VALVE ON THE PIPELINE WHEN THE BACKHOE INADVERTENTLY STRUCK A 2" CONNECTION TO THE PIPELINE, CAUSING THE RELEASE. THE PIPELINE HAD BEEN SHUT-IN PRIOR TO THIS WORK, HOWEVER, DUE TO THE ELEVATION OF THE LINE, 505 BBLS WERE RELEASED. ALL CRUDE OIL WAS CONTAINED IN THE IMMEDIATE AREA OR WITHIN THE EXCAVATION BELLHOLE.
2017-09-29 08:50 | YES | NO | 19990064 | 1999-05-10 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1999-04-14 | 1115 | KS | RENO |  | NO |  | NO | NE 1/4 SECTION 34, TOWNSHIP 23 SOUTH, RANGE 4 WEST, RENO COUNTY, KS 4 MILES WEST OF BURRTON, KS AND 1 1/2 MILES SOUTH |  | NO DATA | PUMP |  | 1992 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2418.6921 | 4879.4788 | CRUDE OIL | 1 | 56 | 20 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | ALLEN R WILKERSON | 3162419270 | DURING HIGH WINDS, A POWER POLE WAS BLOWN OVER HITTING AN INJECTION PUMP ANDBREAKING THE BLEEDER VALVE ON TOP OF CHECK VALVE. A PLUG WAS INSTALLED INCHECK AND RECOVERED SOME OIL AND DOING SOIL REMEDIATION ON THE AREA.
2017-09-29 08:50 | YES | YES | 19990065 | 1999-01-06 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1998-12-03 | 1038 | UT |  | GRAND | NO |  | YES | THREE MILES NORTH OF MOAB, UTAH ON THE WEST SIDE OF HIGHWAY 191 GRAND COUNTY, UTAH |  | LINE PIPE | PIPE |  | 1980 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 4 | 4 | 0 | 70000 | 48987.5666 | 98827.7087 | NATURAL GAS LIQUID | 2 | 10007 | 0 | YES | YES | 10.75 | 0.25 | 2276 | WELDED |  | 1650 | 697 | YES | 24 | 2349 | 11 | 80 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | JOHNNY CAVITT | 9185736336
2017-09-29 08:50 | YES | NO | 19990066 | 1999-05-12 | 21031 | PG & E TEXAS PIPELINE, L.P. | NO | 1999-04-06 | 610 | TX |  | JIM WELLS | NO |  | NO | ONE MILE NE OF FM 624 ON FM 552; APPROXIMATELY 4 MILES EAST OF ORANGE GROVE, TX. |  | TANK FARM | OTHER | TUBING | 1998 | OTHER | FAILED STAINLESS STEEL TU | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 310974.6931 | 627361.5635 | NOT GIVEN | 2 | 3 | 0 | YES | YES | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | MICHAEL PAWELEK | 2105284204
2017-09-29 08:50 | YES | NO | 19990067 | 1999-05-18 | 22175 | DYNEGY MIDSTREAM SERVICES, L.P. | NO | 1999-04-28 | 1330 | TX | HEDERSON |  | NO |  | YES | LOOP 317 AROUND ATHENS, TX @ MILE MARKER 14.1 OFF HWY 31 AND FM 1616 |  | LINE PIPE | PIPE |  | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 518291.1551 | 1045602.6059 | NATURAL GAS LIQUID | 2 | 327 | 0 | NO | NO | 4.5 | 0.19 | 52000 | WELDED |  | 2160 | 900 | YES | 24 | 3316 | 11 | 79 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | OJ MUNNS | 9034513004
2017-09-29 08:50 | YES | NO | 19990068 | 1999-05-14 | 4906 | EXXON PIPELINE CO | YES | 1999-04-19 | 1000 | TX | HAWKINS | WOOD | NO |  | NO | HAWKINS GATHERING SYSTEM, WOOD COUNTY, TEXAS - COBB FOUNDATION PROPERTY |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5182.9116 | 10456.0261 | CRUDE OIL | 1 | 50 | 49 | NO | NO | 12 | 0.22 | 42 | WELDED |  | 188 | 50 | YES | 8 | 780 | 6 | 98 | INTERNAL | Null | YES | OTHER | INTERNAL | NO DATA |  | Null | NO DATA |  | Null | Null | J B BARN | 7136562204
2017-09-29 08:50 | YES | NO | 19990069 | 1999-05-18 | 31325 | PACIFIC PIPELINE SYSTEM LLC | NO | 1999-04-15 | 430 | CA | KERN |  | NO |  | NO | 7901 GRAPEVINE RD, LEBEC, CA. GRAPEVINE PUMP STATION IS LOCATED 1 MILE SOUTH OF THE INTERSECTION OF INTERSTATE 5 AND GRAPEVINE RD, KERN CO, CA. |  | PUMPING STATION | BOLTED FITTING |  | 1998 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 172763.7184 | 348534.202 | CRUDE OIL | 1 | 480 | 478 | NO | NO | 20 | 0.5 | 65000 | FLANGED |  | 1460 | 1239 | YES | 4 | 2128 | 11 | 1998 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | IRVIN TOOLE JR | 5627282810 | AT APPROXIMATELY 6:45 A.M., A COMPANY EMPLOYEE DISCOVERED THAT A LEAK IN THE VAULT INSIDE GRAPEVINE STATION RESULTED IN A RELEASE OF CRUDE OIL. THE LEAK OCCURRED AT AN INSULATING FLANGE GASKET ON THE HIGH PRESSURE SIDE OF THE STATION BYPASS CHECK VALVE. A 1/2" WIDE PIE SHAPED PIECE OF GASKET WAS BLOWN OUT AT THE 12 O'CLOCK POSITION. THE VALVE IS LOCATED APPROXIMATELY 4 FEET BELOW GROUND SURFACE IN A CONCRETE VAULT WITH STEEL GRATING ON THE TOP. OIL FROM THE FLANGE SPRAYED 30' TO 40' IN THE AIR. STRONG WINDS CARRIED A MIST OF OIL OVER AN AREA APPROXIMATELY 1000' WIDE BY 4000' LONG. THE IMPACTED AREA IS PRIMARILY AGRICULTURAL PROPERTY. SEVERAL SMALL BUILDINGS, A WATER TANK, A RESIDENCE, AND SOME VEGETATION (NATURAL GRASS AND SOME EUCALYPTUS TREES) DOWN-WIND OF THE STATION WERE OILED. THE CAUSE OF THE GASKET FAILURE APPEARS TO BE EITHER INCORRECT GASKET MATERIAL SELECTION AND/OR IMPROPER INSTALLATION.
2017-09-29 08:50 | YES | NO | 19990070 | 1999-05-21 | 30755 | CITGO PRODUCTS PIPELINE CO | NO | 1999-05-07 | 1500 | TX | CALDWELL | LULING | NO |  | NO | IN TEXAS DOT HWY RIGHT OF WAY, ON NORTH SIDE OF HWY 183, APPROXIMATELY ONE MILE NORTH WEST OF ITS INTERSECTION WITH INTERSTATE HWY 10, IN CITY LIMITS |  | NO DATA | PIPE |  | 1048 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 172763.7184 | 348534.202 | GASOLINE |  | 389 | 40 | NO | NO | 8 | 0.32 | 35000 | WELDED |  | 625 | 100 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | OTHER | DIG TESS | NO | YES | SAM BENTLEY | 8308755214
2017-09-29 08:50 | YES | NO | 19990071 | 1999-05-21 | 2552 | COLONIAL PIPELINE CO | YES | 1999-04-21 | 343 | GA | COBB | POWDER SPRINGS | NO |  | NO | COLONIAL PIPELINE COMPANY'S ATLANTA JUNCTION FACILITY |  | TANK FARM | TANK |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 331273 | 228927.8211 | 461839.8827 | GASOLINE | 1 | 280 | 21 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | STEPHEN E GILLIAM | 4048412314
2017-09-29 08:50 | NO | NO | 19990072 | 1999-05-25 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 1999-04-04 | 1545 | PA | LUZERNE | BERWICK | NO |  | NO | SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1932 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 48373.8411 | 97589.5765 | GASOLINE | 3 | 8 | 7 | NO | NO | 6.63 | 0.26 | 800 | WELDED |  | 800 | 250 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | ROBERT GRAY
2017-09-29 08:50 | NO | NO | 19990073 | 1999-05-25 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | NO | 1999-04-30 | 1400 | NJ | GLOUCESTER |  | NO |  | NO | OFF OF BUDD BLVD W OF ROUTE 45 IN GLOUCESTER COUNTY, NJ NEARBY THE MATTHEW BROOK CREEK |  | LINE PIPE | WELDING FITTING |  | 1945 | FAILED WELD | DAMAGE BY NATURAL FORCES | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 48373.8411 | 97589.5765 | TRANSMIX (PART.REFINED PETRO) | 1 | 7 | 3 | NO | NO | 16 | 0.28 | 0 | WELDED |  | 965 | 880 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY NATURAL FORCES |  | Null | NO DATA |  | Null | Null | D'VEDA HOLLEY | 2159376241
2017-09-29 08:50 | YES | NO | 19990074 | 1999-06-01 | 443 | AMOCO PIPELINE CO | YES | 1999-05-01 | 952 | TX | HARRIS | LAPORTE | NO |  | NO | SPENCER HIGHWAY (MAIN STREET FEEDER) & 18TH STREET IN LAPORTE, TX. |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | GASOLINE | 3 | 725 | 668 | NO | NO | 18 | 0.22 | 52000 | WELDED |  | 910 | 245 | YES | 8 | 1145 | 12 | 90 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | KIM D FREEMAN | 4099386970
2017-09-29 08:50 | YES | NO | 19990075 | 1999-06-03 | 22855 | KOCH PIPELINE COMPANY, L.P. | YES | 1999-05-01 | 1245 | IA | POLK | PLEASANT HILL | NO |  | NO | SEE ENCLOSE AERIAL PHOTO OF SITE |  | LINE PIPE | PIPE |  | 1995 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1600000 | 1105687.7975 | 2230618.8925 | CRUDE OIL | 1 | 3663 | 3662 | NO | NO | 24 | 0.31 | 60000 | WELDED |  | 975 | 700 | YES | 8 | 1369 | 2 | 95 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | ROY GENEVICH | 6514381261
2017-09-29 08:50 | YES | NO | 19990076 | 1999-05-27 | 443 | AMOCO PIPELINE CO | YES | 1999-04-23 | 1705 | MN | OTTERTAIL | FERGUS FALLS | NO |  | NO | NEAR FERGUS FALLS, MN ON ZIEGLER DEALER SHIP PROPERTY AT MP624 18 ON HWY 210 |  | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GASOLINE | 1 | 600 | 150 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1440 | 750 | NO | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DALE NEILAN | 6124254201
2017-09-29 08:50 | YES | NO | 19990077 | 1999-05-26 | 9175 | JAYHAWK PIPELINE L.L.C. | YES | 1999-05-09 | 1003 | KS | MCPHERSON |  | NO |  | NO | SW 1/4 SECTION 36, TOWNSHIP 21 SOUTH, RANGE 5 WEST, MCPHERSON COUNTY, KANSAS |  | NO DATA | PIPE |  | 1935 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 3800.8018 | 7667.7524 | CRUDE OIL | 1 | 100 | 0 | NO | NO | 8.63 | 0.25 | 30000 | WELDED |  | 700 | 520 | YES | 8 | 903 | 3 | 88 | INTERNAL | Null | YES | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | ALLEN R WILKERSON | 3162419270
2017-09-29 08:50 | YES | NO | 19990078 | 1999-06-03 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 1999-04-22 | 1000 | IL |  | GRANT PARK | NO |  | NO | SECTION 20, TOWNSHIP 32 N. RANGE 14E, YELLOWHEAD TOWNSHIP, KANKAKEE COUNTY, IL 1/2 MILE EAST OF GRANT PARK, IL |  | LINE PIPE | PIPE |  | 1939 | OTHER | UKNOWN, PIPE BEING ANALYZ | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 183000 | 126463.0418 | 255127.0358 | TRANSMIX (PART.REFINED PETRO) | 3 | 0 | 0 | NO | NO | 12 | 0.25 | 52000 | WELDED |  | 1170 | 500 | YES | 8 | 1463 | 0 | 1995 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A SCHELL | 4194213201 | ON APRIL 22, AT APPROXIMATELY 10AM, A MARATHON ASHLAND PIPELINE (MAPL) EMPLOYEE NOTED DISTRESSED VEGETATION NEAR A TEST STATION AND CASING VENT WHERE THE MAPL WABASH 12" PRODUCTS PIPELINE CROSSES UNDER IL STATE ROUTE #1 EAS OF GRANT PARK, IL. THE CASING WAS EXCAVATED AND A SMALL AMOUNT OF PRODUCT (LESS THAN ONE GALLON) WAS OBSERVED COMING FROM THE CASING. THE DECISION WAS MADE TO REPLACE THE CASED CROSSING AND A NEW PIPELINE WAS INSTALLED UNDER THE HIGHWAY BY HORIZONTAL DIRECTIONAL DRILLING. APPROXIMATELY 294 FEET OF 0.500" WALL THICKNESS, X-52 PIPE AND 10 FEET OF 0.375 WALL THICKNESS, X-52 PIPE WAS INSTALLED. PRIOR TO INSTALLATION A HYDROSTATIC TEST WAS CONDUCTED ON THE NEW SECTION OF PIPE AT 1858 (MINIMUM) PSIG. THE NEW PIPE WAS TIED IN TO THE EXISTING, UNAFFECTED PIPE. THE PIPELINE WAS THEN STARTED BACK UP AT APPROXIMATELY 7PM CST ON APRIL 27, 1999. THE AFFECTED SECTION OF PIPE WAS PULLED FROM THE CASING. A VERY SMALL ANOMALY OF UNKNOWN ORIGIN WAS DISCOVERED. THE SECTION OF PIPE WAS SHIPPED TO KIEFNER & ASSOCIATES FOR ANALYSIS. THE REPORT FROM KIEFNER STATED THAT THE ANOMALY APPEARED TO HAVE BEEN CAUSED BY THE ELECTRICAL ARCING BETWEEN THE PIPELINE AND CASING. APPARENTLY AN ELECTRICAL POWER LINE LOCATED IMMEDIATELY ABOVE THE PIPELINE CASING VENT WAS DOWNED AND MADE CONTACT WITH THE VENT PIPE, WHICH PROVIDED AN ELECTRICAL PATH FOR THE FAULT CURRENT TO TRAVEL FROM THE POWER LINE TO THE CASING, FROM WHERE THE CURRENT ARCED TO THE CARRIER PIPE. THE PRESENCE OF A LARGE HOLE MELTED IN THE CASING VENT PIPE AND AN APPARENT SPLICE IN THE OVERHEAD POWER LINE IMMEDIATELY ABOVE THE PIPELINE FURTHER SUPPORTS KIEFNERS CONCLUSIONS. THE REPORT ALSO STATED THAT IT WAS UNLIKELY THAT THE ELECTRICAL DAMAGE WAS CAUSED BY LIGHTNING DUE TO THE CHARACTERISTICS OF THE DAMAGE. A DETERMINATION THAT PROPERTY DAMAGE FROM THE INCIDENT EXCEEDED $50,000 WAS MADE ON MAY 6, 1999 AT WHICH TIME THE INCIDENT WAS REPORTED BY TELEPHONE TO THE NRC. A DOT FORM 7000-1 WAS FILED WITH THE O
2017-09-29 08:50 | YES | NO | 19990079 | 1999-06-01 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 1999-04-28 | 1530 | CA | LOS ANGELES |  | NO |  | NO | 20410 S WILMINGTON AVE, CARSON, CA 90810 |  | TANK FARM | TANK |  | 1989 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 235000 | 162397.8953 | 327622.1498 | TURBINE FUEL | 1 | 0 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | EDWARD A FANT | 7138449526
2017-09-29 08:50 | YES | NO | 19990080 | 1999-06-04 | 3466 | DOME PIPELINE CORP | YES | 1999-05-03 | 1844 | MI |  | MONROE | NO |  | NO | 10743 STONE QUARRY ROAD, RIGA, MI 49276 COCHIN PUMP SHED RIGA PUMP STATION |  | PUMPING STATION | PUMP |  | 1999 | OTHER | MECHANICAL PART FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PROPANE | 2 | 5 | 0 | YES | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | D D MALLOY | 3193547722
2017-09-29 08:50 | YES | NO | 19990081 | 1999-06-17 | 2731 | CHEVRON PIPELINE CO | NO | 1999-04-22 | 915 | TX | ECTOR |  | NO |  | NO | GOLDSMITH GATHERING SYSTEM, 4" DISCHARGE LINE AT 541 BATTERY ON THE KEYSTONE TO MIDLAND, TX PIPELINE SYSTEM SECTION 30, BLOCK 45 |  | LINE PIPE | NO DATA |  | 1998 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 150 | 140 | NO | NO | 4 | 0 | 0 | OTHER |  | 90 | 45 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | DAVE ROGERS | (281)363-7
2017-09-29 08:50 | YES | NO | 19990082 | 1999-06-11 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | NO | 1999-05-13 | 1007 | TX |  | COLLEGE STATION | NO |  | NO | EAST HIGHWAY 6 AND GREENS PRAIRIE RD |  | LINE PIPE | PIPE |  | 1993 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 27642.1949 | 55765.4723 | NOT GIVEN | 2 | 330 | 0 | NO | NO | 4.5 | 0.19 | 42000 | WELDED |  | 1440 | 420 | YES | 24 | 2527 | 0 | 93 | NO DATA | Null | Null | NO DATA |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | CHRIS MASON | 7132153022
2017-09-29 08:50 | YES | NO | 19990083 | 1999-06-11 | 26058 | LOS ANGELES DEPT OF WATER & POWER | NO | 1999-05-11 | 20 | CA | LOS ANGELES | WILMINGTON | NO |  | NO | SITE MAP ATTACHED |  | TANK FARM | WELDING FITTING |  | 1975 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | NOT GIVEN | 1 | 535 | 535 | NO | NO | 20 | 0.59 | 0 | WELDED |  | 465 | 650 | YES | 4 | 581 | 9 | 94 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | RANDOLPH J DREYER | 3105221606
2017-09-29 08:50 | NO | NO | 19990085 | 1999-06-25 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-05-17 | 1030 | TX | ROBERTSON |  | NO |  | NO | HWY 79 4 MILES NORTH OF HEARNE STATION |  | LINE PIPE | WELDING FITTING |  | 1948 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | GASOLINE | 1 | 10 | 10 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | G L ZIMMERMAN | 7132415334 | THE RELEASE OCCURRED AT A RAILROAD/HIGHWAY CROSSING. A CRACK DEVELOPED IN THEFILLET WELD OF THE WELD-PLUS END, CAUSING PRODUCT TO BE RELEASED.
2017-09-29 08:50 | YES | NO | 19990086 | 1999-06-23 | 15490 | PHILLIPS PIPE LINE CO | YES | 1999-05-20 | 2245 | KS | SEDGWICK |  | NO |  | NO | LRW-1-47- BORGER-E CHICAGO LINE - WICHITA TERMINAL - MP 273.20 SEC. 27, T 26S, R1E, SEDGWICK CO., KS |  | PUMPING STATION | OTHER | RELIEF SYSTEM | 1997 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 469.9173 | 948.013 | BUTANE | 2 | 50 | 0 | NO | NO | 0 | 0 | 0 | NO DATA |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J SCHMITZ | 9186614814 | DELIVERY TO A THIRD PARTY PIPELINE BECAME RESTRICTED CAUSING PRESSURE TO BUILDUP IN THE METER PIPING. RECENT PIPING MODIFICATIONS EFFECTIVELY BYPASSED THEAUTOMATIC BLOCK VALVE. AS A RESULT, THE RELIEF VALVE VENTED MORE PRODUCT THANIT WAS DESIGNED TO DO. SURGE PRESSURE DID NOT EXCEED 100% OF MOP.
2017-09-29 08:50 | YES | NO | 19990087 | 1999-06-23 | 15490 | PHILLIPS PIPE LINE CO | YES | 1999-05-26 | 930 | IL | KANKAKEE |  | NO |  | NO | LRW-1A-44-22 BORGER-E, CHICAGO LINE- BLUE LINE - MP 916-16+43 SEC 3, T32N, R13E, KANKAKEE CO., IL |  | LINE PIPE | PIPE |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13821.0975 | 27882.7362 | PROPANE | 2 | 35 | 0 | NO | NO | 8.63 | 0.19 | 42000 | WELDED |  | 960 | 300 | YES | 8 | 1495 | 6 | 82 | EXTERNAL | Null | YES | GALVANIC |  | NO DATA |  | Null | NO DATA |  | Null | Null | LINUS J SCHMITZ | 9186614814 | SMALL CORROSION PIT REQUIRED REPLACEMENT OF PIPE. MOST OF COST DUE TO STOPPLEINSTALLATION.
2017-09-29 08:50 | YES | NO | 19990088 | 1999-06-30 | 22610 | WILLIAMS PIPELINE CO | YES | 1999-05-10 | 1157 | KS | ATCHISON |  | NO |  | NO | NORTEAST QUARTER OF SECTION 7-TOWNSHIP 5 SOUTH - RANGE 21 EAST, (SEE ATTACHED PLAT) |  | LINE PIPE | NO DATA |  | 1968 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 691054.8735 | 1394136.8078 | DIESEL FUEL | 1 | 4565 | 2794 | NO | NO | 16 | 0.31 | 0 | WELDED |  | 1150 | 902 | YES | 8 | 1894 | 7 | 88 | NO DATA | Null | Null | NO DATA |  | NO DATA |  | Null | NO DATA |  | Null | Null | KENNETH L LYBARGER | 9185735774 | AT 11:57 A.M. ON MAY 10, THE SCADA ALARM SOUNDED IN THE OPERATIONS CONTROLCENTER OF WILLIAMS PIPELINE COMPANY IN TULSA, OK. SIMULTANEOUSLY, THE LINEPRESSURE AT THE ATCHISON PUMP STATION DROPPED FROM 902 PSIG TO 27 PSIG,FOLLOWED BY A PROPORTIONALLY EQUIVALENT DROP TO 23 PSIG FROM 771 PSIG AT THEAT THE NEAREST DOWNSTREAM PUMP STATION. THE MAINLINE STATE PUMPS WERE STOPPEDAT 11:59, THE MAINLINE VALVE CLOSED AT 12:00 AND PRODUCT IN THE LINE WASDRAINED TO THE WPL DES MOINES, IA FACILITY. FIELD PERSONNEL IMMEDIATELY BEGANSEARCHING FOR SIGNS OF A PRODUCT LOSS BY AIRPLANE, BY DRIVING THE LINE ANDALSO BY WALKING ALONG THE PIPELINE EASEMENT ON FOOT. A FARMER FISHING ININDEPENDENCE CREEK NOTICED PRODUCT IN THE CREEK AND TELEPHONED THE WPLEMERGENCY CONTACT TELEPHONE NUMBER. PERSONNEL WERE IMMEDIATELY DISPATCHED TOTHE LOCATION, WHERE CONTAINMENT EQUIPMENT WAS DEPLOYED AND RECOVERY WASSTARTED USING ENVIRONMENTAL CONTRACTORS PREVIOUSLY DISPATCHED TO THE AREA.RECOVERY OPERATIONS CONTINUED AROUND THE CLOCK UNTIL ALL RECOVERABLE PRODUCTWAS RECOVERED AND THE SITE RESTORED TO THE SATISFACTION OF FEDERAL AND STATEENVIRONMENTAL OFFICIALS. A TEMPORARY REPAIR WAS MADE BY INSTALLING A SECTIONOF 8-INCH DIAMETER PIPELINE OVER THE CREEK WHILE A 1,000 FOOT LONG SECTION OFNEW PIPE WAS BORED UNDER THE CREEK. THE NEW SECTION WAS INSTALLED AND TESTEDACCORDING TO DOT REGULATIONS AND PLACED IN SERVICE ON JUNE 6, 1999. THEDAMAGED SECTION OF PIPE WAS RECOVERED AND SUBJECTED TO METALLURGICAL ANALYSISTO DETERMINE THE CAUSE OF THE FAILURE.
2017-09-29 08:50 | YES | NO | 19990089 | 1999-06-29 | 22610 | WILLIAMS PIPELINE CO | YES | 1999-05-24 | 1000 | IA | WORTH |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1950 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 283000 | 195568.5292 | 394540.7166 | DIESEL FUEL | 1 | 73 | 0 | NO | NO | 12 | 0.25 | 0 | WELDED |  | 1050 | 882 | YES | 8 | 1388 | 8 | 1994 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KENNETH L LYBARGER | 9185735774 | PERSONNEL IN THE LOCAL OPERATION OFFICE OF WILLIAMS PIPELINE COMPANY RECEIVEDA TELEPHONE CALL FROM A FARMER WORKING ON HIS DRAIN TILE INDICATING HE SAW ASHEEN ON THE WATER IN A DRAINAGE DITCH. WPL PERSONNEL INVESTIGATED ANDDISCOVERED A LEAK FROM THE #4-12"LINE. OPERATIONS CONTROL IN TULSA WASNOTIFIED TO SHUT DOWN THE LINE, AND THE NEAREST MAINLINE BLOCK VALVE WASCLOSED TO ISOLATE THE LINE. TELEPHONIC WAS MADE TO THE NATIONAL RESPONSECENTER, THE IOWA DEPARTMENT OF NATURAL RESOURCES (SERC), AND WORTH COUNTY LEPCIN ACCORDANCE WITH REGULATIONS. COMPANY AND CONTRACT CREWS WERE DISPATCHED TOTHE AREA WHERE REPAIR AND RECOVERY EFFORTS WERE CONDUCTED SIMULTANEOUSLY. ASA PRECAUTION CONTAINMENT BOOMS WERE DEPLOYED BUT NEVER PICKED UP ANY PRODUCT.APPROXIMATELY 43 FEET OF PIPE WAS REPLACED, HYDROTESTED AND THE LINE RETURNEDTO SERVICE ON MAY 28. THE SECTION OF THE PIPE WHICH FAILED WAS DISCOVERED TOHAVE A SPLIT APPROXIMATELY 1 INCH LONG IN THE SEAM. THE DEFECTIVE PIECE WASCUT OUT AND SENT TO A METALLURGY COMPANY FOR ANALYSIS.
2017-09-29 08:50 | YES | NO | 19990091 | 1999-07-08 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-06-01 | 1830 | OK | PAYNE |  | NO |  | NO | CUSHING TANK FARM |  | TANK FARM | TANK |  | 1995 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13821.0975 | 27882.7362 | CRUDE OIL | 1 | 300 | 300 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ENVIRONMENTAL COORDINATOR | 9182232402 | THE VALVE FOR TANK 226 HAD BEEN CLOSED BY THE OPERATOR. THE VALVE MALFUCTIONED AND REOPENED. WHEN THE TANK 214 WAS OPENED BY THE OPERATOR, THE CRUDE OIL GRAVITY FED TO TANK 226 AND OVERFLOWED THE TANK. A SPILL OCCURRED AT TANK 226 DUE TO A VALVE MALFUNCTION (THE VALVE REOPENED FOLLOWING CLOSING). ALL PRODUCT WAS CONTAINED IN THE TANK DIKE AND RECOVERED.
2017-09-29 08:50 | NO | NO | 19990092 | 1999-07-16 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1999-06-30 | 1015 | OK |  | CUSHING | NO |  | NO | NE/4 SECTION 22-T17N-R5E, LINCOLN COUNTY, OK |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 8292.6585 | 16729.6417 | CRUDE OIL | 3 | 10 | 4 | NO | NO | 10 | 0.37 | 0 | WELDED |  | 396 | 10 | YES | 8 | 495 | 0 | 1994 | INTERNAL | Null | YES | OTHER | SULFATE REDUCING BACTERIA |  |  | Null |  |  | Null | Null | JAMES A HENRY | 5802557151 | PIPELINE WAS PURGED AND INACTIVATED IN 1997. A SMALL AMOUNT OF PRODUCT REMAINED IN SYSTEM AND COLLECTED AT LOW POINT ON THE PIPELINE RESULTING IN INTERNAL CORROSION. PIPELINE SYSTEM WILL BE PIGGED TO REMOVE ANY ADDITIONAL PRODUCT IN SYSTEM.
2017-09-29 08:50 | YES | NO | 19990093 | 1999-07-15 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1999-06-21 | 1530 | OK |  | MUSTANG | NO |  | NO | EOTT-MORGAN ROAD STATION, NE/4 SECTION 2-T10N-R5W, CANADIAN COUNTY, OK |  | PUMPING STATION | PUMP |  | 1987 | OTHER | BROKEN BELTS ON SHIPPING PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1036.5823 | 2091.2052 | CRUDE OIL | 3 | 105 | 105 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES A HENRY | 5802557151 | BELTS ON PIPELINE SHIPPING PUMP BROKE ALLOWING TANK TO OVER-FILL. PRODUCT CONTAINED INSIDE SECONDARY CONTAINMENT.
2017-09-29 08:50 | YES | NO | 19990094 | 1999-07-15 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1999-06-16 | 2009 | LA |  | CADDO | NO |  | NO | 3/4 MILES SOUTH OF BERT KOUNS STREET | 487779 | LINE PIPE | PIPE |  | 1948 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | GASOLINE | 3 | 1163 | 263 | NO | NO | 8 | 0.19 | 35000 | WELDED |  | 640 | 20 | YES | 0 | 800 | 0 | 1948 |  | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | WILLIAM J JALL |  | APPROXIMATELY 2100 HRS, CDT, JUNE 16, 1999, OPERATIONS AT TEPPCO'S BOSSIER CITY TERMINAL RECEIVED A CALL FROM THE CADDO PARRISH SHERIFF'S DEPARTMENT REGARDING THE PRESENCE OF A STRONG PRODUCT VAPORS NEAR OUR PIPELINE. TEPPCO'S EMERGENCY RESPONSE PLAN WAS IMMEDIATELY INITIATED. PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE SITE OF THE RELEASE TO DETERMINE IF THE RELEASE WAS ASSOCIATED WITH OUR PIPELINE SYSTEM. THE LINE HAD BEEN SHUT DOWN ON JUNE 13, 1999, AND THE PRESSURE RELIEVED AT THAT TIME. BLOCK VALVES WERE CLOSED UPSTREAM TO ISOLATE THE RELEASE SITE. IT WAS DETERMINED LOCAL EXTERNAL CORROSION IN AN AREA OF LAMINATION LOCATED AT 5 O'CLOCK ON THE PIPE CAUSED THE RELEASE. NECESSARY REPAIRS WERE COMPLETED AND THE SYSTEM WAS RETURNED TO SERVICE ON JUNE 18, 1999. TEPPCO IS CURRENTLY AWAITING APPROVAL OF ITS SITE REMEDIATION PLAN BY THE STATE ENVIRONMENTAL AGENCY TO COMPLETE THE REMEDIATION.
2017-09-29 08:50 | YES | NO | 19990095 |  | 2190 | CENTRAL FLORIDA PIPELINE CORP | NO | 1999-06-27 | 548 | FL | OSCEOLA |  | NO |  | NO | OSCEOLA COUNTY FLORIDA NEAR OLD LAKE WILSON ROAD AND INTERSTATE #4. LOCATED AT PIPELINE VALVE SITE NUMBER 20. | 489101 | LINE PIPE | OTHER | VALVE SITE EQUIPMENT | 1996 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 31097.4693 | 62736.1564 | GASOLINE | 1 | 0 | 0 | YES | NO | 16 | 0.31 | 1440 | WELDED |  | 1440 | 200 | YES | 24 | 1881 | 4 | 1996 |  | Null | Null |  |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | JAMES PASTERNAK | 8132482148 | ON 6/27/1999 DURING A SEVERE THUNDERSTROM, VALVE SITE NUMBER 20 LOCATED IN OSCEOLA COUNTY, OFF OLD LAKE WILSON ROAD RECEIVED A DIRECT LIGHTNING STRIKE. THE LIGHTNING STRIKE DAMAGE SOME VALVE STATION ELECTRICAL EQUIPMENT INCLUDING A LIGHT POLE AND PUNCTURED A 3/8" PRESSURE GAUGE LINE WHICH RELEASED A SMALL QUANTITY OF UNLEADED PREMIUM GASOLINE THAT WAS IGNITED IMMEDIATELY. NO FUEL SPILL WAS INVOLVED, SINCE ALL PRODUCT RELEASED, BURNED IN THE RESULTING FIRE. THE LIGHTNING STRIKE AND RESULTING FIRE WAS SEEN BY A BYSTANDER AND REPORTED IMMEDIATELY. THE FIRE WAS PUT OUT BY OSCEOLA COUNTY FIRE RESCUE WITH NO DAMAGES TO THIRD PARTIES. THE PIPELINE VALVE 20 WAS STILL OPERABLE. VALVE 20 IS LOCATED ON CFAL'S 16" PIPELINE FROM TAMPA TO ORLANDO, FL.
2017-09-29 08:50 | YES | NO | 19990096 | 1999-07-01 | 2552 | COLONIAL PIPELINE CO | YES | 1999-02-10 | 102 | TN |  | KNOXVILLE | NO |  | NO | NEAR HENLEY STREET BRIDGE AT PITNER PL AND GOOSE CREEK, KNOXVILLE, TN | 473483 | LINE PIPE | NO DATA |  | 1963 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6900000 | 4768278.6269 | 9619543.9739 | FUEL OIL | 1 | 1275 | 1048 | NO | NO | 0 | 0.25 | 42000 | WELDED |  | 521 | 90 | YES | 8 | 720 | 2 | 1995 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | STEPHEN E GILLIAM, REGULATORY ADMINISTRATOR | 4048412314 | ON 2/10/99 AT 02:30 LINE # 18 BETWEEN KNOXVILLE DELIVERY AND EAST KNOXVILLE DELIVERY WAS STARTED TO MAKE A NORMAL DELIVERY. NO FLOW RATE AT EAST KNOXVILLE WAS OBSERVED AND THE CONTROL CENTER WAS NOTIFIED. THE CONTROL CENTER INSTRUCTED THE KNOXVILLE OPERATOR TO DIVERT THE STREAM BACK TO KNOXVILLE DELIVERY. AT 4:00 A CPC EMPLOYEE ARRIVED AT EAST KNOXVILLE D.F AND CHECKED THE FACILITY YARD AND FOUND NO EVIDENT PROBLEMS. AT 04:20 THE EAST KNOXVILLE D.F. TAKEOFF VALVE WAS OPENED AT KNOXVILLE TO RESUME DELIVERY AT EAST KNOXVILLE D.F. THE OPERATOR AT KNOXVILLE DELIVERY, EAST KNOXVILLE D.F., AND CONTROLLER REMAINED ON THE PHONE MONITORING PRESSURES AND FLOW RATES. THE SENIOR CONTROLLER RECEIVED A CALL FROM A KNOXVILLE FIRE DEPARTMENT AND INFORMED THE CONTROLLER TO SHUT DOWN THE LINE BECAUSE OF REPORTED PRODUCT ON THE GROUND IN KNOXVILLE. THE CONTROLLERWAS IN THE PROCESS OF SHUTTING DOWN THE LINE AND DELIVERY WHEN THE CALL FROM THE FIRE DEPRATMENT CAME IN . THE LOW FLOW RATE AND OSCILLATING CONTROLL VALVE AT EAST KNOXVILLE WAS FURTHER INDICATION WE HAD A LEAK AND THE FIRE DEPARTMENT HAD FOUND IT. AT 4:30 THE CONTROLLER NOTIFIED THE KNOXVILLE DELUVERY OPERATOR THAT THE KNOXVILLE FIRE DEPARTMENT HAD CALLED IN A REPORT OF A PRODUCT RELEASE. THE KNOXVILLE OPERATOR SENT A CPC EMPLYOEE TO THE SITE OF THE RELEASE AND HE CONFIRMED THE RELEASE WAS FROM COLONIALSS 10 INCH LINE. EMERGENCY RESPONSE EFFORTS WERE INITIATED. THE RELEASED PRODUCT WAS CONTAINED AND RECOVERY EFFORTS INITIATED. THE FAILED SECTION OF THE 10 INCH LINE WAS CUT OUT AND REPLACED AT ABOUT 02:00 ON FRIDAY 1/12/99. THE NTSB TOOK CUSTODY OF THE DAMAGED SECTION OF PIPE AND SENT TO THEIR LAB IN WASHINGTON D.C.
2017-09-29 08:50 | YES | NO | 19990097 | 1999-07-21 | 12470 | MID - VALLEY PIPELINE CO | YES | 1999-06-23 | 1700 | TX | GREGG |  | NO |  | NO | 4 MILES SE OF WHITE OAK, TX; 1 MILE EAST OF INTERSECTION OF HARRISON ROAD (FM 2206) AND STATE HWY 42. 3595400 M N; 327800 M E |  | TANK FARM | TANK |  | 1989 | OTHER | ROOF DRAIN FAILURE ON EFR TANK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5182.9116 | 10456.0261 | CRUDE OIL | 1 | 694 | 680 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDITH F COEN | 9185866942 | AT 1700 HOURS CST 6/23/99 THE LONGVIEW TERMINAL OPERATOR ON DUTY WAS INSPECTING THE TANK FARM DIKES DUE TO RAINFALL AND THE POTENTIAL NEED TO OPEN THE DIKE DRAIN VALVES. THEREBY DRAINING THE AREAS. HE DISCOVERED OIL IN THE FIREWALL OF TANK 4 AND TANK 5 IN THAT THE TWO DIKE AREAS WERE COMMON. THE ORIGIN OF THE OIL WAS THE ROOF DRAIN ON TANK 4. THE TERMINAL OPERATOR CLOSED THE ROOF DRAIN. NO CRUDE OIL ESCAPED THE FIREWALL CONFINEMENT. IT WAS DISCOVERED THAT THE ROOF DRAIN ON THIS EXTERNAL FLOATING ROOF FAILED IN A FITTING NEAR THE ROOF ALLOWING OIL INTO THE DRAIN. THE DRAIN WAS OPEN TO THE DIKE AREA AT THE TIME OF FAILURE TO ALLOW RAINWATER TO DRAIN FROM THE ROOF. THE RECOVERED CRUDE OIL WAS RETURNED TO THE PIPELINE SYSTEM.
2017-09-29 08:50 | YES | NO | 19990098 | 1999-07-21 | 31339 | HUNTSMAN POLYMERS CORP | NO | 1999-07-12 | 725 | TX | ECTOR | ODESSA | NO |  | NO | NORTH OF THE HUNTSMAN POLYMERS CORP EAST SIDE COMPLEX AT THE TIE-IN TO PHILLIPS PIPELINE PUMP STATION | 491011 | PUMPING STATION | BOLTED FITTING |  | 1999 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 2 | 8 | 0 | NO | NO | 6 | 0.432 | 800 | FLANGED |  | 1440 | 468 | YES | 0 | 2160 | 0 | 0 |  | Null | YES |  |  | OTHER | COLD SLUG OF PRODUCT | Null | ONE CALL |  | Null | Null | VOLLEY VESSELS | 9156408518 | AT 7:25AM ON 7-12-99 A LEAK WAS DISCOVERED IN THE CATHODIC PROTECTION ISOLATION FLANGE GASKET. THE GASKET CONTRACTED DUE TO COLD SLUG OF PRODUCT AND STARTED LEAKING. GASKET WAS CHECKED AND TIGHTENED AND THE LINE WAS PUT BACK INTO SERVICE.
2017-09-29 08:50 | YES | NO | 19990099 | 1999-07-28 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1999-06-24 | 604 | PA | ALLEGHENY |  | NO |  | NO | SEE ATTACHED DRAWING NUMBER 11866-A | 488628 | PUMPING STATION | TANK |  | 1976 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 4300 | 2971.536 | 5994.7883 | GASOLINE | 3 | 100 | 99 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | CARL A OSTACH, MANAGER | 6107704495 | A BUCKEYE STATION OPERATOR ALIGNED A VALVE IN AN INCORRECT POSITION PRIOR TO A SPLIT STREAM DELIVERY. THIS ALLOWED GASOLINE TO OVERFLOW THE STATION'S RELIEF TANK ON JUNE 24, 1999 AT 0604 HOURS. THE NATIONAL RESPONSE CENTER, DEPARTMENT OF ENVIRONMENTAL PROTECTION, AND MOON TOWNSHIP FIRE DEPARTMENT WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE CONDUCTED IMMEDIATELY.
2017-09-29 08:50 | YES | NO | 19990100 | 1999-07-27 | 4906 | EXXON PIPELINE CO | YES | 1999-06-29 | 940 | TX | RUSK | NEW LONDON | NO |  | NO | EAST TEXAS GATHERING SYSTEM PIPELINE. THE LEAK LOCATION IS 200 TO 300 YARDS EAST OF HWY 42, ON THE SOUTHEAST SIDE OF THE INTERSECTION OF HWYS 1513 AND 42. | 489342 | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 38937 | 26907.6036 | 54283.5049 | CRUDE OIL | 1 | 133 | 128 | NO | NO | 4 | 0.24 | 30000 | WELDED |  | 100 | 80 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER |  |  |  | Null |  |  | Null | Null | J B BARR, AREA MANAGER | 7136562203 | LEAK WAS CAUSED BY EXTERNAL CORROSION. THEY WAS SHUT IN. A CLAMP WAS INSTALLED AS A TEMPORARY REPAIR. THE SPILL WAS CONTAINED USING BOOMS AND FLUME PIPES. CLEAN UP ACTIVITIES INCLUDED THE USE OF VACUUM TRUCKS AND ABSORBENT MATERIAL TO MAXIMIZE OIL RECOVERED. A FULL ENCIRCLEMENT SLEEVE HAS BEEN WELDED IN PLACE AS A PERMANENT REPAIR.
2017-09-29 08:50 | YES | NO | 19990101 | 1999-07-26 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1999-07-04 | 600 | NM | EDDY | LOCO HILLS | NO |  | YES | UNIT C, SECTION 3, T-18-S, R-30-E |  | TANK FARM | TANK |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 24186.9206 | 48794.7883 | CRUDE OIL | 1 | 3900 | 3763 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LENNAH FROST, SR ENVIRONMENTAL ENGINEER | 9156843467 | ELECTRICAL FAILURE CAUSED VALVE TO SHUT AND OVERFILLED TANK
2017-09-29 08:50 | YES | NO | 19990102 | 1999-07-26 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 1999-07-11 | 1137 | TX | HASKELL |  | NO |  | NO | FROM HASKELL, TX TAKE HWY 277 NORTH 8.3 MILES TO FM 1080. GO EAST TO CR 277 GO SOUTH APPROXIMATELY 2.5-3 MILES TO GATE ONE EAST SIDE OF ROAD. LEAK IN MIDDLE |  | LINE PIPE | PIPE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13821.0975 | 27882.7362 | CRUDE OIL | 1 | 516 | 320 | NO | NO | 10 | 0.37 | 24000 | WELDED |  | 720 | 850 | YES | 8 | 889 | 5 | 1999 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LENNAH FROST, SR ENVIRONMENTAL ENGINEER | 9156843467 | OPERATOR ERROR.
2017-09-29 08:50 | YES | NO | 19990103 | 1999-07-28 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1999-07-03 | 1700 | WY | NIOBRARA |  | NO |  | NO | T36N, R65W, SECTION 31 LANCE CREEK PUMP STATION AND TANK FARM |  | TANK FARM | VALVE |  | 1938 | OTHER | VALVE BODY FAILURE ON 8" MAINLINE SUCTION VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69105.4873 | 139413.6808 | CRUDE OIL | 1 | 4700 | 3700 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RANDY W BEGGS, DIRECTOR, REGULATORY COMPLIANCE | 3036494090 | THE INCIDENT OCCURRED SOMETIME BETWEEN 1700 AND 1900 ON JULY 3, 1999. WHILE DELIVERING CRUDE OIL OUT OF TANK #1 TO THE 8" MAINLINE, THROUGH A COMMON SUCTION LINE WITH TANK #2, THE 8" SUCTION VALVE BODY ON TANK #2 FAILED. THE VALVE BODY CRACKED FROM THE VALVE BONNETT FLANGE, AROUND THE BOTTOM OF THE VALVE BODY, HALF WAY UP THE OTHER SIDE OF THE VALVE. THE CRACK WAS 1/8' AT THE WIDEST POINT. THE FAILURE RESULTED IN A 4700 BBL RELEASE CONTAINED IN THE TANK DIKE. THERE WAS NO OFF SITE IMPACT. A SKILLET WAS INSTALLED ON THE SUCTION SIDE OF THE FAILED VALVE, UNTIL THE TANK CAN BE EMPTIED, TO REMOVE AND REPLACE THE VALVE. OIL WAS COLLECTED IN VAC TRUCKS AND PUMPED INTO TANK #1. REMEDIATION OF IMPACTED SOIL IN ONGOING WITH THE WYOMING DEQ AND REGION 8 EPA.
2017-09-29 08:50 | YES | NO | 19990104 | 1999-07-22 | 30903 | ARCO PIPE LINE COMPANY | YES | 1999-07-05 | 1550 | TX | MIDLAND |  | NO |  | NO | LEAK SITE APPROX 3/4 MILE SOUTH OF 1-20, NEAR INTERSECTION OF HWY 349 AND I-20. LEGAL DESCRIPTION -N/2 NE/4 OF SECTION 11, BLOCK 39, T2-S & P RR CO. | 490093 | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 27642.1949 | 55765.4723 | CRUDE OIL | 3 | 190 | 165 | NO | NO | 8 | 0.32 | 2613 | WELDED |  | 600 | 90 | YES | 12 | 1072 | 0 | 1973 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | MIKE A SCHMIDT, OPERATIONS SUPERINTENDENT | 9182232957 | ON JULY 5, 1999 ARCO PIPE LINE (APL) MADE A TELEPHONIC REPORT (REPORT NO. 490093) OF A CRUDE OIL SPILL ON APL'S CRANE TO MIDLAND 8 INCH PIPELINE AT A LOCATION APPROXIMATELY 3/4 MILE SOUTH OF INTERSTATE 20 NEAR THE INTERSECTION OF I-20 AND HWY 349 (RANKIN ROAD). THERE WERE NO INJURIES, FIRES, OR EXPLOSIONS RESULTING FROM THIS INCIDENT AND THE RELEASED PRODUCT DID NOT REACH ANY WATERWAYS. A VOLUME DISCREPENCY WAS NOTICED BY THE MIDLAND CONTROL CENTER OPERATOR, AND HE SUSPECTED A LEAK. AT APPROXIMATELY 350PM ON JULY 5, THE AERIAL PATROL PILOT CONFIRMED A CRUDE OIL LEAK RESULTING FROM CONSTRUCTION ACTIVITY ON THE PIPELINE RIGHT-OF-WAY. MAINTENANCE CREWS WERE IMMEDIATELY DISPATCHED TO CLOSE BLOCK VALVES AND ISOLATE THE AFFECTED LINE SECTION. ALSO, EMERGENCY RESPONSE AND CLEANUP PERSONNEL WERE IMMEDIATELY SUMMONED TO THE SITE TO UNDERTAKE CONTAINMENT, REPAIR, AND CLEAN UP ACTIVITIES. THE SOURCE OF THE LEAK WAS DETERMINED TO BE THIRD PARTY DAMAGE BY A BULLDOZER WHICH STRUCK THE UNDERGR
2017-09-29 08:50 | YES | NO | 19990105 | 1999-07-08 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-06-08 | 1500 | CA | KERN |  | NO |  | NO | 1.9 MI., NW MOCAL ROAD & SHELL ROAD, .3 E OF MOCAL, SEC 26, T31S-R22W |  | LINE PIPE | PIPE |  | 1983 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6910.5487 | 13941.3681 | CRUDE OIL | 1 | 670 | 650 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | L D SHAMP | 7132412241 | THIRD PARTY HAD A SMALL SPILL AROUND THEIR WELLHEAD AND WAS SCRAPING UP FRESH DIRT TO REPLACE THE STAINED SOIL. UNFORTUNATELY THEY DID NOT REALIZE THE SPOT THEY HAD CHOSEN TO TAKE THE DIRT FROM WAS DIRECTLY ON TOP OF OUR LINE. LINE MARKERS WERE PRESENT.
2017-09-29 08:50 | YES | NO | 19990106 | 1999-08-17 | 30991 | MOBIL OIL CORPORATION | YES | 1999-07-21 | 1150 | TX | YOAKUM | SEAGRAVES | NO |  | NO | MALLET TO SEMINOLE 8" MAINLINE, APPROX 3 1/2 MILES NORTH OF MOBIL PIPE LINE COMPANY'S SEAGRAVES STATION APPROX 10 MILES WEST OF WILLMAN, TX ON HWY 213, YOAKUM | 492166 | LINE PIPE | PIPE |  | 1940 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 6219.4939 | 12547.2313 | CRUDE OIL | 1 | 335 | 260 | NO | NO | 8.63 | 0.28 | 35000 | WELDED |  | 1200 | 214 | YES | 24 | 1500 | 2 | 1971 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | S S SOBEY, MANAGER | 7146585914 | YOAKUM COUNTY TEXAS MAINTENANCE CREW WAS CLEANING OUT DRAINAGE DITCHES WITH A ROAD GRADER AND STRUCK THE PIPELINE WITH BLADE CAUSING PIPELINE IN RUPTURE. THE COUNTY MAINTENACE CREW NOTIFIED MOBIL AND THE PIPELINE WAS IMMEDIATELY SHUTDOWN AND ISOLATED BY DALLAS PIPELINE OPERATIONS CONTROL CENTER WHO HAD ALREADY RECOGNIZED A DEVIATION IN PRESSURE. COMPANY MAINTENANCE PERSONNEL WERE DISPATCHED TO THE SITE TO INITIATE CONTAINMENT AND CLEAN UP PROCEDURES. PERMANENT REPAIRS WERE MADE BY REPLACING DAMAGED SECTION OF PIPE. ALL REQUIRED NOTIFICATIONS ARE MADE IN ACCORDANCE WITH DOT PART 195 REGULATIONS.
2017-09-29 08:50 | YES | YES | 19990107 | 1999-08-18 | 30781 | OLYMPIC PIPE LINE COMPANY | YES | 1999-06-10 | 1528 | WA | WHATCOM | BELLINGHAM | NO |  | NO | SEE MAP ATTACHED TO THE ORIGINAL 7000-1 REPORT | 487019 | LINE PIPE | PIPE |  | 1966 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 3 | 0 | 3 | 8 | 0 | 8 | 45000000 | 31097469.3059 | 62736156.3518 | GASOLINE | 3 | 5475 | 234 | YES | NO | 16 | 0.312 | 52 | WELDED |  | 1320 | 0 | YES | 24 | 1620 | 6 | 1966 |  | Null | Null |  |  | OTHER | SEE PART K- ACCOUNT OF ACCIDENT | Null | ONE CALL |  | NO | NO | FRANK HOPF & FRED CROGNALE | 4252357735 | MAINLINE 16" PIPLINE RUPTURE. CAUSE IS BEING INVESTIGATED BY THE NTSB AND DOT OFFICE OF PIPELINE SAFETY. INITIAL EXAMINATION OF THE PIPE REVEALED A 28" LONGINTUDINAL SPILL AND GOUGES AND DENTS ADJACENT TO THE RUPTURE AREA. DETAILS TO BE PROVIDED FOLLOWING THE NTSB INVESTIGATION. SUPPLEMENTAL INFO: MAINLINE 16" PIPELINE RUPTURED. INITIAL EXAMINATION OF THE FAILED PIPE REVEALED AT 28" LONGITUDINAL SPLIT WITH GOUGES AND DENTS ADJACENT TO THE RUPTURE AREA. THE IMPACT OF THIS DAMAGE ON THE PIPES FAILURE, AS WELL AS ALL OTHER POTENTIAL CAUSES INCLUDING THE FUNCTIONING OF SURGE RELIEF EQUIPMENT, IS UNDER CURRENT INVESTIGATION BY THE NTSB AND THE DOT OFFICE OF PIPELINE SAFETY.
2017-09-29 08:50 | YES | NO | 19990108 | 1999-08-20 | 4906 | EXXON PIPELINE CO | NO | 1999-06-28 | 1019 | TX | HARRIS | BAYTOWN | NO |  | NO | THE LINE IS LOCATED ON BUSCH ISLAND WHICH IS BETWEEN THE SAN JACINTO BAY TO THE WEST AND THE HOUSTON SHIP CHANNEL TO THE EAST. |  | LINE PIPE | PIPE |  | 1937 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1250000 | 863818.5918 | 1742671.0098 | CRUDE OIL | 1 | 3000 | 2546 | NO | NO | 10 | 0.365 | 25000 | COUPLED |  | 715 | 400 | YES | 8 | 894 | 10 | 1991 |  | Null | YES | OTHER |  |  |  | Null |  |  | Null | Null | RAMONA PULLIN/AREA MANAGER | 7136562232 | THE LEAK WAS SPOTTED BY A LINE FLIER. THE LINE WAS SHUT DOWN. EPC TRAVELED BY BOAT TO ISLAND TO CONFIRM LEAK. MOBILIZED RESPONSE TO IMPLEMENT CONTAINMENT AND CLEANUP. MOBILIZIED PIPELINE REPAIR TEAM. ADJACENT 8" LINE WAS COMMISSIONED AND TIED INTO THE SYSTEM. THE SYSTEM WAS PLACED BACK IN SERVICE. CLEANUP EFFORTS ARE IN PROGRESS.
2017-09-29 08:50 | YES | NO | 19990109 | 1999-08-20 | 3012 | PRIDE TEXAS PLAINS L.P. | NO | 1999-08-05 | 2200 | TX | KING |  | NO |  | NO | SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1927 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 24186.9206 | 48794.7883 | CRUDE OIL | 3 | 1200 | 0 | NO | NO | 10.75 | 0.365 | 25000 | WELDED |  | 800 | 550 | YES | 8 | 0 | 6 | 1976 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LELAND HASTINGS | 9156748189 | AT APPROXIMATELY 2200 HOURS ON 8/4/99, OUR GILES STATION WENT DOWN DUE TO ELECTRICAL OUTAGE. THE RESULTING SURGE CAUSE A RUPTURE IN THE LINE. THE WAS WAS SHUT DOWWN AND VALVES WERE CLOSED. DUE TO DARKNESS, CREWS WERE NOT DISPATCHED UNTIL THE MORNING OF AUGUST 5, 1999. THE LEAK WAS LOCATED BY AIR PATROL AT 10:30 AM, AND THE LINE WAS REPAIRED. CLEANUP HAS BEGUN IN ACCORDANCE WITH STATE WIDE RULE #91.
2017-09-29 08:50 | YES | NO | 19990110 | 1999-08-20 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 1999-08-10 | 330 | TX | UPTON | MCCAMEY | NO |  | NO | 1 MILE EAST OF MCCAMEY, TEXAS ON HWY 67, NORTH SIDE OF ROAD. |  | PUMPING STATION | BOLTED FITTING |  | 1999 | OTHER | GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 98 | 15 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LENNAH FROST, SR ENVIRONMENTAL ENGINEER | 9156843467 | 600# SYSTEM. WE HAD 390# ON SYSTEM WHEN GASKET FAILED.
2017-09-29 08:50 | YES | NO | 19990111 | 1999-08-23 | 18718 | SUN PIPE LINE CO | NO | 1999-08-04 | 1600 | OK | PAYNE | CUSHING | NO |  | NO | HWY 33 AND LINWOOD AVENUE | 493903 | LINE PIPE | PIPE |  | 1975 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL |  | 360 | 360 | NO | NO | 30 | 0.375 | 65000 | WELDED |  | 275 | 4 | YES | 24 | 1255 | 1 | 1975 | INTERNAL | Null | YES | OTHER | INTERNAL |  |  | Null |  |  | Null | Null | EDITH F COEN, MANAGER HES | 9185866942 | LEAK OCCURRED ON A 30" LINE WITH LOW LOW. PLANS AND MATERIAL FOR REPAIRING THIS LINE ARE IN PROGRESS WHICH INCLUDE REDUCING THE LINE SIZE TO 18". LINE SHOULD BE REPAIRED AND BACK IN OPERATION BY AUGUST 31, 1999.
2017-09-29 08:50 | YES | NO | 19990112 | 1999-08-30 | 4805 | EXPLORER PIPELINE CO | YES | 1999-07-15 | 1200 | TX | TARRANT | GRAPEVINE | NO |  | NO | IN THE CITY OF GRAPEVINE, TEXAS FROM INTERSECTION OF WILLIAM D TATE AND MUSTANG STREETS GO 508 FEET NORTH EAST ON WILLIAM D. TATE THEN 440 FEET SOUTEAST. | 491439 | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 51829.1155 | 104560.2606 | JET FUEL | 3 | 160 | 130 | NO | NO | 8 | 0.188 | 35000 | WELDED |  | 720 | 261 | YES | 24 | 1000 | 8 | 1973 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ROGER W FLEMING | 9184935112 | ON JULY 15, 1999 A CONTRACTOR WAS EXCAVATING, WITHOUT EXPLORER'S KNOWLEDGE, OVER OUR 8" DALLAS, FORT WORTH JET FUEL PIPELINE IN GRAPEVINE, TEXAS. AT 11:59 A.M. THE CONTRACTOR OPERATING A TRACK HOE PUNCTURED A 1 1/2 INCH DIAMETER HOLE IN THE 8" PIPELINE AT MILEPOST 2.0 CAUSING THE RELEASE OF JET FUEL. EXPLORER'S CENTRAL CONTROL TECHINICANS RECEIVED A RATE OF CHANGE ALARM AND WERE IN THE PROCESS OF SHUTTING DOWN THE PIPELINE WHEN THE CALL CAME IN FROM THE CONTRACTOR ON SITE REPORTING THE RELEASE OF JET FUEL. THE PIPELINE WAS SHUT DOWN AND BLOCK VALVES CLOSED BY 12:07 P.M. COMPANY PERSONNEL, MAINTENANCE AND ENVIRONMENTAL CONTRACTORS, AND VACCUUM TRUCKS WERE IMMEDIATELY DISPATCHED TO THE SITE. VACUUM TRUCKS REMOVED THE RELEASED JET FUEL FROM THE BELL HOLE INITIALLY EXCAVATED BY THE CONTRACTOR. THE LINE WAS DRAINED DOWN AND REPAIRED BY REPLACING THE DAMAGED SECTION WITH 6.25 FEET OF 0.188 WT PIPE. IT WAS PLACED BACK INTO SERVICE AT 1544 HOURS ON JULY 16, 1999. CLEANUP, CONTAMINATE
2017-09-29 08:50 | YES | NO | 19990113 | 1999-08-30 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 1999-07-27 | 1401 | NM | SANDOVAL |  | NO |  | NO | ON HIGHWAY 44 @ MILE MARKER 41.6 TURN WEST ON GRAVEL ROAD. GO 11 MILES, TURN NW ON RIGHT OF WAY ROAD. GO 4.0 MILE SW TO STATION. SEE ATTACHED PLAT |  | PUMPING STATION | NO DATA |  | 1999 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 86381.8592 | 174267.101 | NATURAL GAS LIQUID | 2 | 5 | 0 | YES | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ROBERT S DAWSON SR | 7132153298 | @ 14:01 HOURS ON MONDAY, JULY 26, 1999, A SEAL FAILED ON PUMP UNIT #2 AT OUR SAN LUIS PUMP STATION. THE RELEASED PRODUCT IGNITED, CAUSING A FIRE. ONSITE WILLIAMS FIELD PERSONNEL RESPONDED, BY CALLING THE OPERATIONS CONTROL CENTER OF WILLIAM'S PIPELINE C
2017-09-29 08:50 | YES | NO | 19990114 | 1999-08-26 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 1999-07-01 | 1135 | MS | AMITE | LIBERTY | NO |  | NO | MS HWY 24 ONE MILE EAST OF LIBERTY, MS @ EQUILON PIPELINE PUMPING STATION. |  | TANK FARM | OTHER | CARBON MECHANICAL SEAL ON TANK MIXER | 1992 | OTHER | SET SCREWS FAILE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 5157 | 5157 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ALLAN R SCHOEN, SR ENVIRONMENTAL ENGINEER | 9032954617 | RELEASE WAS CAUSED BY LEAKAGE FROM THE CARBON MECHANICAL SEAL AROUND THE MIXER SHAFT. IT APPEARS THAT THE SET SCREWS HOLDING THE SEAL COLLAR IN PLACE FAILED ALLOWING THE SEAL TO BECOME UNSEATED . THE MIXERS WERE REPLACED IN 1992 AND EOTT BELIEVES THE SEAL LIFE EXPECTING WAS NOT EXCEEDED. THE RELEASE WAS CONTAINED TO THE FIREWALL AREA AROUND THE TANK.
2017-09-29 08:50 | YES | NO | 19990115 | 1999-08-25 | 22387 | WEST EMERALD PIPE LINE CORP | YES | 1999-07-01 | 2200 | NM |  | GUADALUPE | NO |  | NO | FROM CUERVO, NM ON I-40, GO NORTH 4 MILES, THEN 2 MILES WEST. LEGAL DESCRIPTION: TOWNSHIP 10 N, RANGE 23 E, SECTION 5. | 489796 | NO DATA | PUMP |  | 0 | OTHER | COMPLETE SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 31097.4693 | 62736.1564 | DIESEL FUEL | 3 | 494 | 17 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | BILL THOMPSON, PIPELINE SAFETY COORDINATOR | 2105924692 | AT APPROXIMATELY 2200 HOURS ON JULY 1, 1999, THERE WAS A COMPLETE SEAL FAILURE ON THE PIPELINE PUMP WHICH FILLED THE SUMP AND THEN OVERFLOWED ONTO ADJACENT PROPERTY. THE RELEASE WAS DISCOVERED BY PIPELINE EMPLOYEES JULY 2, 1999 AT 0800 HOURS. EMERGENCY RESPONSE NOTIFICATIONS WERE MADE (INCLUDING THE NATIONAL RESPONSE CENTER, REPORT 489796), AND RECOVERY ACTIVITIES WERE BEGUN IMMEDIDATELY. AFTER RECOVERY OF THE SPILLED DIESL FUEL, THE SEAL WAS REPLACED, ALL SYSTEM COMPONENTS WERE CHECKED, AND THE PUMP WAS RETURNED TO SERVICE. CLEAN UP AND REMEDIATION OF THE SPILL AREA IS ONGOING.
2017-09-29 08:50 | YES | NO | 19990117 | 1999-08-25 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-07-20 | 1830 | TX |  | KERMIT | NO |  | NO | HENDRICK TANK FARM |  | TANK FARM | OTHER | FILL LINE | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13821.0975 | 27882.7362 | CRUDE OIL | 1 | 618 | 64 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | GARY L ZIMMERMAN | 7132415334 | A BURIED 24" FILL LINE TO TANK 259 HAD A HOLE IN THE BOTTOM OF THE PIPE, WHICH ALLOWED CRUDE TO ESCAPE.
2017-09-29 08:50 | YES | NO | 19990118 | 1999-08-25 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-07-23 | 745 |  |  |  | YES | LAT 28.2604 LONG 91.0204 | NO | SHIP SHOAL, BLOCK 241 |  | LINE PIPE | PIPE |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 691054.8735 | 1394136.8078 | CRUDE OIL | 1 | 3180 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | OTHER | FACE TO FACE MEETING | NO | NO | G L ZIMMERMAN | 7132415334 | A CONTRACTOR WAS IN THE PROCESS OF SETTING A LIVING QUARTERS ON SHIP SHOAL PLATFORM 241A, LOCATED ABOUT 114 MILES SW OF NEW ORLEANS. DURING THE OPERATION, A JACK-UP LIFT BOAT SET TWO OF ITS LEGS DOWN ON THE PIPELINE, CAUSING IT TO RUPTURE. THE OIL WAS A LIGHT, SWEET CRUDE AND THE OIL SHEEN ASSOCIATED WITH THE RELEASE DISSIPATED QUICKLY, DUE TO EVAPORATION AND WAVE AGITATION. NO OTHER CLEANUP OPERTIONS WERE NEEDED GIVEN THE NATURAL CONDITIONS WHICH EXISTED AT THE TIME.
2017-09-29 08:50 | YES | NO | 19990120 | 1999-08-31 | 443 | AMOCO PIPELINE CO | NO | 1999-07-26 | 1200 | TX | GRIMES |  | NO |  | NO | THE LEAK OCCURED ON APL'S MEXIA TO HUFSMITH P/L NEAR MP 95 AT CANEY CREEK. | 492800 | LINE PIPE | PIPE |  | 1925 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 51829.1155 | 104560.2606 | CRUDE OIL |  | 40 | 30 | NO | NO | 8 | 0.322 | 25000 | THREADED |  | 528 | 327 | YES | 8 | 905 | 6 | 1976 | EXTERNAL | Null | YES | OTHER |  |  |  | Null |  |  | Null | Null | ROY BOWDEN | 4097782036 | ON 1/26/99 AT APPROXIMATELY 1200 HOURS THE APL AERIAL PATROL PLACE SPOTTED A CRUDE OIL LEAK AROUND MP 94.5. APPROPRIATE PIPELINE PERSONNELL WERE NOTIFIED AND DISPATCHED TO LEAK SITE. AGENCIES WERE NOTIFIED AND THE RESPONSE PLAN ACTIVATED. CREWS WERE DISPATCHED TO PICKUP ALL FREE OIL. A FLUME WAS PLACED IN THE CREEK SOUTH OF THE FURTHEST POINT THE OIL HAD REACHED TO PREVENT ANY FURTHER MOVEMENT IN THE WATER. ABSORBENT BOOMS WERE STRATEGICALLY PLACED ALONG THE CREEK TO THE SOUTH FOR ADDED PROTECTION. SMALL POOLS OF OIL WERE CLEANED UP WITH ABSORBENT PADS AND OIL EATING MICROBES WERE USED TO CLEAN THE VEGETATION THAT HAD BEEN CONTAMINATED ALONG THE CREEK BED. VISUAL INSPECTIONS WILL BE PERFORMED THREE TIMES A WEEK TO ENSURE NO FURTHER CONTAMINATION OF THE CREEK. THE CLEAN UP PLAN HAS BEEN VERY SUCCESSFUL IN CLEANING UP THE CONTAMINATED VEGETATION ALONG THE CREEK BED. THE LINE WAS ISOLATED AND PURGED. LINE REPAIRS WILL BE COMPLETED IN AUGUST.
2017-09-29 08:50 | YES | YES | 19990122 | 1999-09-21 | 18194 | SEMINOLE PIPELINE CO | YES | 1999-08-10 | 1000 | TX | WILLIAMSON |  | NO |  | NO | WEST SIDE OF NEWLY DEVELOPED PRIVATE ROAD, SHOWHORSE DRIVE, IN THE SUNDANCE RANCH SUBDIVISION | 494571 | LINE PIPE | PIPE |  | 1981 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 1 | 0 | 1 | 0 | 0 | 0 | 380000 | 262600.8519 | 529771.987 | NATURAL GAS LIQUID | 2 | 17288 | 0 | YES | YES | 14 | 0.25 | 65000 | WELDED |  | 1440 | 1160 | YES | 24 | 2193 | 0 | 1981 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | CHRIS MASON, SENIOR COMPLIANCE SPECIALIST | 7132153022 | OPS NOTE: OPERATOR ORIGINALLY SUBMITTED REPORT AS "MID-AMERICA PIPELINE CO (MAPCO)" (OPID 12452). SUPPLEMENTAL RECEIVED 1/16/2003 FROM KEN LYBARGER, WILLIAMS ENERGY SERVICES, REQUESTED CHANGE OF OPERATOR NAME TO SEMINOLE PIPELINE COMPANY. COMMENTS SUBMITTED ON ORIGINAL REPORT WILL SUPPORT THIS. AT 10AM ON AUGUST 10, 1999, OPERATIONS CONTROL RECEIVED A CALL FROM A LOCAL RESIDENT REPORTING THAT AN EXPLOSION HAD OCCURRED. AT 10:01AM ANOTHER LOCAL RESIDENT CALLED REPORTING A LARGE FIRE AT APPROXIMATELY 200 YARDS EAST OF COUNTY ROAD 200 AND 1.5 MILES NORTH OF HWY 29. OPERATIONS CONTROL THEN CALLED THE LOCAL SHERIFF DEPARTMENT AND PIPELINE FIELD PERSONNEL. AT 10:31 AM THE NEAREST UPSTREAM VALVE FROM THE ACCIDENT WAS CLOSED ON THE SEMINOLE BLUE LINE TO EXTINGUISH FIRE AND INITIATED REPAIRS. ON 8/12/99 REPAIRS WERE COMPLETED AND THE SEMINOLE BLUE LINE WAS RETURNED TO SERVICE, (SEE ATTACHED TIME LINE FOR MORE DETAILS). SUBSEQUENT INVESTIGATION HAS REVEALED THAT URBAN ELECTRIC, A CONTRACTOR OF PEDERNALES ELECTRIC COOP, STRUCK THE SEMINOLE BLUE LINE WHILE INSTALLING TELEPHONE POLES. AN EMPLOYEE OF URBAN ELECTRIC, RUDY LOPEZ, WAS KILLED. SEMINOLE PIPELINE IS COOPERATING WITH THE TEXAS RAILROAD COMMISSIONS INVESTIGATION OF THIS INCIDENT.
2017-09-29 08:50 | NO | NO | 19990123 | 1999-09-21 | 31193 | PRIDE PIPELINE CO | NO | 1999-09-02 | 1700 | TX | JONES | HAWLEY | NO |  | NO | SEE ATTACHED DRAWING | 497369 | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6910.5487 | 13941.3681 | CRUDE OIL | 1 | 40 | 40 | NO | NO | 6 | 0.28 | 25000 | THREADED |  | 500 | 50 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | LELAND S HASTINGS | 9156748189 | AT 5:00 PM ON 9/2/99 RECEIVED A CALL THAT THERE WAS OIL IN THE CLEAR FORK OF THE BRAZOS RIVER. LINE WAS SHUTDOWN, CREWS WERE DISPATCHED TO CLOSE VALVES ON BOTH SIDES OF THE RIVER. OIL WAS CONTAINED TO 150 YARDS BY 12' WIDE. OIL WAS VACUUMED UP INTO TRUCKS AND HAULED TO PRIDE'S HAWLEY STATION. LINE WAS DISPLACED WITH NITROGEN AND IS SCHEDULED FOR PERMANENT REPAIRS.
2017-09-29 08:50 | YES | NO | 19990124 | 1999-09-01 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1999-08-17 | 1830 | TX | NUECES |  | NO |  | NO | 1/2 MILE WEST OF THE INTERSECTION OF COUNTY ROAD 61 AND COUNTY RD 34 ON COUNTY ROAD 34 IN NUECES COUNTY, NEAR VIOLET, TX | 495420 | LINE PIPE | PIPE |  | 1926 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 240 | 1 | NO | NO | 8 | 0.322 | 1075 | WELDED |  | 720 | 86 | YES | 8 | 930 | 2 | 1997 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | MICHAEL R HALLGARTH | 3612425524 | A FARMER WAS PLOWING IN A FIELD THROUGH WHICH THE PIPELINE RAN. THE FARMER HIT THE LINE SUBSEQUENTLY, THE LINE RUPTURED RELEASING THE OIL.
2017-09-29 08:50 | YES | NO | 19990125 | 1999-09-08 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1999-08-08 | 1441 | NY | ONONDAGA |  | NO |  | YES | SEE ATTACHED DRAWING NUMBER 11868-A | 494356 | LINE PIPE | PIPE |  | 1958 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 276421.9494 | 557654.7231 | TRANSMIX (PART.REFINED PETRO) | 3 | 64 | 21 | NO | NO | 10 | 0.279 | 2390 | WELDED |  | 1400 | 610 | YES | 24 | 1745 | 3 | 1969 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | CARL A OSTACH | 6107704495 | ON AUGUST 8, 19999, A BUCKEYE TECHINICAN NOTICED AND REPORTED PETROLEUM ODOR WHILE TRAVELING TO A WORK LOCATION. BUCKEYE MAINTENANCE EMPLOYEES INVESTIGATED AND DISCOVERED RELEASED PETROLEUM PRODUCT. THE D-802 PIPELINE SYSTEM WAS SHUT DOWN AND ISOLATED. ALL APPLICABLE AGENCIES WERE NOTIFIED. RECOVERY AND CLEAN-UP ACTIVITIES WERE PERFORMED UNDER THE SUPERVISION OF THE NEW YORK DEPARTMENT OF ENVIRONMENTAL CONSERVATION AND THE NEW YOUR PUBLIC SERVICE COMMISSION. ON AUGUST 9,1999, A BOLT ON REPAIR SLEEVE WAS TEMPORARILY INSTALLED. ON AUGUST 11, 1999, THE PIPE FAILURE AREA WAS CUT OUT AND REPLACED WITH A FULL JOINT OF PRE-TESTED CERTIFIED LINE PIPE. A FOLLOW UP INVESTIGATION REVEALED THAT AS PART OF A TRAINING EXERCISE ON MARCH 6, 1999, A U.S. MARINE CORP RESERVE M-88 TANK RETRIEVAL VEHICLE WAS STUCK OVER BUCKEYE'S D-802, 10 INCH AUBURN, NY TO UTICA, NY PIPELINE SYSTEM RIGHT OF WAY. THE M-88 TANK RETRIVAL VEHICLE'S METAL TRACK DENTED AND GOUGED THE PIPELINE. BUCKEYE WAS NOT ADVISED
2017-09-29 08:50 | YES | NO | 19990126 | 1999-09-03 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 1999-08-06 | 0 | IA |  | SIOUX CITY | NO |  | NO | WILLIAMS PIPELINE COMPANY SIOUX CITY TERMINAL, 4300 41ST STREET, SIOUX CITY, IOWA |  | TANK FARM | TANK |  | 1946 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 51829.1155 | 104560.2606 | FUEL OIL | 3 | 100 | 38 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KENNETH L LYBARGER | 9185735774 | ON AUGUST 5, 1999 AT APPROXIMATELY 20:06 HOURS PRODUCT WAS INITIATED IN TANK 514 OF THE WILLIAMS PIPELINE COMPANY SIOUX CITY, IA TERMINAL BY THE PIPELINE CONTROL CENTER IN TULSA, OK. DELIVERY INTO THE TANK WAS MONITORED BY AN OPERATOR AT THE SIOUX CITY TERMINAL. AT 21:55 ON AUGUST 6, 1999 THE SIOUX CITY OPERATOR NOTIFIED THE DISPATCHTER THAT HE WAS LEAVING AND THE TANK WOULD NOT BE OBSERVED DURING THE REMAINDER OF THE FILL PROCEDURE. ABOUT 2:15, THE DISPATCHER INFORMED THE OPERATOR THAT HE MAY HAVE INADVERENTLY OVERFILLED THE TANK. THE OPERATOR AND AREA COORDINATOR OF MAINTENANCE EACH MADE A PHYSICAL CHECK OF THE TANK AND CONFIRMED THAT A PRODUCT WAS FLOWING OUT OF THE MANWAY AND ROOF VENT. THE DELIVERY OF PRODUCT INTO THE TANK WAS IMMEDIATELY HALTED, AND PRODUCT WAS REDIRECTED TO ANOTHER TANK. PRODUCT ON THE GROUND WAS RECOVERED WITH ABSORBENT MATERIAL. SOIL REMOVAL WAS PROMPTLY BEGUN UNDER THE SUPERVISION OF APPLICABLE ENVIRONMENTAL AGENCIES AND WILL CONTINUE UNTIL ALL RECOVE
2017-09-29 08:50 | YES | NO | 19990127 | 1999-09-13 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1999-08-22 | 1030 | OK |  | MUSTANG | NO |  | NO | NW/4 SECTION 2-T10N-R5W OKLAHOMA COUNTY |  | PUMPING STATION | PUMP |  | 1987 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 1727.6372 | 3485.342 | CRUDE OIL | 3 | 225 | 215 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES A HENRY | 5802557151 | TANK LEVEL GUAGE MALFUNCTIONED PREVENTING PUMPS FROM OPERATING AUTOMATICALLY. THIS ALLOWED TANK TO OVERFILL, RESULTING IN RELEASE OF PRODUCT TO SECONDARY CONTAINMENT.
2017-09-29 08:50 | YES | NO | 19990128 | 1999-09-15 | 30903 | ARCO PIPE LINE COMPANY | YES | 1999-08-24 | 730 | TX | JACK |  | NO |  | NO | SIX MILES SE OF THE TOWN O JACKSBORO, TX AT SEAWAY PIPELINE CO. JACKSBORO STATION ON FM 3324. LATITUDE 33 08' 12" N, LONG 98 07' 26 "W, DANIEL CRENSHAW SURVEY | 496144 | TANK FARM | PIPE |  | 1959 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 51829.1155 | 104560.2606 | CRUDE OIL | 3 | 254 | 100 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER |  |  |  | Null |  |  | Null | Null | GLENN W HOFFEMYER | 9182232952 | AT 9:35 ON AUGUST 24, 1999 ARCO PIPE LINE COMPANY (APL) MADE A TELEPHONIC REPORT TO THE NRC (REPORT NO.. 496144) OF A CRUDE OIL SPILL AT SEAWAY PIPELINE COMPANYS JACKSBORO STATION, LOCATED APPROXIMATELY SIX MILE SOUTHEAST OF JACKSBORO, TEXAS ON FM 3324. APL IS THE OPERATOR OF SEAWAY PIPELINE, WHICH EXTENDS FROM GALENA PARK, TEXAS TO CUSHING, OKLAHOMA. AT APPROXIMATELY 7:30 ON AUGUST 24, 1999, A LEAK WAS DISCOVERED BY A COMPANY EMPLOYEE ARRIVING FOR WORK AT THE FACILITY. THE SOURCE OF THE RELEASE WAS IDENTIFIED AS AN INTERNAL CORROSION PIT AT THE SIX OCLOCK POSITION ON A BELOW GROUND PORTION OF THE 20-INCH SUCTION/FILL HEADER TO TANK 307. THE TANK LINE WAS INACTIVE AT THE TIME OF THE INCIDENT. IMMEDIATELY AFTER DISCOVERY OF THE RELEASE, THE TANK LINE WAS ISOLATED, STOPPING THE SOURCE OF CRUDE OIL, AND EMERGENCY REPONSE AND CLEANUP PERSONNEL WERE CALLED TO THE SITE TO UNDERTAKE CONTAINMENT, CLEANUP AND REPAIR ACTIVITIES. NO WATERWAYS WERE AFFECTED AND THE AREA IMPACTED BY THE RELEASE WAS CONFINED TO THE PIPING AREA WITHIN THE STATION MANIFOLD AREA. TANK LEVEL MEASUREMENTS, AND AN ESTIMATE OF THE TANK LINE DRAIN-UP, INDICATED A TOTAL RELEASE VOLUME OF 254 BARRELS. APPROXIMATELY 100 BARRELS OF LIQUID WERE RECOVERED FROM THE RELEASE SITE AND RE-INJECTED INTO SYSTEM. CRUDE OIL AFFECTED SOIL WAS REMOVED AND STOCK PILED AT THE FACILITY FOR FUTURE REMEDIATION. CLEAN UP OF THE SPILL SITE IS BEING COORDINATED BY REPRESENTATIVES OF APLS ENVIRONMENTAL, HEALTH AND SAFETY GROUP, WITH ASSISTANCE FROM GARNER ENVIRONMENTAL SERVICES.
2017-09-29 08:50 | NO | NO | 19990129 | 1999-09-15 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 1999-08-19 | 1750 | TX | WISE |  | NO |  | NO | J J GHOLSON A-324 SURVEY - 2 1/2 MILES NNW OF BOOSNVILLE, TX |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | NO | NO | 4 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | NO |  |  |  |  | Null |  |  | Null | Null | BOB AEBI | 5803956294 | LANDOWNER FOUND THE PIPELINE SEEPING A FEW DROPS OF SOME PRODUCT. HE CALLED THE TEXAS RAILROAD COMMISSION AND ASK FOR ASSISTANCE. THE RRC INFORMED KOCH OF THE INCIDENT AND SAID THAT LESS THAN 12 DROPS OF PRODUCT WAS RELEASED FROM THE ABANDONED PIPE INTO A STAGNATE POOL OF WATER 5 FEET BY 15 IN AREA.
2017-09-29 08:50 | YES | YES | 19990130 | 1999-09-14 | 2731 | CHEVRON PIPELINE CO | YES | 1999-08-10 | 1630 | TX | FREESTONE |  | NO |  | NO | RELEASE OCCURRED IN THE STATION MANIFOLD AREA OF CHEVRON PIPE LINE'S WORTHAM STATION. THE STATION IS LOCATED APPROX 3 MILES EAST OF WORTHAM, TX OF FM 27 |  | PUMPING STATION | OTHER | UNDETERMINED (SEE PART K) | 1952 | OTHER | UNDETERMINED (SEE PART K) | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 3 | 3 | 0 | 2500000 | 1727637.1837 | 3485342.0195 | CRUDE OIL | 1 | 15007 | 25 | YES | YES |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES R BURKE | 2815963569 | PERSONNEL ON SITE - 2 CHEVRON PIPELINE EMPLOYEES AND 8 CONTRACT EMPLOYEES. SCOPE OF WORK - TO ISOLATE THE WORTHAM STATION BYPASS (A SECTION OF PIPE BETWEEN THE STATION INCOMING STREAM AND THE STATION OUTGOING STREAM), CUT AND REMOVE A 4 SECTION OF THE BYPASS, AND INSTALL WELDCAPS OF EACH OF THE OPEN ENDS TO ISOLATE THE INCOMING AND OUTGOING STREAMS. THE VALVES ON BOTH ENDS OF THE BYPASS LINE WERE CLOSED, LOCKED OUT AND TAGGED. THE OIL IN THE ISOLATED BYPASS LINE WAS DRAINED TO THE SUMP AND VENTS WERE OPENED ON BOTH ENDS TO AID DRAINAGE AND TO INSURE THAT PRESSURE WOULD NOT BUILD IN THE WORK AREA. TWO COLD CUTS WERE MADE, USING A PNEUMATIC SAW AND A 4 SECTION OF PIPE WAS REMOVED. A GEL PLUG WAS INSTALLED IN EACH END AS A VAPOR BARRIER AND THE WELDER BEGAN TO HAND BEVEL THE PIPE ON THE INCOMING SIDE WITH HIS TORCH. THE GEL PLUG IN THE OUTGOING SIDE (BEHIND THE WELDER AS HE WORKED) WAS PUSHED OUT AND VAPORS IGNITED BURNING THE WELDER AND THE TWO CHEVRON EMPLOYEES WHO PULLED HIM TO A SAFE AREA. THE FIRE DAMAGED THE STATION MANIFOLD AND THE PUMP STATION, BUT WAS CONTAINED WITHIN THE STATION PROPERTY.
2017-09-29 08:50 | YES | NO | 19990131 | 1999-09-17 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1999-08-30 | 1100 | TX | SAN PATRICIO |  | NO |  | NO |  | 496917 | LINE PIPE | PIPE |  | 1969 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | GASOLINE | 3 | 50 | 25 | NO | NO | 12 | 0.208 | 2471 | WELDED |  | 1000 | 950 | YES | 0 | 0 | 2 | 1989 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | D C HUNT JR | 3618662190 | THE LEAK WAS CAUSED BY A PIN-HOLE THAT DEVELOPED EXTERNAL CORROSION. THE PIPE WAS LOCATED IN A 14 INCH CASINO LOCATED UNDER COUNTY ROAD 96. THE GASOLINE FILLED THE CASINO AND FLOWED OUT OF THE CASINO VENT AND WAS REPORTED BY A LOCAL FARMER
2017-09-29 08:50 | YES | NO | 19990132 | 1999-09-20 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 1999-08-17 | 1148 | KS | ALLEN |  | NO |  | NO |  |  | LINE PIPE | NO DATA |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 17276.3718 | 34853.4202 | DATA NOT SPECIFIED | 3 | 316 | 103 | NO | NO | 8 | 0.172 | 0 | WELDED |  | 1400 | 415 | YES | 1891 | 1891 | 7 | 1992 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KENNETH L LYBARGER | 9184462517 | AT APPROXIMATELY 11:48 ON AUGUST 17, 1999, THE WILLIAMS PIPELINE COMPANY (WPL) OPERATIONS DEPARTMENT IN TULSA, OKLAHOMA RECEIVED A CALL FROM THE WPL STATION OPERATOR AT HUMBOLDT, KANSAS REPORTING THAT A LOCAL FARMER HAD TOLD THE STATION OPERATOR THAT HE HAD PUNCTURED THE PIPELINE WHILE PLOWING THIS FARM. THE PIPELINE WAS SHUT-IN AT THE TIME OF THE RELEASE WITH APPROXIMATELY 415 PSIG REGISTERED ON THE SCADA SYSTEM IN OPERATIONS CONTROL. TELEPHONIC NOTICE WAS MADE TO THE NATIONAL RESPONSE CENTER, LEPC AND ALLEN COUNTY SHERIFF. LOCAL OPERATIONS AND MAINTENANCE PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE SITE AND THE REMAINING PRODUCT IN THE PIPELINE WAS DRAINED INTO TRANSPORTS AND HAULED TO A WPL FACILITY. MAINLINE VALVES WERE CLOSED AND THE DAMAGED PORTION OF THE LINE WAS REPLACED WITH NEW PIPE IN ACCORDANCE WITH 49 CFR PART 195, AND THE LINE SUBSEQUENTLY RESTORED TO SERVICE AT 19:00 ON AUGUST 18. ALL THE CONTAMINATED SOIL WAS REMEDIATED ON SITE UNDER THE SUPERVISION OF THE STATE ENVIRONMENTAL AGENCY WITH THE CONCURRENCE OF THE FEDERAL EPA.
2017-09-29 08:50 | YES | NO | 19990133 | 1999-09-20 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1999-08-16 | 600 | TX | LA SALLE |  | NO |  | NO | 3.5 MILES NORTH OF THE COASTAL STATES CRUDE GATHERING CO MCCUNN STATION |  | LINE PIPE | PIPE |  | 1938 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1382.1097 | 2788.2736 | CRUDE OIL | 3 | 232 | 0 | NO | NO | 6 | 0.188 | 0 | WELDED |  | 500 | 300 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | REX J PROSSER | 7138777370 | A LOSS OF PRESSURE WAS REPORTED BY THE DISPATCHER THE PIPELINE WAS SHUT IN AND PERSONNEL WERE DISPATCHED TO INVESTIGATE. A OIL STAIN WAS OBSERVED ABOVE THE PIPELINE AT A LOCATION 3.5 MILES NORTH OF MCCUNN STATION. THE PIP WAS UNCOVERED AND A CORROSION HOLE WAS LOCATED AT THE 6 OCLOCK POSITION. A CLAMP WAS PLACED OVER THE HOLE AND THE PIPE RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19990134 | 1999-09-09 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1999-08-06 | 1730 | AR | UNION | EL DORADO | NO |  | NO | 4021 CALION HWY |  | TANK FARM | TANK |  | 1942 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 33500 | 23150.3383 | 46703.5831 | GASOLINE | 3 | 785 | 320 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ERNEST P HAGAN | 7137593845 | A MISTAKE MADE IN IDENTIFYING AVAILABLE STORAGE SPACE RESULTED IN THE OVERFILLING OF AN UNLEADED REGULAR GASOLINE TANK. UPON DISCOVERY, THE OPERATOR IMMEDIATELY SHUT OFF FLOW TO THE TANK AND STOPPED THE OVERFLOW OF PRODUCT. THERE WERE APPROXIMATELY 320 BARRELS OF PRODUCTS TRANSFERRED FROM THE CONTAINMENT DIKE AREA TO AN ADJACENT STORAGE TANK. THE ADDITONAL PRODUCT WAS LOST TO EVAPORATION AND ABSORPTION INTO THE CONTAINMENT AREA. CURRENTLY, ASSESSMENTS ARE BEING MADE FOR DEVELOPMENT OF A PLAN ACCEPTABLE BY THE APPROPRIATE STATE AGENCY AT WHICH TIME REMEDIATION WILL BEGIN.
2017-09-29 08:50 | YES | NO | 19990136 | 1999-09-27 | 1845 | BUCKEYE PIPELINE CO LP | YES | 1999-02-16 | 919 | NY | NEW YORK CITY | QUEENS | NO |  | NO | SEE ATTACHED DRAWING NUMBER 11820-A |  | NO DATA | SCRAPER TRAP |  | 1965 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 62194.9386 | 125472.3127 | GASOLINE | 3 | 40 | 38 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | CARL A OSTACH | 6107704495 | ON TUESDAY, FEBRUARY 16, 1999, A BUCKEYE EMPLOYEE WAS LOOSENING THE BOLTS ON A SCRAPER TRAP DOOR TO REMOVE A SCRAPER. WHILE LOOSENING ONE OF THE BOLTS, THE SCRAPER TRAP DOOR CAME PARTIALLY OPEN AND RELEASED SPRAYING GASOLINE. THE EMPLOYEE ISOLATED THE SCRAPER TRAP AND REPORTED THE RELEASE TO HIS LOCAL SUPERVISOR IMMEDIATELY. THE NEW YORK CITY FIRE DEPARTMENT RESPONDED AND, AS A PRECAUTIONARY MEASURE, SPRAYED FOAM OVER THE IMMEDIATE AREA. CONTAINMENT BOOMS WERE ALSO DEPLOYED TO PREVENT PRODUCT FROM MIGRATING INTO THE NEWTOWN CREEK. ALL APPLICABLE AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE PERFORMED UNDER THE SUPERVISION OF THE NEW YORK DEPARTMENT OF ENVIRONMENTAL CONSERVATION AND THE NEW YORK CITY FIRE DEPARTMENT. THE SCRAPER TRAP DOOR WAS REPAIRED AND THE SCRAPER TRAP WAS PRESSURIZED AND TESTED. THE PIPELINE SYSTEM WAS PUT BACK IN SERVICE LATER THAT DAY.
2017-09-29 08:50 | YES | NO | 19990137 | 1999-09-28 | 5165 | FINA OIL & CHEMICAL CO (NOW TRUST & RIVER P/L CO ) | NO | 1999-07-29 | 1630 | TX | HOWARD |  | NO |  | NO | 32 17' 26" N AND 101 11' 41" W; SECTION 12, BLK 30, TWP 1-S, T&P RR SURVEY 4000' W OF HOWARD-MITCHELL COUNTY LINE; APPROX 6.8 MI SE OF THE TOWN OF COAHOMA; |  | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 155487.3465 | 313680.7818 | DIESEL FUEL |  | 50 | 26 | NO | NO | 6.625 | 0.188 | 42000 | WELDED |  | 1050 | 565 | YES | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | ROBERT K REED | 9152639256 | THIS LEAK WAS DISCOVERED AND REPORTED TO FINAS (TRUST PIPE LINE CO) PIPELINE CONTROL CENTER IN BIG SPRING, TEXAS, AT 4:30 PM ON JULY 29, 1999 BY AERIAL PATROL PILOT. THE LEAK WAS REPORTED AS A "STAIN" OF DARKENED SOIL ON THE PIPELINE ROW. A PIPELINE EMPLOYEE (JOHNNY JACKSON) WAS IMMEDIATELY DISPATCHED TO INVESTIGATE, AND AT 6:35PM THE SITE WAS LOCATED AND CONFIRMED, WITH A SURFACE AREA OF 40 X 80 APPEARING TO BE AFFECTED. THE PIPELINE WAS SHUT-IN AT 6:40 PM. EQUIPMENT AND ADDITIONAL PERSONNEL WERE ORDERED OUT, AND AT 8:38 PM THE LEAK HAD BEEN EXCAVATED, AND WAS CONFIRMED AS HAVING ORIGINATED FROM FINAS 6" (TRUST) PIPELINE. BETWEEN 8:49 AND 9:03PM STATE AGENCIES WERE NOTIFIED, WITH THE TOTAL VOLUME BEING REPORTED AS A LOSS OF 25-40 BBLS OF GASOLINE. AT 9:05 PM, A CLAMP HAD BEEN INSTALLED ON THE PIPELINE. ON JULY 30TH, AT 9:15AM, THE PIPELINE WAS PLACED BACK INTO SERVICE. AT 10:12 AM ON JULY 30TH NOTIFICATION WAS MADE TO THE NRC AS AN "ESTIMATED LEAK OF MORE THAN 50 BBLS". THROUGHOUT THE WEEKEND OF JULY 30 - AUGUST 1, THE LEAK SITE WAS MONITORED AND A TOTAL OF 26 BBLS OF PRODUCT WAS RECOVERED BY VACUUM TRUCK. ON AUGUST 2ND, FINAS CONTRACTOR BEGAN EXCAVATING CONTAMINATED SOIL. DURING THIS PROCESS, AN ADDITIONAL "ACTIVE" LEAK-SITE WAS DISCOVERED APPROXIMATELY 50 WEST OF THE ORIGINAL LEAK-SITE, AND TWO OLD REPAIR-SITES WERE FOUND AT LOCATION 62-70 WEST OF THE ORIGINAL LEAK-SITE, WITH THE PIPE BEING FOUND TO HAVE AREAS OF CORROSION THROUGHT AN OVERALL LENGTH OF 310 (THIS LENGTH OF PIPE WAS SUBSEQUENTLY REPLACED). THE SOIL EXCAVATION WORK WAS CONTINUED THRU AUGUST 16TH, BY WHICH TIME 15,120 C.Y. OF CONTAMINATED SOIL WAS EXCAVATED AND TAKEN OFF SITE FOR REMEDIATION. CLEAN BACK-FILL IS BEING REPLACED WITHIN THE EXCAVATION. BETWEEN AUGUST 31 AND SEPTEMBER 10, A TOTAL OF FIVE SOIL BORINGS WERE MADE IN THE AREA IN ORDER TO DETERMINE THE VERTICAL DELINEATION OF THE CONTAMINATION. TWO OF THE BORINGS WERE ADVANCED TO 260-27- BELOW THE BASE OF THE EXCAVATION.
2017-09-29 08:50 | YES | NO | 19990138 | 1999-09-27 | 30991 | MOBIL OIL CORPORATION | YES | 1999-08-28 | 500 | TX | HARDIN |  | NO |  | NO | BRAGG PIPELINE STATION IS LOCATED IN HARDIN COUNTY, TX OFF STATE HIGHWAY 1293 BETWEEN THE CITIES OF KOUNTZ & THICKETT BRAGG PUMP STATION IS PART OF MOBIL PIPE | 496707 | PUMPING STATION | VALVE |  | 1994 | OTHER | FAILED GASKET 16" CHECK VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 31097.4693 | 62736.1564 | CRUDE OIL | 3 | 645 | 595 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null | ONE CALL |  | Null | Null | S S SOBEY, MANAGER | 2146585914 | TOP GASKET ON #2 UNIT 16" BYPASS CHECK VALVE FAILED CAUSING SPILL. LEAK WAS DISCOVERED BY A LOGGER WHO CALLED THE HARDIN COUNTY SHERIFFS DEPT WHO IN TURN NOTIFIED MOBIL PIPE LINE COMPANY. MOBILS PIPELINE OPERATIONS CONTROL CENTER IN DALLAS IMMEDIATELY SHUT DOWN THE PIPELINE SYSTEM AND ACTIVATED ITS EMERGENCY RESPONSE UNIT TO BEGIN CONTAINMENT AND CLEANUP ACTIVITIES. REPAIRS MADE TO THE CK VALVE BY REPLACING THE FAULTY GASKET. ALL NOTIFICATIONS MADE IN ACCORDANCE WITH DOT PART 195 REGULATIONS. MOBIL HAS INVESTIGATED THIS INCIDENT AND A COPY OF THE INVESTIGATION REPORT WILL BE PROVIDED TO THE REGIONAL OFFICE OF THE DOTS OFFICE OF PIPELINE SAFETY IN HOUSTON, TX.
2017-09-29 08:50 | NO | NO | 19990139 |  | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1999-08-23 | 1430 | CA | CONTRA COSTA |  | NO |  | NO | MOCOCCO ROAD 1/2 MILE NORTH OF WATER FRONT RD JUST EAST OF I-680 ON THE SOUTH SHORE LINE OF CARQUINEZ STRAIT |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 56500 | 39044.6004 | 78768.7296 | TURBINE FUEL | 3 | 0 | 0 | NO | NO | 10 | 0.219 | 52000 | WELDED |  | 1360 | 20 | YES | 24 | 1910 | 1 | 1968 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | EDWARD A BUZZ FANT | 7138449526 | A FOREIGN PIPELINE COMPANY WAS EXCAVATING THEIR PIPELINE, WHICH PARALLES AND IS IN CLOSE APPROXIMATELY TO KINDER MORGANS PIPELINE- LS 95. THE TRENCH WAS BEING BACKFILLED. THE BACKHOE BUCKET WAS FILLED WITH SOIL AND RAISED FOR TRAVELING. AS THE BACKHOE APPROACHED THE DITCH, IT TILTED OVER FALLING INTO THE TRENCH. A TOOTH OF THE BACKHOE BUCKET STRUCK KINDER MORGANS PIPELINE PUNCTURING IT. AN UNKNOWN AMOUNT OF TURBINE FUEL WAS RELEASED. KINDER MORGANS LOCAL EMERGENCY RESPONSE TEAM WAS ACTIVATED AS WELL AS THE FOREIGN COMPANYS. BOOMS WERE DEPLOYED AND CLEAN UP WAS ACCOMPLISHED BY VACUUM TRUCKS.
2017-09-29 08:50 | YES | NO | 19990140 | 1999-09-28 | 13162 | NAVAJO REFINING CO | NO | 1999-08-20 | 250 | NM | CHAVES |  | NO |  | YES | SEE ATTACHED DRAWING |  | PUMPING STATION | VALVE |  | 1997 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4146.3292 | 8364.8208 | DIESEL FUEL | 1 | 50 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JIM G TOWNSEND | 5057483311 | NAVAJO PERSONNEL WERE IN THE PROCESS OF PURGING NITROGEN OUT OF THE PIPELINE WITH DIESEL FUEL. THE PRODUCT ARRIVED BEFORE ANTICIPATED RESULTING IN NOT GETTING VALVE CLOSED UNTIL APPROXIMATELY 50 BARRELS WERE SPILLED.
2017-09-29 08:50 | YES | NO | 19990141 | 1999-09-23 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1999-08-25 | 1104 | MN |  |  | NO |  | NO | CLEARBROOK TERMINAL (PUMPING BUILDING), |  | PUMPING STATION | NO DATA |  | 0 | OTHER | FAILURE TO USE PROPER LOCKOUT/TAGOUT PROCEDURES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 1 | 0 | YES | NO |  |  | 0 | FLANGED |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | YES |  |  |  |  | Null |  |  | Null | Null | L H DIBUYI, VP OPERATIONS | 2187250102 | AT THE TIME OF THE INCIDENT, CONSTRUCTIONS FOR PUMP MODIFICATIONS, (ORBIT VALVE REPLACEMENT) WAS TAKING PLACE ON UNIT 1.2. THE ADJACENT UNIT 1.1 HAD BEEN TAKEN OUT OF SERVICE FOR SIMILAR WORK. WHEN IT WAS DETERMINED THAT UNIT 1.2 WOULD BE DONE FIRST, AND THE EDMONTON CONTROL CENTER REQUIRED UNIT 1.1, IT WAS REQUIRED TO BE PUT BACK INTO SERVICE. PRIOR TO ADVISING THE EDMONTON CONTROL CENTER THAT THE UNIT WAS READY TO BE PUT BACK INTO SERVICE, AN INSPECTION OF THE UNIT WAS DONE. PROPER DOCUMENTED COMPANY PROCEDURES FOR LOCKOUT/TAGOUT AND RETURNING THE UNIT TO SERVICE WERE NOT FOLLOWED. THE UNIT RAN FOR 44 SECONDS WHEN A FLASH FIRE OCCURRED. A TEMPERTURE MONITORING DEVICE, CALLED A MULTILIN, NORMALLY WOULD HAVE SHUTDOWN THE UNIT WHEN PUMP TEMPERATURES EXCEED 50 DEGREES C. THE MULTILIN HAD BEEN PREVIOUSLY DAMAGED AND FAILED AT THE TIME OF THE INCIDENT. IT HAS BEEN REMOVED, REPLACED, AND IS BEING ANALYZED FOR POSSIBLE FAILURE CAUSES. EMERGENCY RESPONSE WAS INSTANTANEOUS AND THE FIRE WAS IMMEDIATELY EXTINGUISHED. THE BUILDING AND THE PUMP WERE DAMAGED. NO INJURIES OCCURRED. FURTHER INVESTIGATIONS AND TRAINING ARE ON-GOING.
2017-09-29 08:50 | YES | NO | 19990142 | 1999-09-28 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 1999-08-27 | 820 | IA | WORTH |  | NO |  | NO |  | 496614 | LINE PIPE | PIPE |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 207316.462 | 418241.0423 | DIESEL FUEL | 3 | 98 | 4 | NO | NO | 12 | 0.25 | 0 | WELDED |  | 1050 | 297 | YES | 8 | 1388 | 8 | 1994 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KENNETH L LYBARGER | 9185735774 | PERSONNEL FROM WILLIAMS PIPELINE (WPL) WERE REMEDIATING SOIL FROM A PREVIOUSLY DISCOVERED LEAK IN THE SEAM OF THE #4-12 PIPELINE WHEN THEY DISCOVERED A SECOND LEAK IN THE PIPE A FEW HUNDRED FEET AWAY. THE LINE WAS IMMEDIATELY SHUT IN AND PRODUCT DRAINED UP TO OTHER WPL FACILITIES. TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER, THE IOWA DEPARTMENT OF NATURAL RESOURCES (SERC), AND WORTH COUNTY LEPC IN ACCORDANCE WITH REGULATIONS. REPAIR AND RECOVERY EFFORTS WERE CONDUCTED SIMULTANEOUSLY. APPROXIMATELY 233 FEET OF HYDROTESTED PIPE WAS REPLACED (SO NEW PIPE WOULD CONNECT TO A SEGMENT OF NEW PIPE PREVIOUSLY REPLACED) AND THE LINE RETURNED TO SERVICE ON AUGUST 28TH. THE DEFECTIVE PIECE WAS CUT AND SENT TO METALLURGY COMPANY FOR ANALYSIS. COMPLETE REMEDIATION OF AFFECTED SOIL WAS CARRIED OUT UNDER THE SUPERVISION OF THE EPA IN ACCORDANCE WITH ITS REQUIREMENTS.
2017-09-29 08:50 | YES | NO | 19990143 | 1999-10-05 | 3012 | PRIDE TEXAS PLAINS L.P. | NO | 1999-09-24 | 1730 | TX | GRAY | PAMPA | NO |  | NO | SEE ATTACHED MAP | 500065 | TANK FARM | SCRAPER TRAP |  | 1927 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3455.2744 | 6970.684 | CRUDE OIL | 3 | 70 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LELAND S HASTINGS | 9156748189 | 10" MOTOR OPERATED VALVE OPENED TO 10" SCRAPPER TRAP RECEIVER. DRAIN WAS OPEN TO SUMP. THIS WAS CONTAINED TO THE STATION AREA ONLY.
2017-09-29 08:50 | YES | NO | 19990144 | 1999-10-01 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 1999-09-26 | 700 | TX | HASKELL | HASKELL | NO |  | NO | N ON HWY 277 FROM HASKELL TO FM 1080, EAST TO CR 249, NORTH TO STATION |  | TANK FARM | TANK |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6910.5487 | 13941.3681 | CRUDE OIL | 1 | 1200 | 1130 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LENNAH FROST | 9156843467 | TANK GAUGE FAILED, CONTROLLER CONTINUED TO PUMP INTO TANK NOT KNOWING THAT TANK WAS AT HIGH LEVEL.
2017-09-29 08:50 | YES | NO | 19990145 | 1999-10-04 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 1999-09-16 | 600 | TX | GLASSCOCK | MIDKIFF | NO |  | NO | APPROX 1 MILE SOUTH OF THE INTERSECTION OF FM 2401 AND FM 1357 | 498971 | PUMPING STATION | PUMP |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3455.2744 | 6970.684 | CRUDE OIL | 1 | 65 | 45 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LENNAH FROST | 9156843467 | PACKING BLEW OUT ON PUMP
2017-09-29 08:50 | YES | NO | 19990146 | 1999-10-12 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | NO | 1999-09-07 | 1245 |  |  |  | YES | SOUTH PASS BLK 55, LAT. 5 | YES | THE RELEASE OCCURRED AT SOUTH PASS BLK 55A PLATFORM, WHICH IS OWNED BY TENNESSEE GAS PIPELINE (TGP) | 497831 | OTHER | OTHER | PIG TRAP DRAIN VALVE | 1982 | OTHER | BALL VALVE FAILURE ON PIG TRAP DRAIN VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 53000 | 36625.9083 | 73889.2508 | CRUDE OIL | 1 | 70 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KEITH A GUILBEAU | 2815963562 | AT APPROXIMATELY 0800 HRS ON 9/7/99, TWO OPERATORS WERE REMOVING A PIG FROM THE RECEIVER OF THE 10" PIPELINE ON SOUTH PASS 55 A (TGP) PLATFORM. AFTER THE PIG REMOVAL, THE PIG RECEIVER WAS CLOSED AND PLACED IN THE RECEIVE MODE. THE PIG TRAP DOOR WAS CLOSED AND SECURED AND THE DRAIN AND VENT VALVES WERE CLOSED. AT APPROXIMATELY 1230 HRS, AN OIL SLICK WAS OBSERVED (BY A TGP AND SGS EMPLOYEE FROM A HELICOPTER OVERFLIGHT) COMING FROM THE SP 55A PLATFORM. THE TGP OPERATOR LANDED ON THE PLATFORM AND CLOSED THE OUTLET VALVE AND SHUT IN ALL INCOMING PRODUCTION FROM THE FIELD. ABSORBENT PADS WERE PUT IN PLACE ON THE PLATFORM DECK TO PREVENT ADDITIONAL OIL FROM DRAINING INTO THE WATER. CHEVRONS PIPELINE OPERATOR ON SP 78B WAS IMMEDIATELY NOTIFIED AND DEPARTED FOR SP 55A. UPON ARRIVING, VERIFICATION WAS MADE THAT ALL LEAKS HAD STOPPED, AND THE SPILL SITUATION EVALUATED, INCLUDING VERFICATION THAT THE INLET AND OUTLET VALVES OF THE PIG TRAP WERE CLOSED. THE NATIONAL RESPONSE CENTER (NRC) WAS IMMEDIATELY NOTIFIED (REPORT #49831), AS WELL AS THE MINERALS MANAGEMENT SERVICE (MMS), SPILL RESPONSE EQUIPMENT, INCLUDING A BOOM DEPLOYMENT VESSEL AND A FAST RESPONSE UNIT (FRU) WAS DISPATCHED TO THE SP 55A LOCATION. AS A RESULT OF THE SPILL INCIDENT, THE DRAIN LINE TO THE TRAP WAS DISCONNECTED AND INSTALLED WITH A BLIND FLANGE AND NEW DRAIN VALVE. ON SEPTEMBER 14TH, THE INSTALLED DRAIN VALVE WAS SENT IN FOR TESTING AND WAS FOUND TO BE FAULTY (LEAKING IN THE CLOSED POSITION).
2017-09-29 08:50 | NO | NO | 19990147 | 1999-10-12 | 30918 | KINDER MORGAN GP, INC. | YES | 1999-09-09 | 3 | IA | POLK | DES MOINES | NO |  | NO | 4401 VANDALIA ROAD, DES MOINES, IA | 498057 | TANK FARM | OTHER | THERMAL RELIEF VALVE | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 691.0549 | 1394.1368 | BUTANE | 3 | 18 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A FANT | 7138449526 | THE PROBABLE CAUSE OF THIS RELEASE IS OPERATOR ERROR. THE FLARE STACK WAS DISCONNECTED FROM A THERMAL RELIEF VALVE FOR MAINTENANCE AND NOT PROPERLY ISOLATED. AN UNANTICPIATED PUMP SHUT DOWN CAUSED THE PRESSURE IN THE PIPING SEGMENT TO EXCEED THE SET POINT OF THE THERMAL RELIEF VALVE. ISOBUTANE, A HVL, WAS RELEASED TO THE ATMOSPHERE.
2017-09-29 08:50 | YES | NO | 19990148 | 1999-10-12 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 1999-09-13 | 740 | OR | WASHINGTON |  | NO |  | NO | 13050 SW TONQUIN RD (2 MILES EAST OF SHERWOOD, OREGON) |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 2920000 | 2017880.2305 | 4070879.4788 | GASOLINE | 3 | 272 | 1 | NO | NO | 8 | 0.188 | 52000 | WELDED |  | 1440 | 680 | YES | 24 | 1600 | 8 | 1962 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | EDWARD A FANT | (713)844-9 | A BACKHOE OPERATOR WAS CLEARING LAND FOR A ROAD IN THE TRI-COUNTY GUN CLUB WHEN HE STRUCK AND PUNCTURED SFPPS LINE SECTION NUMBER 14 AT MILE MARKER 18.3. GASOLINE WAS RELEASED. THE SCADA SYSTEM DETECTED MEASUREMENT IMBALANCE AND THE PORTLAND OPERATOR SHUT DOWN THE LINE IMMEDIATELY, PRIOR TO BEING NOTIFIED BY THE CONTRACTOR. THE EMERGENCY PLAN WAS PUT INTO PLACE AND PERSONNEL DISPATCHED TO THE SCENCE. KINDER MORGAN PERSONNEL CLOSED VALVES ON EITHER SIDE OF THE RELEASE SITE ISOLATING A 7.6 MILE SECTION LIMITING THE AMOUNT OF THE RELEASE TO A 40 FOOT BY 40 FOOT WET SPOT. CLEAN UP WAS INITIATED BY KINDER MORGANS EMERGENCY RESPONSE CONTRACTOR. THE ORIGINAL DEPTH OF COVER AT THE POINT OF CONTACT WAS 48 INCHES AND A LINE MARKER WAS APPROXIMATELY 40 FOOT AWAY. KINDER MORGAN WAS NOT NOTIFIED OF EXCAVATION RELATED ACTIVITY PRIOR TO THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 19990149 | 1999-09-28 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 1999-09-04 | 1040 | OK |  | TULSA | NO |  | NO | WILLIAMS PIPELINE CO WEST TULSA PUMP STATION, 2120 S 33RD WEST AVENUE, TULSA OK 74107 | 497579 | TANK FARM | OTHER | PIPE NIPPLE | 0 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3455.2744 | 6970.684 | JET FUEL | 3 | 84 | 83 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | OTHER |  | Null |  |  | Null | Null | KENNETH L. LYBARGER, SR. COMPLIANCE SPECIALIST, DOT SAFETY | 9185735774 | APPROXIMATELY 2 HOURS AND 26 MINUTES AFTER DELIVERY OF PRODUCT INTO TANK 1207 WAS COMPLETED, A STATION OPERATOR ON ROUTINE INSPECTION NOTICED PRODUCT LEAKING OUT OF A BROKEN A 0.5 INCH THREADED NIPPLE ON THE TANKS WATER DRAW LINE. PRODUCT WAS IMMEDIATLEY PUMPED OUT OF THE TANK TO MINIMIZE THE AMOUNT OF PRODUCT RELEASED, A VACCUM TRUCK BROUGHT IN TO RECOVER PRODUCT WHICH WAS CONTAINED IN A CONCRETE CONTAINMENT AREA, AND A CONTRACTOR CALLED IN TO EXCAVATE ADJACENT SOIL WHIHC MAY HAVE BEEN CONTAMINATED. TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER, STATE EMERGENCY RESPONSE COMMISSION AND LOCAL EMERGENCY PLANING COMMITTEE IN ACCORDANCE WITH APPLICABLE REGULATIONS. CONTAMINATED SOIL WAS REMEDIATED IN ACCORDANCE WITH APPLICABLE EPA GUIDELINES. A FELXIBLE HIGH-PRESSURE HOSE WAS INSTALLED BETWEEN THE WATER DRAW PIPE AND THE 1/2-INCH PIPE FITTING TO ELIMINATE VIBRATION (INSTEAD OF THE ORIGINAL RIGID STEEL TUBING) AND A NEW SCHEDULE 80 NIPPLE INSTALLED.
2017-09-29 08:50 | YES | NO | 19990150 | 1999-10-15 | 30909 | TRANSMONTAIGNE PIPELINE INC | YES | 1999-09-19 | 0 | IN | LAKE | DYER | NO |  | NO | SE & SW 1/4 SEC 12 T35N-R1-W- CITY OF DYER, INDIANIA WITHIN DYER SEWER PLANT PROPERY, LOCATED AT 518 EDMOND DRIVER, DYER, IN |  | LINE PIPE | PIPE |  | 1998 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 375000 | 259145.5775 | 522801.3029 | FUEL OIL |  | 2492 | 1300 | NO | NO | 8 | 0.219 | 2129 | WELDED |  | 665 | 300 | YES | 8 | 895 | 11 | 1998 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | RICK HOOD | 5015716903 | THE NORCO WEST LINE WAS SHUT DOWN DUE TO A HYDROTEST BEING PERFORMED ON ANOTHER SECTION OF PIPE FURTHER WEST. A PRESSURE DROP WAS NOTICED AT THE SECTION BEGINNING IN SCHERERVILLE THAT SECTION WAS SHUT IN A PRESSURED TO MONITOR ITS INTEGRITY. THE LINE CONTINUED TO LOSE PRESSURE, SO IT WAS DECIDED TO PUT WATER IN THE LINE TO TEST IT FURTHER - LINE WAS INSPECTED ON FOOT AND BY AIR - NOTHING WAS FOUND. A 7.8 MILE SECTION WAS BLOCKED IN AND FREEZE CHAMBERS WERE USED TO TEST A SMALLER SECTION AT A TIME - THIS CONTINUED UNTIL IT WAS DETERMINED ON SUNDAY 9/19/99 THAT THERE WAS A LEAK IN A NEW BORE AT THE DYER SEWER PLANT.
2017-09-29 08:50 | YES | NO | 19990151 | 1999-10-15 | 443 | AMOCO PIPELINE CO | YES | 1999-09-11 | 1030 | OK | CADDO |  | NO |  | NO | FROM ALBERT, OK; SOUTH OF HWY 146 7/10 MILE THEN WEST OF HIGHWAY 1/2 MILE IN MIDDLE OF FIELD | 498367 | LINE PIPE | PIPE |  | 1944 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 27642.1949 | 55765.4723 | CRUDE OIL | 1 | 75 | 45 | NO | NO | 16 | 0.25 | 35000 | WELDED |  | 788 | 318 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | THOMAS J BROZOVICH, CORE TEAM LEADER | 8068977000 | LANDOWNER HIRED A CONTRACTOR TO CLEAR A WATERWAY (DITCH) IN HIS FIELD. CONTRACTOR USED A BULLDOZER FOR THE JOB. AS THE BULLDOZER DROVE ON THE BACK OF THE DITCH, A CLEAT ON THE TRACK HIT THE PIPELINE, LOCATED IN THE BOTTOM OF THE DITCH, CAUSING DAMAGE AND THE LEAK. AMOCO PIPELINE DID NOT RECEIVE A NOTIFICATION FROM THE OKIE ONE-CALL SYSTEM REGARDING THIS WORK. AN AMOCO PIPELINE COMPANY RIGHT OR WAY MARKER IS AT THIS LOCATION AND WAS IN PLAIN SIGHT OF DOZER OPERATOR.
2017-09-29 08:50 | YES | NO | 19990152 | 1999-09-17 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 1999-09-17 | 1030 | TX |  | SCURRY | NO |  | NO | CHEVRON PIPELINE EL PASO CRUDE SYSTEM, 8" SHARON RIDGE, MILE POLE MARKER 3.1, H&TC RR CO BLK 23 SECT 125 | 499135 | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 345.5274 | 697.0684 | CRUDE OIL | 3 | 75 | 72 | NO | NO | 8 | 0.322 | 42000 | WELDED |  | 1125 | 0 | YES | 8 | 1580 | 0 | 1996 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | KEITH A GUILBEAU, EMERGENCY RESPONSE SPECIALIST | 2815963562 | EXXON (PROPERY OWNER) GAUGER, WHILE MAKING HIS ROUNDS IN THE FIELD, NOTICED THE RELEASE OF CRUDE OIL AND NOTIFIED CHEVRON PIPELINE COMPANY. CHEVRON IMMEDIATELY NOTIFIED THE NATIONAL RESPONSE CENTER (REPORT #499135) AND THE TEXAS RAILROAD COMMISSION (REPORT 99-4805) THE 8" PIPELINE WAS SHUTDOWN CLAMPED TO STOP THE LEAK AND WILL BE PERMANENTLY REPAIRED AT A LATER DATE. CHEVRONS EMERGENCY RESPONSE CONTRACTOR WAS CALLED AND BEGAN RECOVERY AND CLEAN UP OPERATIONS. 72 BARRELS WERE RECOVERED AND PUMPED INTO STORAGE TANKS ON THE FACILITY. THE CONTAMINATED SOIL IS CURRENTLY BEING BLENDED AND FERTILIZED, WITH NEW SOIL ADDED. ALL REMEDIATION WILL OCCUR ON-SITE.
2017-09-29 08:50 | YES | NO | 19990153 | 1999-10-15 | 30829 | TEPPCO | NO | 1999-09-14 | 800 | TX | FAYETTE |  | NO |  | NO | LA GRANGE TEXAS 1 MILE N E ON FM 2145 FROM THE INTERSECTION OF FM 2145 AND HWY 77. |  | LINE PIPE | NO DATA |  | 1929 | FAILED WELD | OTHER | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 650 | 0 | NO | NO | 12 | 0.375 | 25000 | WELDED |  | 224 | 80 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | OTHER | CRACKED WELD | Null |  |  | Null | Null | FRED CLAKLEY, EH&S MANAGER | 4052395716 | PIPELINE WAS REPAIRED IN THE PAST WITH A FULL ENCIRCLEMENT SLEEVE. LEAK OCCURRED WHEN A FILLET WELD ON THE SLEEVE CRACKED. ONE HUNDRED AND FOUR FEET OF TESTED 12" PIPE WAS INSTALLED TO REPLACE SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19990154 | 1999-10-20 | 31146 | EQUISTAR PIPELINE OPERATIONS | NO | 1999-09-15 | 1950 | TX | BRAZORIA |  | NO |  | NO | ON PIPELINE RIGHT OF WAY APPROXIMATELY 1/2 MILE OFF COUNTY RD, 20, 2 MILES EAST OF INTERSECTION OF COUNTY RD 20 AND HWY 36 BETWEEN W COLUMBIA & DAMON | 498876 | LINE PIPE | PIPE |  | 1979 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 163000 | 112641.9444 | 227244.2997 | NATURAL GAS LIQUID | 2 | 19 | 0 | NO | NO | 6 | 0.219 | 42000 | WELDED |  | 1440 | 800 | YES | 24 | 2770 | 8 | 1979 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LESLIE RAY | 7138446942 | AN AERIAL PATROL PLANE FIRST DISCOVERED THE FAILURE WHEN A PATCH OF BROWN GRASS WAS SPOTTED FROM THE AIR. THE FINDING WAS CALLED IN AND INVESTIGATED THE SAME DAY. IT WAS CONFIRMED THAT THE BROWN GRASS WAS THE RESULT OF AN EQUISTAR PIPELINE LEAK AT APPROXIMATELY 7:50 PM THAT EVENING. THE PIPELINE WAS DEINVENTORIED USING A SMOKELESS PORTABLE FLARE, A NEW SECTION OF PIPELINE WAS INSTALLED, AND THE LINE WAS PLACED BACK INTO SERVICE THE FOLLOWING WEEK. THE PIPE FAILED DUE TO MECHANICAL DEFECT IN THE PIPE. AN INVESTIGATION OF THE INCIDENT IS ON GOING.
2017-09-29 08:50 | YES | NO | 19990155 | 1999-10-28 | 30781 | OLYMPIC PIPE LINE COMPANY | YES | 1999-08-29 | 2020 | WA | KING | RENTON | NO |  | NO | SEE ATTACHED MAP | 496845 | PUMPING STATION | PUMP |  | 1973 | OTHER | MECHANICAL FAILURE OF INJECTION PUMP STATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 207316.462 | 418241.0423 | TRANSMIX (PART.REFINED PETRO) | 3 | 80 | 42 | NO | NO |  |  | 0 | OTHER |  | 1390 | 954 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | C CRAIG HAMMETT, ENGINEERING COORDINATOR | 3607339715 | A MECHANICAL FAILURE OF A PISTON IN AN INJECTION PUMP OCCURRED AT RENTON STATION AT APPROXIMATELY 20:20, ON AUGUST 29, 1999, CAUSING 80 BARRELS OF TRANSMIX TO SPILL ONTO THE GROUND WITHIN A CONTAINMENT AREA. THE SPILL WAS NOTICED AT APPROXIMATELY 21:00 WHEN THE CONTROL CENTER RECEIVED A HIGH SUMP INDICATION. THE SUMP WAS VISUALLY INSPECTED, THE INJECTION PUMP WAS SHUTDOWN, AND A FIELD OPERATOR WAS CALLED TO RENTON. THE OPERATOR ARRIVED ON SCENE AT 21:35 AND REPORTED PRODUCT ON THE GROUND. REMEDIATION EXPECTED TO BE COMPLETE FEBRUARY, 2000.
2017-09-29 08:50 | YES | NO | 19990156 | 1999-10-28 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-09-30 | 2230 | TX | MIDLAND |  | NO |  | NO | 1301 SOUTH CR 1150 (NW NW SECTION 45, T-1-S, BLK 38, T&P RR SURVEY | 500837 | TANK FARM | OTHER | SUMP | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL | DAMAGE BY OPERATOR OR ITS CONTRACTOR | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 148830 | 102849.6968 | 207489.3811 | GASOLINE | 1 | 1360 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null |  |  | Null | Null | GARY L ZIMMERMAN | 7132415334 | SUMP OVERFLOWED DUE TO 2" DRAIN VALVE ON SCRAPER TRAP BEING MISTAKENLY LEFT IN OPEN POSITION BY MAINTENANCE PERSONNEL WHO HAD WORKED AT THE SITE EARLIER DURING A SCHEDULED SHUTDOWN OF THE PIPELINE. WHEN THE PIPELINE WAS RETURNED TO SERVICE, THE OPEN 2" DRAIN VALVE CAUSED THE SUMP TO OVERFLOW.
2017-09-29 08:50 | YES | NO | 19990157 | 1999-11-08 | 443 | AMOCO PIPELINE CO | NO | 1999-10-07 | 945 | ND |  | TIOGA | NO |  | NO |  |  | PUMPING STATION | PUMP |  | 1989 | OTHER | COATING FAILURE ON ROD CAUSING PACKING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL |  | 90 | 85 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES F WARD | 3072684513 | MATERIAL FAILURE OCCURRED WITHIN THE POSITIVE DISPLACEMENT PUMP PACKING WHICH CAUSED THE RELEASE OF CRUDE OIL. THE CRUDE OIL WAS CONTAINED WITHIN THE STATION.
2017-09-29 08:50 | YES | NO | 19990158 | 1999-11-02 | 30991 | MOBIL OIL CORPORATION | YES | 1999-10-04 | 855 | CA | KERN | BELRIDGE | NO |  | NO | HWY 33 & LOST HILLS RD |  | NO DATA | PUMP |  | 1989 | OTHER | LINER COVER GASKET FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10365.8231 | 20912.0521 | CRUDE OIL |  | 370 | 300 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | F ANDY ANDERSON | 6617637602 | FIELD GAUGER ARRIVED AT STATION TO FIND OIL SPRAYING FROM #7 PUMP. GAUGER PRESSED EMERGENCY STOP AND NOTIFIED APPROPIATE MOBIL PERSONNEL.
2017-09-29 08:50 | YES | NO | 19990159 | 1999-11-02 | 1734 | BRIDGELINE GAS DISTRIBUTION LLC | NO | 1999-10-04 | 1600 | LA | ASSUMPTION | BELLE ROSE | NO |  | NO | NORTH SIDE OF LA STATE HWY 996 IN AN AREA CALLED BRULY ST. MARTIN. SEE ATTACHED MAP | 501205 | LINE PIPE | VALVE |  | 1980 | OTHER | HYDRATE FORMATION IN BLOCK VALVE CAUSED THEM NOT T | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | BUTANE | 2 | 231 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | MORRIS J OLIVIER, PIPELINE SAFETY SPECIALIST | 5047125653 | DURING PIPELINE PIGGING OPERATIONS, TWO VALVES IN SERIES FAILED TO COMPLETELY CLOSE DUE TO THE FORMATION OF HYDRATES IN THE VALVE OPENINGS. THIS CAUSED IS0-BUTANE FROM AN ASSOCIATED PIPELINE SYSTEM TO BE VENTED TO ATMOSPHERE THROUGH THE VALVE SITE/PIG TRAP VENT HEADER SYSTEM. THIS RELEASE THROUGH THE SITE VENT SYSTEM RESULTLED IN THE FORMATION OF AN ISO-BUTANE VAPOR CLOUD THAT ENGULFED THE ENTIRE VALVE SITE UNTIL THE ASSOCIATED PIPELINE SEGMENT COULD BE DEPRESSURIZED. ONCE THE VAPOR CLOUD HAD DISSIPATED, METHANOL INJECTION WAS USED TO CLEAR THE HYDRATE PLUG ALLOWING THE VALVES CONNECTED TO THE VENT HEADER TO BE CLOSED. THE RELEASE OF ISO-BUTANE ENDED APPROXIMATELY 17 HOURS AFTER IT BEGAN. THERE WAS NO INJURIES OR THIRD PARTY DAMAGE AS A RESULTED OF THIS RELEASE.
2017-09-29 08:50 | YES | NO | 19990160 | 1999-11-04 | 15674 | PLANTATION PIPE LINE CO | YES | 1999-10-13 | 2347 | MS | COVINGTON |  | NO |  | NO | HIGHWAY 588, COLLINS, MS | 502302 | TANK FARM | PUMP |  | 1969 | OTHER | MECHANICAL FAILURE OF PUMP EQUIPMENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 207316.462 | 418241.0423 | DIESEL FUEL | 3 | 0 | 0 | YES | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JACQUE L WILLIAMS JR | 7707514095 | AT APPROXIMATELY 11:55 P.M. CDST ON 10/13/99, A FIRE OCCURRED IN THE WEST MANIFOLD AT PLANTATIONS TANK FARM FACILITY AT COLLINS, MS. THE FIRE WAS EXTINGUISHED AT APPROXIMATELY 12:30 A.M. BY PLANTATION AND COLLINS FIRE DEPARTMENT PERSONNEL. AN INITIAL INSPECTION OF THE FACILITIES IN THE IMMEDIATE AREA OF THE FIRE INDICIATES A PUMPING UNIT FAILED DURING A DIESEL FUEL DELIVERY TO A LOCAL CUSTOMER AT COLLINS, MS. THE CAUSE OF THE EQUIPMENT FAILURE AND SUBSEQUENT FIRE IS UNKNOWN AT THIS TIME. THE AMOUNTOF PRODUCT SPILLED IS A POST-FIRE ESTIMATE. AMOUNT OF PRODUCT RECOVERED AND RETURNED TO THE SYSTEM IS ESTIMATED TO BE ONE HALF, WITH THE REMAINING AMOUNT RECOVERED WITH SOIL AND GRAVEL IN THE AREA.
2017-09-29 08:50 | YES | NO | 19990161 | 1999-11-15 | 443 | AMOCO PIPELINE CO | YES | 1999-10-11 | 1130 | OK | LINCOLN |  | NO |  | NO | NW/4, SECTION 24, TOWNSHIP 17 N, RANGE SE, CORNER OF HARMONY ROAD & TEXACO RD OUTSIDE OF CUSHING OK |  | TANK FARM | NO DATA |  | 1922 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 800 | 795 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | STEWART F CARSE, TEAM LEADER | 9182231101 | TANK FILL VALVE WAS INADVERTENTLY OPENED. TANK WAS OVERFILLED WHILE DELIVERIES WERE BEING MADE INTO ANOTHER TANK. OPERATING PERSONNEL WERE UNAWARE TANK VALVE WAS OPEN. THUS NO ATTEMPT WAS MADE TO MONITOR TANK LEVEL.
2017-09-29 08:50 | NO | NO | 19990162 | 1999-11-16 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 1999-11-03 | 900 | NJ | UNION | LINDEN | NO |  | Null | WALTER STREET AND FEDOR STREET |  | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | GASOLINE | 1 | 4 | 4 | NO | NO | 12 | 0.25 | 5200 | WELDED |  | 0 | 12 | YES | 8 | 1518 | 5 | 1981 | EXTERNAL | Null | YES | OTHER | ISOLATED PITTING UNDER DISBONDED COATING | DAMAGE BY NATURAL FORCES |  | Null |  |  | Null | Null | D'VEDA I C HOLLEY | 2159376241 | A NEIGHBOR REPORTED TO SUN PIPE LINE(SPL) ON 11/3/99 OF GASOLINE ODORS. SPL RESPONDED TO THE SCENE AND NOTICED A SHEEN OF GASOLINE IN A NEARBY MANHOLE. SPL MARKED AND EXCAVATED IN THE AREA TO LOCATE SPL PIPE. THE PIPE WAS EXCAVATED APPROXIMATELY 50 FEET LONG. SPL EMERGENCY RESPONDERS AND SUBCONTRACTORS SEARCHED FOR THE SOURCE OF THE LEAK. THE PRODUCT WAS FOUND TO BE LEAKING, DUE TO CORROSION, FROM THE MEETING POINT OF PIPE COATING. ON NOVEMBER 3, 1999 SPL INSTALLED A PLIDCO SLEEVE TO ENCASE THE LEAKING AREA OF PIPE. DURING THE WEEK OF NOVEMBER 15, 1999, SPL IS TENTATIVELY PERFORMING A LINE REPAIR ON THE CORRODED SECTION OF PIPE.
2017-09-29 08:50 | YES | NO | 19990163 | 1999-11-15 | 31347 | UNOCAL ALASKA RESOURCES | NO | 1999-10-23 | 440 |  |  |  | YES | DILLON PLATFORM, COOK INL | NO | THE LEAK IS APPROX MIDWAY ALONG THE PIPELINE ROUTE BETWEEN PLATFORM DILLON AND ITS SHORE CROSSING NEAR EAST FORELANDS, ABOUT 2 1/2 MILES OFFSHORE IN AK STATE | 503397 | LINE PIPE | PIPE |  | 1966 | OTHER | UNKNOWN AS OF THIS WRITING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 103658.231 | 209120.5212 | CRUDE OIL | 3 | 12 | 4 | NO | NO | 8 | 0.593 | 35000 | WELDED |  | 1480 | 74 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RAND PRICE | 9072835514 | AT APPROXIMATELY 2315 HRS ON OCTOBER 22, 1999, THE DILLON PLATFORM OPERATOR PICKED UP A LOW PRESSURE ALARM ON THE OIL SHIPPING PIPELINE. THE OPERATOR ACKNOWLEDGED THE ALARM AND IT CLEARED. AT 0440 HR ON OCTOBER 23, 1999, THE OPERATOR RECEIVED ANOTHER LOW PRESSURE ALARM ON THE OIL PIPELINE, WHICH WOULD NOT RESET. THE OPERATOR SHUT IN THE PIPELINE. AFTER CONSULTING WITH THE LEAD OPERATOR AND PERFORMING DIAGNOSTICS TO CONFIRM THE LIKELIHOOD OF A PIPELINE LEAK, AN OVERFLIGHT WAS ARRANGED FOR FIRST LIGHT AND UNOCALS FIELD SUPERINTENDENT WAS NOTIFIED AT 0815 HR. AGENCY NOTIFICATION BEGAN AT 0924 WITH A CALL TO THE NRC (REPORT 503397). THE LOCAL SPILL RESPONSE CO-OP, CISPRI, WAS MOBILIZED. 4 VESSELS WERE MOBILIZED FOR CONTAINMENT AND SPILL RECOVERY. UPON VISUAL SIGHTING OF EXTENSIVE OIL SHEEN, A DECISION WAS MAKE TO CHANGE OVER THE PIPELINE TO WATER, TO CONTROL THE SOURCE OF POLLUTION. ISOLATION PIGS WERE PLACED IN THE PIPELINE AND PUMPED TO SHORE WITH FRESH WATER. THE PIGS PASSED BY THE SPILL SITE BY APPROXIMATELY 1800 HRS, ENDING THE RELEASE OF CRUDE OIL. THE WATER WAS THEN DISPLACED WITH NATURAL GAS. NO SHEEN EMANATED FROM THE LEAK SITE DURING THIS CHANGEOVER. A SLIGHT GAS FLOW CONTINUED TO KEEP THE LINE FREE OF WATER, TO PREVENT FREEZE UP AT ITS SHORE CROSSING. ON WATER SPILL RESPONSE AND RECOVERY ACTIVITIES CONTINUED THROUGH SUNSET, 10/24/99. ON MONDAY 10/25/99, OVERFLIGHTS CONFIRMED NO RECOVERABLE OIL REMAINED, AND THE SPILL RESPONSE WAS ENDED BY DECISION OF THE UNIFIED COMMAND. THE PLATFORM IS SHUT IN AT THIS WRITING.
2017-09-29 08:50 | YES | NO | 19990164 | 1999-10-18 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 1999-10-18 | 1140 | LA |  | PLAQUEMINES | NO |  | YES | BAYOU GRAND LAURDS, BETWEEN VENICE AND EMPIRS, LA | 502771 | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 276421.9494 | 557654.7231 | CRUDE OIL | 3 | 100 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | KEITH A GUIBEAU, EMERGENCY RESPONSE SPECIALIST | 2815963562 | AT 11:40 AM, ON 10/18, CHEVRON PIPELINE COMPANYS CUSTOMER SERVICE CENTER (CSC) WAS NOTIFIED. SUBSEQUENTLY, CSC SHUT-IN THE 12" CRUDE OIL PIPELINE FROM BENICE, LA TO EMPIRE, LA WHERE THE 12" CROSSES BAYOU LAURD. USCG, MSO IN NEW ORLEANS WAS IMMEDIATELY NOTIFIED OF THE RELEASE. CHEVRON PIPE LINES EMERGENCY RESPONSE CONTRACTOR, PHILLIP SERVICES WAS IMMEDIATELY DISPATCHED TO BOOM OF THE PIPELINE CANAL, NEARBY MARSH AND INITIATE CLEANUP OPERATIONS. USCG ARRIVED AT THE SPILL SITE AND REPORTED ADDITIONAL POCKETS OF HEAVY OIL. SUBSEQUENTLY, THE VOLUME RELEASE WAS UPGRADED TO 100 BBLS (FROM THE INITIAL 10 BBLS ESTIMATE). ALL STATE AND FEDERAL AGENCIES WERE NOTIFIED. ON 11/4/99, A TOTAL OF 2716 FEET OF 12" LINE WAS REPLACED AND THE PIPELINE SYSTEM WAS PUT BACK ON-LINE OF 11/5/99. ON 11/8, PERMISSION WAS GIVEN BY THE USCG TO REMOVE ALL THE SORBENT BOOM FROM THE WEST BAY LEAK SITE WITH THE EXCEPTION OF OUR PIPELINE CANAL, WHERE CHEVRON PIPE LINE WILL BE JETTING TO REPLACE PIPE NOT ASSOCIATED WITH THIS RELEASE.
2017-09-29 08:50 | YES | NO | 19990165 | 1999-11-19 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 1999-10-19 | 900 | TX | FREESTONE |  | NO |  | NO | THE RELEASE WAS LOCATED AND CONFINED TO CHEVRON PIPE LINE COMPANY'S TANK FARM AT WORTHAM, TX JAMES STRICKLAND SURVEY, A 550-ON THE WEST TEXAS GULF, MP 192.5 |  | TANK FARM | OTHER | 1" NIPPLE | 1988 | OTHER | FRACTURE ON 1" NIPPLE THREADS CONNECTED TO 24" PIP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 1727.6372 | 3485.342 | CRUDE OIL | 3 | 681 | 680 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KEITH A GUILBEAU | 2815963562 | AT 0900 HRS ON 10/19/99, CHEVRON PIPELINE COMPANY OPERATOR NOTICED THAT CRUDE WAS BEING RELEASED FROM 1" NIPPLE CONNECTED TO THE 24" PIPING TO TANK 44. THE TANK GATE VALVE ON TANK 44 WAS IMMEDIATELY CLOSED TO STOP THE LEAD AND ISOLATE THE 24" PIPELINE. ALL FREE STANDING OIL CAS COLLECTED USING A VACUUM TRUCK AND RETURNED TO TANKAGE. THE FRACTURED 1" NIPPLE WAS REMOVED AND PLUGGED. ALL CONTAMINATED SOIL WILL BE REMOVED AND REPLACED WITH FRESH/CLEAN SOIL. THE RELEASED WAS CONFINED TO CHEVRON PROPERTY.
2017-09-29 08:50 | YES | NO | 19990166 | 1999-11-22 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-10-05 | 1530 | TX | HARRIS |  | NO |  | NO | 3/4 WEST OF THE DEER PARK REFINERY |  | LINE PIPE | LONGITUDINAL WELD |  | 1942 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 138210.9747 | 278827.3616 | DIESEL FUEL | 2 | 350 | 40 | NO | NO | 8 | 0.322 | 25000 | WELDED |  | 760 | 760 | YES | 8 | 950 | 0 | 1992 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | GARY L ZIMMERMAN, MANAGER | 7132415334 | THE PIPE RUPTURED ALONG ONE EDGE OF THE LAP WELD, DUE TO FLAWS IN THE WELD, WHERE THE STEEL HAD BEEN OVERHEATED DURING WELDING OPERATIONS, WHICH CAUSED INTERGRANUAL CRACKING. 750 YARDS OF CONTAMINATED SOIL WAS REMOVED FROM THE SITE.
2017-09-29 08:50 | YES | YES | 19990167 | 1999-10-06 | 30918 | KINDER MORGAN GP, INC. | YES | 1999-10-06 | 915 | IA | POLK | DES MOINES | NO |  | NO | 4401 VANDALIA RD, DES MOINES, IA |  | TANK FARM | BOLTED FITTING |  | 1974 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | 0 | LOSS: 0; RECOV: 0; FIRE: YES; EXP: NO; SMYS: 0; DSPRS: 0; ACPRS: 0; PRTST: Null; DUR: 0; MXPRS: 0; TSTMM: 0; TSTYY: 0; FACTD: Null; FACAT: Null; PREVT: Null; EXCAL: Null; TMPMK: Null; PNAME: EDWARD A FANT; PHONE: 7138449526 | THE PROBABLE CAUSE OF THIS RELEASE IS OPERATOR ERROR. DURING A MAINTENANCE PROJECT, AN ELECTRIC IMPACT WRENCH WAS BEING USED TO UNBOLT A FLANGE ON PIPING WITHIN THE STORAGE FIELD. RESIDUAL VAPORS WERE IGNITED BY THE IMPACT WRENCH. A FLASH FIRE ENSUED INJURING ONE EMPLOYEE. HE SUFFERED FIRST AND SECOND DEGREE BURNS ON HIS FACE AND EARS WHICH REQUIRED MEDICAL ATTENTION. THE INJURED EMPLOYEE WAS OFF DUTY 8 WORKING DAYS.
2017-09-29 08:50 | YES | NO | 19990168 | 1999-12-01 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1999-11-02 | 605 | MI |  |  | NO |  | NO | TOWNSHIP: 43N SECTION: 26, QUARTER: SW QUARTER OF THE NW QUARTER, RANGE 33W, TRACT:M2-27A, MERIDIAN:MICHIGAN LON 84/21/53 | 504447 | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 172763.7184 | 348534.202 | NATURAL GAS LIQUID | 1 | 5300 | 2750 | YES | NO | 30 | 0.281 | 52000 | WELDED |  | 748 | 291 | YES | 8 | 939 | 7 | 1992 |  | Null | Null |  |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | Null | Null | LARRY D BREJIN, VICE PRESIDENT OPERATIONS | 2187250102 | LAKEHEAD CONTROL CENTER RECEIVED A CALL FROM GREAT LAKES GAS PERSONNEL MAKING NOTIFICATION OF A VAPOR CLOUD AND POOLED OIL ON THE GROUND APPROXIMATELY 2 MILES WEST OF CRYSTAL FALLS, MICHICAN. COMPANY RESOURCES WERE MOBILIZED AND CALLED TO THE SITE AT MP 1286. THE IRON RIVER STATION ELECTRICAL AND THE IRONWOOD PIPELINE MAINTENANCE (PLM) SUPERVISOR WERE THE FIRST TO ARRIVE ON THE SCENE. UPON ARRIVAL ON THE SCENE, THE PLM SUPERVISOR FOUND THAT LOCAL RESPONDERS, POLICE AND FIRE DEPARTMENT, HAD REROUTED TRAFFIC ON APPROXIMATELY A FOUR MILE STRETCH OF U.S. 2 AND WERE EVACUATING LOCAL RESIDENTS AS A PRECAUTIONARY MEASURE. APPROXIMATELY 500 RESIDENTS WERE INVOLVED DURING THE INITIAL EVACUATION THAT INCLUDED ABOUT 100 NURSING HOME RESIDENTS. THE PLM SUPERVISOR ALSO VERIFIED THAT NGL WAS LEAKING FROM THE LAKEHEAD PIPELINE AND THAT A VAPOR CLOUD HAD FORMED AND SETTLED IN A PEAT BOG ON THE ROW ABOUT 150 FEET UPSTREAM OF THE LEAK. AFTER CONSULTING WITH LOCAL RESPONDERS AND ENSURING THE IMMEDIATE AREA AROUND THE VAPOR CLOUD WAS EVACUATED, THE VAPOR CLOUD WAS INTENTIONALLY IGNITED AT APPROXIMATELY 09:15A.M. CST ON NOVEMBER 2, 1999. THE IGNITED GAS SPREAD BEYOND THE VISIBLE VAPOR CLOUD AREA AND BURNED OVER TO AND UNDERNEATH A HIGH VOLTAGE UTILITY LINE OPERATED BY WISCONSIN ELECTRIC. THE ENSUING FIRE SCORCHED ON UTILITY POLE AND BURNED THROUGH ONE OF PHASE CARRIER CONDUCTORS. THIS RESULTED IN A POWER OUTAGE OF APPROXIMATELY ONE HOUR IN DURATION TO CRYSTAL FALLS AND THE SURROUNDING AREA UNTIL WISCONSIN ELECTRIC WAS ABLE TO REROUTE SERVICE. ONCE POWER WAS REROUTED, THERE APPROXIMATELY SIX RESIDENTS IN THE IMMEDIATE VICINITY THAT WENT WITHOUT POWER UNTIL THE OVERHEAD LINE WAS REPAIRED BY WISCONSIN ELECTRIC ON NOVEMBER 3, 1999 AT APPROXIMATELY 15:30 CST. AFTER THE INITIAL FLARING THE NGL VAPOR CLOUD, ALL RESIDENTS EXCEPT FOR SIX RESIDENTS LOCATED IN CLOSE PROXIMITY TO THE FIRE WERE ALLOWED TO RETURN TO THEIR HOMES. THE RESULTING FIRE WAS MONITORED AND LEFT TO BURN UNTIL IT WAS EXTINGUISHED BY FIREFIGHTERS FROM THE CRYSTAL FALLS FIRE DEPARTMENT ON NOVEMBER 3, 1999 AT 15:00 CST. AT THAT TIME, DIKES WERE IN PLACE TO FORM COLLECTION POOLS FOR THE PRODUCT LEAKING FORM THE PIPE, OF WHICH 2750 BARRELS WERE PICKED UP WITH VACUUM TRUCKS AND HAULED TO THE SUPERIOR TERMINAL BY A TANKER TRUCKS. EXCAVATION BEGAN DURING THE EARLY A.M. HOURS ON NOVEMEBER 4, 1999 AND IT REVEALED THAT THE PIPELINE WAS RESTING ON A ROCK THAT RESULTED IN A FOUR TO FIVE INCH HAIRLINE CRACK TO THE PIPE. A FOUR FOOT PLIDCO SLEEVE WAS INSTALLED AND WELDED INTO PLACE FOR THE REPAIR. AT APPROXIMATELY 00:50 CST, ON NOVEMBER 5, 1999, THE PIPELINE RESUMED NORMAL OPERATION.
2017-09-29 08:50 | YES | NO | 19990169 | 1999-11-26 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 1999-10-31 | 1031 | CA |  | SAN JOAQUIN | NO |  | NO | 25705 W PATTERSON PASS ROAD, TRACY, CA |  | PUMPING STATION | OTHER | FLANGE GASKET | 1990 | OTHER | FLANGE GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69105.4873 | 139413.6808 | CRUDE OIL | 1 | 4917 | 4817 | NO | NO |  |  | 0 | FLANGED |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | GARY L ZIMMERMAN | 7132415334 | FLANGE GASKET FAILED WITHIN A VALVE VAULT AT TRACY STATION.
2017-09-29 08:50 | YES | NO | 19990170 | 1999-11-24 | 9175 | JAYHAWK PIPELINE CORP | YES | 1999-11-01 | 1410 | KS | BARTON |  | NO |  | NO | SW OF NW 1/4 SECTION 2, TOWNSHIP 17 SOUTH, RANGE 13 WEST, BARTON COUNTY, KS | 504391 | NO DATA | OTHER | HOSE ON FRAC TANK | 1999 | OTHER | HOSE BROKE AT FRAC TANK CONNECTIONS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 829.2658 | 1672.9642 | CRUDE OIL | 1 | 52 | 12 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ALLEN R WILKERSON, SUPERINTENDENT OF OPERATIONS | 3162419270 | JAYHAWK PERSONNEL WERE PURGING 6-INCH GATHERING LINE INTO A FRAC TANK, WHEN THE HOSE CONNECTION ON THE FRAC TANK BROKE, SPILLING OIL INTO TANK DYKE. THE AIR COMPRESSOR WAS SHUT DOWN AND VALVE CLOSED. OIL RECOVERED AND REMEDIATION WAS BEGUN THE SAME DAY.
2017-09-29 08:50 | YES | NO | 19990171 | 1999-11-03 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 1999-10-29 | 1135 | MN | WEST POPE |  | NO |  | NO |  |  | LINE PIPE | NO DATA |  | 1946 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 86381.8592 | 174267.101 | DIESEL FUEL | 3 | 200 | 0 | NO | NO | 8 | 0.219 | 0 | WELDED |  | 1150 | 122 | YES | 8 | 1492 | 0 | 1990 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KENNETH L LYBARGER SR | 9185735774 | AT APPROXIMATELY 11:35 A.M. WHILE PLOWING AN ALFAFA FIELD ON THE REFERENCED PROPERTY, AN EMPLOYEE OF A CORPORATE FARM COMPANY STRUCK THE PIPELINE WITH A SUB-SOIL PLOW, CUTTING A HOLE APPROXIMATELY 4 INCHES IN DIAMETER IN THE LINE. THE PIPELINE WAS SHUT-IN AT THE TIME. PERSONNEL IN THE WPL OPERATIONS CONTROL DISPATCH CENTER IN TULSA, OKLAHOMA WERE NOTIFIED OF THE BREACH BY AN ALARM AND AN IMMEDIATE DROP IN PRESSURE ON THE SCADA MONITORING SYSTEM. DISPATCH PERSONNEL IMMEDIATELY NOTIFIED PERSONNEL IN THE ALEXANDRIA PUMP STATION OF THE SUDDEN DROP IN PRESSURE. A MAINLINE VALVE AT WILMAR, MINNESOTA WAS PROMPTLY CLOSED TO ISOLATE THE SECTION OF THE PIPELINE AND SIMULTANEOUSLY MAINTENANCE CREWS WERE MOBILIZED. AT 11:54 A.M. THE MANAGER OF THE FARMING COMPANY FARMING CALLED THE EMERGENCY TELEPHONE NUMBER INTO PIPELINE CONTROL AND REPORTED THAT ONE OF ITS EMPLOYEES HAD PUNCTURED THE PIPELINE. TELEPHONIC NOTIFICATION WAS TIMELY MADE TO THE NATIONAL RESPONSE CENTER, THE MINNESOTA POLLUTION CONTROL AGENCY, THE STATE EMERGENCY RESPONSE OFFICE AND THE LOCAL EMERGENCY PLANNING COMMITTEE IN ACCORDANCE WITH REGULATIONS, AND THE MINNESOTA OFFICE OF PIPELINE SAFETY WAS REMOVED AND HANDLED IN ACCORDANCE WITH INSTRUCTIONS FROM THE MCPA.
2017-09-29 08:50 | YES | NO | 19990172 | 1999-12-09 | 10012 | KANEB PIPELINE CO | YES | 1999-11-05 | 1345 | KS | SALINE |  | NO |  | NO | INTERSECTION OF CRAWFORD STREET AND I-135 IN SALINA, KANSAS. LEGAL DESCRIPTION: SW 1/4, SEC 15, RANGE 3 WEST, TOWNSHIP 14 SOUTH, SALINE COUNTY, KS. | 504863 | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 103658.231 | 209120.5212 | PROPANE | 2 | 1869 | 0 | NO | NO | 10.75 | 0.25 | 42000 | WELDED |  | 1336 | 500 | YES | 24 | 1670 | 0 | 1972 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | L LEROY ANDERSON | 3167739000 | VALLEY TRENCHING WAS PLOWING IN A BUNDLE OF FIBER OPTIC CONDUIT PARALLEL TO I-135 AT A DEPTH OF APPROXIMATELY 42 INCHES. KANEB PIPELINE OPERATING PARNTERSHIP, LPS 10 INCH DIAMETER PIPELINE ALSO PARALLELS I-135 AT THE ACCIDENT SITE. KANEB PIPELINE OPERATING PARNTERSHIP LP PERSONNELS FAILURE TO ACCURATELY MARK THE ROUTE OF ITS PIPELINE AS THE PRIMARY CONTRIBUTING CAUSE TO THIS ACCIDENT. VALLEY TRENCHINGS EQUIPMENT PUNCTURED THE PIPELINE WHICH RESULTED IN THE RELEASE OF PROPANE.
2017-09-29 08:50 | YES | NO | 19990173 | 1999-12-09 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 1999-11-30 | 0 | NM | LEA |  | NO |  | NO | SEC 28, T-20-S, R-37-E |  | PUMPING STATION | PUMP |  | 0 | OTHER | MATERIAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 1500 | 1168 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LENNAH FROST | 9156843467
2017-09-29 08:50 | YES | NO | 19990174 | 1999-12-09 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 1999-11-10 | 933 | TX |  | FORT BEND | NO |  | NO | APPROXIMATELY 3/4 MILE SOUTH OF FM HIGHWAY 2759 OFF OF CATTLE PEN ROAD |  | LINE PIPE | PIPE |  | 1966 | OTHER | CAUSE IS STILL UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | DIESEL FUEL |  | 100 | 60 | NO | NO | 12.75 | 0.203 | 1464 |  |  | 1054 | 1050 | YES | 8 | 1325 | 0 | 1990 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JOHN W CARICO, VICE PRESIDENT | 7138776015 | INCIDENT OCCURRED SHORTLY AFTER A CHANGE OF DELIVERY POINTS. THE UNAFFILIATED RECEIVING LOCATION HAD LEFT A VALVE CLOSED. ACCIDENT IS STILL UNDER INVESTIGATION.
2017-09-29 08:50 | YES | NO | 19990175 | 1999-12-10 | 30918 | KINDER MORGAN GP, INC. | YES | 1999-11-06 | 1015 | IL | GRUNDY |  | NO |  | NO | 4755 EAST ROUTE 6 MORRIS, ILLINOIS 60450 |  | TANK FARM | OTHER | MAINLINE FILTER CASE | 1970 | OTHER | STATIC ELECTRICITY | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 691.0549 | 1394.1368 | OIL AND GASOLINE | 2 | 0 | 0 | NO | YES |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A FANT | 7138449526 | WHILE CHANGING FILTERS IN THE PIPELINE 105 MAINLINE FILTER, DIRT WAS BEING REMOVED FROM THE FILTER CASE BY USE OF A PNEUMATIC VACUUM. APPROXIMATELY 10 MINUTED INTO THE VACUUMING PROCESS, RESIDUAL VAPORS IGNITED AND PRODUCED A FLASH FIRE WITHIN THE FILTER CASE. THE IGNITION SOURCE APPEARS TO BE "STATIC ELECTRICITY" WITHIN THE PLASTIC PVC HOSE ATTACHMENT ON THE PNEUMATIC VACUUM. THE FIRE WAS EXTINGUISHED WITH THE USE OF 30 LB. FIRE EXTINGUISHING UNIT. AN EMPLOYEE SUSTAINED SLIGHT STINGING OF THE EYEBROWS AND MUSTACHED, NO MEDICAL OR FIRST AID TREATMENT WAS REQUIRED. NO OTHER INJURIES OR EQUIPMENT WAS DAMAGED.
2017-09-29 08:50 | NO | NO | 19990176 | 1999-12-15 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 1999-11-15 | 1150 | WI | TAYLOR |  | NO |  | NO | MP 0116.03 TOWNSHIP: PERSHING, SECTION: 18, QUARTER: SE, RANGE: 4W, TRACT# W212-6 & W-212-RX | 505859 | LINE PIPE | PIPE |  | 1968 | OTHER | ORIGINAL CONSTRUCTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 63800 | 44089.3009 | 88945.9283 | OIL AND GASOLINE | 1 | 15 | 14 | NO | NO | 34 | 0.281 | 52000 | WELDED |  | 618 | 320 | YES | 24 | 776 | 11 | 1968 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LARRY DI BURGIN, VP OPERATIONS | 2187250102 | THE APPARENT CAUSE WAS FROM A METAL FATIGUE CRACK ASSOCIATED WITH MECHANICAL DAMAGED. THERE WERE THREE DENTS IN THE PIPE AT THE 12, 10, AND 9 OCLOCK POSITIONS (LOOKING DOWNSTREAM). THE PIPE WOULD HAVE BEEN DAMAGED DURING ORIGINAL CONSTRUCTIONS BECAUSE OF THE LOCATION OF THE DENTS INSIDE THE CASING. TWO LPL EMPLOYEES PERFORMING RIGHT OF WAY MAINTENANCE DUTIES DISCOVERED CRUDE OIL WEEPING FROM A CASING VENT PIPE ON LINE 6A AT MP116, COUNTY HIGHWAY M, THREE MILES DOWN STREAM OF SHELDON STATION. SUPERIOR CONTROL WAS ADVISED AND BOTH LINES 6A AND 14 WERE SHUT DOWN. FIVE GALLONS OF CRUDE WERE ESTIMATED TO BE ON THE GROUND AROUND THE VENT PIPE.
2017-09-29 08:50 | YES | NO | 19990177 | 1999-12-21 | 4906 | EXXON PIPELINE CO | YES | 1999-12-01 | 1110 | LA | WEST BATON ROUGE | BRUSLY | NO |  | NO | 16" CRUDE OIL LINE FROM BELLE ROSE TO ANCHORAGE NEAR EXXON PIPELINE COMPANY'S BLUE WATER ETHANE VALVE SITE | 650297 | LINE PIPE | VALVE |  | 1954 | OTHER | BACKHOE HIT AN OBSCURED VALVE RISER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 4837.3841 | 9758.9577 | CRUDE OIL | 1 | 200 | 180 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J BRECK BACON | 7136562203 | EXXON PIPELINE COMPANY WAS EXCAVATING A SECTION OF THE 16" CRUDE OIL LINE FROM BELLE ROSE TO ANCHORAGE IN PREPARATION TO HYDROTEST THE LINE. THE SPILL OCCURRED WHEN THE BACKHOE EXCAVATING THE LINE INADVERTENTLY HIT AN OBSCURED 2" RISER THAT EXTENDED 2" ABOVE THE LINE IN THE 12 OCLOCK POSITION. THE LINE WAS SHUT IN AND ISOLATED. THE LEAK WAS PRIMARILY CONTAINED IN THE PIPELINE DITCH. A VACUUM TRUCK WAS USED TO RECOVER THE SPILLED CRUDE AND ABSORBENT PADS WERE USED TO CLEANUP TO RESIDUAL OIL. THE LINE WAS TEMPORARILY CLAMPED AND WILL BE PERMANENTLY REPLACED SUBSEQUENT TO THE HYDROTEST. THERE WAS NO HARM TO PERSONNEL OR EQUIPMENT OTHER THAN THE PIPELINE RISER AS A RESULT OF THIS SITUATION.
2017-09-29 08:50 | YES | YES | 19990178 | 1999-12-21 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 1999-11-17 | 1435 | TX | HUDSPETH |  | NO |  | YES | EL PASO TEXAS TO WINK, TEXAS 20" PIPELINE, MILEPOLE 80, BLOCK 67 & 68 TOWNSHIP 3 | 506152 | LINE PIPE | VALVE |  | 0 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 2 | 0 | 2 |  | 0 | 0 | CRUDE OIL | 3 | 10205 | 1301 | YES | YES | 20 |  | 0 | WELDED |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | OTHER | THIRD PARTY PIPELINE CAUGHT FIRE | Null |  |  | Null | Null | KEITH A GUILBEAU, EMERGENCY RESPONSE | 2815963562 | THE BLOCK VALVE AND PIPELINE AT MP 80.3 ON THE CHEVRON PIPE LINE COMPANY 20" EL PASO TO WINK CRUDE OIL LINE WAS ENGULFED IN FIRE, STEMMING FROM THE RUPTURED AND FIRE OF A THIRD PARTY PIPELINE. DURING THE FIRE, THE MAIN LINE BLOCK VALVES WERE CLOSED TO ISOLATE THE AFFECTED SEGMENT AND THE CRUDE OIL WAS ALLOWED TO BURN OFF. AFTER THE FIRE EXTINGUISHED, THE 20" VALVE AND PIPELINE WAS REPAIRED AND PUT BACK INTO OPERATION. ALL CONTAMINATED SOIL WILL BE REMOVED AND REPLACED WITH FRESH/CLEAN SOIL. THE AFFECTED SOIL IS CURRENTLY BEING REMEDIATED ON SITE. NOTE: THE ACTUAL REPORTED LOSS OF PRODUCT OF CRUDE OIL WAS REPORTED AS 10.205 BARRELS, THE TOTAL VOLUME THAT WAS BURNED AND SPILLED. OF THAT QUANTITY, ONLY 50 BARRELS AFFECTED THE SURROUNDING SOIL OF WHICH 48 BARRELS WERE RECOVERED.
2017-09-29 08:50 | YES | YES | 19990179 | 1999-12-21 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1999-10-28 | 1120 | OK | KAY | PONCA CITY | NO |  | NO | INCIDENT OCCURRED WITHIN CONOCO'S PONCA CITY COMPLEX LOCATED AT 1000 SOUTH PINE STREET, PONCA CITY, OK |  | TANK FARM | TANK |  | 1992 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 2 | 2 | 0 | 2000000 | 1382109.7469 | 2788273.6156 | OIL AND GASOLINE | 3 | 0 | 0 | YES | YES |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | VANCE WEBB | 5807674845 | AT APPROXIMATELY 11:20 HRS ON 10-28-99 AN IGNITION INVOLVING TANK 118 LOCATED AT CONOCOS PONCA CITY REFINERY RESULTED IN THE INJURY OF TWO CONOCO EMPLOYEES. TANK 118 IS A 250,000 BBL INSULATED TANK THAT WAS BEING USED FOR GAS-OIL STORAGE INCIDENTAL TO SCHEDULED REFINERY MAINTENANCE. THE TWO INJURED INDIVIDUALS WERE ENGAGED IN THE PROCESS OF REMOVING INSULATION NEAR THE TOP OF THE TANK IN PREPARATION FOR AN INSPECTION. THE SOURCE OF THE IGNITION IS UNKNOWN AT THIS TIME. HOWEVER, A ROOT CAUSE FAILURE ANALYSIS (RCFA) IS BEING CONDUCTED IN COOPERATION WITH OSHA. THE RESULTS OF THIS INVESTIGATION WILL BE MADE AVAILABLE TO THE OFFICE OF PIPELINE SAFETY UPON COMPLETION. WITH REGARD TO THE STATUS OF THE TANK, THE FIRE WAS EXTINGUISHED AT APPROXIMATELY 1600 HRS ON 10-28-99 USING FOAM SUPPRESSION. THE REMAINING GAS-OIL AND WATER IN THE TANK, APPROXIMATELY 4 FEET, WAS TRANSFERRED INTO ANOTHER TANK, NO PRODUCT WAS RELEASED FROM CONTAINMENT DURING INCIDENT. AT THE ONSET OF THE FIRE CONOCO IMPLEMENTED ITS EMERGENCY ACTION PLAN AND MADE THE REQUIRED NOTIFICATION TO THE NRC. THE NOTIFICATION WAS MADE BY JIM METZGER OF CONCO INC TO PETTY OFFICER FLETCHER OF THE NRC AND ASSIGNED AN INCIDENT # 503958. IMPLEMENTATION OF THE EMERGENCY ACTION PLAN INVOLVES ACTIVATING CONOCOS INCIDENT COMMAND SYSTEM (ICS). ADDITIONALLY, AND AS REQUIRED BY THE PLAN, THE EMERGENCY OPERATIONS CENTER (EOC) WAS OPENED AND A UNIFIED COMMAND WAS ESTABLISHED WITH THE EPAS FEDERAL ON SCENE COMMANDER AND OSHA. THE EOC WAS OPERATED THROUGHOUT THE DURATION OF THE INCIDENT.
2017-09-29 08:50 | YES | YES | 19990180 | 1999-12-16 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 1999-11-17 | 1535 | TX | HUDSPETH |  | NO |  | NO | SEGMENT OF PIPELINE THAT PARALLELS HIGHWAY 62/180, 1/4 MILE FROM THE CITY OF SALT FLAT POST OFFICE, 20 MILES SOUTH OF DELL CITY. |  | LINE PIPE | LONGITUDINAL WELD |  | 1952 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 2 | 0 | 2 | 217000 | 149958.9075 | 302527.6873 | PROPANE | 2 | 6195 | 0 | YES | YES | 8.625 | 0.25 | 42000 | WELDED |  | 1308 | 1050 | YES | 8 | 1635 | 2 | 1997 | EXTERNAL | Null | YES | OTHER | SELECTIVE SEAM CORROSION |  |  | Null |  |  | Null | Null | CHRIS MASON | 7132153022 | RIO GRANDE PIPELINE COMPANYS 8" PROPANE PIPELINE RUPTURED AT ABOUT 100FT DOWNSTREAM OF THE MAINLINE VALVE NEAR MILEPOST 148. THE SEGMENT OF PIPELINE INVOLVED WAS LOCATED PARALLEL TO HWY 62/180. DIRECTLY AFTER THE RUPTURE A VAPOR CLOUD ENSUED AND DRIFTED ACROSS THE HIGHWAY. THE VAPOR CLOUD WAS SOMEHOW IGNITED CAUSING AN EXPLOSION. A TRACTOR TRAILER TRUCK THAT WAS ON THE HIGHWAY WAS CAUGHT IN THE ENSUING FIRE. THE DRIVER OF THE TRUCK, ALONG WITH THE DRIVER OF ANOTHER TRUCK FOLLOWING BEHIND WAS INJURED AND AIR LIFTED TO A HOSPITAL FOR TREATMENT.
2017-09-29 08:50 | YES | NO | 19990181 | 1999-12-15 | 30829 | TEPPCO | NO | 1999-11-15 | 400 | TX | WHARTON |  | NO |  | NO | APPROXIMATELY 1 MILE EAST OF EL CAMP ON HWY 59 | 505868 | LINE PIPE | PIPE |  | 1988 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | NATURAL GAS LIQUID | 2 | 650 | 0 | NO | NO | 3.5 | 0.125 | 42000 |  |  | 1440 | 1065 | YES | 8 | 1852 | 11 | 1988 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | FRED CLAKLEY, EH&S MANAGER | 4052395716 | OPERATOR RESPONDED TO THE "ONE CALL" AND MARKED PIPELINE WITH THE PRESENCE OF THE EXCAVATOR. AS THE EXCAVATOR APPROACHED PIPELINE R.O.W., HE PULLED UP HIS RIPPER. HE THEN DROVE OVER THE R.O.W. AND SET HIS RIPPER DOWN ON THE OTHER SIDE OF R.O.W. THE EXCAVATOR PLOWED FOR A FEW FEET AND THEN PLOWED THROUGH THE PIPELINE AT 4:00 P.M. THE OPERATOR WASNT AWARE THE PIPELINE TURNED PARELLEL WITH THE HIGHWAY, AND THEN TURNING AGAIN HEADING TOWARDS THE NORTH. THE LOCAL OFFICIALS WERE NOTIFIED AND BOTH LANES OF HIGHWAY 59 WERE SHUTDOWN. THE PIPELINE WAS SHUT DOWN, VALVES CLOSED, AND REMAINING PRODUCT BLOWN DOWN. ON 11-118-99 PERMANENT REPAIRS WERE MADE BY INSTALLING PRETESTED PIPE, AND PIPELINE WAS RETURNED TO SERVICE.
2017-09-29 08:50 | YES | NO | 19990182 | 1999-12-13 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 1999-11-09 | 318 | MN | LYON |  | NO |  | NO | SEE ATTACHED PLAT |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 138210.9747 | 278827.3616 | DIESEL FUEL | 3 | 300 | 260 | NO | NO | 8 | 0.203 | 0 | WELDED |  | 1150 | 1021 | YES | 8 | 1492 | 0 | 1990 | EXTERNAL | Null | YES | OTHER | PENDING METALLURGICAL ANALYSIS |  |  | Null |  |  | Null | Null | KENNETH L LYBARGER | 9185735774 | AT APPROXIMATELY 03:18 A.M. THE SCADA SYSTEM IN THE OPERATIONS CONTROL CENTER PIPELINE COMPANY INDICATED A RAPID INCREASE IN THE FLOW RATE ACCOMPANIED BY A RAPID DECREASE IN THE DISCHARGE PRESSURE AT THE MARSHALL PUMP STATION ON THE #1-8 PIPELINE BETWEEN SIOUX FALLS, SD AND ALEXANDRIA, MINNESOTA. OPERATIONS CONTROL CONFIRMED THE PRESSURE DROP AND ALERTED FIELD PERSONNEL WHO BEGAN CHECKING THE LINE FOR INDICATIONS OF A LEAK. MAINLINE BLOCK VALVES WERE CLOSED TO ISOLATE THE LINE, AND PERSONNEL SIMULTANEOUSLY DROVE, WALKED AND FLEW PORTIONS OF THE LINE UNTIL THE RELEASE WAS FOUND. EMERGENCY TELEPHONIC NOTICE WAS TIMELY MADE TO THE NATIONAL RESPONSE CENTER, THE MINNESOTA POLLUTION CONTROL AGENCY AND THE LOCAL EMERGENCY PLANNING COMMITTEE IN ACCORDANCE WITH REGULATIONS. THE LINE WAS TIMELY REPAIRED IN COMPLIANCE WITH REGULATIONS AND RESTORED TO SERVICE. FREE STANDING AND MIXED PRODUCT WAS RECOVERED FROM THE GROUND, AND CONTAMINATED SOIL IS BEING STOCK PILED ON SITE UNTIL SPRING PER MCPA INSTRUCTIONS, WHEN IT WILL BE COMPLETELY REHABILITATED IN ACCORDANCE WITH MCPA INSTRUCTIONS. THE SPECIMEN OF PIPE CONTAINING THE BREACH WAS SENT TO A METALLURGY FIRM FOR A THOROUGH ANALYSIS.
2017-09-29 08:50 | YES | NO | 19990183 | 1999-12-21 | 4906 | EXXON PIPELINE CO | YES | 1999-11-13 | 2030 | TX | GRIMES | NAVASOTA | NO |  | NO | NAVASOTA REFINED PRODUCTS STATION-100 YARDS TO THE EAST OF HIGHWAY 6 | 505702 | PUMPING STATION | PUMP |  | 1940 | OTHER | SEE PART K | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 2764.2195 | 5576.5472 | GASOLINE | 3 | 125 | 15 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RAMONA PULLIN | 7136562232 | A FLUID CUT ON THE INTERNAL SIDE OF THE PUMP SEAL FLUSH TUBING CAUSED THE TUBING TO BREAK AND THE PRODUCT TO BE RELEASED. SOME PRODUCT ESCAPED THE FIREWALL ONTO THE ADJACENT TRINITY INDUSTRIES PROPERTY. A BERM WAS CONSTRUCTED TO CONTAIN THE RELEASE AND THE PRODUCT WAS RECOVERED WITH A VACUUM TRUCK. THE TUBING HAS BEEN PERMANENTLY REPLACED.
2017-09-29 08:50 | NO | NO | 19990184 | 1999-12-13 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1999-10-20 | 1530 |  |  |  | YES | 0.5 MILES W OF GRAND ISLE | NO | 0.5 MILES W OF GRAND ISLE STATE PARK IN BAYOU FIFI, GRAND ISLE, LA. IN STATE WATERS. SW CORNER OF T21S R25E, JEFFERSON PARISH. |  | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 44918.5668 | 90618.8925 | CRUDE OIL | 3 | 0 | 0 | NO | NO | 8 | 0.375 | 42000 | WELDED |  | 800 | 250 | YES | 8 | 1010 | 8 | 1993 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | JAMES J JONES, DIRECTOR | 3374974813 | AT APPROXIMATELY 15:30 ON 10/20/99, EXXON PIPELINE CO CALLED AND REPORTED THAT A SHEEN WAS APPEARING NEAR WHERE CONOCO PIPE LINE CO., BP OIL PIPELINE AND EXXON PIPELINE CO ALL CROSS, JUST OFF-SHORE FIFI ISLAND, LA. AFTER INVESTIGATION BY PERSONNEL OF ALL 3 OPERATORS, IT WAS DETERMINED THAT THE SHEEN WAS ORIGINATING FROM THE CONOCO PIPE LINE CO. GRAND ISLE TO GOLDEN MEADOW CRUDE OIL PIPELINE. SORBENT BOOM WAS DEPLOYED TO CONTAIN THE SHEEN AND PRESSURE WAS REMOVED FROM THE PIPELINE TO CONTROL FURTHER LEAKAGE. THE PIPELINE WAS SHUTDOWN UNDER APPROXIMATELY 250 PSI AT THE TIME THE LEAK WAS DETECTED. THE LINE WAS JETTED OUT AND DIVERS SENT DOWN TO INVESTIGATE DURING THE DAY ON 10/21/99 AND 10/22/99. THE DAMAGED SECTION OF PIPE WAS LOCATED AND A PLIDCO SPILT SLEEVE INSTALLED ON 10/23/99 AS A PERMANENT REPAIR. DAMAGE WAS DETERMINED TO HAVE BEEN CAUSED BY A DRAG LINE BUCKET, OPERARTED BY A CONTRACTOR FOR THE CITY OF GRAND ISLE, LA WHILE IN THE PROCESS OF CONSTRUCTING A NEW PORTABLE WATER LINE JUST OFF SHORE IN BAYOU FIFI.
2017-09-29 08:50 | NO | NO | 19990185 | 1999-12-30 | 2552 | COLONIAL PIPELINE CO | YES | 1999-12-01 | 1400 | TN | DAVIDSON | NASHVILLE | NO |  | NO | ON BRUCE HARDWOOD COMPANY PROPERY ADJACENT TO COLONIAL PIPELINE CO, NASHVILLE DELIVERY FACILITY AT 1455 FIFTY FIRST AVE, NASHVILLE, TN 37209 |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | DIESEL FUEL | 1 | 3 | 3 | NO | NO | 8 | 0.277 | 42000 | WELDED |  | 450 | 90 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | PITTING |  |  | Null |  |  | Null | Null | STEPHEN E GILLIAM, REGULATORY ADMINSTRATOR | 4048412314 | AT APPROXIMATELY 1400 HRS ON 12/01/99 THE COLONIAL PIPELINE CONTROL CENTER IN ATLANTA, GA RECEIVED A TELEPHONE CALL FROM A BRUCE HARDWOOD COMPANY EMPLOYEE THAT HE HAD SPOTTED PRODUCT ON THE GROUND ON THEIR PROPERTY. THEIR PROPERTY IS LOCATED ADJACENT TO THE WILLIAMS (OLD AMOCO) TERMINAL, WHICH IS ADJACENT TO COLONIAL PIPELINE COMPANY IN NASHVILLE, TN DELIVERY FACILITY. THE CONTROL CENTER FOLLOWED PROCEDURES AND SHUT DOWN LINE 19 AND 20 GOING INTO NASHVILLE AND NOTIFIED THE NASHVILLE D. F. OPERATORS. AFTER FURTHER INVESTIGATION THE SOURCE OF THE LEAK WAS DETERMINED TO BE COLONIALS 8" DELIVERY LINE TO MOTIVA. THERE WAS NO DELIVERY BEING MADE TO MOTIVA AT THE TIME OF THE ACCIDENT. REPAIR CREWS WERE BROUGHT IN AND REPAIR SLEEVE WAS INSTALLED AND THE LINE WAS RETURNED TO SERVICE ON 12/3/99.
2017-09-29 08:50 | NO | NO | 19990186 | 1999-12-30 | 2552 | COLONIAL PIPELINE CO | YES | 1999-12-02 | 2007 | NC | GUILFORD | GREENSBORO | NO |  | NO | COLONIAL PIPELINE COMPANY TANK FARM @ 411 GALLIMORE DAIRY RD, GREENSBORO 27419 | 507621 | TANK FARM | OTHER | STRINGER SYSTEM | 1979 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | FUEL OIL | 1 | 12 | 9 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | STRINGER SYSTEM |  |  | Null |  |  | Null | Null | STEPHEN E GILLIAM | 4048412314 | AT APPROXIMATELY 2007 ON 12/2/99, DURING A ROUTINE STATION CHECK A GREENSBORO JUNCTION EMPLOYEE DISCOVERED PRODUCT ON THE GROUND AT THE OIL MANIFOLD. CONTRACTORS BEGAN SOIL EXCAVATION TO EXPOSE A 6" DRAIN LINE FOR THE STRINGER SYSTEM GOING TO TANK 899. AFTER EXPOSING THE DRAIN LINE A TEMPORARY CLAMP WAS INSTALLED. SOIL EXCAVATION AND SITE ASSESSMENT ARE CONTINUING.
2017-09-29 08:50 | YES | NO | 20000002 | 2000-02-01 | 31147 | DYNEGY MIDSTREAM SERVICES INC | YES | 2000-01-14 | 100 | LA |  | PLAQUEMINES | NO |  | NO | INSIDE VENICE TERMINAL |  | LINE PIPE | PIPE |  | 1967 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7614 | 5155.1275 | 10399.9745 | DATA NOT SPECIFIED | 2 | 277 | 0 | NO | NO | 6 | 0.432 | 42000 | FLANGED |  | 1440 | 1100 | YES | 10 | 2450 | 12 | 1991 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC |  |  | Null |  |  | Null | Null | JIMMY OXFORD | 5045344050 | COATING FAILURE AT GROUND LEVEL PERMITTED CORROSION TO THIS PIPE TO 0.080 INCH THICK OVER 4 INCH LONG REGION. THINNED REGION BLEW OUT AND LEAKED. SPOOL PIECE REPLACED WITH NEW PIPE, ELL AND FLANGES.
2017-09-29 08:50 | YES | NO | 20000003 | 2000-01-11 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 1999-12-05 | 1230 | TN | DYER | NEWBERN | NO |  | NO | TENNESSE HWY 77 @ MP 443 |  | LINE PIPE | PIPE |  | 1967 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1665000 | 1150606.3643 | 2321237.785 | CRUDE OIL | 2 | 90 | 85 | NO | NO | 40 | 0.312 | 52000 | WELDED |  | 585 | 582 | YES | 24 | 965 | 0 | 1968 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF, SR ENGINEER | 7132414381 | APPROXIMATELY 129 FEET OF 8.5" OF 40" X 0.312 PIPE WAS REMOVED FROM THE CASED CROSSING OF TENNESSEE HWY 77. THE FAILURE WAS DUE TO A LONGITUDINAL CRACK APPROXIMATELY 3" LONG, LOCATED IN A SURFACE GROVE. THE FAILED PIPE WAS REPLACED WITH 40 X 0.406 APIL 5LX52 DSAW PIPE.
2017-09-29 08:50 | YES | NO | 20000005 | 2000-01-13 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 1999-12-18 | 1800 | TX | CRANE |  | NO |  | NO | CHEVRON PIPELINE COMPANY'S CORDONA LAKE GATHERING STATION SECTION 27, BLOCK 2 H & T RRCO |  | TANK FARM | TANK |  | 1982 | OTHER | MALFUNCTION OF THE TANK GAUGE SYSTEM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 51000 | 35243.7985 | 71100.9772 | CRUDE OIL | 1 | 500 | 480 | NO | NO |  | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KEITH A GUILBEAU | 2815963562 | THIRD PARTY PERSONNEL (CITATION) NOTIFIED CHEVRON PIPE LINE COMPANY THAT THE TANK LOCATED AT THE CHEVRON CORDONA LAKE STATION WAS RUNNING OVER. CHEVRON PIPE LINE MADE IMMEDIATE NOTIFICATIONS TO STOP THE DELIVERY OF CRUDE OIL INTO THE TANK. CHEVRON PIPE LINES CUSTOMER SERVICE CENTER IN HOUSTON WAS ALSO IMMEDIATELY NOTIFIED TO BEGIN PUMPING OPERATIONS (FROM THE TANK) TO START LOWERING THE LEVEL OF CRUDE OIL IN THE TANK. CHEVRON PIPE LINE PERSONNEL ON LOCATION BEGIN CLEAN UP ASSESSMENTS, WHICH INCLUDED CONTACTING EMERGENCY RESPONSE CONTRACTORS TO BEGIN REMOVING FREE STANDING OIL. OF THE ESTIMATED 500 BARRELS OF CRUDE OIL RELEASED, 480 BARRELS OF FREE STANDING OIL WAS RECOVERED AND RECYCLED. THE CRUDE OIL RELEASED WAS CONTAINED WITHIN THE TANK BERM AREA AND CONFINED TO CHEVRON PIPE LINE COMPANY PROPERTY. THE TEXAS RAILROAD COMMISSION (ALEX RAMIREZ 463-6788), AS WELL AS THE TEXAS NATURAL RESOURCES AND CONSERVATION COMMISSION (LANCE BOWERS 915-579-1359) WERE NOTIFIED. THE TEXAS RAILROAD COMMISSION SENT A TEAM TO THE SPILL SITE TO ASSESS THE RESPONSE AND CLEAN UP OPERATIONS. SITE REMEDIATION (ON-SITE) IS ONGOING.
2017-09-29 08:50 | YES | NO | 20000006 | 2000-01-21 | 31045 | GENESIS CRUDE OIL LP | YES | 1999-12-20 | 1045 | MS | JONES |  | NO |  | NO | LAT 31 47.1 NORTH LONG 89 22.9 WEST APPROXIMATELY 3 MILES NORTHEAST OF THE COMMUNITY OF HOT COFFEE, MS | 509534 | LINE PIPE | PIPE |  | 1968 | OTHER | CORROSION, INTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 1730 | 1750 | NO | NO | 8 | 0.188 | 25000 | WELDED |  | 460 | 350 | YES | 8 | 575 | 0 | 1968 | INTERNAL | Null | YES | OTHER | TO BE DETERMINED BY LAB TEST |  |  | Null |  |  | Null | Null | BARRY S DAVIS | 7138602750 | LEAK WAS REPORTED BY THE PUBLIC TO THE LOCAL SHERIFF, WHO REPORTED IT TO GENESIS. LINE WAS IMMEDIATELY SHUTDOWN AND EMERGENCY RESPONSE BEGAN.
2017-09-29 08:50 | YES | NO | 20000007 | 2000-01-27 | 30918 | KINDER MORGAN GP, INC. | YES | 1999-12-28 | 2120 | IA | JOHNSON |  | NO |  | NO | WEST LUCAS TOWNSHIP, JOHNSON COUNTY, IA |  | PUMPING STATION | VALVE |  | 1976 | OTHER | FAILURE OF THE PUMP SUCTION AND DISCHARGE VALVES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 691.0549 | 1394.1368 | BUTANE | 2 | 13 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A FANT | 7138449526 | THE PROBABLE CAUSE OF THIS RELEASE IS A SEAL LEAK WITH INCOMPLETE SEALING OF THE PUMP SUCTION AND DISCHARGE VALVES. THE SEAL LEAK DECTECTOR DETECTED A LEAKING SEAL AND ACTIVATED THE STATION SHUTDOWN PROCESS, WHICH INCLUDED THE SHUTDOWN OF THE PUMP AND THE CLOSING OF BOTH THE PUMP SUCTION AND DISCHARGE VALVES. HOWEVER, BOTH VALVES DID NOT SEAT, ALLOWING INTO THE PUMP SEALS AND THE SUBSEQUENT RELEASE OF BUTANE INTO THE ATMOSPHERE. THE BUTANE WAS ALLOWED TO PASSIVELY DISSIPATE.
2017-09-29 08:50 | YES | NO | 20000008 | 2000-01-24 | 2325 | CHEVRON USA INC | YES | 2000-01-08 | 824 |  |  |  | YES | LAT 29 04' 24" LONG 90 09 | Null | 10" OIL LINE FROM GRAND ISLE 37 "R" TO FOURCHON TERMINAL, SEGMENT 3584 - 1/4 MILE EAST OF WELL GUARD #57 IN BAY MARCHAND BLOCK 2, STATE LEASE 1366 |  | LINE PIPE | PIPE |  | 1960 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | CRUDE OIL | 1 | 6 | 6 | NO | NO | 10 | 0.594 | 1711 | WELDED |  | 720 | 60 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER |  |  |  | Null |  |  | Null | Null | T RYDER BOOTH | 5045926249 | 12 BARRELS RECOVERED WITH OIL & WATER EMULSION.
2017-09-29 08:50 | YES | NO | 20000009 | 2000-01-27 | 15674 | PLANTATION PIPE LINE CO | YES | 2000-01-10 | 1640 | VA | FAIRFAX | NEWINGTON | NO |  | NO | DRAWING ATTACHED | 516620 | LINE PIPE | OTHER | DYE RECEIVING UNIT LOCATED NEXT TO INCOMING BLOCK | 2000 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 700000 | 473941.3281 | 956131.0912 | GASOLINE | 3 | 100 | 20 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JACQUE WILLIAMS JR | 7707514095 | AT APPROXIMATELY 4:30 PM EST, MONDAY, JANUARY 10, 2000, A PETROLEUM RELEASE FROM PLANTATIONS 12-INCH PIPELINE WAS DISCOVERED APPROXIMATELY 600 FEET FROM THE COMPANYS NEWINGTON, VA PIPELINE TERMINAL. A PIPELINE INSTRUMENT (DYE RECEIVING UNIT) WAS THE SOURCE OF THE RELEASE. THE INSTRUMENT IS USED BY PLANTATION TO DETECT AND TO MAINTAIN THE SEGREGATION OF OUR CUSTOMERS PRODUCTS. THE PETROLEUM RELEASE (A MIXTURE OF GASOLINE AND COMMERICAL JET FUEL) ENTERED A STORM WATER CULVERT NEAR THE RELEASE SITE ALONG TERMINAL ROAD AND FLOWED TO A STORM WATER RETENTION POND AT THE END OF TERMINAL ROAD. THE PETROLEUM THEN FLOWED INTO A WETLANDS AREA NEAR THE RETENTION POND. THIS FORM 7000-1 SUPERSEDES TWO FORMS PREVIOUSLY SUBMITTED FOR THIS INCIDENT ON 1/25/00 AND 7/18/00. THE CAUSE OF ACCIDENT WAS CHANGED TO "INCORRECT OPERATION BY OPERATOR PERSONNEL." AS AN INVESTIGATION REVEALED THAT THE RELEASE RESULTED FROM IMPROPER MAINTENANCE BEING PERFORMED ON THE DYE RECEIVING UNIT.
2017-09-29 08:50 | YES | NO | 20000010 | 2000-01-31 | 30991 | MOBIL OIL CORPORATION | YES | 1999-12-25 | 1117 | TX | HOWARD |  | NO |  | NO | MP 47.4 - HOWARD COUNTY, TEXAS 5 MILES SOUTH OF INTERSTATE 20 ON THE EAST SIDE OF BIG SPRING, TX |  | LINE PIPE | GIRTH |  | 1928 | OTHER | ACETYLENE WELD CRACKED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 69105.4873 | 139413.6808 | CRUDE OIL | 3 | 400 | 35 | NO | NO | 8 | 0.322 | 35000 | WELDED |  | 720 | 300 | YES | 8 | 900 | 12 | 1996 |  | Null | YES |  |  |  |  | Null |  |  | Null | Null | S S SOBEY, MGR | 2146585914 | AN ACETYLENE WELD CRACKED CAUSING THE SPILL. LINE WAS CONSTRUCTED IN 1928 WITH THIS TYPE OF WELD. MOBIL PIPE LINE COMPANYS OPERATIONS CONTROL CENTER IN DALLAS SHUT DOWN THE PIPELINE SYSTEM IMMEDIATELY AND DISPATCHED EMERGENCY CREWS TO THE SITE. REPAIRS CLEANUP PROCEDURES INITIATED. PERMANENT REPAIRS MADE BY INSTALLING WELD + END. SOIL WILL BE BLENDED WITH CLEAN SOIL TO LESS THAN 1%.
2017-09-29 08:50 | YES | YES | 20000011 | 2000-01-31 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 1999-09-16 | 1305 | PA | TIOGA |  | NO |  | YES | 0.31 MILES SOUTH OF GAINES STATION OFF HANKY PANKY RD | 498953 | LINE PIPE | PIPE |  | 1964 | OTHER | SYSTEM TAKEN OUT OF SERVICE FOR A RELOCATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | 0 | PROPANE | 2 | 1 | 0 | YES | NO | 8.625 | 0.203 | 42000 | WELDED |  | 1125 | 0 | YES | 24 | 1910 | 0 | 1986 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES E MIKA | 7137593755 | DURING THE REPLACEMENT OF A SECTION OF AN 8" LINE IN TIOGA COUNTY, PA, A FLASH FIRE OCCURRED IN A TIE-IN BALLHOLE. WHEN THE WELDER ATTEMPTED TO LIGHT HIS CUTTING TORCH TO TRIM THE EXISTING PIPE FOR THE TIE-IN WELD, VAPOR IN THE PIPE IGNITED. THE FIRE WAS EXTINGUISHED BY COMPANY PERSONNEL STANDING FIRE WATCH OVER THE TIE-IN SITE WITHIN 15 SECONDS. THE FLASH FIRE RESULTED IN FIRE RESULTED IN FIRST AND SECOND DEGREE BURNS TO THE WRISTS AND FACE OF THE WELDER.
2017-09-29 08:50 | YES | NO | 20000012 | 2000-02-03 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 1999-12-28 | 1210 | CO | ADAMS |  | NO |  | NO | T3S, R67W, SEC 18, DIRECTLY EAST OF THE VASQUEZ BLVD CROSSING |  | LINE PIPE | GIRTH |  | 1954 | FAILED WELD | SUBSIDENCE | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 76016.0361 | 153355.0489 | JET FUEL | 1 | 500 | 0 | NO | NO | 8.625 | 0.219 | 35000 | WELDED |  | 720 | 200 | YES | 8 | 510 | 9 | 1986 |  | Null | Null |  |  | SUBSIDENCE |  | Null |  |  | Null | Null | RANDY W BEGGS | 3036494090 | THE 8 INCH PORTION OF THE DENVER JET FUEL DELIVERY LINE RELEASED APPROXIMATELY 500 BARRELS OF COMMERICAL JET FUEL WHEN THE WELD LOCATED DIRECTLY EAST OF THE VASQUEZ BLVD BRIDGE SPLIT AT THE BOTTOM OF THE GIRTH WELD. THE WELD OCCURRED DURING THE DELIVERY OF AN 18000 BARREL BATCH OF JET FUEL TO CHASE TERMINAL AT APPROXIMATELY 12:10 (MOUNTAIN STANDARD) DEC. 28, 1999. THE FAILED WELD WAS FORCED APART ON THE BOTTOM SIDE OF THE PIPE, POSSIBLY DUE TO EROSION (FROM THE BRIDGE DRAIN) AND/OR IMPROPER COMPACTION UPON BACKFILL OF THE 2-INCH GAS PIPELINE PARALLELING THE JET LINE. THE SMALL LEAK FROM THE WELD SLOWLY WASHED THE SANDY SOIL AWAY FOR THE BOTTOM OF THE PIPE UNTIL THERE WAS A LARGE VOID FROM THE PRODUCT VELOCITY TO INITIATE THE WELD RUPTURE. REMEDIATION OF THE SITE CONTINUES WITH REMOVAL OF CONTAMINATED IMPACT SOIL AS PER EPA AND STATE ENVIRONMENTAL AGENCIES.
2017-09-29 08:50 | YES | NO | 20000013 | 2000-01-18 | 9175 | JAYHAWK PIPELINE CORP | YES | 1999-12-22 | 1145 | KS | HASKELL |  | NO |  | NO | SE OF SW 1/4, SECTION 21, TOWNSHIP 28 SOUTH, RANGE 34 WEST, HASKELL COUNTY, KS | 515155 | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10365.8231 | 20912.0521 | CRUDE OIL | 1 | 1058 | 570 | NO | NO | 4 | 0.156 | 35000 | WELDED |  | 600 | 170 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | MICROBIOLOGICAL INFLUENCED CORROSION |  |  | Null |  |  | Null | Null | ALLEN R WILKERSON | 3162419270 | ON WEDNESDAY MORNING, DECEMBER 22, 1999, JAYHAWKS AREA GAUGER FOUND THE FIELD METER SHORT FROM THE DAY BEFORE FIELD RUNS. JAYHAWK PERSONNEL BEGAN DRIVING AND WALKING IN PIPELINE AND FOUND THE LEAK. A GAS PIPELINE HAD BEEN LAID UNDER THE JAYHAWK LINE SOMETIME IN THE PAST FEW YEARS, AND COATING HAD BEEN DAMAGED TO JAYHAWKS LINE. AT THIS SAME POINT, JAYHAWK HAD SOME EXTERNAL CORROSION, BUT INTERAL WAS THE CAUSE OF LEAK. JAYHAWK RECOVERED ALL THAT WAS POSSIBLE, AND SOIL REMEDIATION IS BEING DONE WITH THE REST OF THE AREA. JAYHAWK REPLACED THE 4" GATHERING LINE WITH NEW PIPE IN THE DAMAGED AREA AND TOOK EXTRA PRECAUTIONS FOR CORROSION DUE TO THE GAS LINE NOT BEING PROTECTED.
2017-09-29 08:50 | YES | NO | 20000014 | 2000-02-11 | 30825 | CITGO PETROLEUM CORPORATION (REFINERY) | NO | 1999-12-07 | 30 | LA |  | SULPHUR | NO |  | YES | LEAK OCCURRED IN PIPELINE ROAD CROSSING TRENCH ON LOUISIANA HIGHWAY 108 WEST; CROSSING IS LOCATED 0.4 MI EAST OF THE MAIN ENTRACE TO THE CITCON REFINERY PLANT. |  | LINE PIPE | PIPE |  | 1949 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 17276.3718 | 34853.4202 | CRUDE OIL | 3 | 100 | 100 | NO | NO | 10 | 0.49 | 24000 | WELDED |  | 250 | 200 | NO | 0 | 0 | 12 | 1999 | EXTERNAL | Null | NO | OTHER | LEAK IN STEAM TRACING CAUSED MOISTURE & EXTERNAL |  |  | Null |  |  | Null | Null | TOM FARRARO | 3377088424 | A LEAK OCCURRED IN THE PIPELINE CROSSING UNDER HIGHWAY 108 BETWEEN THE CITGO REFINERY AND THE CITCON REFINERY. THE LEAK WAS DISCOVERED DURING NORMAL OPERATOR GROUND PATROL OF THE LINE. THE LEAK WAS CONTAINED WITHIN A CONCRETE CULVERT WHICH PASSED UNDER THE ROAD. OIL WAS FOUND RUNNING OUT OF THE NORTH END OF THE CULVERT BY THE OPERATOR. INITIAL OBSERVATION THE VOLUME OF THE LEAK WAS ESTIMATED AT 10 BBLS, HOWEVER AFTER ALL CLEAN UP WAS COMPLETED A VOLUME OF APPROXIMATELY 100 BBLS WAS DETERMINED TO BE THE TOTAL VOLUME OF THE RELEASE. THE SECTION OF THE PIPELINE TO BE THE TOTAL VOLUME OF THE RELEASE. THE SECTION OF THE PIPELINE WHICH LEAKED WAS COMPLETELY REPLACED AND THE NEW SECTION WAS HYDROTESTED AND RETURNED TO SERVICE. THE LEAK WAS FOUND TO BE CAUSED BY EXTERNAL CORROSION DUE TO MOISTURE FROM LEAKING STEAM TRACING LINE LOCATED NEAR THE PIPELINE.
2017-09-29 08:50 | YES | NO | 20000015 | 2000-02-16 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | NO | 2000-02-14 | 1445 | ID |  | BOISE | NO |  | NO | CHEVRON PIPELINE CO, BOISE STATION, 201 NORTH PHILLIPPI, BOISE, ID (TANK 14 AREA) 8 T-3 N R 2 E |  | TANK FARM | BOLTED FITTING |  | 1992 | OTHER | BLIND FLANGE ON 6" PIPING LOOSE AND NOT FITTED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 20311.7712 | 40977.0468 | GASOLINE | 2 | 160 | 0 | NO | NO | 6 | 0.25 | 1900 | FLANGED |  | 0 | 0 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KEITH GUILBEAU, EMERGENCY RESPONSE SPECIALIST | 2815963562 | BOISE STATION, FLANGE ON 6" PIPE, TANK 14 - UNLEADED GASOLINE. AN ESTIMATED 6,720 GALLONS (160 BBLS) GASOLINE LEAKED OUT OF A DEAD LEG LINE AND LOOSELY BOLTED FLANGE. WATER IN LINE FROZE AT THE VALVE, CAUSING A BLOCKAGE. AFTER THAWING, THE WATER & PRODUCT WAS RELEASED AND LEAKED INTO THE GROUND. NO PRODUCT WAS RECOVERED. BLIND FLANGE WAS LOOSE AND NOT FITTED UP TO THE VALVE. AGENCIES CONTACTED: STATE OF IDAHO AND DEQ ON 1/14/00 @ 15:56 (REPORT #2000-158). PHONE NUMBER 800-632-8000. AGENCY NOTIFICATION COMMENTS: CONFERENCE CALL WITH DEQ, HAZMAT AND BOISE RESPONSE TEAM (FIRE DEPT) DEQ AND BOISE FIRE DEPT TO COME TO SPILL AREA TO WORK WITH CHEVRON PIPELINE.
2017-09-29 08:50 | YES | NO | 20000016 | 1999-12-23 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 1999-11-24 | 310 | LA | JEFFERSON | FOUR BAYOU | NO | LAT 29 19.775 LON 89 51.5 | NO | 20" FOURCHON TERMINAL TO EMPIRE TERMINAL CRUDE PIPELINE QUATRE BAYOU PASS, NORTHEAST OF GRAND TERRE BARRIER ISLAND MILEPOST 25.21 | 506763 | LINE PIPE | PIPE |  | 1963 | FAILED PIPE | OTHER | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 3200000 | 2211375.5951 | 4461237.785 | CRUDE OIL | 3 | 850 | 190 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 780 | 110 | YES | 24 | 1170 | 3 | 1963 |  | Null | Null |  |  | OTHER | CPL IS STILL PURSUING 3RD PARTY OUTSIDE FORCE | Null |  |  | Null | Null | KEITH A GUILBEAU | 2815963562 | AT 0310 HOURS ON 11/24/99, CHEVRON PIPE LINE COMPANY, CUSTOMER SERVICE CENTER IN HOUSTON, TX RECEIVED A PRESSURE IMBALANCE ALARM ON THE 20" FOURCHON, LA TO EMPIRE, LA PIPELINE SYSTEM. THE PIPELINE SYSTEM WAS IMMEDIATELY SHUT DOWN AND ARRANGEMENTS WERE MADE TO PULL SUCTION OF BOTH ENDS OF THE PIPELINE. A THIRD PARTY SPILL RESPONSE TEAM WAS IMMEDIATELY CONTRACTED TO BEGIN OIL SPILL CLEAN UP. A UNIFIED COMMAN, INCLUDING CHEVRON, STATE AND FEDERAL (USCG) INCIDENT COMMANDERS WAS SET UP A CHEVRONS GRAVIER STREET, NEW ORLEANS, LA COMMAND POST. THE UNIFIED COMMAND WAS INVOLVED IN ALL PHASES OF THE RESPONSE. FREE OIL ON WATER WAS SKIMMED AND CLEANUP PLANS TO ALL AFFECTED BEACHES WERE SUBMITTED AND APPROVED BY INTERESTED AGENCIES PRIOR TO AND UPON COMPLETION OF RESPONSE AND CLEANUP OPERATIONS. PIPELINE REPAIR PLANS WERE DEVELOPED AND APPROVED BY THE JOINT UNIFIED COMMAND. THE PIPELINE HAS SINCE BEEN REPAIRED AND THE SYSTEM PUT BACK INTO SERVICE. AIR SURVELLIANCE OF THE SPILL IMPACT AREA IS ONGOING ON A REGULAR SCHEDULED BASIS. THE INVESTIGATION TEAM PERFORMED A "WHY TREE ANALYSIS" TO INVESTIGATE THE ROOT CAUSES OF THE INCIDENT. THE ANALYSIS WAS DIVIDED INTO THREE COMPONENTS. EXTERNAL FORCES, INTERNAL FORCES AND MATERIAL DEFECTS. INTERNAL FORCES AND MATERIAL DEFECTS DID NOT LEAD US TO ROOT CAUSES. ALL THE ROOT CAUSES CAME FROM EXTERNAL FORCES. THE TEAM DETERMINED THAT THE ACCIDENT WAS CAUSED BY EXCESSIVE STRESS CREATED BY WATER CURRENT PASSING OVER THE SPANNING PIPE. THE PIPE WAS SPANNING BECAUSE OUR INSPECTION CYCLE FREQUENCY WAS TOO LONG FOR THIS SPECIFIC LOCATION. HIGHER THAN NORMAL TIDAL CURRENTS IN THIS AREA CAUSED LINE-LONG SPANNING PROBLEMS FASTER THAN NORMAL. ANOTHER EXTERNAL FORCE THAT CONCERNED THE TEAM IS THIRD PARTY DAMAGE. WE COULD NOT CONTINUE THE INVESTIGATION ON THIS CAUSE DUE TO LACK OF DATA FROM A CALIPER SMART PIG INSPECTION. TEPCOS CREWS AND CONTRACTORS WORKING IN THE VICINITY OF OUR PIPELINE DURING THE TIME OF THE INCIDENT IS A VERY COINCIDENTAL CIRCUMSTANCE THAT NEEDS DATA DRIVEN INVESTIGATION. ADDITIONAL DATA WILL NEED TO BE GATHERED TO DETERMINE IF THIRD PARTY DAMAGE WAS THE CAUSE OF THE INCIDENT.
2017-09-29 08:50 | YES | NO | 20000017 | 2000-02-22 | 31189 | BP AMOCO | NO | 2000-01-18 | 825 | TX | BRAZORIA | ALVIN | NO |  | NO | 2 MILES SOUTH OF INTERSECTION OF FM 1297 AND FM 2004, INSIDE FENCE AT PERIMETER OF BP AMOCO CHEMICAL PLANT, CENTRAL METER YARD | 517290 | LINE PIPE | OTHER | SCRAPER TRAP, DOOR SEAL | 1999 | OTHER | SCRAPER TRAP DOOR SEAL FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | L. P. G. | 2 | 139 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | GERALD J LAUER | 8154786122 | AN APPARENT FAILURE OF SCRAPER TRAP DOOR SEAL ON A 12 INCH ETHYLENE PIPELINE SYSTEM RESULTED IN THE RELEASE OF APPROXIMATELY 139 BARRELS OF ETHYLENE PRODUCT TO ATMOSPHERE ON JANUARY 18, 2000 AT BP AMOCO PIPELINE FACILITES LOCATED INSIDE PLANT FENCELINE AT PERIMETER OF AMOCO CHOCOLATE BAYOU CHEMICAL PLANT IN BRAZORIA COUNTY, TX. SCRAPER TRAP WAS TEMPORARY INSTALLATION TO LAUNCH AN INTERNAL INSPECTION TOOL. INTERNAL INSPECTION TOLL WAS LOADED AND LAUNCHED 18 JANUARY 2000. FAILURE OF SCRAPER TRAP DOOR SEAL OCCURRED SHORTLY AFTER INSPECTION TOOL WAS LAUNCED. ETHYLENE PRODUCT ESCAPED TO ATMOSPHERE FROM FAILED SEAL AREA AROUND SCRAPER TRAP DOOR. EMERGENCY CREWS ISOLATED AREA AND PIPELINE SYSTEM WAS SHUTDOWN AND ISOLATED. RELEASE ENDED AS SYSTEM BLOCK VALVES WERE SAFETY CLOSED.
2017-09-29 08:50 | YES | NO | 20000018 | 2000-02-22 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-01-21 | 1000 |  |  |  | YES | LAT 28'6.3, LONG 90'47.6 | NO | 1.5-2 MILES NORTH OF SHIP SHOAL 332 | 517462 | LINE PIPE | PIPE |  | 1997 | OUTSIDE FORCE DAMAGE | SHIP ANCHOR | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | 0 | 0 | 0 | 0 | 0 | 0 | 16420948 | 11117951.291 | 22429398.4711 | CRUDE OIL | 1 | 2240 | 0 | NO | NO | 24 | 0.562 | 65000 | WELDED |  | 1950 | 550 | YES | 8 | 2440 | 0 | 1996 |  | Null | Null |  |  | SHIP ANCHOR |  | Null |  |  | Null | Null | G.L. ZIMMERMAN (MANAGER) | 7132414381 | AN ANCHOR FROM THE TRANSOCEAN 96 SEMISUBMERSILE DRILLING RIG STRUCK THE POSEIDON PIPELINE CAUSING THE RELEASE. THE PIPELINE AND NEARBY PLATFORM AUTOMATICALLY CEASED OPERATION. ALL APPLICABLE NOTIFICATIONS WERE MADE. FIVE OIL SPILL RESPONSE VESSELS WERE ACTIVATED, EITHER ON LOCATION OR NEAR STANDBY. TWO AERIAL APPLICATIONS OF DISPERSANTS WERE MADE ON 1/21/00 AND TWO ADDITIONAL APPLICATIONS WERE MADE ON 1/22/00. THE APPLICATIONS WERE VERY SUCCESSFUL. OTHER RESOURCES DEPLOYED INCLUDE SURVEILLANCE AIRCRAFT AND DEEP WATER DIVE SUPPORT VESSELS.
2017-09-29 08:50 | YES | NO | 20000019 | 2000-02-22 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-01-22 | 1201 | LA | PLAQUEMINES |  | NO |  | NO | CHEVRON PIPE LINE CO. (OPERATOR) GRAND BAY- 10 PIPELINE (CYPRESS PIPELINE CO. OWNER) APPRX 1,500 FT BEHIND OSTRICA TERMINAL, EMPIRE, LOUISIANA | 517555 | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 81247.0848 | 163908.1871 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 10 | 0.365 | 0 | WELDED |  | 720 | 10 | YES | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | IMPRESSED |  |  | Null |  |  | Null | Null | J.R.BURKE (DOT SPECIALIST) | 2815963569 | GRAND BAY-10 PIPELINE (CYPRESS P/L CO) WEST BAY SYSTEM- CRUDE ; A SHEEN NOTICED ON ADJACENT WATERWAY AND LATER DETERMINED TO BE ON THE 10" GRAND BAY PIPELINE. 20 GALLONS OF CRUDE OIL RELEASED INTO THE ENVIRONMENT (MUDDY SHORELINE DURING LOW TIDE AND LEACHED TO SURFACE WATER). THIS WAS REPORTED AS A SPILL TO WATER TO THE USCG & NRC ALTHOUGH THE PRIMARY RECEIVING MEDIUM WAS LAND. AGENCIES CONTACTED: NATIONAL RESPONSE CENTER ON 1/22/00 AT 13:44 (REPORT #517555). PHONE NUMBER (800)424-8802, PO CHANCELLOR. OTHER AGENCY NOTIFICATIONS :LA STATE AND POLICE AND LA DEQ/ KEVIN SCOTT/2259256599/INCIDENT #0367/ CALLED IN AT 14:08; PLAQUEMINES LEPC/ GLADYS ENCALADE/504-682-1446/INCIDENT#2000-22 CALLED IN AT 14:19
2017-09-29 08:50 | YES | NO | 20000020 | 2000-02-22 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-01-21 | 1100 | UT | BOX ELDER | CORRINE | NO |  | YES | CHEVRON PIPE LINE CO. (SALT LAKE TEAM) 8" PRODUCTS SYSTEM, OIL LINE #1 MILE POST 68 T-10-N, R-4 & R-5 S-18 (ON THE OLD RAILROAD GRADE) | 517493 | LINE PIPE | PIPE |  | 1949 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 101558.856 | 204885.2338 | DIESEL FUEL | 1 | 35 | 0 | NO | NO | 8.625 | 0.25 | 45000 | WELDED |  | 1870 | 1725 | YES | 8 | 2340 | 8 | 1987 |  | Null | YES |  |  |  |  | Null |  |  | Null | Null | GARY M SAENEZ (DOT SPECIALIST) | 2815963568 | PRODUCTS SYSTEM 8"OIL LINE #1 MILE POST 68- DIESEL; THIRD PARTY (RANCHER) SMELLED DIESEL FUEL FUMES. HE INVESTIGATED AND AREA WHERE DIESEL FUEL WAS ON THE WATER IN MARSHY AREA. THIRD PARTY CONTACTED CSC USING ONE OF OUR NUMBERS OFF THE SIGN. CSC CONTACTED SALT LAKE STATION OPERATOR WHO IMMEDIATELY SHUT DOWN BOTH LINES. LEAK WAS APPROX. 35 BARRELS ON THE WATER, WITH APPROX 1 BARREL OF PRODUCT RECOVERED. AGENCIES CONTACTED: NATIONAL RESPONSE CENTER ON 1/21/00 AT 16:15 (REPORT# NOT DISCLOSED). PHONE NUMBER (800) 4248802, LT JOHNSON
2017-09-29 08:50 | YES | NO | 20000021 | 2000-02-28 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2000-01-27 | 1212 | KY |  |  | NO |  | NO | APPROXIMATELY 2 MILES SOUTH OF THE TOWN WINCHESTER KENTUCKY. SECTION 13 RANGE 64 CARTER COORDINATES CLARK COUNTY | 517991 | LINE PIPE | PIPE |  | 1973 | OTHER | CORROSION FATIGUE IN DENT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15800000 | 10697532.8342 | 21581244.6299 | CRUDE OIL | 1 | 11644 | 9640 | NO | NO | 24 | 0.25 | 52000 | WELDED |  | 780 | 606 | YES | 24 | 1003 | 11 | 1973 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A SCHELL (P.E REGULATORY COMPLIANCE COORDINATOR) | 4194213201 | ON JAN 27, 2000 THE MAPL OWENSBORO TO CATLETTSBURG 24 CRUDE OIL PIPELINE RELEASED AN ESTIMATED 11644 BARRELS OF PETROLEUM CRUDE OIL APPROXIMATELY 2 MILES SOUTH OF TOWN WINCHESTER KY, NEAR THE FIFTH HOLE OF THE SOUTHBOND COURSE. THE RELEASED OIL IS TRAVELED APPROXIMATELY 1.5 MILES OF GOV. AGENCIES NOTIFICATIONS WERE MADE AS REQUIRED. A CLARK COUNTY ROAD CREW AT THE REQUEST OF THE CLARK COUNTY FD USED CONSTRUCTION EQUIPMENT TO ERECT A CONTAINMENT DAM ON TWO MILE CREEK WHICH UNSUCCESSFULLY STOPPED FURTHER OIL TRAVEL. MAPL EMERGENCY RESPONSE CONTRACTORS SUBSEQUENTLY INITIATED OPERATIONS TO INSTALL ADDITTIONAL CONTAINMENT DAMS AND TO RECOVER RELEASED OIL. RECOVERED OIL WAS TRUCKED TO THE MAP CATLETTSBURG REFINERY. AS OF FEB 5, 2000, AN ESTIMATED 8000 BBLS OF OIL HAVE BEEN RECOVERED FROM THE CREEK AND TRIBUTARY. RECOVERY AND REMEDIATION ACTIVITIES CONTINUE UNDER THE OVERSIGHT OF KENTUCKY DEP. THE FAILED SECTION WAS REPLACED WITH PRE TESTED PIPING. THE SYSTEM WAS RESTARTED WITH OPS AND KY-PSC CONCURRENCE AT A REDUCE OPERATING PRESSSURE ON JAN.29. AT APPROXIMATELY 2000 HRS CST. THE CAUSE OF THE PIPE FAILURE IS UNKNOWN AT THIS TIME. THE NTSB HAS TAKEN POSSESSION OF THE FAILED SECTION OF PIPE FOR LABORATORY EVALUATION. LABORATORY ANALYSIS CONDUCTED BY THE NTSB SUGGESTS THAT THE CAUSE OF THE FAILURE WAS CORROSION FATIGUE IN A DENT. PROPERTY DAMAGE REVISED 3-14-2003
2017-09-29 08:50 | NO | NO | 20000022 | 2000-02-28 | 14194 | OILTANKING OF TEXAS PIPELINE CO | NO | 2000-01-28 | 730 | TX | HARRIS |  | NO |  | NO | SOUTH OF RR TRACK AT THE INTERSECTION OF JACINTOPORT BLVD AND APELT DRIVE 1000 FT EAST OF BELTWAY 8, PORT OF HOUSTON AUTHORITY RR FEE STRIP. | 518038 | LINE PIPE | WELDING FITTING |  | 1978 | OTHER | SPLIT IN FITTING SEAM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3385.2952 | 6829.5078 | CRUDE OIL | 1 | 5 | 4 | NO | NO | 24 | 0.281 | 820 | WELDED |  | 530 | 210 | YES | 12 | 738 | 3 | 1998 |  | Null | YES | OTHER | IMPRESSED |  |  | Null | ONE CALL |  | Null | Null | GIL CHARTIER, ENGINEER | 2814577973 | 1-28-00, 7:30 RECEIVED REPORT FROM AIR PATROL OF OIL IN STORM WATER DITCH NEAR CHANNELVIEW FACILITY. 0740 DETERMINE IT MAY BE CRUDE OIL, SHUT DOWN PIPELINE BLOCKED IN CLOSET VALVES. 0825 NOTIFICATION SENT OUT, RRC, EPA, TNRCC ETC. 0830 ONE CALL SENT OUT, TERMINAL EQUIPMENT ARRIVE CONFIRMATION #285175. 0910 EMERGENCY RESPONSE, (CLEAN UP & TRACK HOE ARRIVED). 0915 SUBCONTRACTOR FOR EXCAVATION NOTIFIED. 0920 SUBCONTRACTOR ARRIVED WITH 790 HOE AND 7 MEN CREW. 0955 FIRST ROLL OFF BOXES ARRIVED. 1015 START EXCAVATION, CONTAINING CONTAMINATED SOIL. 19000 TEMPORARY CLAMP PUT ON LEAK WHILE OUR LINE IS STILL DOWN. 1-29-00 0800 SETUP STOFFEL LINE AND REPLACED SECTION 0900 START EXCAVATION 1600 SPLIT TEE ARRIVED, WELDED HORIZIONTALS, TEMPORARY PATCH PUT ON THE SPLIT. 2-7-00 PUT MINIMUM FLOW ON LINE TO WELD OUT SPLIT TEES NOT LEAKS, HOLE WATCH WHILE PUMPING.0900 RECEIVED MATERIAL FOR REPAIR (1) 3 DIAMETER 45 25 OF 375 WT GR.B PIPE WELD OUT AND SETUP TO TEST 820 PSI. 2-8-00 SETTING UP UNIVERSAL TESTING IN HYDRO 4 HOUR TEST AT ENERPIPE YARD. WELDERS QUALIFIED. 0830 SETTING UP T.D. WILLIAMS CUTTER AND CUT IN TWO (2) STOFFEL TEES. 2-9-00 0700 START STOFFEL PLUGS. 0900 START VAC TRUCK EST. 83 BARRELS. 1430 COLD CUT DAMAGE SECTION, INSTALL MUD PLUGS 2 BACK 1600 START HOT WORK. 2030 X-RAY TIE INS. 2250 GAVE OPERATIONS BACK LINE REDUCED FLOW RATE. 2-10-00 0730 VAC TRUCK ARRIVED PULLING AND SETTING STOFFEL CAP PLUGS. 0900 BREAKING DOWN T.D. WILLIAMS EQUIPMENT. 1500 BLINDS ON STOFFEL TEES GAVE OPERATION OK TO GO TO FULL RATES. CLEANING UP AREA DOPE AND WRAP PIPE. 2-11-00 - CLEAN UP
2017-09-29 08:50 | YES | NO | 20000023 | 2000-02-29 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-02-03 | 1020 | TX | NAVARRO |  | NO |  | NO | WEST TEXAS GULF 26" CRUDE OIL PIPELINE RIGHT OF WAY AT MILEPORT 219.01 1.5 MILES EAST OF FM 744 WILLIE SPARKS SURVEY# A-738 NAVARRO COUNTY TEXAS | 519045 | LINE PIPE | BOLTED FITTING |  | 1962 | OTHER | SUBSIDENCE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 231000 | 156400.6383 | 315523.2601 | CRUDE OIL | 1 | 4000 | 40 | NO | NO | 26 | 0.312 | 46000 | FLANGED |  | 750 | 675 | NO | 0 | 0 | 10 | 1997 |  | Null | YES |  |  | SUBSIDENCE |  | Null |  |  | Null | Null | RANDY BURKE (DOT SPECIALIST) | 2815963569 | SLOW UNDERGROUND LEAK FOUND AT A BURIED FLANGE ON A MAINLINE BLOCK VALVE ON WTG 26" CRUDE OIL LINE. TO ISOLATE THE LEAK, THE 26" GATE VALVE AT MP 219.01 WAS CLOSED AND THE SYSTEM WAS DRAINED TO WORTHAM STATION TANKAGE. ALL FREE STANDING OIL WAS RECOVERED APPROX 400 BARRELS USING VACUUM TRUCKS AND RETURNED TO STATION TANKAGE. THE 26 BOLTS AND GASKET WERE REPLACED AND THE SYSTEM RETURNED TO SERVICE. IMMEDIATE ACTION WAS TAKEN TO DELINEATE THE SPILL SITE, BOTH HORIZONTALLY AND VERTICALLY TO A CONDITION LESS THAN 1% THC. VOLUME RELEASED WAS 1150 BARRELS BASED ON SAMPLE ANALYSIS. APPROXIMATE QUANTITY RECOVERED WAS 40 BARRELS. TO DATE A TOTAL OF 7,000 CUBIC YARDS OF SOIL THAT WAS PURCHASED FROM THE ADJOINING PROPERTY. AGENCY NOTIFICATIONS: TEXAS RAILROAD COMMISSION ON 02/03/00. CONTACT BOB OLDHAM. OTHER AGENCY NOTIFICATIONS: NRC ON 02/07/00. CONTACT:MR GARNEAU 800-424-8802. OTHER AGENCY NOTIFICATIONS: TNRCC ON 02/07/00. CONTACT CHUCK KNOWLAN AT 512-463-7727 AND MR JEFFERSON AT 817-469-6750. 2/8/02 AFTER EXTENSIVE SITE ASSESSMENT CPL REVISED TOTAL BARRELS RELEASED FROM ORIGINAL NUMBER OF 1,150 TO AN ESTIMATED RANGE OF 3000 TO 4000 BARRELS.
2017-09-29 08:50 | YES | NO | 20000024 | 2000-03-08 | 1248 | BELLE FOURCHE PIPELINE CO | NO | 2000-02-18 | 1630 | WY | CAMPBELL |  | NO |  | NO | S/2 SECTION 36 T47N-R74W, CAMPBELL COUNTY, WY |  | LINE PIPE | PIPE |  | 1997 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13541.1808 | 27318.0312 | DIESEL FUEL | 3 | 400 | 300 | NO | NO | 4 | 0.156 | 42000 | WELDED |  | 1120 | 100 | YES | 8 | 1400 | 0 | 1997 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | ROBERT STAMP | 3072660361 | EMPLOYEE WORKING FOR A PIPELINE CONTRACTOR WAS EXCAVATING WITH A TRACKHOE. HIT THE BFPL 4" PRODUCT LINE, PULLING IT OUT OF THE GROUND. CONTRACTOR WAS INSTALLING A GAS GATHERING PIPELINE AT THE TIME. ALL RELEASED PRODUCT WAS CONTAINED IN THE OPEN EXCAVATION.
2017-09-29 08:50 | YES | NO | 20000025 | 2000-03-06 | 22610 | WILLIAMS PIPE LINE COMPANY | NO | 2000-02-02 | 750 | KS |  | KANSAS CITY | NO |  | NO | WILLIAMS PIPELINE COMPANY KANSAS CITY TERMINAL LOCATED AT 401 EAST DONOVAN ROAD, KANSAS CITY, KS |  | TANK FARM | OTHER | PUMP SEAL | 1990 | OTHER | BEARING FAILED ON VERTICAL PRODUCT PUMP CAUSING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 16926.476 | 34147.539 | JET FUEL | 3 | 350 | 350 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KENNETH L LYBARGER | 9185735774 | AT APPROXIMATELY 0750 A CONTRACTOR EMPLOYEE OBSERVED PRODUCT COMING FROM THE PUMP SEAL ON THE PRODUCT PUMP ON TANK #1243. THE LINE FEEDING INTO THE TANK WAS IMMEDIATELY STOPPED AND THE PUMP ISOLATED THE MINIMIZE THE AMONT OF PRODUCT LOST. VACUUM TRUCKS WERE USED TO COLLECT PRODUCT FROM THE DIKED CONTAINMENT AREA SURROUNDING THE TANK. THE REMAINING PRODUCT WAS RECOVERED BY SOIL EXCAVATION AND WILL BE LAND FARMED ON THE TERMINAL PROPERTY UNDER THE APPROVAL OF THE KANSAS DEPARTMENT OF HEALTH OF ENVIRONMENT. SUBSEQUENT INVESTIGATION REVEALED THE UPPER BEARING OF THE PUMP HAD EXCESSIVE WEAR CAUSING THE PUMP SHAFT TO WOBBLE, WHICH IN TURN, CAUSED EXCESSIVE WEAR IN THE PUMP CASE WEAR RING AND ULTIMATELY RESULTING IN SEAL FAILURE PERMITTING PRODUCT TO BE RELEASED. TERMINAL MANAGEMENT AND ENGINEERING SUPPORT INITIATED A REVIEW TO DETERMINE AN APPROPRIATE PERMANENT SOLUTION, INCLUCING A REVIEW OF THE PUMP AND PUMP MOTOR.
2017-09-29 08:50 | NO | NO | 20000026 | 2000-02-22 | 30918 | KINDER MORGAN GP, INC. | YES | 2000-01-22 | 1015 | IL | GRUNDY |  | NO |  | NO | 4755 EAST RT 6 MORRIS, ILLINOIS, 60450 | 517558 | TANK FARM | PIPE |  | 1975 | OTHER | SUB ZERO TEMPERATURE FROZE WATER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 40623.5424 | 81954.0935 | L. P. G. | 3 | 0 | 0 | NO | NO | 0 | 0 | 0 | WELDED |  | 0 | 40 | YES | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A FANT | 7138449526 | IT APPEARS THAT THE PIPE WAS OVERSTRESSED DUE TO THE FORMATION OF ICE IN WATER THAT WAS TRAPPED IN A 6 INCH BYPASS LINE AROUND THE FREE WATER KNOCKOUT VESSEL IN OUR ETHANE CAVERN DEHYDRATION SYSTEM. MORRIS EXPERIENCED SUB-ZERO TEMPERATURE FOR SEVERAL DAYS PRIOR TO THE RELEASE.
2017-09-29 08:50 | YES | NO | 20000027 | 2000-03-07 | 1845 | BUCKEYE PIPELINE CO LP | YES | 2000-01-10 | 1410 | CT | NEW HAVEN |  | NO |  | NO | SEE DRAWING | 516601 | LINE PIPE | PIPE |  | 1961 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1040000 | 704141.4017 | 1420537.6212 | KEROSENE | 3 | 20 | 20 | NO | NO | 12 | 0.219 | 1790 | WELDED |  | 275 | 40 | YES | 24 | 402 | 0 | 1978 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | CARL A OSTACH | 6107704495 | ON MONDAY, JANUARY 10,2000, A LOSS OF PRESSURE WAS OBSERVED WHILE CONDUCTING A ROUTINE PRESSURE CHECK ON A SHUTDOWN SHIPPER LINE. AFTER FURTHER INVESTIGATION BY BUCKEYE PERSONNEL, A SMALL CORROSION PIT WAS DISCOVERED. THIS SECTION OF THE PIPELINE WAS CUT OUT AND REPLACED. ALL APPLICABLE REGULATORY AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITES WERE PERFORMED UNDER THE SUPERVISION OF THE CONNECTICUT DEPARTMENT OF ENVIRONMENTAL PROTECTION AND US COAST GUARD.
2017-09-29 08:50 | YES | NO | 20000028 | 2000-03-09 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | NO | 2000-02-05 | 1415 | PA | PHILADELPHIA |  | NO |  | YES | JOHN HEINZ NATIONAL WILDLIFE REFUGE 84TH STREET AND LINDBURGH AVE PHILADELPHIA, PA | 518875 | LINE PIPE | PIPE |  | 1950 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 4200000 | 2843647.9686 | 5736786.5472 | CRUDE OIL | 1 | 4571 | 4100 | NO | NO | 24 | 0.375 | 0 |  |  | 285 | 60 | YES | 8 | 365 | 0 | 1989 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | THOMAS A CRAWFORD | 2159773350 | A HIKER REPORTED A STRONG PETROLEUM ODOR COMING FROM THE POND AREA. THE SUNOCO REFINERY PERSONNEL WERE ALERTED AND DISPATCHED A TEAM TO ASSESS THE SITUATION. CRUDE OIL WAS DISCOVERED ON THE GROUND NEAR THE PIPELINE MARKERS. THE REFINERY PERSONNEL NOTIFIED THE SUN PIPE LINE PERSONNEL OF THE LEAK WHO RESPONDED TO THE SCENE. FIVE LINES ARE PRESENT IN THIS PARTICULAR AREA. ALL WERE SHUT DOWN. EXCAVATING EQUIPMENT WAS CALLED IN THE UNCOVER THE LINES TO DETERMINE THE SOURCE OF THE LEAK. VACUUM TRUCKS WERE ON SCENE TO BEGIN RECOVERY OPERATIONS. THE 24-INCH "NORTH SHIP" LINE WAS DETERMINED TO BE LEAKING. A FULL SCALE INCIDENT COMMAND ACTIVATION WAS INITIATED TO RESPOND TO THIS INCIDENT.
2017-09-29 08:50 | YES | NO | 20000029 | 2000-03-08 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 2000-02-07 | 431 | MN | CLEARWATER |  | NO |  | NO | STATION: AT MILEPOST 0920.6 TOWNSHIP: 148N SECTION 24 QUARTER SE RANGE 36, TRACT T-661/662, MERIDIAN:W OF 5TH E OF 6TH |  | LINE PIPE | WELDING FITTING |  | 1994 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 192000 | 129995.3357 | 262253.0993 | CRUDE OIL | 1 | 25 | 10 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LAWRENCE DE BRIYN | 2187250102 | THE DOWNSTREAM FILLET WELD ON AN EXSISTING 34 STOPPLE FITTING FAILED RELEASING CRUDE OIL ONTO THE GROUND. THE STOPPLE TEE HAS BEEN CUT OUT REPLACED WITH LINE PIPE AND HAS BEEN SENT TO METALLURGICAL LAB FOR ANALYSIS.
2017-09-29 08:50 | YES | NO | 20000030 | 2000-03-15 | 1248 | BELLE FOURCHE PIPELINE CO | NO | 2000-03-03 | 900 | WY | JOHNSON |  | NO |  | NO | SECTION 36-T43N-R78W JOHNSON COUNTY WYOMING |  | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 20311.7712 | 40977.0468 | DIESEL FUEL | 2 | 100 | 0 | NO | NO | 6 | 188 | 42000 |  |  | 1120 | 350 | YES | 8 | 1400 | 0 | 1997 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | ROBERT STAMP | 3072660361 | LEAK WAS RESULT OF EXTERNAL CORROSION IN AREA WHERE THE COATING (TAPE) HAD SKIDDED OVER A 1 WIDE SECTION. LEAK OCCURED IN A SMALL CORRSION PIT. THIS SECTION OF PIPELINE WAS INSTALED IN 1963.
2017-09-29 08:50 | YES | NO | 20000031 | 2000-03-20 | 18718 | SUN PIPE LINE CO | NO | 2000-03-01 | 900 | TX | KING |  | NO |  | NO | SECTION 2 BLOCK 2 G C + S F R R CO 5 MILES NORTH OF STATE HIGHWAY 82/114 ON SUN PIPE LINE RIGHT OF WAY. |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 338.5295 | 682.9508 | CRUDE OIL | 1 | 450 | 400 | NO | NO | 10 | 0.365 | 25000 | WELDED |  | 800 | 480 | YES | 8 | 1000 | 0 | 1976 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | EDITH F COEN | 9185866942 | LEAK WAS CAUSED BY EXTERNAL CORROSION. LEAK WAS DETECTED BY SCADA OPERATORS.
2017-09-29 08:50 | YES | NO | 20000032 | 2000-03-22 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2000-02-02 | 1015 | TX | JEFFERSON |  | NO |  | NO | 50 FT WEST OF HWY 366 - THOMAS MCKINNEY A-41, TEXACO INC PROPERTY | 518524 | LINE PIPE | NO DATA |  | 1952 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 50779.428 | 102442.6169 | CRUDE OIL | 1 | 18 | 18 | NO | NO | 22 | 0.312 | 52000 | WELDED |  | 736 | 125 | YES | 9 | 920 | 2 | 1998 | INTERNAL | Null | YES | OTHER | NO FLOW |  |  | Null |  |  | Null | Null | G E MERRITT | 7132410351 | EMPLOYEE MAKING INSPECTION ROUNDS DISCOVERED RELEASE. PIPELINE WAS SHUTDOWN AND BLOCK VALVES CLOSED. CLEANUP AND REPAIRS COMMENCED AFTER RELEASE AREA WAS SECURED. RELEASE WAS LOCATED ON A SECTION OF DEAD-LEG OR NO-FLOW PIPING. REPAIRS WERE MADE BY REMOVING DEAD-LEG PIPING.
2017-09-29 08:50 | YES | NO | 20000033 | 2000-03-22 | 10012 | KANEB PIPELINE CO | YES | 2000-02-24 | 1628 | NE | YORK |  | NO |  | NO | NW 1/4, SECTION 10, RANGE 2 WEST, TOWNSHIP 11 NORTH |  | LINE PIPE | PIPE |  | 1959 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 118485.332 | 239032.7728 | PROPANE | 2 | 5808 | 5808 | NO | NO | 6.625 | 0.188 | 42000 | WELDED |  | 1312 | 500 | YES | 24 | 1640 | 0 | 1979 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | L LEROY ANDERSON | 3167739000 | AN INDIVIDUAL WAS PREPARING AN AREA FOR FARMING THAT HAD PREVIOUSLY NOT BEEN IN AGRICULTURAL PRODUCTION. IN HIS EFFORTS TO PREPARE THE GROUND FOR FARMING, THE INDIVIDUAL REMOVED APPROXIMATELY 24 INCHES OF COVER DIRECTLY OVER KANEBS SIX INCH PIPELINE. SUBSEQUENT TO THIS ACTIVITY, THE INDIVDUAL RUPTURED KANEBS SIX-INCH PIPELINE WITH A DEEP CHISEL FARM IMPLEMENT. THE INDIVDUAL TELEPHONED KANEBS CONTROL CENTER APPROXIMATELY 10 MINUTES AFTER HE RUPTURED THE PIPELINE. THE PIPELINE WAS IMMEDIATELY SHUT DOWN AND BLOCK VALVES WERE CLOSED EITHER BY REMOTE CONTROL OR PERSONNEL. WHILE UNDER CONSTANT SURVEILLANCE, THE PIPELINE WAS ALLOWED TO DEPRESSURIZE OVER A PERIOD OF SEVERAL DAYS ACCOUNTING FOR THE LARGE RELEASE VOLUME. KANEB DID NOT HAVE THE OPPORTUNITY TO IDENTIFY AND MARK THE LOCATION OF ITS PIPELINE BECAUSE THE INDIVIDUAL RESPONSIBLE FOR THE DAMAGE TO KANEBS PIPELINE FAILED TO NOTIFY THE NEBRASKA ONE CALL SYSTEM. THIS IS A SUPPLEMENTAL REPORT THE PURPOSE OF WHICH IS TO CORRECT THE RELEASE VOLUME AMOUNT. THE REPORT SUBMITTED ON MARCH 22, 2000 INCORRECTLY LISTED THE RELEASE VOLUME AS 5,808 BARRELS. THE CORRECT RELEASE VOLUME IS ZERO BARRELS.
2017-09-29 08:50 | YES | NO | 20000034 | 2000-03-21 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 2000-02-23 | 704 | MN | CASS |  | NO |  | YES | @ MILEPOST 0957.1000 145N, SECTION: 13, QUARTER: NW, 31W, TRACT #: T-511-A W OF 5TH | 520827 | LINE PIPE | LONGITUDINAL WELD |  | 1954 | OTHER | PINHOLE LEAK ON LONGITUDINAL WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | CRUDE OIL | 1 | 10 | 5 | NO | NO | 26 | 0.218 | 52000 | WELDED |  | 809 | 626 | YES | 4 | 1075 | 8 | 1995 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | L H DEBREIR | 2187250102 | AN ODOR WAS DETECTED BY A COMPANY EMPLOYEE WHILE TRAVELING TO A JOB SITE. THE LINES WERE IMMEDIATELY SHUTDOWN AND FIELD VERIFICATION CONFIRMED A LEAK AT MP 957.1. APPROXIMATELY 10 BARRELS WERE RELEASED TO THE SURROUNDING LAND. PLM RESOURCES WERE IMMEDIATELY DISPATCHED AND CLEAN-UP AND REPAIR WERE INITIATED. THE PIPE JOINT CONTAINING THE PINHOLE LEAK WAS REMOVED FROM SERVICE TO CONFIRM THE CAUSE THROUGH METALLURGICAL ANALYSIS.
2017-09-29 08:50 | YES | NO | 20000035 | 2000-03-30 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 2000-02-26 | 725 | IA | JOHNSON |  | NO |  | NO | WILLIAMS PIPELINE CO, IOWA CITY REFINED PRODUCTS TERMINAL, 912 FIRST AVENUE, CORALVILLE, IA 52241 | 521204 | OTHER | BOLTED FITTING |  | 1983 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 270823.6161 | 546360.6235 | DIESEL FUEL | 3 | 756 | 566 | NO | NO | 3 |  | 275 | OTHER |  | 220 | 6 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | OTHER | ICE EXPANSION IN/NEAR FLANGE | Null | ONE CALL |  | Null | Null | KENNETH L LYBARGER |  | SOME TIME PRIOR TO 7:00 ICE FORMED IN OR AROUND A BOLTED FLANGE CONNECTION OF A 3-INCH DIAMETER TRANSFER LINE BETWEEN BREAKOUT TANKS 1362 AND 1436 AT THE WPL REFINED PRODUCTS TERMINAL AT CORRALVILLE, IA. THE ICE EXPANSION CAUSED TWO LOWER BOLTS CONNECTING THE FLANGE TO BREAK, ALLOWING PRODUCT TO SPILL FROM THE LINE. TELEPHONIC NOTICE WAS TIMELY MADE TO NATIONAL RESPONSE CENTER, THE IOWA DEPARTMENT OF NATURAL RESOURCES (STATE EPA) AND OTHER AGENCIES IN ACCORDANCE WITH APPLICABLE REGULATIONS. FREE PRODUCT WAS RECOVERED IMMEDIATELY, AND CONTAMINATED SOIL AND WATER ARE BEING REMEDIATED IN CONJUNTION WITH THE IOWA DNR. BLIND FLANGES HAVE BEEN INSTALLED AT BOTH ENDS OF THE LINE, COMPLETELY ISOLATING THE LINE HAS BEEN TAKEN OUT OF SERVICE.
2017-09-29 08:50 | YES | NO | 20000037 | 2000-04-06 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 1999-11-13 | 1700 | TX | MIDLAND |  | NO |  | NO | E/2 SE/4 SEC 44, BLK 38, T-1-5, T& P RY CO |  | LINE PIPE | PIPE |  | 1951 | OTHER | MATERIAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 34552.7437 | 69706.8404 | CRUDE OIL | 1 | 10500 | 1 | NO | NO | 8 | 0.322 | 25000 | WELDED |  | 752 | 563 | YES | 8 | 940 | 7 | 1991 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LENNAN FROST | 9156843467
2017-09-29 08:50 | YES | NO | 20000038 | 2000-04-05 | 4805 | EXPLORER PIPELINE CO | YES | 2000-03-09 | 2220 | TX | HUNT |  | NO |  | NO | TWO MILES NORTH AND FOUR MILES WEST OF THE CITY OF GREENVILLE, TX. 2 MILES NORTH OF THE INTERSECTION OF HIGHWAYS 380 & 903. | 522524 | LINE PIPE | PIPE |  | 1970 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 35000000 | 23697066.4048 | 47806554.56 | GASOLINE | 3 | 13436 | 3292 | NO | NO | 28 | 0.281 | 52000 | WELDED |  | 751 | 705 | YES | 24 | 955 | 2 | 1971 | EXTERNAL | Null | YES | OTHER | UNDETERMINED AT THIS TIME |  |  | Null |  |  | Null | Null | ROGER W FLEMING | 9184935106 | 10:20 P.M. - NUMBERS 2 AND 3 PUMPS AT GREENVILLE STATION SHUT DOWN. 10:21 P.M. - DISCUSSION AMONG OPERATING PERSONNEL REGARDING PROBABLE CONTROL VALVE ISSUE. SHUTDOWN OF DURANT PUMP STATION. 10:24P.M. - BEGIN SHUTDOWN OF PUMPS ON 28 INCH MAINLINE SOUTH OF GREENVILLE TO DURANT MAINLINE. 10:55 P.M. - GREENVILLE BLOCK VALVE CLOSED. 10:57 P.M. - CONTROL CENTER SUPERVISOR NOTIFIED OF POSSIBLE LEAK. CARETAKER FOR SHELDON RANCH OUTSIDE GREENVILLE CONTACTS GREENVILLE AREA HSE COORDINATOR REGARDING PETROLEUM ODORS NEAR COUNTY ROAD (CR) 903. 10:58 P.M. - EXPLORER GREENVILLE AREA SUPERVISOR CONTACTED BY TULSA CONTROL CENTER AND ADVISED OF PRESSURE LOSS. CARETAKE FOR THE SHELDON RANCH (CR 903) CONTAXTS LOCAL EXPLORER SAFETY ENVIRONMENTAL ENGINEER THAT ARE STRONG PETROLEUM ODORS ON PROPERTY ON CR 903. CONTROL CENTER SUPERVISOR NOTIFIED OF POSSIBLE LEAK. 0:59 - DURANT BLOCK VALVE CLOSED. LINE ISOLATED. 11PM- OVER/SHORT REPORT REFLECTS 4800 BARRELS SHORT AT GLENPOOL. 11:05 PM- GREENVILLE AREA SUPERVISOR CONFIRMS THAT LOCAL POLICE AND FIRE NOTIFIED BY 911 CALLS. EXPLORER PERSONNEL ARRIVE AT INTERSECTION OF CR 380 AND 903 AND MEET WITH SHERIFF DEPARTMENT PERSONNEL. EXPLORER PERSONNEL TRAVEL NORTH ON 903 TO CADDO CREEK AND OBSERVE GASOLINE FLOWING UNDER 903 BRIDGE AND REQUEST LOCAL BACKHOE CONTRACTOR TO RESPOND TO THE CADDO CREEK CROSSING ON CR 903. 11:40 PM- CONTROL CENTER SUPERVISOR ARRIVED AT CONTROL CENTER AND COMMUNICATES WITH GREENVILLE AREA SUPERVISOR. 11:45PM- GREENVILLE AREA SUPERVISOR REPORTS LOCATION OF SPILL SITE, ARRIVAL OF POLICE AND FIRE DEPARTMENTS AT THE INTERSECTION OF HIGHWAYS 380 AND 903. CONTROL CENTER SUPERVISOR STARTED NOTIFYING INCIDENT RESPONSE TEAM MEMBERS. 11:53PM- HUNT COUNTY EMERGENCY COORDINATOR (EMC) ARRIVES ON SCENE AND ASSUMES INCIDENT COMMAND. ESTABLISHES PRIORITY TO SECURE COUNTY ROADS IMMEDIATELY EAST AND WEST OF THE SITE. EMC DETERMINES NOT TO EVACUATE RESIDENTS BECAUSE THE GASOLINE VAPORS ARE NOT POSING A SERIOUS PROBLEM TO THE RESIDENTS IN THE IMMEDIATE AREA. FIRE UNITS FROM CADDO MILLS DISPATCHED TO DETERMINE THE SOURCE OF THE ODORS. SEE REPORT FOR ADDITIONAL REMARKS
2017-09-29 08:50 | NO | NO | 20000039 | 2000-04-17 | 26058 | LOS ANGELES DEPT OF WATER & POWER | NO | 2000-03-21 | 919 | CA | LOS ANGELES | LONG BEACH | NO |  | NO | IN RAILROAD RIGHT OF WAY NEAR PIER B ST/SANTA FE (SEE MAP ATTACHED) PIPELINE DESIGNATED: CSFM #1022 OTF TO ARCO | 523733 | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33852.952 | 68295.0779 | TRANSMIX (PART.REFINED PETRO) | 1 | 2 | 0 | NO | NO | 12 | 0.375 | 0 | WELDED |  | 470 | 0 | YES | 4 | 590 | 11 | 1998 | EXTERNAL | Null | YES |  |  | DAMAGE BY NATURAL FORCES |  | Null | ONE CALL |  | NO | NO | RANDOLPH J DREYER | 3105221606 | MTF CONTROL ROOM RECEIVED "CALL WHEEL" LEAK REPORT AT 0919. OIL OPERATIONS SUPERVISOR RESPONDED TO REPORTED LOCATION. REPRESENTATIVES FROM OTHER COMPANIES WITH PIPELINES IN THE AREA WERE ALSO AT SITE. SOUTHWESTERN CONTRACTORS EXPOSED THE PIPELINE AFTER PRESSURIZING THE PIPELINE FOR TEST, BY LOCATION AND OTHER FACTORS LADWP CLAIMED THE LEAK. CSFM #1022 OTF AND ARCO T2 BEGAN SPILL RESPONSE/NOTIFICATION PROCEDURES AT 1347.
2017-09-29 08:50 | YES | NO | 20000041 | 2000-04-13 | 12628 | MOBIL PIPELINE CO | YES | 2000-03-11 | 1045 | RI |  | CUMBERLAND | NO |  | NO | APPROXIMATELY 1/2 MILE EAST OF MENDON ROAD (ROUTE 122) WITHIN THE CONSTRUCTION SITE OF THE CUMBERLAND CROSSINGS APARTMENT COMPLEX. SEE ATTACHED DIAGRAM. | 522649 | LINE PIPE | PIPE |  | 1931 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | GASOLINE | 1 | 185 | 143 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 1100 | 707 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | MICHAEL F MCQUADE | 4014342900 | A FRONT END LOADER OPERATED BY NATIONWIDE, SUBCONTRACTOR FOR D. W. WHITE, PUNCTURED THE PIPELINE WHILE SCOOPING STONE FROM THE PILE OF STONE PLACED OVER OUR PIPELINE WHICH PROTECTED THE PIPELINE DURING BLASTING OPERATIONS. AN EMPLOYEE OF MOBIL PIPE LINE HAS BEEN ON SITE CONTINUOUSLY, DURING THE PAST 6-8 WEEKS, TO OVERSEE BLASTING AND CONSTRUCTION ACTIVITIES IN THE VICINITY OF THE PIPELINE. HOWEVER, NO WORK IN THE AREA OF THE PIPELINE RIGHT OF WAY WAS SCHEDULED ON THE DATE OF THE INCIDENT SATURDAY, THEREFORE NO PIPELINE EMPLOYEE WAS ON SITE. THE PIPELINE WAS MARKED IN THE IMMEDIATE AREA OF THE CONSTRUCTION ACTIVITY. THE PIPELINE EMPLOYEE ASSIGNED TO THE PROJECT HAD COMMUNICATED WITH HEAVY EQUIPMENT OPERATORS ABOUT THE PIPELINES LOCATION.
2017-09-29 08:50 | YES | NO | 20000042 | 2000-04-14 | 31415 | CLARK PORT ARTHUR PIPELINE CO | YES | 2000-03-09 | 1900 | TX | JEFFERSON | BEAUMONT | NO |  | NO | SOUTH OF HWY 69, OFF WEST PORT ARTHUR ROAD INSIDE LUCAS STATION TANK FARM . SEE ATTACHED MAP |  | TANK FARM | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33852.952 | 68295.0779 | CRUDE OIL | 1 | 600 | 580 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | PIT CORROSION |  |  | Null |  |  | Null | Null | MORRIS CARTER JR | 4099851358 | AT APPROXIMATELY 7PM ON MARCH 9, 2000 A SPILL WAS DISCOVERED IN THE LUCAS STATION TANK FARM. THE SPILLED MATERIAL WAS CRUDE OIL. THE CRUDE OIL WAS CONTAINED PRIMARILY IN DRIED DRAINAGE DITCHES. THERE WAS NO SURFACE WATER PRESENT IN THE SPILL AREA. THE OUTSIDE OPERATOR NOTIFIED THE INSIDE OPERATOR AND INITIATED EMERGENCY RESPONSE ACTIVITIES. THE SPILL WAS CONTAINED ON-SITE AND THERE WAS NO THREAT TO SURFACE WATERS. FREE OIL RECOVERY WAS BEGUN AND TEMPORARY EARTHEN DAMS WERE CONSTRUCTED TO PREVENT FURTHER MIGRATION OF THE OIL DOWN THE DRAINAGE DITCHES. THE INITIAL SOURCE WAS BELIEVED TO BE AND IDLE, UNDERGROUND 10" SPUR. THIS LINE WAS ISOLATED. THE INITIAL ESTIMATE OF THE AMOUNT RELEASED WERE ONLY 25 BARRELS AND THE RAILROAD COMMISSION OF TEXAS WAS NOTIFIED. UPON ARRIVAL OF ADDITIONAL RESPONSE CREW AND FURTHER ANALYSIS OF THE SITUATION, THE ESTIMATION OF AMOUNT RELEASED WAS REVISED TO 120 BARRELS AND THE DEPARTMENT OF TRANSPORTATION WAS NOTIFIED AT THAT TIME. FREE OIL RECOVERY CONTINUED AND MR. BILL LANGSTON ARRIVED ON SITE AT APPROXIMATELY 10PM TO INVESTIGATE. AT THAT TIME, IT APPEARED THE SPILL WAS UNDER CONTROL AND BEING FULLY RECOVERED. IN THE MORNING, DURING DAYLIGHT HOURS, IT BECAME APPARENT THAT THE SOURCE WAS NOT THE IDLE 10" LINE, BUT ANOTHER UNDERGROUND LINE LOCATED APPROXIMATELY 20 FEET AWAY FROM THE 10". THE 20" FILL LINE FROM THE WEST TEXAS GULF LINE WAS UNCOVERED AND THE SOURCE EXPOSED. THE SOURCE WAS A PINHOLE CAUSED FROM EXTERNAL PIT CORROSION. CLEANUP CONTINUED THROUGHOUT THE DAY, RECOVERING 580 BARRELS OF CRUDE OIL. IMPACTED SOILS WERE REMOVED TO BE BIO-TREATED ONSITE. REPRESENTATIVES FROM THE TNRCC AND THE RCT INSPECTED THE SITE. MR. BARNEY GANDY OF THE RCT VERBALLY APPROVED THE SITE CLEANUPS COMPLETION. CONFIRMATION SAMPLES WERE COLLECTED ON MARCH 16, 2000 WHICH DEMONSTRATE THAT THE SOIL WS REMEDIATED TO LESS AND 1% TOTAL PETROLEUM HYDROCARBONS.
2017-09-29 08:50 | YES | NO | 20000043 | 2000-04-14 | 4906 | EXXON PIPELINE CO | NO | 2000-03-13 | 943 | TX | HARRIS | WEBSTER | NO |  | NO | HARRIS COUNTY, TX CITY OF WEBSTER, TX AVE AT COLE STREET |  | LINE PIPE | PIPE |  | 1945 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15270 | 10338.6915 | 20857.3168 | CRUDE OIL | 1 | 100 | 96 | NO | NO | 8 | 0.322 | 25 | WELDED |  | 573 | 25 | YES | 8 | 717 | 0 | 1991 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | RAMONA PULLIN | 7136562232 | CONTRACTOR DOING STREET WORK WITH TRACKHOE DUG THROUGH 8" STEEL PIPELINE. WORK IN THE AREA HAD BEEN ONGOING, BUT NO UPDATES WERE RECEIVED, AND THE WORK PROCEEDED UP A SIDE STREET. EXCAVATOR DID NOT CALL WHEN WORK MOVED FROM PREVIOUS SITE. LINE MARKERS WERE PRESENT.
2017-09-29 08:50 | YES | NO | 20000044 | 2000-04-18 | 18194 | SEMINOLE PIPELINE CO | NO | 2000-03-16 | 2216 | TX | WILLIAMSON |  | NO |  | NO | 1 1/2 MILES NORTH OF COUPLAND, TEXAS OFF COUNTY ROAD 454, 200 YARDS EAST OF HWY 95 |  | PUMPING STATION | PUMP |  | 1998 | OTHER | SEAL FAILURE ON #4 PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 4062.3542 | 8195.4094 | NATURAL GAS LIQUID | 2 | 340 | 0 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | IRVIN BANG SAFETY REP | 2812405100 | AT 22:16 THE PIPELINE CONTROL CENTER IN TULSA, OK, RECEIVED A SEAL FAIL ALARM FROM THE COUPLAND STATION ON THE SEMINOLE PIPELINE COMPANY (SPC) MAINLINE IN WILLIAMSON COUNTY. THE CONTROLLER PROMPTLY NOTIFIED SPC TECHNICAL PERSONNEL THAT WERE ON CALL TO INVESTIGATE. THE COUNTY SHERIFF DEPARTMENT WAS CONTACTED BY AN UNARMED LOCAL SOURCE AND DISPATCHED OFFICERS, AS WELL AS PERSONNEL FROM THE LOCAL FIRE DEPARTMENT TO THE SCENE, WHO INSTITUTED AN INCIDENT COMMAND STRUCTURE. UPON INVESTIGATION BY PIPELINE PERSONNEL, THE CAUSE WAS IDENTIFIED AND A DISCHARGE VALVE CLOSED, ELMINATING THE RELEASE. TELEPHONIC NOTIFICATION TO REGULATORY AGENCIES WAS TIMELY MADE IN ACCORDANCE WITH REGULATIONS. AS A PRECAUTION, THE SHERIFF AND FIRE DEPARTMENT HALTED TRAFFIC ON NEARBY ROADS AND EVACUATED ONE RESIDENCE. REPAIRS WERE PROMPTLY MADE AND THE LINE RETURNED TO SERVICE; THE ROADS WERE REOPENED, AND AFTER THE EVACUATED OCCUPANTS WERE CHECKED AND FOUND TO BE SAFE, THEY WERE PERMITTED TO RETURN HOME. ALL PARTICIPANTS IN THE INCIDENT COMMAND WERE DEBRIEFED IN ACCORDANCE WITH REGULATIONS, AS WELL AS, COMPANY PROCEDURE AND THE INCIDENT COMMAND WAS DISBANDED.
2017-09-29 08:50 | YES | NO | 20000045 | 2000-04-25 | 21031 | PG & E TEXAS PIPELINE, L.P. | NO | 2000-03-22 | 930 | TX | DUVAL |  | NO |  | NO | APPROXIMATELY 12 MILES NW OF FREER, TEXAS @ COUNTY ROAD 401, 3 MILES NORTH OF STATE HWY 44 |  | LINE PIPE | PIPE |  | 1981 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 66213 | 44830.1102 | 90440.4399 | NATURAL GAS LIQUID | 2 | 2923 | 0 | NO | NO | 0 | 0.25 | 42000 |  |  | 1424 | 900 | YES | 25 | 1811 | 4 | 1981 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | NO | MIKE PAWELEK | 2105284204 | THE PIPELINE WAS STRUCK BY A CONTRACTOR WORKING FOR PG&E TEXAS PIPELINE, LP. THE CONTRACTOR WAS PERFORMING COATING REHABILITATION WORK ON 20" PF&E TEXAS PIPELINE, LP GAS LINE WHICH LIES WITHIN THE SAME RIGHT OF WAY AS THE 6" LIQUID LINE. THE CONTRACTOR WAS TERRACING AND CREATING A SAFE ENTRANCE WAY TO THE BELLHOLE ON THE 20" PIPELINE WHEN THE 6" PIPELINE WAS HIT BY ITS TRACKHOE. CONTRACTOR WAS INFORMED OF THE 6" PIPELINES EXISTENCE AND LOCATION PRIOR TO EXCAVATION OF THE 20" PIPELINE.
2017-09-29 08:50 | YES | NO | 20000046 | 2000-04-28 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-02-10 | 2250 | OK | KAY | PONCA | NO |  | NO | INCIDENT OCCURED WITHIN CONOCO'S PONCA CITY COMPLEX LOCATED AT THE PONCA CITY PUMP STATION HWY. 60 SE/4 SECT 33 TOWNSHIP NORTH RANGE 2 EAST KAY COUNTY, OK. | 519477 | PUMPING STATION | PUMP |  | 1999 | OTHER | FAILED PUMP SEAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3385.2952 | 6829.5078 | DIESEL FUEL | 1 | 70 | 55 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | VANCE WEBB | 5807674845 | AT 22:50 HRS ON FEBUARY 10TH, 2000 THE OPERATOR AT CONOCO PIPELINES (CPL) CHEROKEE PUMP STATION, LOCATED IN PONCA CITY, OKLAHOMA OBSERVED A SEAL FAILURE ON THE NUMBER THREE WOOD RIVER PUMP. THE UNIT WAS IMMEDIATELY SHUT DOWN, ISOLATED AND RECOVERY OPERATIONS IMPLEMENTED. THE APPROXIMATELY 70 BBLS OF DIESEL FUEL RELEASED AT THE TIME OF THE INCIDENT WERE CONTAINED ON CPLS PROPERTY. THIS WAS ACCOMPLISHED VIA EXISTING CONTAINMENT SYSTEMS. PRODUCT WAS RECOVERED UTILIZING A VACCUM TRUCK AND ABSORBENT MATERIALS. THE FAILED SEAL WAS REMOVED FOR ANALYSIS TO DETERMINE IF POSSIBLE, THE REASON FOR FAILURE.
2017-09-29 08:50 | YES | NO | 20000047 | 2000-04-28 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-04-01 | 1300 | OK | KAY | PONCA | NO |  | NO | INCIDENT OCCURRED WITHIN CONCO'S PONCA CITY COMPLEX LOCATED AT 1000 S PINE STREET, PONCA CITY, OK SE/4 SECT 33 TOWNSHIP 26 NORTH RANGE 2 EAST KAY COUNTY, OK |  | TANK FARM | BOLTED FITTING |  | 2000 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6770.5904 | 13659.0156 | GASOLINE | 1 | 200 | 195 | NO | NO |  |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | VANCE WEBB | 5807674845 | ON APRIL 1, 2000 AT 1300 HOURS, A CONOCO TANK FARM OPERATOR DISCOVERED GASOLINE BEING RELEASED FROM A 6" - 150# FLANGE. THE FLANGE WAS LOCATED ON TANK CIRCULATION LINE IMMEDIATELY ADJACENT TO TANK 156 IN CONOCOS PONCA CITY REFINERY TANK FARM. UPON DISCOVERY, THE TANK WAS IMMEDIATELY ISOLATED AND CONTAINMENT AND RECOVERY OPERATIONS IMPLEMENTED. THE INITIAL INVESTIGATION INTO THE INCIDENT REVEALED THAT A 5-INCH GASKET HAD BEEN INSTALLED IN A 6-INCH FLANGE. THIS OCURRED WHEN BLINDS WERE REMOVED TO PLACE THE TANK BACK IN SERVICE AFTER IT HAD UNDERGONE AND INSPECTION.
2017-09-29 08:50 | YES | NO | 20000048 | 2000-05-08 | 26094 | SUPPORT TERMINALS OPERATING PARTNERSHIP, L. P. | NO | 2000-04-07 | 1600 | MD | PRINCE GEORGES |  | NO |  | NO | ADJACENT TO SWANSONS CREEK NEAR VALVE BOX |  | LINE PIPE | PIPE |  | 1973 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50000000 | 33852952.0069 | 68295077.9428 | TRANSMIX (PART.REFINED PETRO) | 3 | 3088 | 0 | NO | NO | 12 | 0.203 | 1608 | WELDED |  | 550 | 280 | YES | 14 | 1600 | 0 | 1973 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ALAN RACLAY | 9729318065 | PIPELINE BETWEEN RYCEVILLE AND CHALK POINT BEING PIGGED IN PREPARATION FOR SMART PIG RUN. PIG DID NOT ARRIVE AT CALCULATED TIME. TANK INVENTORIES AT RYCEVILLE, MORGANTOWN, CHALK POINT AND PINEY POINT CHECKED, SHOWING DISCREPANCY. SYSTEM SHUTDOWN AND OVERFLIGHT ORDERED. EVIDENCE OF OIL FOUND IN MARCH AREA NORTH OF SWANSONS CREEK VALVE BOX. EMERGENCY RESPONSE PLAN IMPLEMENTED.
2017-09-29 08:50 | YES | NO | 20000049 | 2000-05-09 | 18718 | SUN PIPE LINE CO | Null | 2000-04-24 | 600 | OK | TULSA |  | NO |  | NO | PUMP MANIFOLD, SUN TULSA REFINERY SW/4 SECTION 10-19N-12E TULSA OKLAHOMA | 527033 | PUMPING STATION | VALVE |  | 1976 | OTHER | DEFECTIVE BOLTS ON VALVE BODY | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 338.5295 | 682.9508 | DATA NOT SPECIFIED | 1 | 140 | 135 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | NO | Null | EDITH F COEN | 9185866942 | BOLTS FAILED ON VALVE ALLOWING OIL TO ESCAPE. VALVE HAS BEEN REMOVED FROM LINE.
2017-09-29 08:50 | YES | NO | 20000050 | 2000-05-09 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | NO | 1999-12-01 | 1325 | NM | SANDOVAL COUNTY | PLACITAS | NO |  | NO |  |  | LINE PIPE | BOLTED FITTING |  | 1983 | OTHER | 8'' O-RING FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 48373.8411 | 97589.5765 | JET FUEL | 2 | 50 | 50 | NO | NO | 8 | 0.188 | 2267 | WELDED |  | 1632 | 0 | YES | 24 | 2131 | 4 | 1973 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J.DENNIS HOLLAND, SAFETY REPRESENTATIVE | 5056324485 | AT 1325 MST ON WEDNESDAY, DECEMBER 1, 1999, THE SANDOVAL COUNTY, NM FIRE DEPARTMENT REPORTED A POSSIBLE PIPELINE LEAK INTO MAPCO PIPELINE CONTROL CENTER LOACTED IN TULSA, OKLAHOMA. WILLIAMS EMPLOYEES RESPONDED TO THE LOCATION AND VERIFIED THE LEAK WAS FROM A WILLIAMS 8 INCH REFINED PRODUCT LINE. THE PIPELINE WAS IN JP-8 FUEL SERVICE AT THE TIME OF THE INCIDENT. THE ISOLATED SECTIONS OF PIPELINE CONTENTS WERE LOADED INTO TRANSPORT TRUCKS. APPROXIMATELY 25 OF PIPELINE WAS REMOVED AND REPLACED. CONTAINED WITHIN THE REMOVED 25 SECTION OF PIPELINE WERE AN 8 INCH TD WILLIAMSON STOPPLE FITTING AND A 2 INCH TOR NIPPLE. THE PIPELINE WAS RETURNED TO SERVICE AT 1230 MST ON DECEMBER 3, 1999.
2017-09-29 08:50 | YES | NO | 20000051 | 2000-05-11 | 443 | AMOCO PIPELINE CO | YES | 2000-04-03 | 1153 | OK | PAYNE |  | NO |  | NO | CUSHING TERMINAL; SEC. 14-T17N-R5E; CUSHING, OK | 524980 | TANK FARM | VALVE |  | 1997 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6770.5904 | 13659.0156 | CRUDE OIL | 1 | 70 | 70 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | STEWART F CARSE | 9182231101 | WHILE EXCAVATING TANK MANIFOLD FOR RENOVATION, A 2" VALVE WAS STRUCK BY A TRACKHOE BUCKET, CAUSING IT TO BECOME DISLODGED, AND RELEASING APPROXIMATELY 70 BBLS OF CRUDE OIL. ALL PRODUCT WAS CONTAINED WITHIN THE EXCAVATION AND IMMEDIATELY PICKED UP AND RETURNED TO THE SYSTEM BY ONSITE VACUUM TRUCKS.
2017-09-29 08:50 | YES | NO | 20000052 | 2000-05-11 | 31436 | PLAINS MARKETING LP | NO | 2000-03-21 | 1450 | TX | RUSK | KILGORE | NO |  | NO | HWY 42 AND 135 ON REED SWITCH RD, N32 19.931/W94 56.420 |  | LINE PIPE | PIPE |  | 1979 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | 9140.297 | 18439.671 | CRUDE OIL | 1 | 1250 | 940 | YES | NO | 10 | 0.219 | 24000 | WELDED |  | 485 | 325 | YES | 8 | 605 | 10 | 1999 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KEVIN E BROWN | 9182230207 | RUSK COUNTY (TEXAS) ROAD GRADER HAD BEEN REMOVING COVER OFF PIPELINE OVER TIME AND DID NOT NOTIFY THE PIPELINE OR ONE OF THE TEXAS ONE-CALL ORGANIZATIONS. PLAINS MARKETING LP IS A MEMBER OF THE TEXAS ONE-CALL AS WELL AS AN ACTIVE GOVERNMENT AND CONTRACTOR AWARENESS PROGRAMS IS IN PLACE. WHILE CLEARING A COUNTY ROAD, A RUSK COUNTY GRADER HIT A PLAINS MARKETING LP/SCURLOCK-PERMIAN LLC 10 INCH ID PIPELINE CAUSING THE RELEASE.
2017-09-29 08:50 | YES | NO | 20000053 | 2000-05-11 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-04-09 | 2045 |  |  |  | YES | LAT 29 14.475, LONG 88 59 | NO | ODYSSEY 12" MP 70 | 525519 | LINE PIPE | PIPE |  | 1968 | OTHER | CAUSE UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 338529.5201 | 682950.7794 | CRUDE OIL | 1 | 14 | 0 | NO | NO | 12 | 0.406 | 5600 | WELDED |  | 1800 | 175 | YES | 24 | 1800 | 0 | 1968 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF | 7132414381 | OIL/SLICK WAS REPORTED BY OTHERS AND CALL MADE TO NRC (REPORT NO 525519). REPLACEMENT OF THE SPOOL PIECE REPAIR UNIT (SPRU) ON THE 12" ODYSSEY (COBIA) PIPELINE IN MP-70 WAS COMPLETED ON SATURDAY, APRIL 22. DIVERS CHECKED THE SPRU FOR LEAKS AND A HELICOPTER WAS DISPATCHED TO PERFORM AN AERIAL SURVEY OF THE AREA. THE PIPELINE WAS RETURNED TO SERVICE ON SATURDAY, 4/22 AT APPROXIMATELY 2330 HOURS. THE EXACT CAUSE OF THIS INCIDENT IS STILL UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE FILED AS SOON AS A FINAL DETERMINATION HAD BEEN MADE.
2017-09-29 08:50 | YES | NO | 20000054 | 2000-05-12 | 443 | AMOCO PIPELINE CO | YES | 2000-04-07 | 1110 | KS |  |  | NO |  | NO | FROM ALTOONA, KS 75/47 HWY JUNCTION 2 MILES EAST ON 47 HWY AND 2.5 MILES SOUTH ON COUNTY ROAD SW 1/4 SECTION TWP 29S RNG 16E AMOCO MP MARKER 118.2 | 525385 | LINE PIPE | PIPE |  | 1937 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 50779.428 | 102442.6169 | CRUDE OIL | 1 | 1230 | 1200 | NO | NO | 12 | 0.281 | 0 | WELDED |  | 825 | 0 | YES | 8 | 1562 | 10 | 1992 |  | Null | NO |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | STEWART F CARSE | 9182231101 | ON FRIDAY, APRIL 7, 2000, AT APPROXIMATELY 1110 HOURS, A CRUDE OIL PIPELINE RELEASE OCCURRED RESULTING IN A 1230 BARREL OIL SPILL CONTAINED AT THE SITE OF INCIDENT IN WILSON COUNTY NEAR ALTOONA, KS (SOUTHEAST KANSAS). NO INJURIES WERE INCURRED AND THERE WAS NO ENVIRONMENTAL IMPACT OUTSIDE THE CONTAINED AREA AT THE SITE. DAMAGE TO THE LINE REQUIRED A PERMANENT LINE REPAIR CONSISTING OF A CUTOUT AND PIPE REPLACEMENT. A THIRD PARTY CONTRACTOR STRUCK THE LINE WHILE PERFORMING AGRICULTURAL RELATED EXCAVATION WORK. THE CONTRACTOR REPORTED THE INCIDENT TO THE BP AMOCO PIPELINE CONTROL CENTER IN TULSA, OK. NOTIFICATIONS WERE SUBSEQUENTLY MADE TO THE APPROPRIATE STATE AND FEDERAL AGENCIES AND BP AMOCO INCIDENT NOTIFICATION CENTER. PIPELINE AND CONTRACTOR PERSONNEL RESPONDED TO THE SCENE AND RECOVERED APPROXIMATELY 1200 BARRELS OF CRUDE OIL BY 2200 HOURS ON THE DAY OF THE INCIDENT. A MAJORITY OF THE RELEASE WAS CONTAINED AND CONTROLLED BY RESPONSE PERSONNEL TO ALLOW AN INITIAL TEMPORARY REPAIR. A REPRESENTATIVE FROM THE STATE ENVIRONMENTAL AGENCY ATTENDED SITE AND WAS SATISFIED WITH RECOVERY OPERATION AND INITIAL REMEDIATION. PIPELINE PERSONNEL ARE WORKING WITH AGENCY TO DEVELOP A WORK PLAN TO COMPLETE REMEDIATION OF CONTAMINATED TOPSOIL.
2017-09-29 08:50 | NO | NO | 20000055 | 2000-05-16 | 22855 | KOCH PIPELINE COMPANY, L.P. | Null | 2000-04-27 | 1430 | LA |  | ST JAMES | NO |  | NO | MILE POST 159.8 ON THE MISSISSIPPI RIVER |  | NO DATA | OTHER | LOADING ARM ON A DOCK | 0 | OTHER | THERMAL BUILDUP IN THE LOADING ARM ON THE DOCK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL |  | 0 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | BOB AEBI | 5803956294 | JEAN ZERINGUE AND CHAD SCHNEEBERGER (BOTH KOCH EMPLOYEES) WAS DOING A VISUAL INSPECTION OF KOCHS FACILITY WHEN THEY DISCOVERED THAT A RELEASE HAD OCCURRED. ALL APPLICABLE PEOPLE WAS NOTIFIED.
2017-09-29 08:50 | YES | NO | 20000056 | 2000-05-19 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2000-04-17 | 1015 | AR | PHILLIPS | HELENA | NO |  | NO | 826 OLD HIGHWAY HELENA, AR |  | TANK FARM | WELDING FITTING |  | 1961 | OTHER | EMPLOYEE WAS OPERATING BACKHOE INSIDE TERMINAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 24000 | 16249.417 | 32781.6374 | GASOLINE | 3 | 50 | 36 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ERNEST P HAGAN | 7137593845 | TEPPCO EMPLOYEE WAS USING A BACKHOE INSIDE TERMINAL WHEN THE BACKHOE SLID DOWN A SLIGHT INCLINE. THE BUCKET OF THE TRACTOR STRUCK PIPING ON THE INCOMING MANIFOLD, BREAKING A NIPPLE UNDER A 1" INSTRUMENTATION VALVE. THE BUCKET ALSO IMPACTED A RELIEF VALVE ASSEMBLY CRACKING A WELD IN 4" X 6" REDUCER. THE EMPLOYEE IMMEDIATELY BEGAN ISOLATING THE AFFECTED AREA OF THE MANIFOLD. ALL RELEASED PRODUCT WAS CONTAINED IN THE TERMINAL MANIFOLD AREA AND SKIMMER POND. THIRTY-SIX BARRELS WERE RECOVERED AND RETURNED TO STORAGE. TEPPCO IS CURRENTLY COMMUNICATING WITH THE STATE ENVIRONMENTAL AGENCY REGARDING SITE CLEAN UP.
2017-09-29 08:50 | YES | NO | 20000057 | 2000-05-24 | 4805 | EXPLORER PIPELINE CO | YES | 2000-04-24 | 1306 | TX | JEFFERSON |  | NO |  | NO | 3 MILES WEST OF WEST PT ARTHUR ROAD (SPUR 93) AND 2000 FEET SOUTH OF FM 365 |  | LINE PIPE | PIPE |  | 1970 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 270823.6161 | 546360.6235 | GASOLINE | 3 | 1 | 0 | NO | NO | 28 | 0.281 | 52000 | WELDED |  | 751 | 586 | YES | 24 | 954 | 2 | 1971 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | ROGER W FLEMING | 9184935112 | ON APRIL 24, 2000 AT 1215 HOURS EXPLORERS AERIAL PATROL PILOT REPORTED SHEEN ON THE WATER NEAR MP 4.0 ON THE 28" PIPELINE FROM PT ARTHUR TO HOUSTON, TX. COMPANY PERSONNEL RESPONDED TO THE SITE AND OBSERVED OCCASIONAL BUBBLES OF GASOLINE SURFACING OVER THE PIPELINE. THE LINE WAS SHUT DOWN AT 1306 HOURS AND ISOLATED BY CLOSING VALVES AT PT. ARTHUR STATION (MP 0) AND MP 5.3 THE REQUIRED GOVERNMENT AGENCIES WERE NOTIFIED AND EXPLORERS ENVIRONMENTAL CONTRACTOR, GARNER ENVIRONMENTAL, WAS DISPATCHED TO THE SITE. BY 1418 HOURS SPILL CONTAINMENT BOOMS, SORBENT BOOMS AND SORBENT PADS WERE DEPLOYED TO CONTAIN THE SHEEN. THE LEAK OCCURRED IN A SWAMP AREA ADJACENT TO HILLEBRANDT BAYOU. APPROXIMATELY THREE FEET OF WATER AND TWELVE FEET OF SILT COVER THE 28" PIPE AT THIS LOCATION. BARGES WITH EXCAVATION AND PILE DRIVING EQUIPMENT WERE DISPATCHED TO THE SITE. DIVERS WITH JET PUMPS WERE USED TO REMOVE COVER AND EXPOSE THE LINE UNDERWATER. EXCAVATION OF THE PIPE WAS VERY DIFFICULT AND SLOW. TWO POSSIBLE LEAK SITES WERE IDENTIFIED BY THE DIVERS AND PLIDCO SPLIT SLEEVES WERE INSTALLED AT THE TWO LOCATIONS. ON MAY 2, 2000 THE PIPELINE WAS REPRESSURED TO CONFIRM INTEGRITY OF THE TEMPORARY SLEEVES AND RETURNED TO SERVICE AT 1120 HOURS. STEEL SHEET PILINGS WERE INSTALLED AROUND THE LEAK SITE AND SOIL/WATER REMOVED TO EXPOSE THE PIPELINE AND PLIDCO CLAMPS. EXPOSURE OF THE PIPELINE SECTION WAS COMPLETED ON MAY 16, 2000. THE PIPELINE WAS SHUTDOWN, ISOLATED, PRESSURE REDUCED AND PLIDCO CLAMPS REMOVED TO INSPECT THE PIPE. ONE LOCATION WAS DETERMINED TO BE UNDAMAGED SO THE PLIDCO CLAMP WAS NOT REPLACED. AT THE OTHER LOCATION, THIRD PARTY DAMAGE OF UNKNOWN TIME AND ORIGIN CAUSED A SMALL DENT AND GOUGE THAT RESULTED IN A 1 1/2 INCH LONG HORIZONTAL CRACK THAT WAS SLOWLY SEEPING GASOLINE. THE SEEPAGE ONLY OCCURRED WHEN PRESSURE EXCEEDED 370 PSI. THE PLIDCO CLAMP WAS REINSTALLED AND THE PIPELINE RETURNED TO SERVICE. ENGINEERING PLANS ARE IN PROGRESS TO MAKE PERMANENT REPAIRS TO THE DAMAGED PIPE.
2017-09-29 08:50 | YES | NO | 20000058 | 2000-05-23 | 15485 | PHILLIPS 66 CO | NO | 2000-04-21 | 5 | TX | BRAZORIA |  | NO |  | NO | ON COUNTY RD 489 GO NORTHWEST FROM INTERSECTION WITH COUNTY RD 803 1 MILE. TAKE LEFT ON PRIVATE ROAD 0.4 MILES TO PIPELINE RIGHT OF WAY. | 526752 | LINE PIPE | PIPE |  | 1981 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 14500 | 9817.3561 | 19805.5726 | BUTANE | 2 | 5 | 0 | NO | NO | 8.6 | 0.188 | 60000 | WELDED |  | 1415 | 650 | YES | 8 | 2224 | 11 | 1990 | EXTERNAL | Null | YES | OTHER | DISBONDED COATING |  |  | Null |  |  | Null | Null | DENNIS TOEPPERWEIN | 9797983954 | AT APPROXIMATELY 12:05 AM ON APRIL 21, 2000, A PRIVATE CITIZEN REPORTED AN ODOR AND A SUSPECTED PIPELINE LEAK ON HIS FATHERS PROPERTY SOUTH OF SWEENY TEXAS. A PHILLIPS EMPLOYEE WAS DISPATCHED TO THE LOCATION TO EVALUATE THE LEAK. EMPLOYEE ARRIVED AT 12:15 AM AND CONFIRMED THERE WAS A LEAK CAUSING A VAPOR CLOUD ON PHILLIPS PIPELINE RIGHT OF WAY. PHILLIPS EMERGENCY RESPONSE PERSONNEL WERE SENT TO THE LOCATION. THE BRAZORIA COUNTY SHERIFFS DEPARTMENT WAS CONTACTED AND DISPATCHED AN OFFICER TO THE SITE. PHILLIPS PERSONNEL ENTERED THE SUSPECTED LEAK AREA WITH HYDROCARBON DETECTOR AND DETERMINED THE LIMITS OF VAPOR CLOUD (USING A 10% LOWER EXPLOSIVE LIMIT CRITERIA) WAS APPROXIMATELY 200 FEET IN RADIUS AT GROUND LEVEL. PUBLIC EVACUATION AND ROADBLOCKS WERE NOT REQUIRED SINCE THERE WERE NO HOUSES OR PUBLIC ROADS IN THE VICINITY. SINCE THERE WERE MULTIPLE LINES IN THIS RIGHT OF WAY INITIAL EFFORTS WERE FOCUSED ON IDENTIFYING THE CORRECT LINE AND SHUTTING DOWN ANY POTENTIAL SUSPECTS. A TOTAL OF FOUR LINES WERE SHUTDOWN DURING THE PROCESS INCLUDING THE BUTANE-BUTYLENE MIX PIPELINE. A SAMPLE OF THE VAPOR WAS TAKEN AND ANALYZED AT THE SWEENY COMPLEX LABORATORY WHICH CONFIRMED THE LEAKING LINE TO BE THE BUTANE-BUTYLENE MIX PIPELINE. THE BUTANE-BUTYLENE MIX PIPELINE TAKES PRODUCT FROM THE SWEENY COMPLEX TO UNDERGROUND STORAGE AT THE CLEMENS TERMINAL STORAGE FACILITY. THE BUTANE-BUTYLENE MIX PIPELINE WAS DEPRESSURIZED TO A SPHERE STORAGE TANK AT THE SWEENY COMPLEX AT APPROXIMATELY 430AM. THIS REDUCED THE PIPELINE PRESSURE FROM APPROXIMATELY 650 PSIG DOWN TO 50 PSIG. AT 1150 AM THE CLEMENS TERMINAL LAUNCHED A PIG TO DISPLACE THE BUTANE-BUTYLENE MIX PIPELINE WITH WATER TO SWEENY COMPLEX. IT IS ESTIMATED THE PIG PASSED THE LEAK LOCATION AT 1018PM APRIL 21, 2000. AT THE TIME OF THE INCIDENT THE SKY WAS CLEAR AND THERE WAS NO WIND. SCATTERED FOG WAS BEGINNING TO FORM ALONG THE PIPELINE RIGHT OF WAY. THE LEAK WAS APPROXIMATELY 2 TO 3 INCHES FROM A WELD AT CLOCK LOCATION 3:30. EXTERNAL CORROSION PITS WERE VISIBLE AT THE LEAK. ONE AT THE 330 POSITION AND ONE AT APPROXIMATELY 3:50 POSITION. WHEN UNCOVERING THE LEAK THERE WAS A THIN WHITE PLASTIC SHEET LOOSELY WRAPPED AROUND THE WELD AREA. COATING MATERIAL IN THE AREA DIRECTLY AROUND THE WELD WAS NOT VISIBLE WHEN THE PLASTIC WAS REMOVED. CATHODIC PROTECTION READINGS AT THE WELD WERE 1724 MV WHICH IS ABOVE THE -850MV CRITERIA USED ON THIS PIPELINE. THE PROBABLE CAUSE OF THE LEAK IS THAT THE COMBINATION OF BAD COATING AND WATER TRAPPED UNDER THE PLASTIC RESULTED IN A CORROSION CELL. THE WELDS APPROXIMATELY 60 FEET EAST AND WEST OF THE LEAK WERE ALSO UNCOVERED FOR INSPECTION. THE COATING AND WRAP WERE FOUND TO BE IN GOOD CONDITION. THE COATING WAS REMOVED AND NO INDICATION OF WATER OR EXTERNAL CORROSION WAS EVIDENT AT THESE TWO LOCATIONS. ULTRASONIC READING ON THE PIPE INDICATED FULL WALL THICKNESS. A PLIDCO 1500 PSI CLAMP WAS BOLTED OVER THE LEAK AND WELDED IN PLACE ACCORDING TO MANUFACTURER RECOMMENDATIONS AND SWEENY COMPLEX WELDING PROCEDURES. PIPELINE WAS PUT BACK IN SERVICE ON APRIL 25, 2000.
2017-09-29 08:50 | YES | NO | 20000059 | 2000-05-23 | 15674 | PLANTATION PIPE LINE CO | YES | 2000-04-25 | 1010 | GA | HARRIS | HAMILTON | NO |  | NO | STATION #3798 + 68 OF SECTION 13B ON THE COLUMBUS LINE |  | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 8124.7085 | 16390.8187 | GASOLINE | 3 | 126 | 126 | NO | NO | 8.6 | 0.188 | 52000 | WELDED |  | 1225 | 70 | YES | 24 | 2034 | 11 | 1971 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | JACQUE WILLIAMS | 7707514095 | DEFECT INDICATED ON SMART PIG RUN WARRANTED VISUAL INSPECTION AND ULTRASONIC TESTING OF PIPE WALL. LINE WAS EXCAVATED FOR INSPECTION AND A SMALL LEAK WAS DISCOVERED. SMART PIG TOOL DID NOT INDICATE A LEAK. THE PIPELINE WAS REPAIRED BY A 3 FOOT "TYPE B" FULL ENCIRCLEMENT SLEEVE AROUND THE CORROSION AREA.
2017-09-29 08:50 | YES | NO | 20000060 | 2000-05-23 | 443 | AMOCO PIPELINE CO | YES | 2000-05-04 | 1515 | TX | MONTAGUE | NOCONA | NO |  | NO | 7 MILES NORTH OF NOCONA, TX OFF OF HWY 103 (AT MP 121.67) | 528057 | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3385.2952 | 6829.5078 | CRUDE OIL | 1 | 60 | 59 | NO | NO | 12 | 0.281 | 35000 | WELDED |  | 975 | 0 | YES | 0 | 0 | 0 | 1976 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | F GABRIEL | 9037594279 | THIRD PARTY CLEANING A PAD FOR A WELL SITE WITH A DOZER. DOZER HIT PIPELINE.
2017-09-29 08:50 | YES | NO | 20000061 | 2000-05-26 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 2000-04-26 | 1745 | MN | PIPESTONE |  | NO |  | NO | SEC 17 TOWNSHIP 108 N RANGE 44 W, 5 MILES NORTH OF HOLLAND, MN |  | LINE PIPE | NO DATA |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 88017.6752 | 177567.2027 | GASOLINE | 1 | 50 | 17 | NO | NO | 8.525 | 0.203 | 36000 | WELDED |  | 1150 | 390 | YES | 8 | 1618 | 8 | 1990 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | JOHNNY L CAVITT | 9185736336 | THE INCIDENT OCCURRED AT 1719 HRS ON APRIL 26, 2000. THE CONTRACTOR (D&G CONSTRUCTION 507-532-2334) CALLED OUR MARSHALL, MN TERMINAL AT 1730 HRS TO REPORT THE INCIDENT. AT THE TIME OF THE INCIDENT THE PIPELINE SEGMENT WAS NOT IN OPERATION HOWEVER, IT WAS UNDER PRESSURE. THE PRESSURE RECORDED AT OUR SIOUX FALLS TERMINAL ON THE SOUTH END OF THE LINE SECTION PRIOR TO THE INCIDENT WAS AT 320 PSI. THE PRESSURE RECORDED ON THE NORTH END OF THE LINE SECTION PRIOR TO THE INCIDENT WAS 390 PSI. REMOTELY OPERATED VALVES AT SIOUX FALLS, SD AND MARSHALL, MN WERE CLOSED AT THE TIME OF THE INCIDENT AS THE LINE WAS SHUTDOWN AND UNDER PRESSURE. A COMBINATION OF CONTRACT RESOUCRES AND COMPANY PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE SITE. THE CONTRACTOR WAS OPERATING A FIELD TILING MACHINE (TRENCHER) INSTALLING DRAIN TILE IN A FIELD. THE TILING MACHINE TORE TWO HOLES IN THE PIPELINE LOCATED ON THE TOP HALF OF THE PIPE. THE UNLEADED GASOLINE THAT ESCAPED FROM THE PIPE THEN FLOWED DOWN THE DRAIN TILE BEING INSTALLED INTO A LOW LYING PASTURE AREA APPROXIMATELY 1000 FEET FROM THE POINT OF THE PUNCTURE. THE CONTRACTOR WAS ABLE TO STOP THE FLOW OF THE DRAIN TILE BY INSTALLING A TRENCH APPROXIMATELY 300 FEET DOWNSTREAM OF THE POINT OF THE RELEASE TO CAPTURE THE MAJORITY OF THE UNLEADED GASOLINE RECOVERED. THE PIPELINE WAS REPAIRED BY INSTALLING A SET OF FLANGES AND 3 OF PIPE. THE LINE WAS PUT BACK INTO SERVICE ON APRIL 28, 2000 AT 0900 HRS. THE FLANGE TIE-IN REPAIR METHOD USED IS CONSIDERED A TEMPORARY METHOD OF PIPELINE REPAIR FOR UNDERGROUND LINES, AND FLANGES WILL BE REMOVED WHEN FUEL OIL CAN BE RESCHEDULED INTO THE PIPELINE IN THE NEAR FUTURE. THE CONTRACTOR HAD NOTIFIED THE GOPHER STATE ONE CALL SYSTEM IN THE STATE OF MINNESOTA FOR WORK TAKING PLACE IN THE AREA, BUT DID NOT CALL IN A REQUEST FOR THE AREA THAT THE INCIDENT TOOK PLACE.
2017-09-29 08:50 | YES | NO | 20000062 | 2000-05-26 | 31147 | DYNEGY MIDSTREAM SERVICES INC | Null | 2000-05-16 | 1030 | LA | PLAQUEMINES |  | NO |  | NO | LOCATED WITHIN DYNEGY VENICE FACILITY. NOTIFIED NRC, STATE POLICE, LEPC AND LOCAL DOT @ 1230PM | 529119 | PUMPING STATION | PUMP |  | 1972 | OTHER | SEAL FAILURE ON PUMP | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 2031.1771 | 4097.7047 | PROPANE | 2 | 1 | 0 | YES | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JIMMY E OXFORD | 5045344050 | SEAL FAILED ON ETHANE PUMP CAUSING ETHANE TO BE RELEASED TO ATMOSPHERE. VAPORS WERE IGNITED (CAUSE TO BE DETERMINED) FIRE WAS PUT OUT IMMEDIATELY BY PLANT PERSONNEL. PUMP SUBSEQUENTLY BLOCKED IN. THIS IS A RARE OCCURRENCE FOR BOTH SIDES OF A TANDEM SEAL TO FAIL. WILL INSPECT CLOSELY WHEN REPLACING.
2017-09-29 08:50 | YES | NO | 20000063 | 2000-05-30 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 2000-04-24 | 1530 | KS | CHAUTAUQUA |  | NO |  | NO | SOUTH HALF SECTION 22, TOWNSHIP 33S, RANGE 12 E, 5 MILES NORTH OF PERU KS |  | LINE PIPE | NO DATA |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 81247.0848 | 163908.1871 | TRANSMIX (PART.REFINED PETRO) | 1 | 394 | 342 | NO | NO | 6.525 | 0.125 | 60000 | WELDED |  | 1632 | 1080 | YES | 24 | 2193 | 9 | 1982 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | JOHNY L CAVITT | 9185736336 | WE CONTACTED A CONTRACTOR WHO HAD MADE A ONE CALL ON 4/13/00, HOWEVER WERE NOT READY TO CROSS THE LINE AND SAID THEY WOULD CALL US BACK. THE CONTRACTOR WAITED UNTIL 4/24/00 TO START DIGGING TO CROSS OUR LINE BUT FAILED TO RECALL US NOR AS REQUIRED BY STATE ONE CALL LAW FOR A TICKET OVER 10 DAYS OLD TO PLACE A ONE CALL. ON THE AFTERNOON OF 4/24/00 OUR SCADA CONTROLS INDICATED A LOSS OF DISCHARGE PRESSURE AT OUR COFFEYVILLE STATION. EMERGENCY ACTIONS WERE TAKEN BY THE CONTROLLER TO SHUTDOWN THE LINE AND NOTIFY FIELD PERSONNEL TO INVESTIGATE. THE COFFEYVILLE STATION RECEIVED A CALL FROM THE CONTRACTOR THAT THEY HAD HIT OUR LINE. EMERGENCY RESPONSE GROUPS RESPONDED TO THE LOCATION AND APPROPRIATE ACTIONS TAKEN. THE LINE WAS REPAIR WITH NEW XRAYED PIPE AND PUT BACK IN SERVICE ON 4/25/00.
2017-09-29 08:50 | NO | NO | 20000064 | 2000-05-31 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-04-29 | 1802 |  |  |  | YES | 29,24,490" N - 89, 31', | NO | QUARANTINE BAY TANK BATTERY #1 TO OSTRICA TERMINAL 6" PIPELINE, NEAR PENNZOIL'S QUARANTINE BAY WAREHOUSE, ABOUT 1,000 FEET FROM CHEVRON PIPELINE RIGHT OF WAY |  | LINE PIPE | PIPE |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 40623.5424 | 81954.0935 | CRUDE OIL | 1 | 1 | 1 | NO | NO | 6 | 0 | 0 |  |  | 720 | 90 | Null | 0 | 0 | 0 | 0 |  | Null | YES |  |  |  |  | Null |  |  | Null | Null | KEITH GUILBEAU | 2815963562 | IN THE PROCESS OF TAKING THE QUARANTINE BAY PIPELINE OUT OF SERVICE, THE PIPELINE FAILED 90 PSI IN TWO PROXIMATE LOCATIONS. THIS OCCURRED WHILE IT WAS BEING DE-OILED WITH APPROXIMATELY 1,800 BARRELS OF BAY WATER. CPL WAS NOTIFIED OF THE SUSPECTED RELEASE BY PENNZOILS FIELD OPERATIONS SUPERVISOR, WHO OBSERVED THAT A SHEEN WAS LOCATED BEHIND OSTRICA. ALL PUMPS WERE IMMEDIATELY SHUTDOWN. PERSONNEL PROCEEDED TO THE POTENTIAL SHEEN SITE AND RAN THROUGH DIESEL SHEEN IN THE CHANNEL NEAR BATTERY 1, BUT FOUND NOTHING ON THE PIPELINE RIGHT OF WAY. UPON RETURNING TO THE WORK BARGE AND CONDUCTING FURTHER SURVEILLANCE OVER THE PIPELINE, A SHEEN NEAR THE BANK WAS DISCOVERED. CPL AND PSC (CONTRACTOR) PERSONNEL LOCATED OIL ON THE SHORELINE BEHIND THE QUARANTINE BAY WAREHOUSE, APPROXIMATELY 1000 FEET FROM THE PIPELINE RIGHT OF WAY. AMOUNT RELEASED WAS ESTIMATED AT 1 BARREL. APPROXIMATELY 1/2 BARREL WAS RECOVERED. COORDINATES OF THE TWO BREAKS IN THE LINE ARE AS FOLLOWS: LEAK #1:29, 24, 490N - 89, 31,126" W. LEAK #2: 29, 24, 380"N - 89, 31,127"W. THESE BREAKS WERE REPAIRED WITH CLAMPS. CPL PROMPTLY NOTIFIED THE NATIONAL RESPONSE CENTER ON 4/29/00 @18:05. NRC REPORT #527541 WAS TAKEN BY P O CHANCELLOR. THIS DOT FORM 7000-1 IS BEING PREPARED BECAUSE THE TOTAL COSTS AND ACCOUNTING SETTLEMENTS FROM THE CLEANUP AND REPAIR PROJECT HAVE BEEN RECENTLY TABULATED AND EXCEED THE $50,000 THRESHOLD REQUIRED FOR GENERATING THIS REPORT. THE BULK OF THE COSTS $55,000 ARE RELATED TO CLEAN UP OPERATIONS. THE OTHER $5,000 ARE MISCELLANEOUS COSTS.
2017-09-29 08:50 | YES | NO | 20000065 | 2000-05-31 | 11551 | LION OIL CO | NO | 2000-05-18 | 1100 | AR | UNION |  | NO |  | NO | 0.25 MILE SOUTH OF UNION COUNTY ROAD 10 (AKA SHULER RD) ON SALEM RD. APPROXIMATEL LAT/LON N33, 10.87' W 92 56.94 |  | LINE PIPE | PIPE |  | 1939 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 7400 | 5010.2369 | 10107.6715 | CRUDE OIL | 1 | 100 | 95 | NO | NO | 8 | 0.322 | 36000 | WELDED |  | 500 | 250 | YES | 20 | 960 | 8 | 1988 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOHN H WARREN | 8708461451 | A UNION COUNTY ROAD GRADER STRUCK LION OIL COMPANYS 8" MAGNOLIA MAIN LINE AT APPROXIMATELY 11:00 AM ON THURSDAY, MAY 18, 2000. THE GRADER BLADE PUNCTURED A HOLE IN THE PIPE WHICH RESULTED IN A LEAK. THE SUPPLY PUMP WAS SHUT DOWN AUTOMATICALLY DUE TO A DROP IN PRESSURE. APPROXIMATELY 100 BARRELS OF CRUDE OIL WAS RELEASED; THE MAJORITY OF THIS CRUDE OIL REMAINED IN THE ROAD DITCHES OR ON THE GRAVEL ROAD. THE GRADER OPERATOR CALLED HIS DISPATCHER WHO NOTIFIED LION OIL CO. A LION OIL CO CLEANUP CREW AND A REPAIR CREW WERE DISPATCHED TO THE SITE. CLEANUP OPERATIONS BEGAN IMMEDIATELY UPON ARRIVAL. THE SITE WAS SECURED AND TRAFFIC WAS REDIRECTED AROUND THE SITE UNTIL THERE WAS NO FIRE OR SAFETY HAZARD. RECOVERED CRUDE OIL WAS TAKEN TO LIONS SLOP TANK AT MAGNOLIA. THE DAMAGED SECTION OF THE PIPELINE WAS REMOVED AND A NEW SECTION OF PIPE WAS INSTALLED IN ITS PLACE. REPAIRS WERE MADE PER 49 CFR 95 REQUIREMENTS AND PER LION OIL COS MAINTENANCE MANUAL. PIPELINE MARKERS WERE IN PLACE AND VISIBLE AT THE TIME OF THE ACCIDENT.
2017-09-29 08:50 | YES | NO | 20000066 | 2000-06-07 | 443 | AMOCO PIPELINE CO | YES | 2000-05-06 | 1137 | MN | HENNEPIN | ROGERS | NO |  | NO | NEAR ROGERS, MN IN OPEN FARM FIELD AT MP474 ADDRESS IS 24910 TERRITORIAL RD., ROGERS MN | 528201 | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 203117.712 | 409770.4677 | GASOLINE | 3 | 425 | 300 | NO | NO | 8 | 0.28 | 35000 | WELDED |  | 1440 | 162 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DALE NEILAN | 7634254201 | LAND OWNER HAD CONTRACTED A CONTRACTOR TO PREPARE AREA FOR THE FUTURE CONSTRUCTION OF A POLL BARN. THIS REQUIRED THE EXCAVATION OF SOIL FROM ONE AREA TO ANOTHER TO BUILD UP THE AREA FOR THE BUILDING. CONTRACTOR STARTED THIS WORK ON A SATURDAY MORNING WITHOUT PERFORMING A STATE ONE CALL NOTICE.
2017-09-29 08:50 | NO | NO | 20000067 | 2000-06-07 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 2000-05-09 | 915 | MN |  |  | NO |  | NO | 148N, SECTION:2, QUARTER NE 1/4 OF SW 1/4 RANGE 37W, TRACT#: T-694, MERIDIAN: W OF 5TH | 528462 | LINE PIPE | OTHER | TIGHT FITTING REPAIR SLEEVE | 1998 | OTHER | FAILED SIDESEAM WELD OF REPAIR SLEEVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 55200 | 37373.659 | 75397.766 | CRUDE OIL |  | 25 | 20 | NO | NO | 34 | 0.344 | 52000 | WELDED |  | 758 | 630 | YES | 4 | 1047 | 10 | 1991 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null |  | 2187250102 | THE PATROL PILOT OBSERVED OIL POOLED ON THE GROUND IN A FIELD AT MP 913.5. FIELD VERIFICATION WAS IMMEDIATE AND RESPONSE CREWS WERE DISPATCHED. THE OIL WAS APPARENTLY LEAKING FROM SIDE SEAM ON AN EXISTING TIGHT-FITTING SLEEVE.
2017-09-29 08:50 | YES | NO | 20000068 | 2000-06-08 | 31147 | DYNEGY MIDSTREAM SERVICES INC | NO | 2000-05-09 | 1045 | LA |  | CAMERON | NO |  | YES | NE 1/4 SE 1/4, SEC 17, T-38, R-13W, CAMERON PARISH, LA, SABINE NATIONAL WILDLIFE REFUGE | 528486 | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | NATURAL GAS LIQUID |  | 845 | 1 | NO | NO | 6 | 0.219 | 2777 |  |  | 1976 | 950 | YES | 8 | 2470 | 0 | 1976 | EXTERNAL | Null | YES | OTHER | DISBONDED COATING |  |  | Null | ONE CALL |  | Null | Null | SOHRAB TAFRESHI | 3375834642 | ON 5/9/00 AT 10:45 AM , DYNEGY RECEIVED A REPORT FROM WILLIAMS FIELD SERVICES IN JOHNSON BAYOU, LA THAT A LEAK HAD BEEN SPOTTED IN A REMOTE AREA OF THE MARSH IN THE SABINE NATIONAL WILDLIFE REFUGE. BOTH COMPANIES OPERATE PIPELINE IN THE VICINITY OF THE REPORTED LEAK. DYNEGY MOBILIZED PERSONNEL AND EQUIPMENT NEEDED TO REACH THE LEAK SITE. AT 3:15 PM, DYNEGY PERSONNEL DETERMINED THAT THE LEAK WAS ORIGINATING FROM DYNEGYS PIPELINE AND BEGAN STEPS TO ISLOATE THE SECTION OF PIPLINE THAT WAS LEAKING. NO VAPOR CLOUD WAS PRESENT AND THERE WAS NO VISIBLE HYDROCARBON SHEEN ON THE WATER. THE LEAKING SECTION OF PIPELINE WAS COMPLETELY DEPRESSURED BY 2:00 AM ON 5/10/00. FURTHER INVESTIGATION OF THE LEAK SITE SHOWED SOME SIGNS OF A PROBABLE LIQUID HYDROCARBON CONTAMINATION. SAMPLES OF THE WATER AND SOLIDS IN THE AREA WERE COLLECTED FOR LAB ANALYSIS. THE SOLID MATERIAL IS COMMONLY KNOWN AS PIPELINE ROUGE.THE LIQUID HYDOCARBON EVAPORATED AND THE PIPIELINE ROUGE WAS RECOVERED. APPROXIMATELY 1 DRUM OF THE PIPELINE ROUGE WAS RECOVERED.
2017-09-29 08:50 | YES | NO | 20000069 | 2000-06-09 | 30922 | HYPERION ENERGY LP | NO | 2000-05-02 | 800 | TX | ANDERSON | NECHES FIELD | NO |  | NO | HERRINGTON A-1047 CO BLK NO 3C-A LOT 2 |  | LINE PIPE | PIPE |  | 1979 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 8124.7085 | 16390.8187 | CRUDE OIL | 1 | 850 | 840 | NO | NO | 10 | 0.349 | 24000 |  |  | 200 | 200 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | GERVARD R STUCKART | 2147501522 | CAUSED A LEAK IN PIPELINE OIL WAS SPOTTED DURING DAILY LINE PATROL AND WAS IN LOW AREA ON NORTH & SOUTH SIDE OF PIPELINE ROW. SPILL CENTRAL PROGRAM WENT INTO EFFECT AND APPROX 840 OF WAS RECOVERED. AREA WAS FLUSHED AND OIL REMOVED. REMAINING WAS BURNED. AREA WAS THEN REFLUSHED. TREATED WITH ABSORBENT MATERIAL AND CLEANED. LINE IS SCHEDULED TO BE REPLACED WHERE AREA DRIES.
2017-09-29 08:50 | YES | NO | 20000070 | 2000-06-13 | 30755 | CITGO PRODUCTS PIPELINE CO | YES | 2000-05-20 | 1100 | TX | HARRIS |  | NO |  | NO | KEP MAP PAGE 413 SECTION L NORTH WEST CORNER HARDY TOLL RD SOUTH OF ALDINE MAIL ROUTE SEE ATTACHMENTS | 529552 | LINE PIPE | PIPE |  | 1948 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 338529.5201 | 682950.7794 | GASOLINE | 3 | 481 | 100 | YES | NO | 10 | 0.307 | 35000 | WELDED |  | 1220 | 1050 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | JERRY FITZGERALD | 2814583936 | PER LABORATORY METALLURGICAL ANALYSIS, THE CAUSE OF THE LEAK WAS THE RESULT OF OUTSIDE FORCE DAMAGE RESULTING IN A DENT. THE DENT FAILED OR SPILT. THIS HAPPEN WITHOUT THE KNOWLEDGE OF CITGO. THE ESTIMATE DATE OF THE DAMAGE TO CITGOS PIPE IS UNKNOWN. THE BEST ESTIMATE THAT THE DAMAGE OCCURRED IS WRITTEN IN THE LAST 5 YEARS. CITGO RAN A CALIBER PIG IN SEGMENT OF PIPE 5 YEARS AGO THAT DID NOT IDENTIFY A DENT OF THIS SIZE IN THIS PARTICULAR LOCATION.
2017-09-29 08:50 | YES | NO | 20000071 | 2000-06-12 | 22387 | WEST EMERALD PIPE LINE CORP | YES | 2000-05-24 | 700 | NM |  | QUAY | NO |  | NO | FROM TUCUMCARI NM PROCEED 3 3/4 MILES NE ON US HIGHWAY 54, THEN EXIT N TO THE PUMP STATION. LEGAL DESCRIPTION: TOWNSHIP 11N RANGE 31E SECTION 4 | 529949 | PUMPING STATION | NO DATA |  | 1997 | OTHER | SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 365000 | 247126.5497 | 498554.069 | GASOLINE | 1 | 767 | 47 | YES | YES | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | BILL THOMPSON | 2105924692 | AT APPROXIMATELY 0700 HOURS ON MAY 24, 2000 THERE WAS A SEAL FAILURE ON THE PIPELINE PUMP WHICH FLOWED APPROXMIATELY 75 DOWNSLOPE TO THE CINDER BLOCK BUILDING HOUSING ELECTRONIC CONTROL EQUIPMENT. GASOLINE SURROUNDED THE BUILDING AND THE ACCUMULATED VAPOR INSIDE WAS IGNITED BY AN ELECTRIC SPARK. THE RESULTING EXPLOSION AND FIRE THEN FLASHED BACK TO THE PUMP IGNITING THE ENTIRE PUMP HOUSE AREA. WITHIN MINUTES OUR CENTRAL CONTROL CENTER WAS NOTIFIED OF THE FIRE AND LOCAL EMPLOYEES WERE IMMEDIATELY DISPATCHED TO IMPLEMENT PROCEDURES LIMITING PROCEDURE RELEASE. BY 08:31 THE INLET AND OUTLET VALVES WERE CLOSED. IT WAS DECIDED THAT THE LOCAL FIRE DEPARTMENT WHICH HAD BEEN ON SITE SINCE 07:51 WOULD NOT ATTEMPT TO EXTINGUISH THE FIRE BUT WOULD STANDBY WHILE FIRE BURNED ITSELF OUT. THE PUMPHOUSE AND CONTOL BUILDING WERE TOTALLY DESTROYED. NO PROPERTY OR FACILITIES OUTSIDE COMPANY PROPERTY WERE DAMAGED. CURRENTLY A NEW PUMPING FACILITY IS BEING BUILT ADJACENT TO THE DAMAGED EQUIPMENT AND SOIL REMEDIATION MEASURES ARE BEING EVALUATED. MOST OF THE PRODUCT RELEASED WAS CONSUMED IN THE FIRE.
2017-09-29 08:50 | YES | NO | 20000072 | 2000-06-13 | 3445 | DIXIE PIPELINE | YES | 2000-05-17 | 1530 | GA | BUTTS COUNTY |  | NO |  | NO | INCIDENT OCCURRED IN THE SE QUADRANT OF THE INTERSECTION OF I-75 AND SR 36 ON THE PROPERTY OF TRUCK STOP AMERICA. | 529277 | LINE PIPE | WELDING FITTING |  | 1967 | OTHER | BOLT TIGHTENING ON BLIND FLANGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | PROPANE | 2 | 0 | 0 | YES | NO | 8 | 0.188 | 2267 | WELDED |  | 1440 | 800 | YES | 8 | 2007 | 5 | 1991 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | CHRIS J GIRRENS | 7703962994 | MAY 17,2000 15:30 EDST DIXIE RECEIVED A REPORT FROM A PROPERTY OWNER OF A FLASH FIRE THAT HAD OCCURRED AT ATLANTA SOUTH TA TRUCK STOP IN THE VICINITY OF OUR PIPILINE. BEGIN SHUT DOWN & ISOLATION PROCEDURE. 15:40 EDST THE DIXIE PRODUCTS MOVEMENT CENTER DISPATCHER COMPLETED THE SHUT DOWN OF THE PIPELINE IN THE AREA OF CONCERN & MINIMIZED THE PIPELINE PRESSURE AND THE LINE SECTION WAS ISOLATED. DIXIE RESPONSE PERSONNEL FOUND NO VISIBLE SIGNS OF A LEAK. THE FLASH FIRE HAD OCCURRED IN 2 DIA BORED EXCAVATION ABOUT 7 DEEP. THE EXCAVATION HAD BEEN MADE ABOUT 2 WEEKS PRIOR & WAS IGNITED BY A WELDING OPERATION AT THE MOUTH OF THE HOLE. THE FIRE QUICKLY BURNED OUT. TWO INDIVIDUALS WERE INVOLVED IN PERFORMING THIS WORK BUT REQUIRED NO MEDICAL ATTENTION OR FIRST AID. THE MAJORITY OF THE PIPELINE RIGHT-OF-WAY ACROSS THIS PROPERTY IS ASPHALT PAVED. THE TRUCK STOP HAS FIVE UNDERGROUND FUEL STORAGE TANKS NEAR DIXIES RIGHT-OF-WAY. DIXIE PIPELINE CO. ATLANTA GAS LIGHT CO & THE TA TRUCK STOP WERE ALL TRYING TO DETERMINE THE SOURCE OF THE HYDROCARBON. SINCE WE COULD NOT RULE OURSELVES OUT AS A POSSIBLE SOURCE FOR THE HYDROCARBON THAT HAD ACCUMULATED IN THE EXCAVATION WE CONTINUED OUR INVESTIGATION. 18:30 EDST A COURTESY CALL WAS MADE TO THE NRC REPORT #529777 ALTHOUGH WE HAD NO POSITIVE SIGNS OF A LEAK FROM OUR PIPELINE. MAY 18, 2000 17:00 EDST COMPLETED DISPLACING THE PROPANE FROM THE PIPELINE SECTION WITH NITROGEN. A RECORDS SEARCH INDICATED THE PRESENCE OF 4 FITTINGS THAT HAD BEEN WELDED TO THIS PIPELINE IN 1967 TO FACILITATE A PIPELINE REROUTE FOR THE CONSTRUCTION OF INTERSTATE 75. MAY 19,2000 EXCAVATED 1 FITTING (8"WELD ON STOPPLE FITTING) & FOUND IT LEKAING NITROGEN. CONTINUED EXCAVATION TO CHECK THE REMAINING 3 FITTINGS (2" TOR FITTING, 8" WELD+END, & 8"X4" BYPASS FITTING). NONE OF THESE 2 WERE LEAKING. MAY 20, 2000 COMPLETE PREPARATIONS TO CUT OUT ALL 4 FITTINGS. MAY 21,2000 CUT OUT APPROXIMATELY 100 OF PIPE CONTAINING THE 4 FITTING & REPLACE WITH 100 OF HYDROTESTED PIPE. MAY 22,2000 APPROXIMATELY 10:00 EDST- NOTIFIED MR. BENNIE ANDREWS, OFFICE OF PIPELINE SAFETY SOUTHERN REGION THAT A SMALL LEAK HAD BEEN FOUND & REPARIED HOWEVER THE LAB TEST HAD BEEN PERFORMED THUS FAR HAD BEEN INCONCLUSIVE IN CLASSIFYING THE SPECIFIC HYDROCARBON SAMPLED FROM THE EXCAVATION. 14:30 RDST RETURNED THE LINE TO SERVICE. MAY 26, 2000 RECEIVED LABORATORY RESULTS THAT INDICATED THE PRESENCE OF PROPANE VAPOR IN THE AIR GRAB SAMPLE TAKEN FROM THE BORED HOLE WHERE THE FLASH FIRE OCCURRED.
2017-09-29 08:50 | YES | YES | 20000073 | 2000-06-09 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-05-09 | 913 | TX | GLASSCOCK |  | NO |  | NO | 8 MIDKIFF TO LEE'S PIPELINE (WEST TEXAS LPG) AT MP 155.6 9 MILES N OF GARDEN CITY, TX AND 1 MILE NW OF RANCH ROAD 33 42 T2S BLK 33 T&PRR, GLASSCOCK COUNTY, TEXA | 528437 | LINE PIPE | PIPE |  | 1997 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 115000 | 77861.7896 | 157078.6793 | L. P. G. | 2 | 4180 | 0 | NO | NO | 8 | 0.188 | 1881 | WELDED |  | 1185 | 399 | YES | 8 | 1817 | 3 | 1973 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | Null | KATHLEEN K. BALDWIN | 2815963569 | AT 09:13 LEES STATION PUMP WENT DOWN ON LOW SUCTION AND PRESSURE CONTINUED TO DROP. CHEVRON PIPE LINE (CPL) CUSTOMER SERVICE CENTER (CSC) CONTROLLER NOTICED THE PRESSURE DROP AND STARTED INVESTIGATING THE CAUSE. HE SUSPECTED A LEAK AND DISPATCHED CPL TECHNICIAN TO INVESTIGATE AT 09:45 A SHERIFF FROM GLASSCOCK COUNTY CALLED THE CSC TO REPORT A LEAK (NEIGHBOR AT SCENE REPORTED INCIDENT TO SHERIFFS DEPT. THE CONTROLLER IMMEDIATELY NOTIFIED CONOCO-STERLING AND DAVIS-STILES TO SHUT DOWN (STERLING SHUTDOWN AT 10:05 STILES SHUT DOWN AT 10:45). A PRIVATE LAND OWNER REPAIRING A STOCK TANK DAM WITH A BULLDOZER SEVERED THE 8" PIPELINE FROM MIDKIFF TO LEES STATION AT MP 155.6 CAUSING THE RELEASE AND PRESSURE LOSS. THE OPERATOR OF THE BULLDOZER BROKE HIS LEG JUMPING OFF THE BULL DOZER AFTER HE HIT THE PIPELINE. THERE WAS NO FIRE. AT 10:10, CPL OPERATOR ARRIVED AT THE SCENE. THE SHERIFFS DEPARTMENT HAD THE ROAD CLOSED AND 2 FIRE TRUCKS AND AN AMBULANCE WERE ALSO ON THE SCENE. AN INCIDENT COMMAND POST WAS SETUP AND THE LEAK SITE WAS SECURED FROM PUBLIC ACCESS. AT 10:40 AN 8" BLOCK VALVE WAS CLOSED TO REDUCE PRODUCT LOSS ON THE MIDKIFF TO LEES LINE AND VALVES WERE CLOSED TO ISOLATE LEES STATION. CPL PIPELINE WARNING SIGNS WERE LOCATED WITHIN 200 FEET OF EITHER SIDE OF THE DOZER AND WERE CLEARLY VISABLE TO THE EQUIPMENT OPERATOR. NO DIG TESS NOTIFICATION WAS MADE PRIOR TO OPERATOR EXCAVATION. AGENCY NOTIFICATIONS: NATIONAL RESPONSE CENTER (NRC REPORT 528437) ON 05/09/00 @ 10:32 JAMES RAINE. OTHER NOTIFICATIONS: TNRCC, TRC OIL & GAS DIV DOT, TESS SERC & LEPC WERE CONTACTED BETWEEN 10:37 AND 11:10 ON 05/09/00 AND WERE UPDATED PERIODICALLY BY CPLS EMERGENCY RESPONSE SPECIALIST. EPA REGION 6 WAS ALSO CONTACTED @ 16:58
2017-09-29 08:50 | YES | NO | 20000074 | 2000-06-19 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 2000-05-17 | 710 | CA |  | YOLO | NO |  | NO | RAILROAD RIGHT OF WAY, EASTSIDE OF YOLO CAUSEWAY, NORTH OF UPRR TRACKS IN YOLO COUNTY, CA |  | LINE PIPE | PIPE |  | 1967 | OTHER | LEAK IN ERW SEAM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 304676.5681 | 614655.7015 | DIESEL FUEL |  | 0 | 0 | NO | NO | 14 | 0.219 | 52000 | WELDED |  | 950 | 241 | YES | 24 | 1464 | 12 | 1967 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD FANT | 7138449526 | THIS RELEASE APPEARS TO BE DUE TO A LEAK IN THE ERW SEAM OF AN 14 INCH PIPELINE.
2017-09-29 08:50 | YES | NO | 20000075 | 2000-06-26 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-05-21 | 1300 | TX | FREESTONE |  | NO |  | NO | WORTHAM STATION 3 MILES EAST OF WORTHAM ON HIGHWAY 27 WORTHAM TX 76693 |  | TANK FARM | NO DATA |  | 0 | OTHER | FAILED VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 35400 | 23967.89 | 48352.9152 | CRUDE OIL | 1 | 620 | 607 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J RANDY BURKE | 2815963569 | AN 8" VALVE ON A TEMPORARY 8" PIPELINE BETWEEN OUT OF SERVICE TANKS #24 AND #25 TO IN SERVICE TANK #43 FRACTURED. RELEASING 620 BARRELS OF WEST TEXAS SOUR CRUDE OIL INSIDE CPLS WORTHAM STATION FACILITY. THE ORIGINAL VOLUME WAS ESTIMATED AT 1,000 BBLS, BUT WAS RECALCULATED TO BE 620 BBLS BASED ON LINE FILL CAPACITY. WE RECOVERED 607 BBLS AND THE REMAINING 13 BBLS IN THE SOIL WAS REMEDIATED ON SITE. THE VALVE FAILED AFTER ITS THIRD DAY IN USE FOR THIS JOB AND CPL IS INVESTIGATING THE ROOT CAUSE FOR THE VALVE THROUGH METALLUGICAL AND STRESS ANALYSIS. AGENCY NOTIFICATIONS: NATIONAL RESPONSE CENTER (NRC REPORT # 529624) ON 05/21/2000 @ 12:30- MR. STEELE. OTHER NOTIFICATIONS: 12:40 JEFF @ TNRCC. 12:45-DISPATCHER @ TRC OIL & GAS DIVISION 12:55- LT TAYLOR (SHERIFF DEPT) @ FREESTONE COUNTY (LEPC) 13:10- DEAN @ STATE EMERGENCY RESPONSE COMMISSION (SERC) 800-832-8224, REPORT # 20001217. AGENCIES ON SITE: SITE VISIT BY TRC OIL & GAS DIVISION DISTRICT 6, SAM NAYFA, 5-21-00 @ 4:00 PM PHONE (903-984-3026 EXT 619. SITE VISIT BY TRC OIL & GAS DIVISION DISTRICT 6 ROGER SATERWHITE, 5-22-00 @ 1:00. REPORT NUMBER 05-311. SITE VISIT BY DOT, RICHARD LOPEZ, 5-22-00 @ 4:15PM.
2017-09-29 08:50 | YES | NO | 20000076 | 2000-06-27 | 31045 | GENESIS CRUDE OIL LP | NO | 2000-05-21 | 1750 | TX | MATAGORDA | BAY CITY | NO |  | NO | WEST OF THE COLORADO RIVER, NORTH SIDE OF STATE HIGHWAY 35 BEHIND JOE BURTON LUMBER CO. ON THE MILLER RANCH |  | LINE PIPE | NO DATA |  | 1941 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 61406 | 41575.4874 | 83874.5511 | CRUDE OIL | 1 | 150 | 90 | NO | NO | 8 | 0.188 | 35000 | WELDED |  | 190 | 145 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | IMPRESSED |  |  | Null |  |  | Null | Null | BARRY DAVIS | 7139602750 | MR. DANIEL MILLER OF THE MILLER RANCH CALLED THE OPERATION CONTROL CENTER @ APPROXIMATELY 1750 HOURS AND REPORTED A STRONG PETROLEUM SMELL AT HIS RANCH ENTRANCE GATE. HE DID NOT SEE ANY PETROLEUM ON THE GROUND. FIELD OPERATIONS PERSONNEL WAS DISPATCHED TO THE LOCATION AND DISCOVERED CRUDE OIL IN THE DRAINAGE DITCH AT THE ENTRANCE TO THE MILLER RANCH. EMERGENCY RESPONSE WAS ACTIVATED AT THIS TIME.
2017-09-29 08:50 | YES | NO | 20000077 | 2000-07-06 | 18718 | SUN PIPE LINE CO | NO | 2000-05-31 | 600 | TX | GRAY |  | NO |  | NO | SECTION 10 BLOCK 30 H & GN R.R. SURVEY |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1015.5886 | 2048.8523 | CRUDE OIL | 1 | 50 | 0 | NO | NO | 6 | 0.28 | 24000 | THREADED |  | 405 | 310 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER |  |  |  | Null |  |  | Null | Null | EDITH F COEN | 9185866942 | ON WEDNESDAY MAY 31, 5:30 PM A PIPELINE WALKING CREW FOUND A DRY OIL STAIN ON TOP OF THE GROUND. THE STAIN WAS 5" IN DIAMETER. THE PIPE WAS EXCAVATED AND A TEMPORARY LEAK CLAMP INSTALLED. SOIL REMEDIATION BEGAN IMMEDIATELY. SOIL SAMPLES HAVE BEEN ANALYZED AND REMEDIATED. SOIL WILL BE BACKFILLED THE WEEK OF JULY 3RD.
2017-09-29 08:50 | YES | NO | 20000078 | 2000-07-05 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-06-12 | 925 | KS |  | ELDORADO | NO |  | NO | EL DORADO TANK FARM, 3913 SW 10TH STREET, ELDORADO, KANSAS |  | TANK FARM | PIPE |  | 1976 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 7500 | 5077.9428 | 10244.2617 | CRUDE OIL | 1 | 135 | 120 | NO | NO | 20 | 0.25 | 42000 | WELDED |  | 275 | 35 | YES | 8 | 350 | 0 | 1976 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | THE SECTION OF PIPE ON WHICH THE LEAK OCCURRED WAS A PIECE OF DEAD LEG PIPING. A TEMPORARY CLAMP WAS INSTALLED AND A PERMANENT REPAIR WILL BE MADE. THE DEAD LEG WILL BE REMOVED.
2017-09-29 08:50 | YES | NO | 20000079 | 2000-07-05 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-01-31 | 1130 | LA |  | PLAQUEMINES | NO |  | NO | MILE POLE 45.9 PORT SULPHUR (JUST OFF GRAND BAYOU) | 518309 | LINE PIPE | PIPE |  | 1959 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 245052 | 165914.6719 | 334716.9088 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 20 | 0.25 | 52000 | WELDED |  | 830 | 431 | YES | 24 | 1040 | 0 | 1959 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F SHEAFF | 7132414381 | THE RELEASE WAS CAUSED BY PIPE LAMINATION WHICH IN TURN CAUSED A FATIGUE CRACK. RELEASE WAS CONTAINED WITHIN SORBENT BOOM DEPLOYED.
2017-09-29 08:50 | YES | NO | 20000080 | 2000-07-05 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-06-01 | 1500 | NM | DONA ANA |  | NO |  | YES | 8" EL PASO TO ALBUQUERQUE PRODUCTS PIPELINE @ MP 62.7 5 MILES NORTH OF LAS CRUCES, NEW MEXICO T21S-R2E-SEC 21 | 530770 | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 77861.7896 | 157078.6793 | DIESEL FUEL | 1 | 1770 | 240 | NO | NO | 8 | 0.25 | 42000 | WELDED |  | 1720 | 1600 | YES | 8 | 2150 | 0 | 1981 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RANDY J BURKE | 2815963569 | A DONA ANA COUNTY ROAD GRADER (THIRD PARTY) HIT OUR 8" DIESEL PRODUCTS LINE & RELEASED 1,770 BARRELS OF DIESEL ONTO THE GROUND & SOIL. APPROXIMATELY 240 BARRELS WERE RECOVERED. THE COUNTY EQUIPMENT HAD FINISHED DOING SURFACE WORK TO THE ROAD WHEN HE BEGAN TO SCRATCH A DRAINAGE CHANNEL AT THE SIDE OF THE ROAD. THE ROAD GRADER SCRATCHED A CHANNEL ABOUT 8" TO 9" DEEP WHEN THE PIPELINE WAS HIT. NO PREVIOUS ONE CALL NOTIFICATIONS WERE MADE BY THE COUNTY. THE DAMAGED PORTION OF PIPE WAS LATER REPLACED ON 06-03-00. THE SPILL OCCURRED IN A REMOTE DESERT AREA ON DEPARTMENT OF AGRICULTURE LAND WITHIN THE JORNADA EXPERIMENTAL GRASSLAND RANGE. (THIS AREA HAS A LOW WATER TABLE AND IS ABOUT 5 1/2 MILES FROM THE CLOSET BODY OF WATER. A SITE REMEDIATION TEAM FROM CHEVRON PIPE LINE COMPANY WAS SENT TO THE RELEASE SITE TO ASSESS THE SITUATION. DONA ANA COUNTY PERSONNEL HELPED CHEVRON PIPE LINE (CPL) DURING THE INITIAL EMERGENCY RESPONSE. COSTS GENERATED BY CPL ARE ESTIMATED AT $50,000 FOR INITIAL RESPONSE CLEANUP AND REPAIR WORK WITH ANOTHER $65,000 FORECASTED FOR SITE REMEDIATION WORK DURING THE NEXT 9 TO 12 MONTHS. AGENCY NOTIFICATIONS: LAS CRUCES OFFICE OF EMERGENCY MGMT (LEPC/SERC) -06-01-00 @ 15:50 (DELIA @ 505-527-8741) DOT-06/01/00 15:50 (ROD SEELEY) NATIONAL RESPONSE CENTER -06/01/00 @ 15:57 (LT. THOMAS REPORT #530770) NEW MEXICO CONSERVATION COMMISSION # 2 (TIM GUM, DISTRICT SUPVR.
2017-09-29 08:50 | YES | NO | 20000081 | 2000-07-03 | 15490 | PHILLIPS PIPE LINE CO | YES | 2000-06-02 | 1030 | CO |  | LINCOLN | NO |  | NO | BORGER-DENVER LINE MP 254-50+49 SEC 22, T165S, R58W, LINCOLN CO, COLORADO 20 MILES SOUTHEAST OF RUSH CO |  | LINE PIPE | PIPE |  | 1971 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 118485.332 | 239032.7728 | DIESEL FUEL | 1 | 60 | 0 | NO | NO | 8.625 | 0.156 | 52000 | WELDED |  | 1350 | 966 | YES | 24 | 1823 | 5 | 1971 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LINUS J SCHMITZ | 9186614814 | COMPANY CONTRACTOR DISCOVERED DIESEL STAIN ON RIGHT OF WAY. THE PIPE WAS REPLACED AND THE SITE IS BEING CLEANED UP. LOCALIZED COLD WELD IN PIPE SEAM CAUSED RELEASE.
2017-09-29 08:50 | YES | NO | 20000082 | 2000-07-10 | 30899 | WOLVERINE PIPELINE COMPANY | YES | 2000-06-07 | 845 | MI |  | JACKSON | NO |  | NO | 2101 MORRELL ROAD, JACKSON, MI ( JACKSON STATION ADDRESS) INCIDENT JUST OUTSIDE STATION FENCE ON WOLVERINE PIPELINE PROPERTY. | 531316 | LINE PIPE | OTHER | STOPPLE FITTING WELD | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 677059.0401 | 1365901.5589 | GASOLINE | 3 | 1700 | 1361 | NO | NO | 16 | 0.312 | 48000 | WELDED |  | 1325 | 900 | YES | 24 | 1665 | 9 | 1975 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JOEL C LARKIN | 7136560227 | ON JUNE 7, 2000, AT APPROXIMATE 0845 EDT, DALLAS CONTROL CENTER WAS MONITORING PRESSURE AND FLOW ASSOCIATED WITH SWITCHING TERMINAL DELIVERIES. ONCE FLOW WAS ESTABLISHED INTO FREEDOM STATION, FLOW AND PRESSURE ALARMS AND FLUCTUATIONS WERE NOTED. THE LINE WAS SHUT DOWN AND BLOCKED IN. A PRESSURE DROP WAS NOTED BETWEEN JACKSON STATION AND FREEDOM STATION, PROMPTING WOLVERINE PERSONNEL TO BE DISPATCHED TO MAJOR ROAD AND WATER CROSSINGS. AN EMPLOYEE DISPATCHED TO JACKSON STATION OBSERVED A LEAK JUST OUTSIDE THE JACKSON STATION FENCE. A VALVE LINEUP WAS MADE ALLOWING PRODUCT TO DIVERT TO THE CITGO TERMINAL. RESPONSE PERSONNEL WERE DISPATCHED TO CONTAIN AND DELINEATE THE RELEASE. THE RAIL TRAFFIC WAS SHUT DOWN, POWER WAS TURNED OFF, AND EVACUATIONS WERE CONDUCTED. APPROPRIATE AGENCY NOTIFICATIONS WERE MADE. A STOPPLE FITTING WAS FOUND TO BE THE SOURCE OF THE RELEASE. THE STOPPLE WAS CUT OUT AND REPLACED WITH NEW PIPE.
2017-09-29 08:50 | YES | NO | 20000083 | 2000-07-17 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | NO | 2000-06-13 | 915 | CA | LOS ANGELES | CARSON | NO |  | NO | 2303 EAST 223RD STREET, CARSON, CA 90745 PIPELINE MILEPOST 5.89 (STATIONING) 459+99) | 531971 | LINE PIPE | PIPE |  | 1922 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 406235.4241 | 819540.9353 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 8 | 0.322 | 0 | WELDED |  | 0 | 25 | YES | 0 | 0 | 0 | 0 |  | Null | NO |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GARY SAENZ, DOT SPECIALIST | 2815963568 | IN A PROACTIVE EFFORT TO PURGE IDLED SYSTEMS OF HYDROCARBONS, THE CHEVRON PIPELINE LOS ANGELES TEAM WAS CONDUCTING LINE PURGING ON A 5,000 FOOT SEGMENT OF THE 8" HYNES TO SAN PEDRO PIPELINE SYSTEM. LINE DISPLACEMENT WAS DONE USING NITROGEN PUSHING A PIG. APPROXIMATELY 3 BARRELLS OF OIL WAS RELEASED ONTO THE CITY STREET DURING PIGGING OPERATIONS AND MADE ITS WAY TO A STORM DRAIN. IT WAS DETERMINED THAT THERE WAS A 6" X 18" HOLE IN THE IDLED PIPELINE CAUSED BY PREVIOUS THIRD PARTY DAMAGE. THERE WERE TWO OTHER SECTIONS THAT WERE GOUGED OUT NEARBY. WATER WAS THE SECONDARY RECEIVING MEDIUM IN THIS (DOMINGUEZ CHANNEL). APPROXIMATELY 99% OF ALL OIL WAS RECOVERED.. CHEVRON WAS ONSITE AND IMMEDIATELY ACTIVATED THE UNIFIED COMMAND SYSTEM. BOOM WAS PRE-POSITIONED FOR PREVENTIVE OPERATIONS AND KEPT IN PLACE THROUGHOUT THE PROJECT. DAMAGES ARE ESTIMATED AT $200K & CLEANUP COSTS AT $400K.. TOTALS COSTS = $600,000.
2017-09-29 08:50 | YES | NO | 20000084 | 2000-07-28 | 31415 | PREMCOR PORT ARTHUR PIPELINE COMPANY | YES | 2000-06-24 | 2315 | TX | BEAUMONT | JEFFERSON | NO |  | NO | IN LUCAS SECTION TANK FARM TANK 1497 |  | TANK FARM | TANK |  | 1926 | OTHER | GAUGING SYSTEM FAILED, ALARM DID NOT GO OFF | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10155.8856 | 20488.5234 | CRUDE OIL | 1 | 200 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | MARY CLAIR HAYDEN | 4099851110 | NIGHT OPERATORS CAME ON SHIFT AT 5:30 PM, JUNE 24, 2000. AT THAT TIME, INITIATING TRANSFERRING CRUDE OIL FROM TANK 1671 TO TANKS 1497, 1525. TANK 1522 FILLED AT 7:35 PM.INITIATED FILL TO TANK 1497 AT 7:45 PM. GAUGE READ TO 363" AND STOPPED READING. THE NO FLOW ALARM DID NOT ALARM. THE MAXIMUM FILL HEIGHT IS 366". HIGH LEVEL ALARM IS 360" AND HIGH IS AT 363". THE ALARM DID NOT GO OFF. THE TANK FARM GAUGER WENT TO GET TANK AT 11:15 PM AND OIL WAS COMING OUT THE TANK VENTS. GAUGER IMMEDIATELY CALLED HEAD OPERATOR TO STOP FLOW AND SWITCHED THE TANK TO ANOTHER LOW TANK (TANK 1525) UNTIL LEAK STOPPED. TANK 1497 BROUGHT TO 340". TANK GAUGER ENSURED THAT THE OIL WAS CONTAINED IN THE TANK LEVEE. THE TERMINAL SUPERVISOR AND THE SPILL RESPONSE CREW WAS CALLED AT 11:30. CONTACTED REFINERY SHIFT SUPERINTENDENT AND THE ENVIRONMENTAL SPECIALIST. SPILL RESPONSE CREWS STARTED ARRIVAL APPROXIMATELY 11:45. INCIDENT COMMAND CONDUCTED A SITE ASSESSMENT. THE SITE ASSESSMENT REVEALED A SMALL LEAK IN THE TANK LEVEE DRAIN. CRUDE OIL WAS SEEPING INTO THE TANK FARM DRAINAGE DITCH. THE ENTIRE WEST TANK FARM (APPROXIMATELY 400 ACRES) DRAINS THROUGH TWO NPDES OUTFALLS AND ARE COMPLETELY CONTAINED. THE FACILITY BACKHOE WAS USED TO DAM THE LEAKING DRAIN. INITIAL ESTIMATE WAS ONLY 45 BARRELS. RRC WAS NOTIFIED OF SPILL AT 12:05 AM. SPILL CREW ARRIVED AT 6:45 AM TO REEVALUATE SPILL. SPILL WAS DETERMINED TO BE APPROXIMATELY 200 BARRELS. THE NATIONAL RESPONSE CENTER WAS CALLED AT 7:30AM. RECEIVED CALLS BACK FROM THE FOLLOWING AGENCIES: EPA-REAGAN BOYLES, TNRCC- GREG CONNLEY, RRC- MARY MCDANIAL. ALL FREE OIL WAS PICKED UP BY VACUUM TRUCK AND RETURNED TO TANKAGE ONSITE BY 1:00 PM. RECEIVED CALL FROM EPA THAT AN INSPECTOR AND DOCUMENTATION CONTRACTOR WERE IN ROUTE TO LUCAS AND WOULD ARRIVE AT APPROX. 3:30PM. LON BIASCO WITH THE EPA ARRIVED ONSITE ALONG WITH THE TWO CONTRACTORS JENNIFER KENNEDY AND ROBERTA HAGLUND. THEY TOURED SITE AND AGREED WITH THE SPILL CLEAN UP PROGRESS AND PLAN. SPILL CREW RETURNED TO SITE ON MONDAY JUNE 26TH, PICKED UP LESS THE 2 BARRELS OF OIL, AND STARTED REMOVING SOIL TO ONSITE REMEDIATION PADS. THESE SOILS WILL REMAIN ON THE PADS UNTIL THE REQUIRED CLEANUP LEVELS HAVE BEEN ACHIEVED. CREWS BEGAN WASHING DOWN TANK. C.R. GRANDY WITH THE RRC VISITED AND APPROVED OF THE CLEANUP. SPOKE ON THE PHONE WITH THE FOLLOWING AND THEY AGREED THAT THIS SPILL WAS RRC JURISDICTION:DOT-RICHARD LOPEZ, US COAST GAURD- JASON IHENFIELD. CLEAN UP WAS COMPLETED BY 06/29/00. CONFIRMATION SOIL SAMPLES WERE COLLECTED JULY 5, 2000. A MAP OF THE SAMPLE LOCATIONS AND THE ANALYTICAL RESULTS ARE ATTACHED. ALL SAMPLES RESULTS WERE BELOW 1% BY WEIGHT TOTAL PETROLEUM HYDROCARBONS.
2017-09-29 08:50 | YES | NO | 20000085 | 2000-08-03 | 1845 | BUCKEYE PIPELINE CO LP | YES | 2000-07-07 | 1945 | OH | ALLEN | SHAWNEE | NO |  | NO | SEE ATTACHED DRAWING NUMBER 11884-A |  | LINE PIPE | PIPE |  | 1955 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 88017.6752 | 177567.2027 | TURBINE FUEL | 3 | 24 | 24 | NO | NO | 8 | 0.322 | 2610 | WELDED |  | 850 | 600 | YES | 24 | 1068 | 9 | 1994 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | CARL A OSTACH | 6107704495 | ON FRIDAY, JULY 7, 2000 AT 1945 HOURS, BUCKEYE PIPE LINE COMPANYS LIMA STATION RECEIVED A TELEPHONE CALL FROM A PROPERTY OWNER REPORTING PRODUCT ON BUCKEYES RIGHT-OF-WAY. THE PIPELINE WAS SHUT DOWN IMMEDIATELY AND A CREW WAS DISPATCHED TO THE SITE. AFTER FURTHER INVESTIGATION, IT WAS DISCOVERED THAT THE PIPELINE WAS DAMAGED FOR A LENGTH OF APPROXIMATELY 10 FEET. IT WAS EVIDENT THAT THE DAMAGE HAD BEEN CAUSED SEVERAL YEARS AGO BY THIRD PARTY EXCAVATION. THE PIPELINE WAS TEMPORARILY REPAIRED BY INSTALLING A SLEEVE ON SATURDAY, JULY 8, 2000. PERMANENT REPAIRS WERE MADE BY REPLACING THE DAMAGED PIPE WITH CERTIFIED REPALCEMENT PIPE ON SUNDAY, JULY 9, 2000. ALL APPLICABLE REGULATORY AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE PERFORMED UNDER THE SUPERVISION OF THE OHIO ENVIRONMENTAL PROTECTION AGENCY, ALLEN COUNTY EMERGENCY MANAGEMENT AGENCY, AND THE SHAWNEE FIRE DEPARTMENT.
2017-09-29 08:50 | YES | NO | 20000086 | 2000-08-01 | 30829 | TEPPCO | NO | 2000-06-25 | 1745 | TX | FAYETTE | LA GRANGE | NO |  | NO | FROM LAGRANGE GO WEST ON HWY 31 TO PRAIRIE VALLEY ROAD, THEN NORTH ON PRAIRIE VALLEY ROAD TO THE OLD PLUM HWY, THEN EAST ON OLD PLUM FOR 2/10 MILE AND SOUTH INT | 533491 | LINE PIPE | PIPE |  | 1929 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | CRUDE OIL | 1 | 100 | 50 | NO | NO | 12 | 0.375 | 25000 | WELDED |  | 150 | 50 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | MICRO-BACTERIAL |  |  | Null |  |  | Null | Null | FRED E CLAKLEY | 4052395716 | CORROSION CAUSED A LEAK IN THE PIPELINE IN THE CASING OF A RAILROAD CROSSING. THE LEAK WAS DETECTED WHEN OIL RAN OUT OF THE VENTS ON BOTH SIDES OF THE CROSSING. THE VOLUME THAT IMPACTED THE SURFACE AT THE VENTS WAS APPROXIMATELY 20 BARRELS, HOWEVER ADDITIONAL CRUDE OIL LEAKED INTO THE SOIL FROM THE CASING BOOT. THE CLEANUP OF THE SURFACE IMPACT IS COMPLETE; HOWEVER THE SUB SURFACE CLEANUP IS ONGOING AT THIS TIME. THE SEGMENT OF PIPE UNDER THE RAILROAD CROSSING WAS REPALCED AND THE ENTIRE PIPELINE IS CURRENTLY BEING RECONDITIONED AND HYDROSTATIC TESTED.
2017-09-29 08:50 | YES | NO | 20000087 | 2000-08-04 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2000-07-06 | 1155 | TX | ANGELINA |  | NO |  | NO | .3 MILES WEST OF ANGELINA COUNTY ROAD 73A. AT A POINT APPROX. 1/4 MILE NORTH OF THE INTERSECTION OF CR73A AND FM 843 |  | LINE PIPE | PIPE |  | 1931 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 345656 | 234029.5196 | 472132.0692 | CRUDE OIL |  | 607 | 456 | NO | NO | 12 | 0.303 | 35000 | WELDED |  | 720 | 228 | YES | 8 | 922 | 4 | 2000 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.F. SHEAFF | 7132414381 | A CONTRACTOR WORKING FOR TEMPLE INLAND FOREST CORPORATION STRUCK AND PUNCTURED THE PIPELINE WITH DEEP PLOWING EQUIPMENT. THE PIPELINE WAS IN OPERATION AT THE TIME AND TRANSPORTING CRUDE OIL TO THE LONGVIEW, TX AREA. THE PIPELINE CONTROL CENTER IMMEDITELY RECEIVED AN ALARM INDICATING A CHANGE IN PRESSURE AND A INCREASE IN FLOW FROM THE SOURCE AND IMMEDIATELY SHUT THE LINE DOWN.
2017-09-29 08:50 | YES | NO | 20000088 | 2000-08-04 | 22430 | WEST SHORE PIPELINE CO | YES | 2000-07-05 | 1420 | IL |  | WINNEBAGO COUNTY | NO |  | NO | SEE ATTACHED | 534424 | LINE PIPE | PIPE |  | 1954 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 50779.428 | 102442.6169 | GASOLINE | 1 | 132 | 64 | NO | NO | 12 | 0.25 | 46000 | WELDED |  | 1000 | 125 | YES | 8 | 1361 | 10 | 1999 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JAY ANDREWS | 8474390270 | THE PIPELINE WAS DAMAGED BY A BULLDOZER WORKING OVER THE PIPELINE MOVING COMPOST PILES. THE DAMAGE RESULTED IN A RELEASE OF PRODUCT. A REPRESENTATIVE OF THE COMPOST COMPANY OBTAINED THE EMERGENCY NUMBER FOR WEST SHORE FROM THE LINE MARKERS LOCATED AT THE SITE. THE PIPELINE CONTROL CENTER WAS CONTACTED TO SHUT DOWN THE PIPELINE. PIPELINE PERSONNEL NEARBY WERE DISPATCHED TO THE LOCATION TO VERIFY THE LEAK. BLOCK VALVES WERE CLOSED TO ISOLATE THE LEAK LOCATION. SPILL RESPONSE CONTRACTORS WERE CONTACTED TO BEGIN CLEANUP.NOTIFICATIONS WERE MADE TO LOCAL, STATE AND FEDERAL AGENCIES. THE PIPELINE WAS EXPOSED ACROSS THE PROPERTY TO VERIFY THAT NO OTHER DAMAGE WAS PRESENT. THE DAMAGED SECTION WAS REMOVED AND REPLACED AND THE PIPELINE WAS PUT BACK IN SERVICE THREE DAYS LATER.
2017-09-29 08:50 | YES | NO | 20000089 | 2000-08-15 | 15490 | PHILLIPS PIPE LINE CO | YES | 2000-07-26 | 1025 | IL | MACON |  | NO |  | NO | BORGER-E. CHICAGO-DECATUR TERMINAL-MP 801 SEC. 11, T17N. R2E, MACON CO.226 E. SHAFER ST. FORSYTH, IL 62235 |  | LINE PIPE | VALVE |  | 1981 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 3100 | 2098.883 | 4234.2948 | PROPANE | 2 | 40 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | NO | YES | LINUS J. SCHMITZ | 9186614814 | BACKHOE
2017-09-29 08:50 | YES | NO | 20000090 | 2000-08-08 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 2000-07-20 | 1100 | TX | REAGAN |  | NO |  | NO | TNP R&R CO. T-5- BLK 37 GPS: 31 34. 30N 101 45.54 W | 536009 | NO DATA | NO DATA |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 1100 | 25 | NO | NO | 10 | 0.365 | 24000 | WELDED |  | 720 | 333 | YES | 8 | 900 | 10 | 1998 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | KEN KIKER | 9156613884 | LEAK SPOTTED BY MOBIL LINEFLYER REPORTED TO GAUGER , NOTIFIED CONTROL CENTER TO SHUT DOWN PUMPS AND CLOSED UPSTREAM BLOCK VALVE. DISPATCHED CREW TO DIG OUT AND CLAMP LEAK. PICKED UP OIL STARDING. ON GOING REMEDIATION IN PROGRESS.
2017-09-29 08:50 | YES | NO | 20000091 | 2000-08-15 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2000-07-12 | 1320 | CA |  | LOS ANGELES | NO |  | NO | LINCOLN & JEFFERSON BLVD. | 535189 | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 677059.0401 | 1365901.5589 | CRUDE OIL | 1 | 398 | 398 | NO | NO | 10.75 | 0.365 | 35000 | WELDED |  | 1696 | 170 | YES | 24 | 2120 | 0 | 1971 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | GARY ZIMMERMAN | 7132415334 | A THIRD PARTY CONTRACTOR WITH CALIFORNIA BORING COMPANY RUPTURED THE LINE WITH A BORING MACHINE. THE DEVELOPER WAS ABLE TO CONTAIN THE PRODUCT BY CONSTRUCTING A CONTAINMENT TRENCH. SANDBAGS WERE PLACED INSIDE THE STORM DRAIN MANWAYS TO PREVENT PRODUCT FROM REACHING THE NEARBY MARSH.
2017-09-29 08:50 | YES | NO | 20000092 | 2000-08-22 | 30829 | TEPPCO | NO | 2000-07-23 | 1730 | TX | AUSTIN | SEALY | NO |  | NO | 2405 SOUTH HWY 36, SEALY, TEXAS 77474 | 536299 | TANK FARM | TANK |  | 1940 | OTHER | LIGHTNING STRUCK TANK RESULTING IN A SEAL FIRE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 |  |  | 0 | 0 | YES | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | FRED CLAKLEY | 4052395716 | ON 7-23-00 A THUNDER STORM OVER SEALY, TEXAS PRODUCED A LIGHTNING STRIKE TO TANK #2414 A 80,000 BARREL EXTERNAL FLOATING ROOF TANK. THE SEAL CAUGHT FIRE AT AROUND 1730 HOURS AND WAS EXTINGUISHED BY WILLIAMS AROUND 0300 HOURS ON 7-24-00. HMT WAS CALLED TO INSPECT THE TANK & ROOF AND THE TANK WAS PUMPED DOWN ON 7-25-00. THE INCIDENT DID NOT CAUSE THE SPILLAGE OF ANY CRUDE OIL. THE TANK WILL BE REPLACED.
2017-09-29 08:50 | YES | NO | 20000093 | 2000-08-22 | 30829 | TEPPCO | NO | 2000-07-13 | 1200 | TX | FAYETTE | LA GRANGE | NO |  | NO | WEST OF LAGRANGE ON THE OLD PLUM HWY, TURN NORTH ON EGYPT RD FOR 2 MILES THEN EAST IN TO | 535279 | LINE PIPE | PIPE |  | 1929 | OTHER | UNKNOWN- WE HAVE NOT STRIPPED OUT RIVER CROSSING T | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 203117.712 | 409770.4677 | CRUDE OIL | 1 | 160 | 10 | NO | NO | 12 | 0.375 | 25000 | WELDED |  | 150 | 50 | NO | 0 | 0 | 0 | 0 |  | Null | YES | OTHER | UNKNOWN AT THIS TIME |  |  | Null |  |  | Null | Null | FRED CLAKLEY | 4052395716 | A SHEEN OF OIL WAS FOUND AT THE COLORADO RIVER CROSSING OF THE TEPPCO CRUDE PIPELINE, LLC LAGRANGE TO ROSANKY 12 PIPELINE. THE SHEEN WAS CONTAINED USING BOOMS & PADS AND CONTINUES TO BE CONTAINED. THE CROSSING WAS REMOVED FROM SERVICE AND FLUSHED TWICE WITH WATER AND REMAINS OUT OF SERVICE. MONITORING WELLS WERE INSTALLED TO DETERMINE THE IMPACT TO THE AREA. THE OIL WAS SURFACING 2 OR 3 FEET FROM THE WEST BANK OF THE RIVER. A RISK ASSESSMENT IS CURRENTLY BEING PERFORMED TO HELP IN THE DEVELOPMENT OF REMEDIATION STRATEGY TO UNDER TAKE THE REMEDIATION OF THE SITE WILL BE UNDERTAKEN IN THE MEAN TIME WE ARE USING WELLS TO RECOVER CRUDE OIL. THE CROSSING IS TO BE REPLACED WITH A NEW CROSSING.
2017-09-29 08:50 | YES | NO | 20000094 | 2000-08-18 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 2000-07-22 | 251 | MN | CLEARWATER |  | NO |  | NO | STATION: AT MILEPOST 0914.1 TOWNSHIP:148N, SECTION: 1, QUARTER:SW1/4 OF SW1/4 RANGE:37W, TRACT#: T-691, MERIDIAN: W OF 5TH | 536193 | LINE PIPE | OTHER | REPAIR SLEEVE | 1998 | OTHER | FAILED REPAIR SLEEVE SIDESEAM WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 306000 | 207180.0663 | 417965.877 | CRUDE OIL |  | 50 | 10 | YES | NO | 34 | 0.344 | 52000 | WELDED |  | 758 | 507 | YES | 4 | 1047 | 10 | 1991 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | L.H. DE BRIYN | 2187250102 | AT 02:51 MST A LANDOWNER CALLED THE ECC COMPLAINING OF STRONG ODORS. THE PIPELINE WERE IMMEDIATELY SHUT DOWN AND DISTRICT PERSONNEL RESPONDED. THE APPROPRIATE NOTIFICATIONS WERE COMPLETED, AND THE CREWS BEGAN CONTAINING THE OIL. THE LEAK WAS SITUATED IN A LOW LYING MARSHY AREA. FOLLOWING AN ASSESSMENT OF CLEAN-UP AND RECOVERY STRATEGIES, A CONTROLLED BURN WAS COMPLETED. CLEAN UP EFFORTS WILL CONTINUE USING CONVENTIONAL METHODS.
2017-09-29 08:50 | YES | NO | 20000095 | 2000-08-26 | 11169 | LAKEHEAD PIPE LINE CO INC | YES | 2000-07-27 | 2126 | WI | DOUGLAS |  | NO |  | NO | STATION: PR AT MILEPOST 1098.0000 TOWNSHIP: 49N, SECTION:36, QUARTER: NE RANGE: 14W, TRACT# W-101-1 |  | PUMPING STATION | OTHER | BOLTED FLANGE CONNECTION | 1988 | OTHER | FAILED GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 135411.808 | 273180.3118 | CRUDE OIL | 1 | 1200 | 1150 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | L.H. DEBRIYN | 2187250102 | AT APPROXIMATELY 11:30 P.M. CENTRAL DAYLIGHT TIME THE SUPERIOR TERMINAL MAINTAINER CONFIRMED AN OIL LEAK NEAR THE LINE 6A STATION, AND THE SUPERIOR CONTROL CENTER WAS CALLED IMMEDIATELY. THE CONTROL CENTER RECEIVED THE GAS DETECTOR ALARM AT ABOUT THE SAME TIME AND LINE 6A WAS IMMEDIATELY SHUT DOWN. UPON INVESTIGATION, IT WAS CONFIRMED THAT OIL HAD BEEN RELEASED FROM A FAILED FLANGE CONNECTION ON THE UNIT 6.4 SUCTION VALVE OUTSIDE THE PUMP BUILDING. OIL HAD TRAVELED SOUTHERLY DOWN THE DITCH ON TERMINAL PROPERTY AND ENTERED AN ON SITE FLUMED CONTAINMENT POND. ALL OIL WAS CONTAINED IN THE DITCHES AND THE POND. A SECOND CONTAINMENT POND IS LOCATED ON COMPANY PROPERTY APPROXIMATELY 100 YARDS FURTHER DOWNSTREAM FROM THE FIRST, BUT LITTLE OR NO OIL WAS RELEASED FROM THE FIRST CONTAINMENT POND.
2017-09-29 08:50 | YES | NO | 20000096 | 2000-08-29 | 1004 | KOCH HYDROCARBON COMPANY | NO | 2000-08-05 | 935 | OK | DEWEY |  | NO |  | NO | NE 1/4 SECTION 5 T19N R17W | 537738 | LINE PIPE | NO DATA |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 51304 | 34735.837 | 70076.2136 | NATURAL GAS LIQUID | 2 | 759 | 0 | NO | NO | 6.625 | 0.188 | 0 | WELDED |  | 1440 | 470 | YES | 8 | 1827 | 7 | 1993 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BOB AEBI | 5803956294 | THE LANDOWNER WAS WORKING HIS FIELD WHEN THE IMPLEMENT PUNCTURED THE PIPELINE. THE LOCATION WAS IN AN AREA WHERE EROSION HAS REMOVE THE COVER OVER THE PIPELINE.
2017-09-29 08:50 | YES | NO | 20000097 | 2000-08-29 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-07-24 | 730 | KS | BUTLER |  | NO |  | NO | NE/4 SECTION 17-T26S-RE | 536326 | TANK FARM | PIPE |  | 1978 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 16926.476 | 34147.539 | CRUDE OIL | 1 | 1005 | 1000 | NO | NO | 10 | 0.188 | 35000 | WELDED |  | 400 | 45 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL CORROSION |  |  | Null |  |  | Null | Null | D.F SHEAFF | 7132414381 | RELEASE WAS CAUSED BY INTERANAL CORROSION OF 10" TANK FARM PIPING. AFTER DISCOVERY OF THE RELEASE SOURCE, THE PIPING WAS CLAMPED AND RETURNED TEMPORARILY TO SERVICE. THE DEADLEG PIPING HAS SINCE BEEN REMOVED FROM SERVICE.
2017-09-29 08:50 | YES | NO | 20000098 | 2000-08-29 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-07-26 | 745 | OK | PAYNE |  | NO |  | NO | SEC 15 T17N R5E |  | TANK FARM | PIPE |  | 1975 | OTHER | SUMP OVERFLOW | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33852.952 | 68295.0779 | CRUDE OIL | 1 | 200 | 174 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | SUMP OVERFLOWED. SOURCE OF PRODUCT GOING TO SUMP WAS 2" DRAIN LINE ON THE BOTTOM OF 30" MANIFOLD PIPE COMING FROM TANK 227. A ROOT CAUSE ANALYSIS TEAM IS CURRENTLY WORKING ON IDENTIFYING/DETERMINING THE ROOT CAUSE. THE 2" DRAIN LINE HAS BEEN EXCAVATED. A SAFE WORK PLAN IS BEING DEVELOPED.
2017-09-29 08:50 | YES | NO | 20000099 | 2000-08-30 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-08-02 | 1030 | MT | CASCADE |  | NO |  | NO | T14N, R1W, SECTION 25, CASCADE, MT. APPROXIMATELY 40 MILES SW OF GREAT FALLS, MT_MP 30.5, HELENA, MT TO GREAT FALLS, MT SEGMENT. | 537392 | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 338529.5201 | 682950.7794 | GASOLINE | 1 | 383 | 0 | NO | NO | 6.625 | 0.188 | 42000 | WELDED |  | 1716 | 270 | YES | 8 | 2072 | 7 | 1999 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RANDY W BEGGS | 3036494090 | AT APPROXIMATELY 10:30 A.M. ON AUGUST 2, 1999,A CONTRACTOR STRUCK THE 6" HELENA, MT TO GREAT FALLS, MT. YELLOWSTONE PIPELINE (OPERATED BY CONOCO PIPELINE CO.) WITH A BACKHOE (PERFORMING WORK FOR MONTANA POWER CO.) WHILE DIGGING POWER POLE GUIDE WIRE ANCHOR PLACEMENTS. ONCE THE LINE HAD BEEN RUPTURED THE CONTRACTOR NOTIFIED CPLS OIL MOVEMENTS GROUP IN HOUSTON AND EVACUATION OF THE LINE BEGAN. LINE MARKING IN THIS AREA WAS ADEQUATE. LINE MARKER IS WHERE THE CONTRACTOR FOUND THE EMERGENCY PHONE NUMBER. THE LINE WAS NOT IN OPERATION AT THE TIME, BUT WAS UNDER PRESSURE DUE TO THE HYDRAULIC PROFILE. PRODUCT WAS IMMEDIATELY DRAINED INTO GREAT FALLS, MT AND HELENA, MT TO MINIMIZE THE RELEASE.
2017-09-29 08:50 | YES | NO | 20000100 | 2000-09-12 | 31051 | TIDEWATER, INC | YES | 2000-07-21 | 1700 | WA | FRANKLIN | PASCO | NO |  | NO | 2900 SACAJAWEA PARK ROAD, PASCO, WA 99301- AT NORTH FENCELINE FOR CHEVRON, NORTHWEST TERMINAL COMPANY. SEE ATTACHED SKETCH |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 800000 | 541647.2321 | 1092721.2471 | GASOLINE | 3 | 900 | 0 | NO | NO | 6.625 | 0.14 | 36900 |  |  | 195 | 195 | YES | 17 | 500 | 10 | 1983 | EXTERNAL | Null | NO | GALVANIC |  |  |  | Null |  |  | Null | Null | PAT JENSEN | 5095477701 | INBOUND 6 INCH GASOLINE PIPELINE FROM NORTHWEST TERMINAL TO TIDEWATER TERMINAL COMPANY FAILED DUE TO CORROSION. GASOLINE LEAKED FROM 1/4" BY 3/8" HOLE IN THE PIPELINE AT THE SOUTH SIDE OF SACAJEWEA ROAD.
2017-09-29 08:50 | YES | NO | 20000101 | 2000-09-14 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2000-08-07 | 1530 | TX | ANGELINA |  | NO |  | NO | .375 MILES WEST OF INTERSECTION OF FM 58 AND PLANTATION DRIVE | 537922 | LINE PIPE | OTHER | GIRTH WELD ON REINFORCEMENT SLEEVE | 1931 | OTHER | PREVIOUSLY INSTALLED REINFORCEMENT SLEEVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 203117.712 | 409770.4677 | CRUDE OIL | 1 | 434 | 250 | NO | NO | 12 | 0.303 | 35000 | WELDED |  | 720 | 500 | YES | 8 | 900 | 4 | 2000 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF, COMPLIANCE ASSURANCE | 7132414381 | THE RELEASE OCCURRED WHEN A PREVIOUSLY INSTALLED REINFORCEMENT SLEEVE FAILED. THE FAILURE WAS DUE TO INADEQUATE WELDING PROCESS. ALL FREE OIL HAS BEEN PICKED UP.
2017-09-29 08:50 | YES | NO | 20000102 | 2000-09-12 | 31445 | THE PREMCOR REFINING GROUP INC | YES | 2000-08-08 | 1408 | IL | COOK |  | NO |  | NO | AT STATE ST AND MARBLE AVE AT PARCEL ILL C-53 AND ILL C-95 |  | LINE PIPE | PIPE |  | 1958 | OTHER | CORROSION, EXTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 20311.7712 | 40977.0468 | GASOLINE | 2 | 50 | 49 | NO | NO | 8 | 0.322 | 42000 | WELDED |  | 600 | 30 | YES | 8 | 1220 | 3 | 1993 | EXTERNAL | Null | YES | OTHER |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | ANDREW J SEABO | 3148549848 | EXCAVATION OF THE UNDERGROUND PIPELINE NEAR A RAILROAD ACCESS ROADWAY, REVEALED THE PIPELINE MARKING POST WAS BENT AND HAD BEEN ATTACHED TO THE TOP OF THE PIPELINE BY A NON-PENETRATING, WELDING FITTING. THE FITTING CONSISTED OF A 4 INCH, 150 CLASS WELD-NECK FLANGE. THE POST CONSISTED OF A MATCHING FLANGE AND APPROXIMATELY 9 FEET OF 4 INCH, SCHEDULE 40 PIPE WITH A PIPE CAP ALL JOINED TOGETHERBY GIRTH (BUTT) WELDS. NO RECORDS INDICATED WHEN THIS WAS INSTALLED TO THE PIPELINE (API 5L X42) THAT WAS BUILT IN 1958. SUBSEQUENT EXAMINATION REVEALED A PIN HOLE TYPE LEAK AT THE FILLET WELD BETWEEN THE ATTACHMENT FITTING AND THE PIPELINE. A SECTION OF THE PIPELINE APPROXIMATELY 3 FEET LONG WAS REMOVED WITH THE ATTACHEMENT FOR FAILURE ANALYSIS. THE NEW SECTION WAS INSTALLED, RADIOGRAPHED, COATED AND APPROVED FOR SERVICE. THE RESULTS OF THE FAILURE INDICATED THE LEAK WAS CAUSED BY THE PROPAGATION OF A CRACK THAT HAD INITIATED PREVIOUSLY DUE TO A RESTRAINT OF THE WELD BETWEEN THE NON-PENETRATING ATTACHMENT AND THE PIPELINE. THE CRACK PROPAGATED TO A THROUGH-WALL LEAK AS A RESULT OF THE ABOVE GROUND MARKER POST BEING STRUCK BY OTHERS.
2017-09-29 08:50 | YES | YES | 20000103 | 2000-09-18 | 15490 | PHILLIPS PIPE LINE CO | YES | 2000-08-11 | 1145 | TX |  | ECTOR | NO |  | NO | MERTEX LINE 80 1-6 GOLDSMITH BENEDUM, MP 17-49+16 - SEC 48, BLOCK 42, T&PRR SURVEY 300' WEST OF YUKON ROAD AND LOOP 338 |  | LINE PIPE | BOLTED FITTING |  | 1981 | OTHER | STOPPLE FITTING GASKET LEAKING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 18000 | 12187.0627 | 24586.2281 | NATURAL GAS LIQUID | 2 | 1 | 0 | NO | NO | 8.625 | 0.25 | 35000 | WELDED |  | 1100 | 697 | YES | 24 | 1375 | 8 | 1976 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LINUS J SCHMITZ, TECH SERVICE DIRECTOR | 9186614814 | A GOLF COURSE EMPLOYEE REPORTED NAUSEA FROM ODORS. HE WENT TO THE CLINIC AND WAS DIAGNOSED AS HAVING BEEN EXPOSED TO H2S. HE WAS NOT HOSPITALIZED AND RETURNED TO WORK ON HIS NEXT SHIFT. UPON INVESTIGATION, A VER SMALL LEAK WAS DISCOVERED IN A STOPPLE FITTING GASKET WHICH WAS LOCATED MORE THAN 1/4 MILE FROM THE GOLF COURSE. NOTHING AT THE LEAK SITE CONFIRMED THE LEAK AS THE ODOR OR H2S SOURCE. NO VAPORS WERE VISIBLE, AND NO H2S WAS DETECTED AT THE SITE. LEL INSTRUMENTS NEVER EXCEEDED MINIMUM LEVELS IMMEDIATELY ABOVE THE BURIED FITTING.
2017-09-29 08:50 | YES | NO | 20000104 | 2000-09-14 | 443 | AMOCO PIPELINE CO | YES | 2000-08-17 | 1341 | TX | FANNIN | LEONARD | NO |  | NO | FROM LEONARD, TX (AT INTERSECTION OF HWY 69 AND HWY 78) TAKE 78 WEST TO CR 4945. TURN RIGHT (GO NORTH) ON CR 4945, GO APPROX 1.5 MILES TO THE PIPELINE ROW. TUR |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 507794.2801 | 1024426.1691 | CRUDE OIL | 1 | 80 | 50 | NO | NO | 8 | 0.188 | 52000 | WELDED |  | 1440 | 700 | YES | 8 | 1800 | 9 | 1989 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | CORE TEAM LEADER-TEXOMA | 9037594279 | ROW CLEARING CONTRACTOR HIT SPAN DURING CLEARING. OPERATIONS RESULTING IN RELEASE.
2017-09-29 08:50 | YES | NO | 20000105 | 2000-09-19 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-07-17 | 2242 | OK | KAY | PONCA CITY | NO |  | NO | INCIDENT OCCURRED WITHIN CONOCO'S PONCA CITY COMPLEX, LOCATED AT 1000 SOUTH PINE STREET, PONCA CITY, OK SE/4, SECT 33 TOWNSHIP 26 NORTH |  | TANK FARM | NO DATA |  | 1976 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6770.5904 | 13659.0156 | GASOLINE | 3 | 641 | 397 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | VANCE WEBB | 5807674845 | AT 20:42 ON JULY 17, 2000 WHILE BLENDING A TANK OF 87 OCTANE UNLEADED GASOLINE, THE BLENDER OPERATOR OBSERVED THAT THE TANK GAUGE FOR TANK 150 HAD CEASED UPDATING. WHILE IN TRANSIT TO PHYSICALLY INSPECT TANK 150, ANOTHER TANK FARM OPERATOR OBSERVED THE TANK BEGINNING TO RUN OVER. THE BLENDER WAS IMMEDIATELY SHUT DOWN AND EMERGENCY RESPONSE PERSONNEL DISPATCHED TO THE LOCATION TO BEGIN RECOVERY OPERATIONS. WHILE BEGINNING RECOVERY OPERATIONS A PRODUCT TRANSFER TO ANOTHER TANK WAS INITIATED TO REDUCE THE PRODUCT LEVEL IN TANK 150. UPON COMPLETION OF THE PRODUCT RECOVERY OPERATIONS, THE FAULTY GAUGE WAS REPLACED.
2017-09-29 08:50 | YES | NO | 20000106 | 2000-10-02 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | NO | 2000-08-28 | 1145 | CA | ORANGE |  | NO |  | NO | EL SEGUNDO TO HUNTINGTON BEACH 6" GATHERING PIPELINE, 300' NORTH OF THE SHIPPING PUMPS IN THE AERA ENERGY LEASE (A SHELL-MOBIL PARTNERSHIP) INTERSECTION OF PALM |  | LINE PIPE | PIPE |  | 1921 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 135411.808 | 273180.3118 | CRUDE OIL | 1 | 65 | 65 | NO | NO | 6 | 0.28 | 0 | WELDED |  | 150 | 60 | YES | 4 | 750 | 9 | 1996 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | GARY SAENZ, DOT SPECIALIST | 2815963568 | AN EXCAVATOR, B & B ENGINEERING (THIRD PARTY), WAS REMOVING ABANDONED PIPELINES IN AN OLD CHEVRON LEASE BEING DEVELOPED FOR A HOUSING TRACT. EXCAVATOR DID NOT DISTINGUISH THE CHEVRON PIPE LINE ACTIVE CRUDE PIPELINE FROM ADJACENT ABANDONED LINES, DESPITE THE FACT THE ACTIVE LINE HAD BEEN MARKED APPROXIMATELY EVERY 10 FEET THRU THE WORK AREA. THE PIPELINE WAS DAMAGED BY THE EXCAVATOR AND AN ESTIMATED 65 BBLS OF CRUDE OIL WAS RELEASED. THE RELEASED OIL WAS CONTAINED WITHIN THE ADJACENT EXCAVATIONS. NO OIL WAS RELEASED TO WATER. AREA WAS ISOLATED AND EMERGENCY RESPONSE ZONES WERE ESTABLISHED. AIR MONITORING WAS ALSO PERFORMED. APPROXIMATELY 45 BARRELS OF FREE-FLOATING OIL WAS RECOVERED BY VAC TRUCKS AND THE REMAINING 25 BARRELS IN THE CONTAMINATED SOIL WAS EXCAVATED BY APPROVED CONTRACTORS UNDER THE DIRECTION OF CHEVRON PIPE LINE COMPANY REPRESENTATIVES. AGENCIES NOTIFIED: COES (REPORT # 00-3873) ON 8/28/00 @13:10. THE NATIONAL RESPONSE CENTER WAS ALSO NOTIFIED.
2017-09-29 08:50 | YES | NO | 20000107 | 2000-09-27 | 30922 | HYPERION ENERGY LP | NO | 2000-09-15 | 745 | TX | CHEROKEE |  | NO |  | NO | 3/4 MILE NORTH OF HWY 79 & FM 921, 1/2 MILE EAST OF NECHES RIVER |  | LINE PIPE | PIPE |  | 1970 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 338.5295 | 682.9508 | CRUDE OIL | 1 | 50 | 0 | NO | NO | 10 | 0.75 | 30000 | WELDED |  | 200 | 100 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | GERARD R STUCKART | 9035843185 | INTERNAL CORROSION CAUSED LEAK INTO DITCH ADJACENT TO PIPELINE. OIL POOLED INTO DITCH (ALREADY DAMNED FROM PREVIOUS LEAK). MAJORITY OF ALL OIL WILL BE COLLECTED. WILL FLOOD DITCH WITH WATER AND SUCK REMAINING OIL UP.
2017-09-29 08:50 | YES | NO | 20000108 | 2000-10-06 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2000-09-07 | 1430 | AR | UNION | EL DORADO | NO |  | NO | 331 CALLON ROAD | 541386 | TANK FARM | PUMP |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 8500 | 5755.0018 | 11610.1633 | DIESEL FUEL | 3 | 60 | 57 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LEONARD W MALLETT, VICE PRESIDENT | 7137593615 | TEPPCO PERSONNEL STARTED A PIPELINE DELIVERY INTO A BREAKOUT AT THE EL DORADO TERMINAL. THE TANK BLOCK VALVE WAS CLOSED, RESULTING IN THE TANK LINE BEING OVERPRESSURIZED CAUSING A FAILURE OF A GASKET ON THE TANK CAN PUMP. UPON DELIVERY, PRODUCT FLOW TO THE TANK WAS SHUT DOWN. ON-SITE TEPPCO PERSONNEL IMMEDIATELY INITIALIZED COMPANY EMERGENCY PROCEDURES. ALL SPILLED PRODUCT WAS CONTAINED AND RECOVERED WITHIN THE SECONDARY CONTAINMENT OF THE TANK. REMEDIATION TO THE AFFECTED SOIL IS CURRENTLY ONGOING.
2017-09-29 08:50 | YES | NO | 20000109 | 2000-10-11 | 26046 | HOLLY CORP | NO | 2000-09-27 | 815 | ID | ELMORE | MT HOME | NO |  | NO | SW 1/4, NW 1/2, SECTION 11, T3S, R6E |  | TANK FARM | TANK |  | 1960 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 50779.428 | 102442.6169 | JET FUEL | 3 | 145 | 109 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JIM G TOWNSEND | 5057483311 | TERMINAL FOREMAN, MR. BLAKE TARVER, ERRANTLY CALCULATED AVAILABLE TANK CAPACITY WHEN RECEIVING A PIPELINE SHIPMENT INTO THE TANK FARM. AT APPROXIMATELY 8:15 A.M., MR. TARVER OBSERVED FUEL BEGINNING TO OVERFLOW FROM THE TANK. HE IMMEDIATELY SHUT DOWN THE RECEIPT AND TRANSFERRED SOME OF THE FUEL INTO ANOTHER AVAILABLE TANK. THE LOCAL AUTHORITIES WERE IMMEDIATELY NOTIFIED. MR. TARVER THEN NOTIFIED MS. LORI CLOWE, REGULATORY COORDINATOR, WHO NOTIFIED THE NATIONAL RESPONSE CENTER AT 9:44 A.M. THE SAME DAY (REPORT #542432) AND THE IDAHO STATE COMMUNICATIONS OFFICER AT 10:15 A.M. MR. TARVER WAS THEN NOTIFIED OF POST ACCIDENT DRUG TESTING AND TESTING OCCURRED ON-SITE THAT SAME DAY. CONTRACTORS BEGAN ARRIVING AT APPROXIMATELY 10 AM AND RECOVERED APPROXIMATELY 30 BARRELS OF THE ESTIMATED 218 BARRELS THAT HAD SPILLED. CONTRACTORS REMAIN ON-SITE CLEANING UP THE SPILL AND BEGAN THE REMEDIATION PROCESS. 10/31/00 - THIS REPORT IS A SUPPLEMENTAL TO THE PREVIOUS 7000-1 SUBMITTED ON OCTOBER 2, 2000, CERTIFIED MAIL ARTICLE #700-0520-0017-1088-9853. DURING THE CLEANUP PROCESS, IT HAS BEEN DETERMINED THROUGH VERIFICATION OF METERED RECEIPT TICKETS AS WELL AS SOIL SAMPLING THAT THE TOTAL ESTIMATED VOLUME SPILLED WAS 144.86 BARRELS AND THE TOTAL RECOVERED PRODUCT IS 104.85 BARRELS. WE HAVE OBTAINED AN APPROVED APPLICATION FOR LAND TREATMENT OF PETROLEUM CONTAMINATED SOIL FROM THE IDAHO DEPARTMENT OF ENVIRONMENTAL QUALITY AND CONTINUE THE REMEDIATION PROCESS. THE MAJORITY OF THE AFFECTED SOILS HAVE BEEN REMOVED AND ARE BEING REMEDIATED PER THE IDEQ APPROVED PROCESS. MONITORING WELLS AND RECOVERY EQUIPMENT IS IN PLACE AND IS BEING OPERATED BY ENVIRONMENTAL CONTRACTORS.
2017-09-29 08:50 | YES | NO | 20000110 | 2000-10-13 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2000-09-13 | 1302 | IN | ORANGE | FRENCH LICK | NO |  | NO | STATE HIGHWAY 56, 3.2 MILES SOUTHWEST OF FRENCH LICK, INDIANA |  | PUMPING STATION | OTHER |  | 0 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 9478.8266 | 19122.6218 | PROPANE | 2 | 11 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | LEONARD W MALLETT | 7137593615 | AT APPROXIMATELY 1302 HOURS, CDT, SEPTEMBER 13, 2000 A PROPANE VAPOR CLOUD WAS NOTICED NEAR THE 20" LINE P2 PUMP AT TEPPCOS FRENCH LICK BOOSTER STATION. TEPPCOS EMERGENCY PLAN WAS IMMEDIATELY INITIATED, THE SYSTEM WAS SHUT DOWN AND PERSONNEL SHUT THE STATION BLOCK VALVES. UPON EXCAVATION OF THE SITE, IT WAS DETERMINED THE LEAK ORGINATED FROM A CORROSION LEAK FROM A BRANCH CONNECTION, A 1" THREADED NIPPLE USED AS AN INTELLIGENCE LINE AT THE PUMP STATION. THE INTERNAL CORROSION WAS FURTHER DETERMINED TO HAVE BEEN GALVANIC IN NATURE. THE NIPPLE WAS REMOVED AND THE CONNECTION WAS BLINED OFF.
2017-09-29 08:50 | YES | NO | 20000111 | 2000-10-17 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 2000-09-15 | 700 | KS | MCPHERSON |  | NO |  | NO | 9 MILES NORTH AND 3 MILES WEST OF THE CITY OF MCPHERSON, KS (COUNTY ROAD 446) |  | LINE PIPE | OTHER | THERMAL RELIEF ON MAINLINE BLOCK VALVE | 1973 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1015.5886 | 2048.8523 | ANHYDROUS AMMONIA | 2 | 50 | 0 | NO | NO | 8.625 | 0.203 | 46000 | WELDED |  | 1559 | 727 | YES | 24 | 2059 | 0 | 1973 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null |  |  | Null | Null | JOHNNY CAVITT | 9185748412 | A LEAK WAS REPORTED TO 911 DISPATCH BY SCHOOL BUS DRIVER, SHERIFFS OFFICER, AND FIRE DEPARTMENT WAS DISPATCHED. UNKNOWN PERSON OR PERSONS HAD REMOVED A THERMAL RELIEF FROM MAINLINE NH, BLOCK VALVE. EMERGENCY ACTION PLAN WAS IMPLEMENTED AND MID-AMERICAS PERSONNEL AND CONTRACT CREW RESPONDED TO SITE WITH THE PROPER PPE. THE LINE PRESSURE WAS LOWERED AND VALVE WAS PLACED ON FITTING.
2017-09-29 08:50 | YES | NO | 20000112 | 2000-10-19 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | NO | 2000-09-26 | 1045 |  |  |  | YES | LAT 29 22.417'; LONG 88 3 | NO | 6" CRUDE OIL PIPELINE FROM MAIN PASS 133 "A" TO MAIN PASS 144 "A" PLATFORMS IN THE GULF OF MEXICO (OCS) MMS PIPELINE SEGMENT #458 | 543326 | LINE PIPE | PIPE |  | 1971 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 121870.6272 | 245862.2806 | CRUDE OIL | 3 | 1 | 0 | NO | NO | 6.625 | 0.344 | 42000 | WELDED |  | 1440 | 180 | YES | 12 | 3925 | 9 | 1972 | EXTERNAL | Null | YES | OTHER | OXIDATION FROM EXPOSURE TO SALTWATER |  |  | Null |  |  | Null | Null | KATHY K BALDWIN, HES TEAM LEADER | 2815963567 | A SHEEN WAS OBSERVED BY A HELICOPTER PILOT IN THE VICINITY OF CHEVRONS MAIN PASS 133 PRODUCTION FIELD. BY THE SHAPE AND LOCATION OF THE SHEEN, IT APPEARED TO BE COMING FROM A UNDERWATER PIPELINE. AFTER DETERMINING WHICH PIPELINES WERE IN THE AREA, APPROPRIATE AGENCIES WERE NOTIFIED, AND SIMULTANEOUSLY, CHEVRON PRODUCTION OPERATORS SHUT-IN THE SUSPECTED 6" PIPELINE AND BEGAN DEPRESSURIZATION. BECAUSE OF THE LIGHT SHEEN, AREA EXTENT OF THE SPILL, AND ENVIRONMENTAL CONDITIONS. CHEVRON CONCLUDED THAT THE OIL WAS NOT SKIMMABLE, IT WAS ALLOWED TO NATURALLY DISSIPATE, WHICH OCCURRED RAPIDLY AS OBSERVED DURING SUBSEQUENT OVERFLIGHTS. REPAIR PLANS WERE QUICKLY DEVELOPED, WITH CONCURRENCE FROM THE MINERALS MANAGEMENT SERVICE, AND CONTRACTORS WERE MOBILIZED TO LOCATE THE LEAK SITE AND PLACE A PERMANENT REPAIR CLAMP OVER THE AFFECTED SECTION OF PIPELINE. THE LINE WAS SLOWLY REPRESSURIZED WHILE DIVERS VERIFIED THAT THE CLAMP WAS NOT LEAKING. THE LINE WAS THEN PLACED BACK INTO SERVICE. AN OFFICIAL INVESTIGATION WAS NOT FEASIBLE, AS THE LEAK SITE OCCURRED IN 170+ FEET OF WATER DEPTH, AND THE SMALL LEAK WAS EASILY REPAIRED WITHOUT REMOVING THE AFFECTED SECTION OF PIPE
2017-09-29 08:50 | YES | NO | 20000113 | 2000-10-24 | 2552 | COLONIAL PIPELINE CO | Null | 2000-05-19 | 645 | NC | GUILFORD | GREENSBORO | NO |  | NO | GREENSBORO, NC COLONIAL PIPELINE COMPANY TANK FARM INSIDE THE FENCE LINE |  | LINE PIPE | PIPE |  | 1995 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33852.952 | 68295.0779 | KEROSENE |  | 50 | 17 | NO | NO | 6 | 0.28 | 42000 | WELDED |  | 720 | 35 | YES | 8 | 2050 | 7 | 1995 | EXTERNAL | Null | YES | OTHER | PITTING |  |  | Null |  |  | Null | Null | STEPHEN E GILLIAM, REGULATORY ADMINISTRATOR | 4048412314 | AT 0645 MAY 19, 2000 THE COLONIAL PIPELINE COMPANY PROJECT MANAGER, GREENSBORO, NC WAS NOTIFIED BY A COLONIAL CONTRACTOR WORKING IN THE TANK FARM THAT HE HAD DISCOVERED AN OIL FILM LOCATED ON THE TANK FARM POND. THE PROJECT MANAGER NOTIFIED THE GREENSBORO TANK FARM CONTROL ROOM AT 0705 AND INSTRUCTED THE OPERATOR TO MAINTAIN THE AIRPORT LINE (THE SUSPECTED SOURCE OF THE PRODUCT) IN THE SHUTDOWN STATUS. THE LINE WAS NOT OPERATING AT THE TIME OF THIS INCIDENT. THE PROJECT MANAGER INITIATED AN INVESTIGATION OF THE AIRPORT LINE. THE INVESTIGATION REVEALED A CORROSION PIT THAT WAS REPAIRED BY INSTALLATION OF A REPAIR SLEEVE. THE REPAIR WAS COMPLETED AT 2100 ON MAY 19, 2000. AT THE TIME OF THE INCIDENT ON MAY 19, 2000 THE INITIAL ESTIMATE OF TOTAL DAMAGED WAS $30,000 AND TOTAL ESTIMATED VOLUME OF RELEASE WAS LESS THAN 50 BBLS. AFTER NEARING COMPLETION OF SOIL REMEDIATION AND IN ADDITION TO THE COST OF REPAIRS THE ESTIMATED TOTAL DAMAGE EXCEEDS $50,000 AS OF OCTOBER 17, 2000. THEREFORE, THE RELEASE IS REPORTABLE. THE NATIONAL RESPONSE CENTER WAS NOTIFIED ON 5/19/00 REPORT NUMBER 529433.
2017-09-29 08:50 | YES | YES | 20000114 | 2000-10-30 | 4906 | EXXON PIPELINE CO | NO | 2000-09-07 | 1654 | TX | TAYLOR |  | NO |  | NO | APPROXIMATELY 1800 FEET SOUTHEAST OF INTERSECTION OF HIGHWAY 36 AND COUNTY ROAD 123. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 1 | 0 | 1 | 2 | 0 | 2 | 300000 | 203117.712 | 409770.4677 | NATURAL GAS LIQUID | 2 | 6800 | 0 | YES | YES | 12.75 | 0.25 | 35000 | WELDED |  | 720 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOEL C LARKIN | 7136560227 | ON SEPTEMBER 7, 2000 A DOZER OPERATOR LAYING A WATERLINE, STRUCK AND DAMAGED AN NGL PIPELINE OPERATED BY EXXONMOBIL PIPELINE COMPANY. THE DAMAGE RESULTED IN A RELEASE OF NGL. THE NGL VAPORS IGNITED, RESULTING IN AN EXPLOSION AND FIRE. THE FIRE DESTROYED A NEARBY HOME, A CAR, AND THE DOZER. THE HOME OWNER AND THE DOZER OPERATOR WERE TREATED FOR INJURIES. THE OCCUPANT OF THE CAR WAS FATALLY INJURED. AN ADDRESS OF 1985 OLD ELMDALE ROAD WAS PROVIDED BY TESS TO EXXONMOBILS CONTRACTOR, CLEVELAND INSPECTION SERVICES(CIS). THIS ADDRESS WAS APPROXIMATELY 1/2 MILE FROM EXXONMOBILS PIPELINE. SINCE THE ADDRESS GIVEN BY TESS WAS NOT WITHIN THE 1000 FOOT BUFFER ZONE AROUND THE PIPELINE, CIS "CLEARED" THE LOCATION AND NO TEMPORARY MARKINGS WERE PLACED BY EXXONMOBIL. HOWEVER, PERMANENT PIPELINE MARKERS WERE PRESENT IN THE IMMEDIATE VICINITY OF THE PIPELINE.
2017-09-29 08:50 | YES | NO | 20000115 | 2000-10-23 | 4906 | EXXON PIPELINE CO | NO | 2000-07-09 | 1240 | TX | UPTON |  | NO |  | Null | WEST OF MIDLAND - STATE HWY 1788 SOUTH TO ST HWY 1787, TURN WEST, 4 MILES ST ST HWY 1492 , 8 MILES, LEAK OCCURRED 1 1/2 MILES EAST OF ST HWY 1492 |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13541.1808 | 27318.0312 |  |  | 800 | 0 | NO | NO | 4 | 0.237 | 35 | WELDED |  | 1029 | 500 | YES | 8 | 1279 | 7 | 1987 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J CHARLES | 7136560227 | LANDOWNER WAS OPERATING A MAINTAINER TO INSTALL A 3" "POLY" WATER LINE WHEN HE STRUCK THE 4" STEEL NGL PIPELINE CAUSING A RELEASE. A PIPELINE MARKER WAS LOCATED WITHIN 8 FEET OF THE 3RD PARTY DAMAGE. THE LINE WAS NOT OPERATING AT THE TIME OF THE INCIDENT, AND VOLUMES LOST WERE THE LINE FILL. NO FIRES, EXPLOSIONS, OR INJURIES, OR INJURIES RESULTED. THE ENGINE ON THE MAINTAINER STOPPED IMMEDIATELY. REPAIR CREWS WERE DISPATCHED TO THE SCENE, AND THE AREA WAS SECURED AND REPAIRS INITIATED. AGENCY NOTIFICATIONS WERE MADE.
2017-09-29 08:50 | YES | NO | 20000116 | 2000-10-31 | 4906 | EXXON PIPELINE CO | NO | 2000-10-03 | 1930 | TX | WINKLER |  | NO |  | NO | HALLEY STATION, WINKLER COUNTY TEXAS, SECTION 6 BLOCK 11 6 MILES SOUTH OF KERMIT, TEXAS ON STATE HWY 18 |  | LINE PIPE | PIPE |  | 1927 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 27082.3616 | 54636.0624 | CRUDE OIL | 3 | 156 | 15 | NO | NO | 10 | 0.365 | 35000 | WELDED |  | 652 | 600 | YES | 19 | 815 | 8 | 1990 | INTERNAL | Null | YES | OTHER |  |  |  | Null |  |  | Null | Null | JOEL C LARKIN | 7136560227 | ON EVENING OF 10/3/2000, THE DALLAS CONTROL CENTER RECEIVED A LINE BALANCE ALARM ON THE HALLEY TO MIDLAND 10" CRUDE SYSTEM. THE LINE WAS SHUT DOWN AND PERSONNEL DISPATCHED TO INVESTIGATE. PERSONNEL ARRIVING AT HALLEY STATION NOTED A RELEASE ON STATION PROPERTY. A CLAMP WAS PLACED ON THE LINE TO STOP THE RELEASE. (PIPELINE REPLACEMENT SCHEDULED) THE RELEASE WAS DETERMINED TO BE REPORTABLE ON THE MORNING OF 10/4/2000. AT THAT TIME, THE NRC WAS NOTIFIED OF THE RELEASE AS WELL AS STATE AGENCIES.
2017-09-29 08:50 | YES | NO | 20000117 | 2000-11-07 | 15674 | PLANTATION PIPE LINE CO | YES | 2000-10-20 | 830 | GA | HARALSON | BREMEN | NO |  | NO | PPL STA 160+21, APPROXIMATELY 3.0 MILES EAST OF BREMEN TANK FARM - SEE ATTACHED SKETCH | 545760 | LINE PIPE | PIPE |  | 1951 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 203117.712 | 409770.4677 | DIESEL FUEL | 3 | 24 | 20 | NO | NO | 14 | 0.375 | 35000 | WELDED |  | 1165 | 970 | YES | 8 | 1710 | 12 | 1995 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JACQUE WILLIAMS | 7707514095 | AT APPROXIMATELY 0830 EDT ON OCTOBER 20, 2000, A LEAK WAS DISCOVERED ON PLANTATIONS 14" O.D. 0.375" W. T., GRADE B, PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN BREMAN, GEORGIA AND GREENSBORO, NORTH CAROLINA. THE LEAK OCCURRED 2,010 FEET EAST OF HURST MILL ROAD IN HARALSON COUNTY. THE SECTION OF PIPE WHICH FAILED HAD ONE LONGITUDINAL HAIRLINE CRACK WITH 7 INCHES VISIBLE AT THE 12 OCLOCK POSITION. THE PIPE FAILED AS A RESULT OF AN INTERNAL MILL DEFECT CAUSING A RELEASE OF APPROXIMATELY 24 BARRELS OF DIESEL FUEL. A SMALL AMOUNT OF DIESEL FUEL ENTERED BUCK CREEK AND WAS CONTAINED AND RECOVERED. APPROXIMATELY 16 BARRELS WAS RECOVERED AS FREE PRODUCT AND 4 BARRELS WAS RECOVERED IN SOIL, VEGETATION, AND ABSORBENT PADS REMOVED FROM THE SITE. THE REMAINING DIESEL FUEL (APPROXIMATELY 4 BARRELS IN UNDISTRUBED SOIL AT THE SITE) WILL NATURALLY ATTENUATE PENDING A SUBSURFACE INVESTIGATION. THE PIPELINE WAS REPAIRED WITH ONE 44 INCH LONG FULL ENCIRCLEMENT "PRESSURE VESSEL" SLEEVE.
2017-09-29 08:50 | YES | NO | 20000118 | 2000-11-02 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | NO | 2000-10-04 | 437 | CA | CONTRA COSTA |  | NO |  | NO | 8" BAY AREA PRODUCTS LINE (BAPL), SACRAMENTO LEG, NEAR PITTSBURG STATION, CA APPROX 0.60 OF A MILE FROM SACRAMENTO RIVER ON SOUTHSIDE OF HONKER BAY, EAST OF MCA | 544138 | LINE PIPE | PIPE |  | 1965 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 700000 | 473941.3281 | 956131.0912 | GASOLINE | 1 | 300 | 0 | NO | NO | 8 | 0.188 | 46000 | WELDED |  | 1440 | 1248 | YES | 4 | 1776 | 0 | 1991 |  | Null | YES |  |  |  |  | Null |  |  | Null | Null | GARY SAENZ, DOT SPECIALIST | 2815963568 | CHEVRON PIPE LINE COMPANY (CPL) CUSTOMER SERVICE CENTER (CSC) IN HOUSTON, TX OBSERVED A PRESSURE DROP ON THE 8" BAPL SYSTEM AT 06:37 (CST) VIA SCADA. SHUTDOWN PROCECURES WERE IMMEDIATELY ACTIVATED. THE TEAM LEADER AT LOS MEDANOS, CA WAS CONTACTED AT 06:50 (CST). A RECONNAISSANCE TEAM WAS DISPATCHED TO THE AFFECTED PIPELINE SEGMENT AREA TO LOCATE THE SUSPECTED RELEASE & AN AIR PATROL WAS ALSO DISPATCHED TO FLY THE PIPELINE RIGHT-OF-WAY. THE PIPELINE VALVE (#346) AT PITTSBURG JUNCTION WAS ISOLATED BY THE CSC. PIPELINE VALVES (#349 & 349A) AT BIRDS LANDING WERE MANUALLY CLOSED TO COMPLETELY ISOLATE THE AFFECTED SEGMENT. CPL PERSONNEL ARRIVED AT THE SPILL SITE, LOCATED APPROX 0.60 MILES FROM THE SACRAMENTO RIVER ON THE SOUTHSIDE OF HONKER BAY, EAST OF MCAVOY BOAT HARBOR IN A WETLAND AREA. NO SHEEN WAS DETECTED ON THE SACRAMENTO RIVER. CHEVRON PERSONNEL SET UP AN INCIDENT COMMAND SYSTEM AT THE SPILL SITE. MARINE SPILL RESPONSE CORPORATION (MSRC) WAS CONTACTED TO PROVIDE SUPPORT AND BOOMS WERE DEPLOYED ACROSS THE SLOUGHS LEADING TO THE SACRAMENTO RIVER TO ISOLATE THE RELEASE. INVESTIGATION OF THE PIPELINE AFTER EXCAVATION SHOWED A RUPTURE ON THE BOTTOM OF A BEND. FURTHER ANALYSIS IS PENDING.
2017-09-29 08:50 | NO | NO | 20000119 | 2000-11-06 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 2000-10-07 | 2135 | AZ | COCHISE |  | NO |  | NO | SEE ATTACHED SKETCH |  | LINE PIPE | PIPE |  | 1964 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | GASOLINE | 3 | 0 | 0 | NO | NO | 12 | 0.188 | 52000 | WELDED |  | 1104 | 228 | YES | 25 | 1492 | 1 | 1965 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | EDWARD FANT | 7133699454 | ON OCTOBER 7 AT APPROXIMATELY 0052, A CONTROLLER IN THE ORANGE CONTROL CENTER SHUTDOWN LS 22, THE 12-INCH INTERSTATE PIPELINE BETWEEN EL PASO, TEXAS AND TUCSON, ARIZONA DUE TO MEASUREMENT IMBALANCE. A STATIC PRESSURE TEST WAS BEGUN AT 0100 HOURS. AT 0435 FIELD PERSONNEL WERE NOTIFIED AND EFFORTS BEGUN TO LOCATE THE SITE OF A POTENTIAL LEAK. FIELD PERSONNEL BEGAN ISOLATING SEGMENTS OF THE PIPELINE AT 0717 HOURS TO HELP PINPOINT THE LEAK: BLOCK VALVES ALONG THE PIPELINE WERE CLOSED AND PRESSURE MONITORED TO DETERMINE THE EFFECT THAT ISOLATING THE DIFFERENT SEGMENTS HAD ON PRESSURES. AT APPROXIMATELY 1820 HOURS THE PIPELINE SEGMENT BETWEEN THE WEST BENSON BLOCK VALVE (MP 262.31) AND THE AMOLE BLOCK VALVE (MP 274.22) WAS IDENTIFIED TO BE LOOSING PRESSURE AND FIELD PERSONNEL WERE DISPATCHED TO DRIVE THAT SEGMENT OF RIGHT-OF-WAY LOOKING FOR EVIDENCE OF A LEAK. AT 2135 HOURS THE LEAK WAS LOCATED. THE LEAK SITE WAS ON RAILROAD RIGHT-OF-WAY OUTSIDE OF THE TOWN SITE OF BENSON ARIZONA APPROXIMATELY 1000 FEET NORTH OF INTERSTATE 10. EFFORTS WERE BEGUN IMMEDIATELY TO MAKE THE AREA SAFE AND MINIMIZE THE AFFECT ON PERSONS, PROPERY AND THE ENVIRONMENT. WHEN THE PIPELINE WAS EXCAVATED, A SMALL CRACK WHICH RESULTED FROM LARGER MECHANICAL DAMAGE CAUSED BY OTHERS (THIRD PARTY) WAS DISCOVERED ON THE PIPE AT APPROXIMATELY THE 10 OCLOCK POSITION.
2017-09-29 08:50 | YES | NO | 20000120 | 2000-11-13 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 2000-09-26 | 200 | IA | POLK | DES MOINES | NO |  | NO | 4401 VANDALIA ROAD, DES MOINES IOWA |  | TANK FARM | VALVE |  | 1998 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 677.059 | 1365.9016 | PROPANE | 2 | 13 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A FANT, DIRECTOR | 7133699454 | THE PROBABLE CAUSE OF THIS RELEASE IS OPERATOR ERROR. A BODY BLEED PORT ON A BLOCK VALVE WAS INADVERTENTLY LEFT OPEN AFTER MAINTENANCE. DURING INITIAL START UP, APPROXIMATELY 13.03 BARRELS OF PROPANE, A HIGHLY VOLATILE LIQUID, WAS RELEASED TO THE ATOMSPHERE.
2017-09-29 08:50 | YES | NO | 20000121 | 2000-11-14 | 4906 | EXXON PIPELINE CO | NO | 2000-10-27 | 2130 | LA | WEST BATON ROUGE | PORT ALLEN | NO |  | NO | SUNRISE, LOUISIANA, LA HWY #986 (RIVER ROAD), EMPCO-S WEST BANK VALVE SITE |  | NO DATA | OTHER | DESITOMETER | 1999 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3038 | 2056.9054 | 4149.6089 | NATURAL GAS LIQUID | 2 | 140 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | OTHER | INSUFFICIENT MAKE UP OF FITTING | Null |  |  | Null | Null | JOEL C LARKIN | 7136560227 | ON 10/27/00, A STAINLESS STEEL TUBE CAME LOOSE FROM THE FITTING ON A DESITOMETER AT THE WEST BANK SURV SITE. NO OVER-PRESSURE CONDITION WAS NOTED. THE TUBING WAS NOT SUFFICIENTLY TIGHT. THIS RESULTED IN A RELEASE OF ABOUT 140 BBLS OF "RAW MAKE", CONSISTING OF ETHANE, ISO BUTANE, AND OTHER HVL MIX. THE RELEASE WAS CONTROLLED BY SHUTTING OFF THE VALVES TO THE DESITOMETER. PERMANENT REPAIRS WERE MADE BY REPLACING THE TUBING, AND FITTING.
2017-09-29 08:50 | YES | NO | 20000122 | 2000-11-20 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 2000-10-13 | 315 | IL | GRUNDY |  | NO |  | NO | 4755 EAST RT 6 MORRIS, IL 60450 |  | TANK FARM | OTHER | RELIEF VALVE | 1980 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5700 | 3859.2365 | 7785.6389 | PROPANE | 2 | 165 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A FANT | 7133699454 | THE PROBABLE CAUSE OF THIS RELEASE IS DUE TO A MALFUNCTIONING RELIEF VALVE ON A PRESSURIZED PROPANE BREAKOUT TANK: THE PILOT TUBE BECAME OBSTRUCTED AND THE RELIEF VALVE RELIEVED PREMATURELY.
2017-09-29 08:50 | YES | NO | 20000123 | 2000-11-20 | 15490 | PHILLIPS PIPE LINE CO | YES | 2000-10-20 | 130 | OK |  | BECKHAM | NO |  | NO | BUXTON-BORGER LINE O SRW 401-28-3 MP 110-08+79 - SEC 11, T11N, R22W APPROXIMATELY 4 MILES NW OF ELK CITY, OK | 545742 | LINE PIPE | PIPE |  | 1951 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | CRUDE OIL | 1 | 407 | 0 | NO | NO | 10.75 | 0.203 | 42000 | WELDED |  | 1125 | 1037 | YES | 24 | 1455 | 8 | 1978 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LINUS J SCHMITZ, TECHNICAL SERVICE MANAGER | 9186614814 | PIPELINE SPLIT IN A SEAM WHILE OPERATING VERY NEAR MAXIMUM OPERATING PRESSURE. METALLURGICAL EXAMINATION REVEALED COPPER PENETRATION THROUGH THE WALL ALONG THE SEAM BOUNDARIES. COPPER WAS DEPOSITED DURING MANUFACTURE OF THE PIPE.
2017-09-29 08:50 | YES | NO | 20000124 | 2000-11-20 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-10-19 | 1220 | MT | PONDERA | CUT BANK | NO |  | NO | T31N, R4W, SECTION 11, PONDERA COUNTY. APPROXIMATELY 25 MILES SE OF CUTBANK, MT | 545707 | LINE PIPE | PIPE |  | 1961 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 270823.6161 | 546360.6235 | CRUDE OIL | 1 | 1390 | 102 | NO | NO | 8.625 | 0.188 | 52000 |  |  | 1621 | 1580 | YES | 8 | 2026 | 0 | 1989 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RANDY W BEGGS | 3036494090 | AT APPROXIMATELY 12:20 P.M. MDT THE OIL MOVEMENTS OPERATIONS COORDINATOR, NOTICED FROM ALARMS THAT THE CUTBANK MAINLINE UNITS SHUT DOWN ON THE GLACIER 8" LINE WHILE PUMPING SWEET CRUDE. CUT BANK STATION WAS NOTIFIED AND THE TECHNICIAN NOTED THAT THE STATION WENT DOWN ON LOW SUCTION. THE PRESSURE HAD DROPPED ON THE DISCHARGE SIDE OF CUTBANK AND ON THE SUCTION SIDE OF CONRAD STATION. LINE FLYER WAS DISPATCHED TO FLY THE PIPELINE ROUTE TO LOOK FOR A POSSIBLE LEAK. THE LINE FLYER FOUND THE LEAK LOCATED APPROXIMATELY 1/4 MILE NORTH OF MP 342, AT APPROXIMATELY 2:00 P.M. FIELD PERSONNEL WERE ALREADY DISPATCHED TO CLOSE MANUALLY OPERATED BLOCK VALVES WITHIN THIS SEGMENT. COMPANY PERSONNEL ARRIVED AT THE LEAK SITE AT APPROXIMATLEY 3:00 P.M. UPON INVESTIGATING THE AREA, IT WAS DETERMINED THAT THE CAUSE OF FAILURE WAS SEAM SPLIT WITHIN THE LONGITUDINAL WELD SEAM (ERW SEAM) OF THE PIPE. THE FAILED SECTION OF PIPE HAS BEEN SENT TO A LAB FOR METALLURGICAL ANALYSIS.
2017-09-29 08:50 | YES | NO | 20000125 | 2000-11-21 | 18386 | BP OIL PIPELINE CO | YES | 2000-10-22 | 1550 | MS | COVINGTON |  | NO |  | NO | 3.5 MI. EAST OF COLLINS, MS., 1/4 MI.. EAST OF ST HWY 588.1/2 MI. PAST PICKERING RD. | 546286 | PUMPING STATION | PUMP |  | 1992 | OTHER | HYDROSTATIC SURGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33852.952 | 68295.0779 | DIESEL FUEL | 2 | 65 | 60 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TERRY L. HUTSON | 4099386992 | ON OCTOBER 22, 2000, AT APPROXIMATELY 3:50PM., A VERTICAL, DEEP-WELL STYLE PUMP SEPARATED BETWEEN THE PUMP CAN PUMP/MOTOR ASSEMBLY, RELEASING 65 BBLS. OF NUMBER 2 DIESEL FUEL.
2017-09-29 08:50 | YES | NO | 20000126 | 2000-11-23 | 19585 | TRANS MOUNTAIN OIL PIPE LINE CORP | YES | 2000-10-26 | 2135 | WA |  | BELLINGHAM | NO |  | NO | TRANS MOUNTAIN LAUREL STATION - 1009 EAST SMITH ROAD, BELLINGHAM, WA 98226 | 546473 | PUMPING STATION | VALVE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 320000 | 216658.8928 | 437088.4988 | CRUDE OIL |  | 645 | 628 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JOHN L FINGARSON | 6047395297 | THE INCIDENT OCCURRED AT 21:35 PACIFIC TIME ON OCTOBER 26, 2000. THE SOURCE OF THE SPILL WAS AN NPS2 VALVE USED AS A VENT ON THE 16" DIAMETER LATERIAL LINE FROM LAUREL STATION TO CONNECTED REFINERIES IN FERNDALE, WASHINGTON. THE VALVE WAS WITHIN THE CONFINES OF THE LAUREL STATION PROPERTY. THE VALVE WAS TEMPORARILY INSTALLED ON EXCAVATED PIPE FOR ONGOING MAINTENANCE BEING CONDUCTED ON THAT PORTION OF THE PIPELINE SYSTEM. THE SECTION OF THE LINE IN QUESTION HAD BEEN DRAINED AND PURGED. AS THE LINE WAS BEING REFLOODED AT THE CONCLUSION OF THE MAINTENANCE IT WAS NOTICED THAT CRUDE OIL WAS ESCAPING FROM THE VENT VALVE. THE VENT HAD BEEN LEFT OPEN. THE AFFECTED SECTION OF THE LINE WAS IMMEDIATELY ISOLATED BUT OIL CONTINUED TO ESCAPE FROM THE VENT AS A RESULT OF GRAVITY DRAINDOWN. SAFETY CONCERNS PRECLUDED PERSONNEL FROM ACCESSING THE VENT VALVE TO CLOSE IT UNTIL DRAINDOWN WAS COMPLETED AND A SUFFICIENT QUANTITY OF OIL HAD BEEN RECOVERED. AN ESTIMATED TOTAL OF 645 BARRELS WAS RELEASED. OF THIS TOTAL, 628 BARRELS WERE RECOVERED IN LIQUID FORM, AND 17 BARRELS IN CONTAMINATED SOIL WAS ALSO RECOVERED. ALL OF THE SPILLED OIL WAS CONTAINED WITHIN THE STATION SITE.
2017-09-29 08:50 | YES | NO | 20000127 | 2000-11-24 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-10-06 | 1845 |  |  |  | YES | X=2,845,568.6 Y=199,313.4 | NO | OCS BLOCK 310 (MAIN PASS) | 544462 | LINE PIPE | OTHER | 6" BREAKWAY JOINT | 1984 | OTHER | RUBBER SEALS AND 0-RINGS INSIDE BREAKAWAY | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 338529.5201 | 682950.7794 | CRUDE OIL | 3 | 4 | 0 | NO | NO | 6.625 | 0.432 | 42000 | WELDED |  | 1440 | 500 | YES | 8 | 3000 | 0 | 1984 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | GARY E MERRITT | 7132414381 | COMMODITY SPILLED DISSIPATED BY NATURAL FORCES. THE BREAKAWAY JOINT WAS REMOVED FROM THE PIPELINE AND REPLACED WITH A NEW 6" SPOOL PIECE, USING TWO MARK V HYDROCOUPLE SUBSEA PIPELINE REPAIR UNITS.
2017-09-29 08:50 | YES | NO | 20000128 | 2000-11-27 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-11-07 | 815 |  |  |  | YES | X=1792590.95 Y=299753.47 | NO | PIPELINE LATERAL RUNNING BETWEEN GARDEN BANKS 260 AND SOUTH MARSH ISLAND 205 |  | LINE PIPE | BOLTED FITTING |  | 1998 | OTHER | LEAKING BLIND FLANGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 406235.4241 | 819540.9353 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 16 | 0.625 | 52000 | FLANGED |  | 2160 | 1450 | YES | 8 | 3378 | 0 | 1998 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF | 7132414381 | REPAIR MADE WITH BLIND FLANGE AND RTJ. COMMODITY SPILLED DISSIPATED BY NATURAL FORCES.
2017-09-29 08:50 | YES | NO | 20000129 | 2000-11-02 | 879 | CHEMOIL REFINING | NO | 2000-10-27 | 800 | CA |  | LONG BEACH | NO |  | NO | VALVE BOX NEAR SEPULVEDA BLVD - SEE MAP ENCLOSED | 546613 | LINE PIPE | BOLTED FITTING |  | 2000 | OTHER | FLANGE GASKET FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 54164.7232 | 109272.1247 | FUEL OIL | 3 | 300 | 300 | NO | NO | 8 | 0.322 | 25000 | FLANGED |  | 600 | 600 | YES | 4 | 1005 | 7 | 2000 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RANDY TUREK | 5629011961 | FLANGE GASKET FAILED, FILLING VALVE BOX AND SPILLING ONTO SEPULVEDA BLVD.
2017-09-29 08:50 | YES | NO | 20000130 | 2000-11-28 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-10-30 | 1430 | LA |  | ST MARYS | NO |  | NO | BERWICK, LOUISIANA (NEAR MORGAN CITY) | 546808 | LINE PIPE | PIPE |  | 1952 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 1015588.5602 | 2048852.3383 | CRUDE OIL | 3 | 940 | 0 | NO | NO | 22 | 0.312 | 52000 | WELDED |  | 849 | 0 | YES | 8 | 1061 | 0 | 1981 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF | 7132414381 | THIS RELEASE WAS CAUSED BY A 2" SLIT (NOT RUPTURE) LOCATED ON THE OUTSIDE ASPECT OF A LONG RADIUS BEND IN THE PIPE. THE LINE WAS REPAIRED WITH A WELDED SPLIT SLEEVE AND MAG-POWDER TESTED. THE PIPELINE WAS BURIED APPROXIMATELY 18 INCHES BELOW GRADE IN AN AREA THAT IS TYPICALLY SWAMPY, BUT THIS YEAR IS BONE DRY WITH LARGE CRACKS IN THE CLAY BASED SOIL. THE PIPELINE WAS "STAND UP TESTED" WITH A STATIC FLOW AT LINE PRESSURE, PASSING TEST.
2017-09-29 08:50 | YES | NO | 20000131 | 2000-11-30 | 12628 | MOBIL PIPELINE CO | YES | 2000-11-03 | 847 | PA | LANCASTER | RAPHO | NO |  | NO | 1214 N STRICKLER RD LANCASTER CO RAPHO TWP MT JOY PA 17545 | 547144 | LINE PIPE | PIPE |  | 1946 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 677059.0401 | 1365901.5589 | DIESEL FUEL | 3 | 1087 | 894 | NO | NO | 8 | 0.322 | 35000 | WELDED |  | 1440 | 775 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOEL C LARKIN | 7136560227 | AT 0845 NOV 3 2000 CONTRACTOR WAS MAKING A TEMPORARY ROADWAY WITH A LOADER. THE ROADWAY WAS BEING GRADED ON A HILLSIDE. THE LOADER HIT THE PIPELINE AND ONE TOOTH OF THE BUCKET RUPTURED THE PIPELINE. NO ONE-CALL NOTICE WAS MADE. PIPELINE CONTROL CENTER SHUTDOWN PIPELINE SYSTEM. NOTIFIED FIELD LOCATION OF SITUATION. MAINLINE GATE VALVES WERE CLOSED AND RECOVERY AND REMEDIATION PROCESSES STARTED.
2017-09-29 08:50 | YES | NO | 20000132 | 2000-12-04 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 2000-09-22 | 1100 | OK | CLEVELAND |  | NO |  | NO | SW 1/4 OF SECTION 16, TOWNSHIP 9N, RANGE 2W | 542963 | LINE PIPE | NO DATA |  | 1940 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33852.952 | 68295.0779 | CRUDE OIL |  | 550 | 480 | NO | NO | 12 | 2.67 | 1480 | WELDED |  | 1185 | 50 | YES | 8 | 887 | 6 | 1994 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES |  | 3166850836 | WHILE PERFORMING WORK IN THE AREA OF OUR PIPELINE THAT WAS FLAGGED A DOZER WITH RIPPERS ON THE REAR STRUCK OUR LINE CAUSING A REALEASE OF CRUDE OIL.
2017-09-29 08:50 | NO | NO | 20000133 | 2000-12-04 | 31058 | MARATHON ASHLAND PIPE LINE LLC | NO | 2000-10-11 | 1930 | KY | JEFFERSON | LOUISVILLE | NO |  | NO | 5501 NALLEY CT, LOUISVILLE, KY | 544917 | LINE PIPE | PIPE |  | 1973 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 57200 | 38727.7771 | 78129.5692 | JET FUEL | 3 | 1 | 1 | NO | NO | 8.625 | 0.219 | 2132 | WELDED |  | 720 | 550 | YES | 8 | 1000 | 12 | 1990 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | TAD A. SCHELL, REGULATORY COMPLIANCE COORDINATOR | 4194213201 | THE SYSYTEM INVOLVED WAS THE MARATHON ASHLAND PIPELINE LLC LOUISVILLE TO LOUISVILLE INTERNATIONAL AIRPORT 8" PRODUCTS PIPELINE SYSTEM. THE SPILL SITE WAS AT THE REAR OF PROPERTY LOCATED AT 5501 NALLEY CT., LOUISVILLE, KY. THE PRODUCT MIGRATED ALONG THE PIPE AND ENTERED CANE RUN DITCH NEAR A RAIN WATER DRAIN. THE PRODUCT WAS STOPPED APPROXIMATELY 800 DOWNSTREAM OF THE LEAK SITE. REGULATORY AGENCIES, INCLUDING THE NRC, WERE NOTIFIED AS NECESSARY. UPON EXCAVATION OF THE LEAK SITE, SEVERAL SMALL DENTS OVER A 2 LONG AREA WERE OBSERVED ON THE TOP (12 OCLOCK POSITION) OF THE PIPELINE. ONE OF THE DENTS CONTAINED A HAIRLINE CRACK APPROXIMATELY 1" IN LENGTH WHICH WAS THE SOURCE OF THE LEAK. THE PIPELINE WAS REPAIRED AND PLACED BACK INTO SERVICE. THERE WAS NO RECENT THIRD PARTY EXCAVATION IN THE AREA, HOWEVER WE BELIEVE THAT THE PIPELINE WAS DAMAGED BY THIRD PARTY ACTIVITY OCCURRING IN PRIOR YEARS. CONTAMINATED SOIL AND DEBRIS WERE REMOVED AND PROPERLY DISPOSED OF AT WASTE MANAGEMENTS OUTER LOOP LANDFILL IN LOUISVILLE, KY. A DETERMINATION THAT RESPONSE ACTIVITIES, REPAIR AND CLEAN-UP COSTS EXCEEDED $50,000 WAS MADE ON NOVEMBER 17, 2000. THIS REPORT WAS AMENDED SEPTEMBER 7,2001 TO REVISE THE DAMAGE ESTIMATE FROM $65,000 TO $57,200. CLEANUP ACTIVITIES ARE COMPLETE.
2017-09-29 08:50 | YES | NO | 20000134 | 2000-08-08 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 2000-07-06 | 1535 | OR | WASHINGTON |  | NO |  | NO | 11911 WALDO WAY SHERWOOD, OREGON |  | LINE PIPE | PIPE |  | 1962 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | DIESEL FUEL | 3 | 245 | 36 | NO | NO | 8 | 0.188 | 46000 | WELDED |  | 1440 | 1000 | YES | 24 | 1600 | 8 | 1962 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | EDWARD A FANT | 7133699454 | A BULLDOZER WAS REMOVING SPOIL PILES FROM OVER PIPELINE WHEN IT STRUCK AND PUNCTURED SFPPS LINE SECTION NUMBER 14 MILE MARKER 19.4. DIESEL WAS RELEASED COVERING APPROXIMATELY A 10-FOOT BY 30-FOOT AREA. THE SCADA SYSTEM DETECTED MEASUREMENT IMBALANCE AND THE PORTLAND OPERATOR SHUT DOWN THE LINE IMMEDIATELY. APPROXIMATELY 38 MINUTES LATER THE TUALATIN VALLEY FIRE DEPARTMENT NOTIFIED THE PORTLAND OPERATOR OF THE RELEASE AND EXACT LOCATION. THE EMERGENCY PLAN WAS PUT INTO PLACE AND PERSONNEL DISPATCHED TO THE SCENE. A COLLECTION PIT WAD DUG DOWNHILL FROM THE RELEASE SITE AND APPROXIMATELY 36 BARRELS OF FREE PRODUCT WAS RECOVERED. CLEAN UP WAS INITIATED BY KINDER MORGANS EMERGENCY RESPONSE CONTRACTOR. KINDER MORGAN WAS NOT NOTIFIED OF EXCAVATION RELATED ACTIVITY PRIOR TO THE ACCIDENT.
2017-09-29 08:50 | NO | NO | 20000135 | 2000-12-07 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2000-11-12 | 1630 | IN |  |  | NO |  | NO | WASHINGTON CO, IN. T1S,R3E. SECT 9, POSEY TOWNSHIP. ROBINSON TO LOUISVILLE 16" PIPELINE SYSTEM. BLOCK VALVE #10 AT THE BLUE RIVER. | 548049 | NO DATA | VALVE |  | 1977 | OTHER | TUBING CONNECTION ON THE VALVE BODY | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 65236 | 44168.6235 | 89105.9541 | GASOLINE | 3 | 0 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A SCHELL, PE REGULATORY | 4194213201 | A LOCAL PROPERTY OWNER CALLED MARATHON ASHLAND PIPE LINE (MAPL) OPERATIONS CENTER AND REPORTED A SHEEN IN THE VICINITY OF THE MAPL ROBINSON TO LOUISVILLE 16" PRODUCTS PIPELINE SYSTEM. THE PIPELINE WAS IMMEDIATELY SHUTDOWN, LOCAL HAZMAT TEAM AND FIRE DEPARTMENT RESPONDED AND DEPLOYED BOOM INTO THE DRAINAGE WAY. MAPL PERSONNEL MADE ALL APPROPRIATE AGENCY NOTIFICATIONS. MAPL RESPONDED AND NOTIFIED KOESTER ENVIRONMENTAL AND BOLINS CONSTRUCTION TO RESPOND WITH EMERGENCY EQUIPMENT AND MANPOWER. THE SHEEN WAS REMOVED FROM THE DRAINAGE WAY AND ABSORBENT MATERIAL WAS DEPLOYED TO CONTAIN ANY LEACHING SHEEN. BLOCK VALVE #10 WAS EXCAVATED AND INSPECTED. A 1/2" TUBING CONNECTION IN THE BOTTOM OF THE VALVE BODY WAS FOUND SEEPING PRODUCT. THE PIPELINE WAS DRAINED OF PRODUCT, THE TUBING REMOVED AND VALVE BODY PLUGGED WITH A 3/4" PLUG. A 3/4" X 1/2" BUSHING WAS FOUND CRACKED AND DETERMINED TO BE THE CAUSE OF THE RELEASE. THE PIPELINE WAS RETURNED TO SERVICE ON 11-15-00. THE VOLUME OF THE RELEASE HAS NOT BEEN DETERMINED AT THIS TIME. FUTURE ACTIVITIES AT THE RELEASE SITE INCLUDE SOIL INVESTIGATION AND REMEDIATION AS APPROVED BY THE INDIANA DEPARTMENT OF ENVIRONMENTAL MANAGEMENT(IDEM).
2017-09-29 08:50 | YES | NO | 20000136 | 2000-12-11 | 18718 | SUN PIPE LINE CO | NO | 2000-11-10 | 938 | TX | JONES |  | NO |  | NO | 2500' NORTH OF JONES COUNTY ROAD 256, PASTURE LAND. | 547912 | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 338.5295 | 682.9508 | CRUDE OIL | 3 | 90 | 75 | NO | NO | 10 | 0.365 | 0 | THREADED |  | 480 | 0 | Null | 8 | 600 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | EDITH F COEN MANAGER | 9185686942
2017-09-29 08:50 | YES | NO | 20000137 | 2000-12-11 | 31462 | DYNEGY CRUDE GATHERING INC | NO | 1999-10-19 | 100 | OK | PAYNE |  | NO |  | NO | JCT. HWY 33 AND LINWOOD AVE IN CUSHING, OK PAYNE CO. 2 1/2 MILES SOUTH ON LINWOOD AVE. EAST SIDE OF ROAD DYNEGY CUSHING SOUTH STATION. |  | TANK FARM | VALVE |  | 0 | OTHER | FAILURE OF 1/2 INCH BALL VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6910.5487 | 13941.3681 | CRUDE OIL | 1 | 20 | 0 | YES | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | SCOTT LEWIS OPERATIONS | 4056915016 | 1/2 BRASS BALL VALVE ON SUCTION SIDE OF PIPELINE PUMP BLOWING CRUDE ONTO ELECTRICAL BOX.
2017-09-29 08:50 | YES | NO | 20000138 | 2000-12-11 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-11-14 | 1530 | WY | SWEETWATER |  | NO |  | YES | T18N,R108W,SECTION 22,SWEETWATER COUNTY. APPROXIMATELY 7 MILES WEST GREEN RIVER, MILE POST 136.1 | 548257 | LINE PIPE | PIPE |  | 1952 | FAILED PIPE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 304676.5681 | 614655.7015 | JET FUEL |  | 900 | 4 | NO | NO | 8.625 | 0.277 | 45000 |  |  | 2081 | 1400 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null |  |  | Null | Null | RANDY W BEGGS DIRECTOR | 3036494090 | AT APPROXIMATELY 14:35 ON 11/14/00 OIL MOVEMENTS RECEIVED NOTICE BY SCADA THAT THE DISCHARGE PRESSURE WENT FROM 1600 PSI TO 200 PSI AT THE PILOT BUTTE PUMP STATION AND THE LINE WAS IN THE PROCESS OF SHUTTING DOWN. PERSONNEL AND THE LINE FLYER WERE IMMEDIATELY DISPATCHED TO CLOSE BLOCK VALVES AND SURVEY THE LINE FOR A LEAK. THE LEAK WAS FOUND AT APPROXIMATELY 16:30. UPON INVESTIGATION, THE LINE HAD BEEN PREVIOUSLY DAMAGED BY THE PIONEER PIPE LINE CO. CONTRACTOR THAT WAS INSTALLING THE NEW 12" LINE ADJACENT TO THE EXISTING 8"LINE. THE LINE HAD BEEN DAMAGED DURING RIGHT-OF-WAY CLEAN-UP ON THE NEW LINE. CLEAN-UP WAS SOMEWHAT COMPLICATED BY SNOW COVER AND NUMEROUS OTHER PIPELINES IN THE AREA. THE DAMAGE OCCURRED SOMETIME BETWEEN NOV 1 AND NOV. 14, WHILE THE WEST END OF PIONEER PIPE LINE WAS BEING PRESSURE TESTED. ONCE THE LINE WAS STARTED BACK UP, AFTER THE PRESSURE TEST, THE LINE FAILED BEFORE REACHING MOP FOR THIS SEGMENT. BEFORE START UP AFTER THE REPAIR, THE LINE WAS WALKED AND DRIVEN FOR 2 MILES ON EACH SIDE OF THE INCIDENT SITE, TO DETERMINE IF THE CONTRACTOR MIGHT HAVE ENCROACHED ON THE EXITING 8" RIGHT-OF WAY. AREAS WERE IDENTIFIED WHERE THE CONTRACTOR ENCROACHED ON THE EXITING RIGHT-OF-WAY. THOSE AREAS WERE EXPOSED AND NO DAMAGE WAS IDENTIFIED. THE LINE WAS RESTARTED ON THURSDAY NOV. 16.
2017-09-29 08:50 | YES | NO | 20000139 | 2000-12-15 | 30871 | MID - VALLEY PIPELINE COMPANY | YES | 2000-11-15 | 2320 | LA | MOREHOUSE |  | NO |  | NO | SW QUARTER, SECTION 12, TOWNSHIP 22 NORTH, RANGE 9 EAST, APPROXIMATLEY ONE MILE NORTHWEST OF INTERSECTION OF STATE HIGHWAYS 585 AND 879. | 548364 | LINE PIPE | VALVE |  | 1991 | OTHER | 1/2" DRAIN PLUG AT BASE OF VALVE BACKED OUT. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 950000 | 643206.0881 | 1297606.4809 | CRUDE OIL | 1 | 1350 | 1325 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDITH F COEN, MANAGER HES-WESTERN AREA | 9185686942 | AT 2320 HOURS ON 11/15/00, A LANDOWNER DISCOVERED CRUDE OIL COMING OUT OF THE GROUND AT THE BASE OF A MAINLINE BLOCK VALVE AT MID-VALLEYS M.P. 200 IN MOREHOUSE PARISH, LOUISIANA. THE LANDOWNER NOTIFIED THE LOCAL SHERIFFS DEPARTMENT AND THE MVPL CONTROL CENTER IN TULSA, OK. THIS PIPELINE SEGMENT HAD BEEN SHUT DOWN AT 2213 FOR NORMAL OPERATIONS AND WAS DOWN AT THE TIME OF CALL IN. THE LINE SEGMENT WAS FURTHER ISOLATED BY REMOTE BLOCK VALVES AT THE TIME OF CALL IN. THE VALVE WAS EXCAVATED AND IT WAS DISCOVERED THAT A 1/2" DRAIN PLUG HAD BLOCKED OUT OF THE BASE OF THE VALVE. THE PLUG HOLE THREADS AND CONDITION OF VALVE WERE INSPECTED AND SHOWED NO SIGNS OF WEAR OR DEFECT. A NEW PLUG WAS INSTALLED AND THE LINE WAS RETURNED TO SERVICE. RECOVERED CRUDE WAS RETURNED TO PIPELINE SYSTEM.
2017-09-29 08:50 | YES | NO | 20000140 | 2000-12-19 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2000-11-19 | 1530 | TX | PARKER |  | NO |  | NO | WEST TEXAS LPG LTD PARTNERSHIP 6" BRIDGEPORT LATERAL PIPELINE RIGHT OF WAY APPROX 2 MILES NORTH OF THE TOWN OF MILSAF, TX MILEPOST 8.00 | 546668 | LINE PIPE | PIPE |  | 1965 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 64300 | 43534.8963 | 87827.4702 | L. P. G. | 2 | 911 | 0 | NO | NO | 6 | 0.28 | 24000 | WELDED |  | 952 | 675 | YES | 8 | 1190 | 3 | 1990 |  | Null | YES |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | RANDY BURKE | 2815963569 | LEAK @ 15:30 ON 6" BRIDGEPORT LATERAL WHEN CONTRACTOR LAYING NEW 10" LINE FOR CPL, DAMAGED EXISTING 6" LPG LINE SOUTH OF MILSAP, TX. THE DAMAGED SECTION OF LAP WELDED PIPELINE WAS BLOCKED IN @ 16:10 @ MP 7.18 AND MP 9.45. AGENCY NOTIFICATIONS: 1533- CALLED 911- CALL WAS TRANSFERRED TO PARKER COUNTY. CHEVRON REQUESTED RESPONSE LOCAL SHERIFF AND FIRE DEPARTMENTS. LOCAL RESPONDERS WERE TOLD TO RESPOND TO THE INCIDENT AT WILSON BEND ROAD, OFF OF COUNTY ROAD 113. 1625- CALLED NATIONAL RESPONSE CENTER (NRC) TO MS. BENNETT (800)424-8802. WAS GIVEN REPORT #548668. CALLED THE LOCAL EMERGENCY PLANNING COMMITTEE (LEPC). SPOKE TO D. SOSDBEE SAID THAT THEY WERE ALREADY AWARE AND RESPONDING. TWO CITY FIRE DEPARTMENTS WERE ALREADY ON SCENE AND NO INJURIES WERE REPORTED. 1630 - CALLED THE TEXAS NATURAL RESOURCES AND CONSERVATION COMMISSION (TNRCC) (512)462-1727 IN AUSTIN. WAS TOLD BY THE AUSTIN OFFICE THAT THEY WOULD CONTACT THE TNRCC REPRESENTATIVE IN THEIR ARLINGTON OFFICE AND THE LOCAL REPRESENTATIVE WOULD CALL BACK EARLIER. MR JIM CURLIN WITH THE TNRCC ARLINGTON OFFICE CALLED TO VERIFY THE INFORMATION THAT HE WAS GIVEN BY HIS AUSTIN OFFICE EARLIER. 1645- CALLED THE TEXAS RAILROAD COMMISSION (TRC) OIL & GAS DIVISION (512)463-6788. KATHY GUZMAN RETURNED THE PHONE CALL AT 1735. KATHY SAID SHE WOULD CALL THE CPL WEATHERFORD OFFICE FOR MORE DETAILS. 1645- CALL THE STATE EMERGENCY RESPONSE COMMISSION (SERC) (800)832-8224 AND SPOKE TO MR. BEAN. THE SERC ISSUED INCIDENT #20003062 TO THE INCIDENT. MR. BEAN ALSO STATED THAT HE WOULD BE FORWARDING THE INFORMATION GIVEN TO HIM TO THE TEXAS GENERAL LAND OFFICE (TGLO). TEXAS NATURAL RESOURCES AND CONSERVATION COMMISSION (TNRCC) AND THE TEXAS RAILROAD COMMISSION.
2017-09-29 08:50 | YES | NO | 20000141 | 2000-12-18 | 18386 | BP OIL PIPELINE CO | NO | 2000-10-09 | 1030 | TX | LUBBOCK |  | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1948 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 101558.856 | 204885.2338 | CRUDE OIL | 1 | 500 | 450 | NO | NO | 8 | 0.277 | 25000 | WELDED |  | 590 | 1100 | YES | 8 | 682 | 6 | 1999 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TONY WOFFORD | 9155733589 | MANIFOLD VALVE WAS CLOSED AND PUMPS CONTINUED TO RUN. THE LINES RELIEF VALVE FAILED TO OPERATE PROPERLY BECAUSE OF OBSTRUCTIONS FOUND IN VALVE.
2017-09-29 08:50 | YES | NO | 20000142 | 2000-12-18 | 31456 | TEPPCO CRUDE GENERAL PARTNER, LLC LIQUID | YES | 2000-11-18 | 605 | TX | GALVESTON | TEXAS CITY | NO |  | NO | SEAWAY PIPELINE CO. TANK FARM, INTERSECTION OF STATE HIGHWAY 3 AN STATE HIGHWAY 146. |  | TANK FARM | BOLTED FITTING |  | 1980 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 67705.904 | 136590.1559 | CRUDE OIL | 1 | 1130 | 1020 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LEONARD MALLETT | 7137593755 | AT APPROXIMATELY 0605 HOURS, NOVEMBER 18, THE SEAWAY PIPELINE COMPANY TEXAS CITY TERMINAL EXPERIENCED AN UNINTENTIONAL VALVE CLOSURE WHICH RESULTED IN AN OVER PRESSURE CONDITION OF METER STATION AND TANK MANIFOLD PIPING. THIS CONDITION RESULTED IN THE FAILURE OF GASKETS IN BOLTED FLANGES.
2017-09-29 08:50 | YES | NO | 20000143 | 2000-12-27 | 30871 | MID - VALLEY PIPELINE COMPANY | YES | 2000-11-24 | 2239 | LA | CLAIBORNE | HAYNESVILLE | NO |  | NO | SE 1/4 OF NE 1/4, SECTION 33, TOWNSHIP 32 N, RANGE 7W; APPROXIMATELY ONE MILE NW OF INTERSECTION OF KENDRICK SPRINGS ROAD AND MADDOX ROAD. |  | LINE PIPE | PIPE |  | 1950 | FAILED PIPE | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 1750000 | 1184853.3202 | 2390327.728 | CRUDE OIL | 1 | 1303 | 1150 | NO | NO | 20 | 0.25 | 1300 | WELDED |  | 840 | 747 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | OTHER | STRESS CORROSION CRACKING |  |  | Null |  |  | Null | Null | EDITH F. COEN | 9185866942 | AT 2239 HOURS CST ON 11/24/00, FOLLOWING THE NORMAL SHUTDOWN OF A DOWNSTREAM PUMPING STATION, THE TULSA CONTROL CENTER SUPERVISOR NOTICED A RAPID PRESSURE DROP IN THE AFFECTED LINE SEGMENT. THE PIPELINE SYSTEM WAS IMMEDIATELY SHUTDOWN AND VALVED OUT. FIELD PERSONNEL WERE DISPATCHED TO INSPECT THE PIPELINE. THE SPILL SITE WAS DISCOVERED AT ABOUT 0400 HRS ON 11/25/00. THE LINE WAS EXCAVATED AND IT WAS DISCOVERED THAT THE PIPE HAD RUPTURED LONGITUDINALLY AT THE 6 OCLOCK POSITION. THE PIPE IS X52, A O SMITH, SEAMED PIPE (SMITHWELD PROCESS-NOT ERW). THE RUPTURE WAS NOT IN THE SEAM. THE PIPE HAS BEEN SENT TO A THIRD PARTY LAB IN FOR METALLURGICAL ANALYSIS TO DETERMINE THE CAUSE OF THE FAILURE-RESULTS ARE FORTHCOMING AND A REVISED 7001 REPORT WILL BE SUBMITTED. THE RUPTURED SECTION OF PIPE WAS CUT OUT AND REPLACED WITH NEW PIPE. THE NEW PIPE HAD BEEN PREVIOUSLY HYDROTESTED AND THE BUTT WELDS WERE X-RAYED. THE LINE MOP WAS DERATED TO 672 PSI PENDING RESULTS OF THE DEFECT ANALYSIS (80% OF THE PREVIOUS MOP OF 840 PSI) AND THE LINE WAS RETURNED TO SERVICE. RECOVERED CRUDE OIL WAS RETURNED TO THE PIPELINE SYSTEM. THE FAILURE WAS CAUSED BY CORROSION - FATIGUE THAT INITIATED FROM NEAR NEUTRAL PH STRESS CORROSION CRACKING (SCC) ON THE OUTSIDE SURFACE OF THE PIPE BODY. THE PIPE FAILED WHEN A PRESSURE SURGE, CAUSED BY AN UNEXPECTED PUMP SHUTDOWN AT THE DOWNSTREAM LOCATION, REACHED THIS POINT.
2017-09-29 08:50 | YES | NO | 20000144 | 2000-12-27 | 31323 | DAKOTA GASIFICATION COMPANY | YES | 2000-11-19 | 1810 | ND | WILLIAMS | TIOGA | NO |  | NO | 1 1/2 MILES EAST OF TIOGA, ND. EASTERN EDGE OF WILLIAMS COUNTY. | 548739 | LINE PIPE | VALVE |  | 1999 | OTHER | FROSTHEAVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 371000 | 251188.9039 | 506749.4783 | CARBON DIOXIDE | 3 | 83 | 0 | NO | NO | 12 | 0.375 | 0 | WELDED |  | 2964 | 2200 | YES | 8 | 3705 | 9 | 1999 |  | Null | Null |  |  | FROSTHEAVE |  | Null | ONE CALL |  | NO | NO | FRED R. STERN | 7018736510 | AT 1810 HRS ON 11-19-00, DAKOTA GASIFICATION RECEIVED A CALL FROM AMERADA HESS GAS PLANT IN TIOGA, ND. THEY INFORMED OUR PROTECTION SERVICES DEPARTMENT THAT THEY SUSPECTED A GAS LEAK WITHIN OUR (DGC) VALVE STATION LOCATED 1 1/2 EAST OF TIOGA. EMERGENCY INVESTIGATION TEAM DISPATCHED FROM DGC AT 1930 HRS. THE PIPELINE WAS ESD AT APPROXIMATELY 1900 HRS. INVESTIGATION TEAM ARRIVED AT SCENE 2240 HRS. LEAK WAS IDENTIFIED AND SECURELY ISOLATED. 0230 HRS-LEAK WAS CONTAINED, 0530 HRS ALL CLEAR NOTIFICATION WAS DECLARED.
2017-09-29 08:50 | YES | NO | 20010001 | 2001-01-08 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 2000-12-06 | 1910 | IL | GRUNDY |  | NO |  | NO | 4755 EAST RT.6, MORRIS, ILLINOIS, 60450 |  | TANK FARM | OTHER | RELIEF VALVE PILOT | 1971 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 7617 | 5157.1587 | 10404.0722 | PROPANE | 2 | 107 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A. FANT | 7133699454 | THE PROBABLE CAUSE OF THIS RELEASE IS DUE TO A CRACKED DIAPHRAGM IN A RELIEF VALVE PILOT ON A PRESSURIZED PROPANE BREAKOUT TANK.
2017-09-29 08:50 | YES | NO | 20010002 | 2001-01-09 | 13162 | NAVAJO REFINING CO | YES | 2000-12-30 | 830 | TX | EL PASO |  | NO |  | YES |  | 552235 | TANK FARM | BOLTED FITTING |  | 1981 | OTHER | EQUIPMENT FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | GASOLINE | 3 | 90 | 60 | YES | YES | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JIM G. TOWNSEND | 5057483311 | DURING THE STARTUP OF A TRANSFER LINE IN OUR EL PASO TERMINAL A FILTER VESSEL BEGAN LEAKING. THE VESSEL LEAKED AT THE TOP CLOSURE GASKET. (O-RING DESIGN) THE TRANSFER PUMP WAS IMMEDIATELY SHUTDOWN AND ISOLATED. THE FIRE DEPARTMENT WAS CALLED AND FOAM WAS APPLIED TO THE AFFECTED AREA OF THE TERMINAL MANIFOLD. OTHER TRANSFERS THAT WERE TAKING PLACE THROUGH MANIFOLD PIPING WAS SHUTDOWN AND ISOLATED. THE VAPORS IN THE AREA WERE MONITORED AS CLEANUP CREWS WERE REMOVING THE FREE PRODUCT.
2017-09-29 08:50 | YES | NO | 20010003 | 2001-01-10 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2000-12-08 | 1430 | TX |  | KERMIT | NO |  | NO | HENDRICK TANK FARM, WINKLER COUNTY | 550424 | PUMPING STATION | VALVE |  | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3385.2952 | 6829.5078 | CRUDE OIL | 3 | 200 | 140 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF | 7132414381 | RELEASE OCCURRED AFTER STRAINERS WERE CHANGED ON METER. A 2" VALVE ON THE STAINER BODY WAS APPARENTLY LEFT OPEN.
2017-09-29 08:50 | YES | NO | 20010004 | 2001-01-16 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | YES | 2000-12-12 | 2258 | CA | CONTRA COSTA | CONCORD | NO |  | NO | APPROXIMATELY 400 FT. EAST OF PACHECO SLOUGH RAILROAD TRESTLE CROSSING ON SOUTH SIDE OF WATERFRONT ROAD, CONCORD, CA. |  | LINE PIPE | PIPE |  | 1967 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 270823.6161 | 546360.6235 | DIESEL FUEL | 3 | 0 | 0 | NO | NO | 14 | 0.219 | 52000 | WELDED |  | 1148 | 763 | YES | 31 | 1450 | 1 | 1967 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A. BUZZ | 7133699454 | THIS RELEASE WAS DUE TO A CRACK THAT DEVELOPED IN A DENT ON THE BOTTOM OF THE PIPE.
2017-09-29 08:50 | YES | NO | 20010005 | 2001-01-12 | 443 | AMOCO PIPELINE CO | YES | 2000-12-10 | 0 | OK | PAWNEE |  | NO |  | NO | SEC. 30, TWP 20 NORTH, RANGE 8 WEST. | 550533 | LINE PIPE | PIPE |  | 1944 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 16 | 0.281 | 1089 | WELDED |  | 784 | 300 | YES | 8 | 980 | 8 | 1992 | INTERNAL | Null | Null | GALVANIC |  |  |  | Null |  |  | Null | Null | STEWART CARSE | 9182231101 | CRUDE OIL WAS RELEASED AS A RESULT OF A NO. 2 PENCIL HOLE SIZED LEAK ON A 16" PIPELINE. OIL TRAVELED DOWN GRADIENT VIA A DRAINAGE DITCH TO HOUSE CREEK. CLEAN UP METHODS HAVE INCLUDED USE OF SKIMMERS, VACUUMING AND PICKUP OF OIL WHICH IS BEING TRANSPORTED FOR RE-INJECTION BACK INTO PIPELINE SYSTEM AT CUSHING, OK. CONTAMINATED SOIL WILL BE TRANSPORTED TO AMOCOS CUSHING, OK. FACILITY FOR BIOREMEDIATION. A ROOT CAUSE FAILURE ANALYSIS INVESTIGATION WILL BE CONDUCTED, FINDINGS SHOULD AND STEPS TAKEN TO PREVENT REOCCURRENCE.
2017-09-29 08:50 | YES | NO | 20010006 | 2001-01-22 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-12-13 | 1430 | MT | LEWIS AND CLARK | HELENA | NO |  | NO | T10N, R3W, SECTION 28, LEWIS AND CLARK COUNTY. APPROXIMATELY 2 MILES EAST OF HELENA, MT. | 550865 | TANK FARM | TANK |  | 1953 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 507794.2801 | 1024426.1691 |  |  | 1247 | 42 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RANDY W. BEGGS | 3036494090 | ON DEC.14, 2000 AT APPROXIMATELY 2:30P.M. AT THE HELENA PRODUCTS TERMINAL A TANK WAS OVERFILLED, RELEASING APPROXIMATELY 1247 BBLS OF UNLEADED GASOLINE. THE SPILL RESULTED IN THE EVACUATION OF AN AREA OF APPROXIMATELY 1/2 MILE IN ALL DIRECTIONS FROM THE FACILITY. PRELIMINARY CONCLUSIONS FROM THE ROOT CAUSE FAILURE ANALYSIS PERFORMED ARE:1) THE FLOW OF PRODUCT FROM THE PIPELINE WAS NOT DIVERTED TO A DIFFERENT TANK AT THE PRESCRIBED TIME, 2) THE LOCAL HARDWARE HIGH LEVEL ALARM FAILED AND 3) OIL MOVEMENTS GROUP HAS NO PROCESS TO RESPOND TO SOFT WARE ALARMS RECEIVED FROM THE TERMINAL.
2017-09-29 08:50 | YES | NO | 20010007 | 2001-01-25 | 31456 | TEPPCO CRUDE GENERAL PARTNER, LLC LIQUID | NO | 2000-09-30 | 2300 | TX |  | BURKBURNETT | NO |  | NO | 1429 CHAPPARAL ST, BURKBURNETT, TX (INTERSECTION OF CHAPPARAL ST & PAWHUSKA) |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 169264.76 | 341475.3897 | CRUDE OIL | 1 | 475 | 35 | Null | Null | 6.625 | 0.322 | 0 | THREADED |  | 575 | 40 | YES | 8 | 725 | 12 | 1995 | EXTERNAL | Null | YES | OTHER | CONCENTRATION CELLS |  |  | Null |  |  | Null | Null | JAMES E MIKA | 7137593755 | CORROSION ON A SEGMENT OF PIPE RESULTED IN THE DEVELOPMENT OF A PINHOLE IN THE PIPE, WHICH ALLOWED CRUDE OIL TO BE RELEASED. A NEW SEGMENT OF PIPE HAS BEEN INSTALLED AND REMEDIAL ACTIVITIES AT THE SITE ARE ONGOING.
2017-09-29 08:50 | YES | NO | 20010008 | 2001-02-05 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2000-12-19 | 635 | KS | GREENWOOD |  | NO |  | NO | W/2 SECTION 13, TOWNSHIP 26 SOUTH, RANGE 11 EAST, GREENWOOD COUNTY, KS (COUNTY RD. 14) | 551381 | LINE PIPE | PIPE |  | 1930 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33852.952 | 68295.0779 | GASOLINE | 2 | 2090 | 660 | NO | NO | 10.75 | 0.25 | 35000 | WELDED |  | 913 | 787 | YES | 8 | 1295 | 0 | 1988 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | VANCE WEBB | 5807674845 | AT 06:35 HRS. ON DECEMBER 19, 2000, CONOCO PIPE LINE (CPL) OIL MOVEMENTS GROUP LOCATED IN HOUSTON TEXAS, RECEIVED AN ALARM THAT INDICATED A LOW SUCTION CONDITION EXISTED AT ONE OF THE PUMP STATIONS ON THE KANSAS CITY PIPE LINE (KCPL) SYSTEM. AFTER EXAMINING THE CONTROL PARAMETERS OF TH3E SYSTEM, THE OPERATIONS COORDINATOR ATTEMPTED TO RESET THE ALARM AND RESTART THE UNIT. UNABLE TO RESTART THE UNIT, THE OPERATIONS COORDINATOR STARTED THE BACK-UP UNIT. WHEN THE CONTROL PARAMETERS FAILED TO INDICATE THE NECESSARY CHANGES CONSISTENT WITH OPERATING THE UNIT, THE LINE WAS IMMEDIATELY SHUT DOWN AND ISOLATED (THE ISOLATION OPERATION WAS COMPLETE BY 06:45 HRS. DECEMBER 19, 2000). SIMULTANEOUSLY TO THE ISOLATION PROCESS, EMERGENCY PERSONNEL WERE NOTIFIED OF THE POTENTIAL LINE FAILURE AND DISPATCHED TO LOCATE THE POSSIBLE RELEASE. WHILE RESPONSE PERSONNEL WERE ATTEMPTING TO LOCATE THE POSSIBLE RELEASE, THE CPL OIL MOVEMENTS GROUP RECEIVED AN EMERGENCY PHONE CALL AT 07:05 HRS. FROM A PASSERBY NEAR EUREKA, KS. THE CALLER REPORTED GASOLINE RUNNING IN A BARROW DITCH ALONG COUNTY RD 14 IN GREENWOOD COUNTY, KS. RESPONSE PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE AREA, WHERE THEY FURTHER ISOLATED THE FAILURE POINT, VIA MANUALLY OPERATED BLOCK VALVES ON EITHER SIDE OF THE RELEASE. CONTAINMENT AND RECOVERY OPERATIONS WERE UNDERWAY BY 08:15.THE INITIAL AGENCY NOTIFICATIONS TO THE NRC AND KDHE WERE MADE AT 09:20 HRS. AND 09:30 HRS. ON DECEMBER 19TH, 2000 RESPECTIVELY. ADDITIONALLY, THE CENTRAL REGION OFFICE OF PIPELINE SAFETY WAS NOTIFIED AS A COURTESY AT 09:35 HRS ON THAT SAME DAY. THE RELEASE VOLUME REPORTED DURING THESE INITIAL AGENCY NOTIFICATIONS, WAS 50 TO 100BBLS. AS THE RECOVERY PROCESS PROGRESSED, IT BECAME EVIDENT THAT MORE PRODUCT HAD BEEN RELEASED THAN ORIGINALLY ESTIMATED. THIS WAS CONFIRMED BY THE QUANTITY OF PRODUCT BEING RECOVERED, AS WELL AS BY THE VOLUMES REQUIRED TO REPACK THE PIPELINE SYSTEM AFTER REPAIRS WERE COMPLETED. THE INITIAL ESTIMATE OF RELEASE PRODUCT WAS BASED SOLELY ON THE FIRST RESPONDERS VISUAL RECONNAISSANCE OF THE RELEASE SITE. UNFORTUNATELY THE RELEASE OCCURED DURING A HEAVY SNOWFALL, AND IT HAS BECOME APPARENT THAT THE SNOWFALL HAMPERED THE FIRST RESPONDERS ABILITY TO SEE PRODUCT THAT HAD MIGRATED BENEATH THE SNOW. THE RELEASE VOLUME IS NOW ESTIMATED AT 2090 BBLS. AN ADDITIONAL CALL WAS MADE TO THE CENTRAL REGION OFFICE OF PIPELINE SAFETY ON JANUARY 3, 2001 @ 09:45 TO UPDATE THEM AS TO THE CURRENT ESTIMATED VOLUME FOR THE RELEASE. ADDITIONALLY, THIS INFORMATION WAS PASSED ON TO THE KDHE. WITH REGARD TO THE FAILURE, A FULL RCFA IS UNDERWAY. HOWEVER, PRELIMINARY RESULTS INDICATE THAT THE FAILURE OCCURRED DUE TO STRESS ASSOCIATED WITH THE HEAT AFFECTED ZONE OF AN OLD PATCH TYPE REPAIR (THE PATCH WAS LOCATED IN AN UNDER-BEND AT A ROAD CROSSING). THE PATCH WAS APPROXIMATELY 12" LONG AND 8" WIDE AND WAS INSTALLED PRIOR TO CPL OPERATING THE PIPELINE SYSTEM. WITH REGARD TO THE REPAIR, CPL MAINTENANCE PERSONNEL REPLACED APPROXIMATELY 180 FEET OF 10" PIPE. THIS FOOTAGE WAS NECESSARY TO ENSURE THE TIE IN LOCATIONS WERE A SUFFICIENTLY SAFE DISTANCE FROM THE AREA OF IMPACTED SOIL.
2017-09-29 08:50 | YES | NO | 20010009 | 2001-02-05 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2001-01-06 | 700 | IL | CLARK |  | NO |  | NO | MAPL MARTINSVILLE, IL PIPELINE STATION. LOCATED 1 MILE WEST OF MARTINSVILLE ON HWY 40. |  | NO DATA | OTHER | EXTERNAL FLOATING ROOF TANK ROOF DRAIN PIPING | 1999 | OTHER | LEAK IN ROOF DRAIN PIPING ON EXTERNAL FLOATING | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 49580.5369 | 100023.9693 | TRANSMIX (PART.REFINED PETRO) | 3 | 440 | 405 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A SCHELL | 4194213201 | THE ROOF DRAIN PIPING ON TANK 19 DEVELOPED A LEAK ALLOWING PETROLEUM NAPTHA TO ENTER THE ROOF DRAIN SYSTEM. A PETROLEUM SENSING DEVICE DETECTED THE PRESENCE OF NAPTHA IN THE ROOF DRAIN SYSTEM AND ACTIVATED AN AUTOMATIC ROOF DRAIN VALVE CLOSURE MECHANISM HOWEVER INSULATION INSTALLED AROUND THE DRAIN VALVE INHIBITED FULL CLOSURE OF THE VALVE ALLOWING PETROLEUM NAPTHA TO DRAIN INTO THE TANK DIKE.THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AND ILLINOIS EPA. AS OF THIS DATE, CLEANUP EFFORTS CONTINUE UNDER THE OVERSIGHT OF ILLINOIS EPA.
2017-09-29 08:50 | YES | NO | 20010010 | 2001-02-05 | 31443 | ALON USA, LP | NO | 2001-01-20 | 1430 | TX | ROBERTSON | HEARNE | NO |  | NO | LAT 30 - DEGREES, 53' 32" N & LONG 96 DEGREES, 33' 13" W APPROX 3 MIL EAST OF HEARNE ON FM-391. LEFT ON WINDING RD (GRAVE) APPROX 1 MI, THROUGH MILLER RANCH GA | 554241 | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3305.3691 | 6668.2646 | CRUDE OIL | 1 | 52 | 0 | NO | NO | 10 | 0.307 | 35000 | WELDED |  | 1050 | 1050 | YES | 8 | 1279 | 9 | 1988 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | BOB REED SR | 9152639256 | AT 2:30 P.M. ON SATURDAY, JANUARY 20TH, LANDOWNER AARON MILLER CALLED ALONS BIG SPRING (TEXAS) PIPELINE CONTROL CENTER TO REPORT THE LEAK ON HIS PROPERTY. THE PIPELINE WAS SHUT-DOWN BETWEEN 2:32-2:40 P.M. BETWEEN 2:25-2:50PM, THE PIPELINES MAINTENANCE AND ADMINISTRATIVE PERSONNEL WERE NOTIFIED. AT 4:55 P.M., 1/20/01, NOTIFICATION WAS GIVEN TO ONE CALL SYSTEMS RE EMERGENCY REPAIR WORK/EXCAVATION ACTIVITIES ON THE PIPELINE. THE REPAIRS WERE COMPLETED AND THE PIPELINE RESTARTED AT 11:10 P.M. 1/20/01. FINAL CLEANUP AND SOIL REMEDIATION WILL BE COMPLETED AS SOON AS SOIL CONDITIONS IMPROVE.
2017-09-29 08:50 | YES | NO | 20010011 | 2001-02-05 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 2000-12-02 | 2015 | TX | SCURRY |  | NO |  | NO | SW 4 SECTION 44, BLK 3 OF H & G NRR SURVEY FROM COLORADO CITY, GO NORTH 11.5 MILES ON HWY 208 TO FM 4156, THEN NORTH INTO STATION. |  | TANK FARM | TANK |  | 0 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3385.2952 | 6829.5078 | CRUDE OIL | 1 | 150 | 130 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RONNY DAVENPORT, SR | 7136466389 | TANK WAS OVERFILLED DUE TO MALFUNCTION OF TANK GAUGE. THE TANK GAUGE STUCK GIVING AN ERROREOUS READING TO THE MIDLAND CONTROL CENTER.
2017-09-29 08:50 | YES | NO | 20010012 | 2001-02-05 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 2000-12-04 | 715 | TX | SCURRY |  | NO |  | NO | SW 4 SECTION 44, BLK 3 OF H & G NRR SURVEY FROM COLORADO CITY, GO NORTH 11.5 MILES ON HWY 208 TO FM 4156, THEN EAST 3 MILES, THEN NORTH INTO STATION |  | TANK FARM | TANK |  | 0 | OTHER | TANK MIXER SEAL FAILED ALLOWING OIL TO RUN OUT | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 16926.476 | 34147.539 | CRUDE OIL | 1 | 6500 | 6450 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RONNY DAVENPORT, SR | 7136466389 | SEAL ON TANK MIXER RELEASING CRUDE OIL TO CONTAINMENT AREA.
2017-09-29 08:50 | YES | NO | 20010013 | 2001-02-05 | 443 | AMOCO PIPELINE CO | NO | 2000-12-24 | 1600 | TX | GARZA | POST | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 50779.428 | 102442.6169 | CRUDE OIL | 1 | 300 | 275 | NO | NO | 8 | 0.322 | 0 | WELDED |  | 270 | 150 | YES | 4 | 600 | 11 | 1996 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | ANTHONY WALFORD | 9155733589 | RECEIVED A CALL ON CHRISTMAS EVE ABOUT A LARGE AMOUNT OF CRUDE OIL OUT ON THE POST-COGDELL LINE. RANCHER WAS OUT FEEDING AND CHECKING ON CATTLE WHEN CAME UPON SPILL CREW WAS NOTIFIED AND RESPONDED. PIPELINE IS BEING OPERATED UNDER 20% SYMS EXEMPTION.
2017-09-29 08:50 | YES | NO | 20010014 | 2001-02-05 | 18718 | SUN PIPE LINE CO | NO | 2000-12-28 | 1530 | TX | COMANCHE | COMYN | NO |  | NO | IN MANIFOLD AREA AT COMYN STATION |  | PUMPING STATION | PIPE |  | 0 | OTHER | 2" UNION CAME APART FOR UNKNOWN REASON | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1354.1181 | 2731.8031 | CRUDE OIL | 1 | 250 | 250 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDITH F COEN | 9185866942 | 2" UNION LOCATED ON THE DISCHARGE SIDE OF THE STATION SUMP PUMP CAME APART ALLOWING 250 BBLS OF CRUDE OIL TO ESCAPE. ALL OIL WAS CONTAINED IN THE CONCRETE CONTAINMENT AREA UNDERNEATH THE MAINFOLD. ALL OIL WAS PICKED UP AND RETURNED TO TANKAGE. NO SOIL OR WATER WAS IMPACTED BY THIS SPILL AS ALL THE OIL WAS CONFINED TO THE CONCRETE CONTAINMENT.
2017-09-29 08:50 | YES | NO | 20010015 | 2001-02-06 | 2371 | CINIZA PIPELINE INC | NO | 2001-01-27 | 1140 | NM | RIO ARRIBA |  | NO |  | YES | SEC 33 T25N R6W | 555047 | PUMPING STATION | OTHER | SEAL POT DEVICE ON INSTRUMENT LINE | 1986 | OTHER | WATER ACCUMULATED IN DEVICE, FROZE & RUPTURED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 661.0738 | 1333.6529 | CRUDE OIL | 1 | 130 | 128 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ROY ARMENTA | 5056328006 | WATER ACCUMULATED IN A SEAL POT DEVICE ON AN INTRUMENT LINE. FREEZING TEMPERATURES CAUSE THE DEVICE TO SPLIT. OIL LEAKED FROM THE DEVICE INTO THE STATION CONTAINMENT AREA. THE OIL WAS RECOVERED BY TRUCK.
2017-09-29 08:50 | YES | NO | 20010016 | 2001-02-06 | 31045 | GENESIS CRUDE OIL LP | NO | 2001-01-24 | 1200 | TX | HARRIS | TOMBALL | NO |  | NO | THE NEAREST INTERSECTION IS HIGHWAY 249 AND BOUDREAUX ROAD IN TOMBALL, TEXAS. LAT 30 0.3' 13.9N LONG 095 38' 26.3" W | 554635 | LINE PIPE | PIPE |  | 1940 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 198322.1477 | 400095.8773 | CRUDE OIL | 1 | 100 | 70 | NO | NO | 4 | 0.25 | 0 | WELDED |  | 0 | 0 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | DANNY F DAVIS | 7138602500 | THE GENESIS ROW PILOT WAS FLYING THE 8" TOMBALL LINE WHEN HE SPOTTED CRUDE OIL IN WILLOW CREEK. THE GENESIS SPILL MANAGEMENT TEAM (SMT) RESPONDED TO THE INCIDENT SITE, WHERE THEY FOUND THE 4" GATHERING LINE LEAKING OIL. UPON FURTHER INVESTIGATION A HOLE WAS FOUND IN THE 4" LINE. THERE WAS EARTH MOVING EQUIPMENT ON SITE BEING UTILIZED BY THE PROPERTY OWNER TO EXCAVATE A POND ON HIS PROPERTY. HE WAS INVOLVED IN CONSTRUCTING A HOME SITE. THE TEAM TOOK PICTURES OF THE EQUIPMENT FOR DOCUMENTATION. THERE WAS SEVERAL EQUIPMENT TRACKS AT THE SPILL SITE AND WITHIN A FEW FEET OF THE ROW POSTED SIGN(S). A "ONE CALL" WAS NOT MADE TO GENESIS CRUDE OIL, LP PRIOR TO THE LANDOWNER BEGINNING EXCAVATION WORK NEAR AND ALONG THE PIPELINE ROW. THE CRUDE OIL IMPACTED SOILS IN THE VICINITY OF THE PIPE BREAK AND IS ESTIMATED AT LESS THAN 2 ACRES IMPACT TO SOILS. IN ADDITION, THE OIL ENTERED WILLOW CREEK AND TRAVERSED ALONG THE CREEK FOR APPROXIMATELY 2 MILES. THE GENESIS (SMT) INSTALLED CONTAINMENT AND SORBANT BOOM ALONG THE CREEK AND STOPPED THE LEADING EDGE OF THE OIL SPILL IN WILLOW CREEK APPROXIMATELY 100 YARDS EAST OF HIGHWAY 249. THE GENESIS SMT OPERATED UNDER THE NATIONAL INTERAGENCY INCIDENT MANAGEMENT SYSTEM (NIIHMS) ICS IN A UNIFIED COMMAND STRUCTURE WITH THE RAILROAD COMMISSION OF TEXAS DISTRICT THREE (3). AN INCIDENT ACTION PLAN (IAP) WAS DEVELOPED BY THE SMT AND DOCUMENTED ACTIONS TAKEN TO SAFELY MITIGATE THE INCIDENT AND MINIMIZING ANY IMPACT TO THE ENVIRONMENT. (A COPY OF THE IAP WAS SUBMITTED TO THE RRC SOSC).
2017-09-29 08:50 | YES | NO | 20010017 | 2001-02-05 | 18091 | SAMEDAN OIL CORP | NO | 2000-12-28 | 1245 |  |  |  | YES | 29 DEG 21 48.80" 89 DEG 1 | NO | OFFSHORE GOM MAIN PASS BLOCK 54 |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 270000 | 182805.9408 | 368793.4209 | CRUDE OIL | 1 | 30 | 0 | NO | NO | 12 | 0.0406 | 3311 | WELDED |  | 1440 | 50 | YES | 12 | 2685 | 10 | 1969 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | PAM TULLOS | 2818766229 | PIPELINE WAS STRUCK BY SEACOR VESSEL, M/V POWER, DAMAGING APPROXIMATELY 25 FEET OF PIPELINE. ADDITIONALLY, AN 18" X 4" OPENING WAS CAUSED BY THE IMPACT.
2017-09-29 08:50 | YES | NO | 20010018 | 2001-02-05 | 31443 | ALON USA, LP | NO | 2000-12-21 | 1000 | TX | FALLS |  | NO |  | NO | LAT 31 DEGREES, 04.935" & LONG 97 DEGREES, 05.311" W. APPROXIMATELY 18 3/4 MIL E OF TEMPLE, TX OFF OF FALLS CO RD 367, 3.5 MILE FROM HWY 53/320 INTERSECTION | 551660 | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 1354.1181 | 2731.8031 | CRUDE OIL | 1 | 65 | 60 | NO | NO | 10 | 0.307 | 35000 | WELDED |  | 1050 | 453 | YES | 8 | 1279 | 9 | 1988 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | BOB REED SR | 9157639256 | ALONS BIG SPRING (TEXAS) CONTROL CENTRAL WAS NOTIFIED OF THE LEAK BY ITS PATROL PILOT AT 10:00 A.M. ON DEC. 21, 2000. PIPELINE WAS NOT IN OPERATION AT THE TIME. PIPELINES MOVS WERE OPENED FOR LINE DRAINAGE TO EAST AT 10:10 A.M. AT APPROXIMATELY 11:00 A.M., PIPELINE PERSONNEL ARRIVED AT THE LEAK SITE, WITH EQUIPMENT ARRIVING LATER. VACUUM TRUCKS WERE DISPATCHED TO PICK-UP FREE OIL. THE LEAK WAS REPAIRED BY 9:45 P.M., BY MEANS OF THE WELDING OF A 14" LENGTH OF WHOLE-WRAP OVER THE LEAK SITE. VACUUM TRUCKS PICKED UP 60 BBLS. OF SPILLED CRUDE OIL. THE AREA OF SOIL (AGRICULTURAL LAND) AFFECTED BY THE SPILL WILL BE TILLED AND FERTILIZED. THERE WERE TWO AREAS SO AFFECTED: 18" WIDE X 40 IN LENGTH, WITH PENETRATION OF ONLY APPROX. 2": THE SOIL WAS WET AT THE TIME OF THIS ACCIDENT. NOTE: TELEPHONIC NOTICE WAS GIVEN TO THE NATIONAL RESPONSE CENTER AT 4:56 P.M. ON DECEMBER 21, 2000: TO NANCY BENNET - REPORT NO. 551660. NOTE: TELEPHONIC NOTICE WAS GIVEN TO THE RRC, OIL & GAS DIV., DIST 5, AT 4:00 P.M.
2017-09-29 08:50 | YES | YES | 20010019 | 2001-02-14 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2001-01-10 | 900 | CA | LOST HILLS |  | NO |  | YES | LOST HILLS DEHY #18, KERN COUNTY, CALIFORNIA. |  | NO DATA | BOLTED FITTING |  | 0 | OTHER | ACCIDENT CIRCUMSTANCES STILL UNDER REVIEW. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 1029431 | 680529.8893 | 1372903.6635 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF | 7132414381 | WHEN CONTRACTOR EMPLOYEE BROKE FLANGE LOOSE (LOOSENED BOLTS) DURING TIE-IN PROCESS, NITROGEN AND CRUDE OIL WERE FORCED OUT OF THE OPEN AREA.
2017-09-29 08:50 | YES | NO | 20010020 | 2001-02-12 | 11169 | LAKEHEAD PIPE LINE COMPANY, LP | YES | 2001-01-25 | 1045 | MN | CLEARWATER |  | NO |  | NO | STATION :AT MILEPOST 0000918.7 TOWNSHIP: 148 N. (DUDLEY), SECTION: 15, QUARTER:SE, RANGE:36W., TRACT#:667, MERIDIAN: | 554725 | LINE PIPE | OTHER | TIGHT FITTING SLEEVE | 1998 | OTHER | FAILED SLEEVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 132214.7651 | 266730.5849 | CRUDE OIL | 1 | 25 | 10 | NO | NO | 34 | 0.312 | 52000 | WELDED |  | 687 | 0 | YES | 8 | 902 | 10 | 1991 |  | Null | YES |  |  |  |  | Null | ONE CALL |  | Null | Null | L H DE BRIYN | 2187250102 | THE PATROL PILOT OBSERVED OIL POOLED ON THE GROUND IN A WOODED AREA @ MP 918.74. THE LINES WERE IMMEDIATELY SHUT DOWN. FIELD VERIFICATION WAS IMMEDIATE, AS STAFF WERE DISPATCHED FROM CLEARBROOK TERMINAL. UPON CONFIRMATION OF THE LEAK, CREWS WERE MOBILIZED FROM BEMIDJI, TRF, SUPERIOR, AND IRONWOOD. OTHER SUPPORT GROUPS WERE ALSO CONTACTED AND WERE PART OF THE INCIDENT COMMAND STRUCTURE. CREWS WORKED THROUGHOUT THE NIGHT AND REPAIRS WERE COMPLETED @ 0447MST AND THE LINE RESTARTED. NO SAFETY RELATED INCIDENTS WERE REPORTED AND ENVIRONMENTAL IMPACT IS EXPECTED TO BE MINIMAL.
2017-09-29 08:50 | YES | NO | 20010021 | 2001-02-20 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 2001-01-20 | 200 | KS | MCPHERSON |  | NO |  | NO | CONWAY DEHYDRATION, REGENERATION, AND SEPARATION PLANT. |  | PUMPING STATION | VALVE |  | 1985 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PROPANE | 2 | 877 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES C. MASON | 9185748016 | AS A PART OF THE DEHYDRATION REGENERATION SYSTEM A VESSEL DESIGNED AS A PROPANE/WATER SEPARATOR IS INCLUDED IN THE FINAL REGEN FLOW AFTER THE HEATED PROPANE HAS FLOWED THROUGH THE DEHY REMOVING THE WATER FROM THE BED. THE WATER IS ALLOWED TO SETTLE OUT IN THIS VESSEL AND COLLECTS IN THE BOOT OF THE VESSEL THAT HAS A DRAIN LINE FROM IT TO THE WATER CONTAINMENT PIT. THIS INCIDENT WAS THE RESULT OF THE 1" BALL VALVE ON THE DRAIN LINE INADVERTENTLY BEING OPENED AND REMAINING SO FOR SEVERAL HOURS. OPERATIONAL MEASURES HAVE BEEN TAKEN TO PREVENT REOCCURRENCE.
2017-09-29 08:50 | YES | NO | 20010022 | 2001-02-20 | 26065 | NATIONAL COOP REFINERY ASSCO | YES | 2001-02-04 | 830 | KS | MARSHALL |  | NO |  | NO | LEGAL DESCRIPTION SW4/19/4S/7E MARSHALL COUNTY, APPROXIMATELY ONE MILE WEST OF BLUE RAPIDS, KANSAS ON HIGHWAY 77 ON THE NORTH SIDE OF THE ROAD AT NCRA'S BLUE RA |  | PUMPING STATION | PUMP |  | 1960 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 16526.8456 | 33341.3231 | FUEL OIL | 3 | 352 | 6 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES H. WILSON | 6202419253 | ON SUNDAY, FEBRUARY 4 AT 8:30 AM A LEAK WAS DISCOVERED AT OUR BLUE RAPIDS, KS PUMP STATION (BLR) BY NCRAS ASSISTANT PRODUCTS PIPELINE SUPERINTENDENT. A HOLE HAD DEVELOPED IN THE SEAL CIRCULATION LINE ON THE BINGHAM PUMP. NO. 2 FUEL OIL WAS SPILLING OUT OF THE 1/2" DIAMETER. SEAL CIRCULATION PIPE. BY THE TIME OUR ASST. SUPT. HAD THE VALVES CLOSED TO STOP THE LEAK, APPROXIMATELY 352 BARRELS OF NO. 2 FUEL OIL (#2 F.O.) WAS ON THE GROUND. THE EVENTS LEADING UP TO THE INCIDENT AS WELL AS CLEANUP AND REMEDIATION ACTIVITIES ARE DESCRIBED BELOW. ON SATURDAY FEBRUARY 3 AT 9:24PM OUR PRODUCTS PIPELINE (PPL) DISPATCHER NOTICED THE MCPHERSON STATION (MCP) DISCHARGE CONTROL VALVE OPEN UP 8%. MCP WAS THE ONLY STATION RUNNING. THE LINE PRESSURES AT ABILENE(ABL). BLUE RAPIDS (BLR), AND TECUMSEH (TEC) STATIONS ALL DROPPED SLIGHTLY. MCP DISCHARGE PRESSURE STAYED AT 1400 PSIG. AT THAT POINT, OUR PPL DISPATCHER THOUGHT SOMETHING UNUSUAL HAD OCCURRED. HE CONTACTED OUR ASST. SUPT. THE FLOW RATES AND LINE PRESSURES WERE MONITORED VERY CLOSELY FOR ABOUT 3-1/2 HOURS. LINE PRESSURES AT ABL, BLR AND TEC ALL INCREASED DURING THIS TIME PERIOD. THE MCP DISCHARGE CONTROL VALVE OPENED 2% MORE. THERE BEGAN TO BE A SIGNIFICANT DIFFERENCE IN THE PRODUCT PUMPED AT MCP VERSUS THE PRODUCT RECEIVED AT THE COUNCIL BLUFFS, IA TERMINAL (COB). MCP AND THE PPL WAS SHUTDOWN AT 1:00 AM ON SUNDAY, FEBRUARY 4.THE NCRA PIPELINE RESPONSE PLAN WAS IMMEDIATELY PLACED INTO EFFECT BY NOTIFYING OUR ENVIRONMENTAL, HEALTH AND SAFETY (EHS) COMPLIANCE SUPERVISOR AND LOCAL RESPONSE EMPLOYEES. OUR EHS COMPLIANCE SUPERVISOR SOON NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) AND THE KANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT, KDHE. CLEANUP AND REMEDIATION ACTIVITIES BEGAN IMMEDIATELY. ADDITIONAL COMMUNICATIONS COMMENCED LATER WITH EPA AND DOT OPS.
2017-09-29 08:50 | NO | NO | 20010023 | 2001-02-07 | 26023 | COASTAL STATES CRUDE GATHERING CO | NO | 2001-01-08 | 900 | TX |  | SAN ANTONIO | NO |  | NO | N 29 DEGREES 27' 332" W 98 DEGREES 24.052' |  | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | DIESEL FUEL | 1 | 12 | 1 | NO | NO | 6 | 0.188 | 0 | WELDED |  | 275 | 50 | Null | 0 | 0 | 0 | 0 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | GLEN W. ESTERHELM | 7138776329 | ON JANUARY 5 & 6, A DIRECTIONAL DRILLING COMPANY DRILLED A BOREHOLE LONGITUDINALLY UNDER THE HYDROCARBON LINE. THE TERMINAL STARTED TO PRESSURE UP THE LINE TO START PUMPING ON 1/8/01 TO PUMP HIGH SULFUR DIESEL TO THE UNION PACIFIC FACILITY. THE OPERATIONS SUPERVISOR RECEIVED A PHONE CALL FROM THE DIRECTIONAL DRILLING COMPANY "THAT THEY SAW RED DIESEL COMING OUT OF THE BORE HOLE. THE OPERATIONS SUPERVISOR CALLED THE TERMINAL TO SHUT DOWN THE PUMPING OPERATION. OPERATIONS PERSONNEL WERE DISPATCHED TO CHECK OUT THE LINE. THEY FOUND OIL IN THE WEST BAR DITCH ON SPRINGFEILD ROAD BETWEEN THE CROSS STREETS OF WEHMAN AND SWAN. SURFACE OIL WAS VACUUMED UP AND EXCAVATION WAS CONDUCTED IN THE LEAK AREA. IT WAS DISCOVERED THAT THERE WERE MULTIPLE HOLES IN THE BOTTOM OF THE 6" LINE. THE DIRECTIONAL-BORING TOOL CAUSED THESE HOLES.
2017-09-29 08:50 | NO | NO | 20010024 | 2001-02-23 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 2001-01-12 | 800 | TX |  | COOKE | NO |  | NO |  |  | LINE PIPE | PUMP |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 20 | 19 | NO | NO | 4 | 0.237 | 600 | WELDED |  | 750 | 600 | YES | 8 | 752 | 7 | 1999 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LARRY R. LOVELESS | 8063422048 | PIPELINE FAILURE RESULTED IN 20 BBLS OF CRUDE OIL SPILLED TO SOIL. CRUDE OIL TRAVELED DOWN A SLOPE 50 FT TO AN UN-NAMED CREEK. SPILL MOVED DOWN THE CREEK APPROX. 1/4 MILE.
2017-09-29 08:50 | YES | NO | 20010025 | 2001-02-27 | 30755 | CITGO PRODUCTS PIPELINE CO | YES | 2001-02-06 | 1845 | TX | HILL | ITASCA | NO |  | NO | 1 MILE WEST OF 35W ON FM 934 (700 SOUTH FILES RD.) 500 YARDS SOUTH OF THIS ADDRESS. NEAR THE TOWN OF ITASCA TX. |  | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 700000 | 462751.6779 | 933557.047 | GASOLINE | 3 | 315 | 230 | NO | NO | 10 | 0.307 | 36000 | WELDED |  | 1225 | 750 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | DALE L. STOGSDILL | 8173554054 | AT 1830HRS. 2/6/2001 THE CONTROL CENTER RECEIVED A CALL FROM A LAND OWNER WHO REPORTED A LEAK ON THE EAGLE SOUTH PIPELINE NEAR THE TOWN OF ITASCA TX. THE PIPELINE WAS SHUT DOWN BY 1832 AND THE SITE WAS ISOLATED BY 1921. CITGO PERSONNEL AND CONTRACTORS WERE ON SITE AT 1921. NATIONAL RESPONSE CENTER NOTIFIED AT 2157. INCIDENT # 55963.
2017-09-29 08:50 | YES | NO | 20010026 | 2001-02-28 | 30922 | HYPERION ENERGY LP | NO | 2000-06-05 | 1330 | TX |  | NECHES | NO |  | NO | A-769 JAMES H SHOW APPROXIMATELY 3/4 MILES OF HWY 69 AND FM 921 IN CHEROKEE COUNTY, TX |  | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 10155.8856 | 20488.5234 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 10 | 0.344 | 0 | WELDED |  | 200 | 200 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | GEORGE R | 2147501522 | INTERNAL CORROSION CAUSED A LEAK IN THE PIPE. OIL RAN DOWN CREEK (WASH) TO A LOW AREA. OIL WAS CONTAINED IN AREA BY BOOMS AND DAMNS. VACUUM TRUCKS PICKING MOST OF OIL AND WATER. CONTINUED RAINS HAVE HAMPERED EFFORTS. PROCESS IS ONGOING AND WILL BE CLEANED UP TILL ABSORBANT PADS AND CHEMICALS WILL COMPLETE THE PROCESS. PIPELINE IS CURRENTLY SCHEDULED TO BE REPLACED AS SOON AS WET AREA DRIES AND ACCESS CAN BE OBTAINED.
2017-09-29 08:50 | NO | NO | 20010027 | 2001-02-28 | 31347 | UNOCAL ALASKA RESOURCES | NO | 2001-02-05 | 1300 |  |  |  | YES | DOLLY VARDEN PLATFORM | NO | THE LEAK LOCATION IS APPROXIMATELY 0.3 MILES FROM THE DOLLY VARDEN PLATFORM TOWARD THE ONSHORE TRADING BAY PRODUCTION FACILITY, ABOUT 6 MILES FROM THE BEACHFALL |  | LINE PIPE | PIPE |  | 1967 | OTHER | UNKNOWN AS OF THIS WRITING, INVESTIGATION IS UNDER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 3 | 0 | 0 | NO | NO | 8.625 | 0.719 | 60000 | WELDED |  | 1096 | 600 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RAND S. PRICE | 9072835514 | AT APPROXIMATELY 1300 HRS ON FEBRUARY 5, 2001, A HELICOPTER PILOT ON CONTRACT TO UNOCAL, OBSERVED A SHEEN ON THE WATER. HE REPORTED THE SHEEN TO THE DOLLY VARDEN PLATFORM AND STOPPED TO PICK UP THE PRODUCTION FOREMAN FOR AN OVERFLIGHT. THE SHEEN WAS A VERY WHITE MILKY COLOR, 2 MILES LONG X 1/2 MILE WIDE STREAMERS, 1/4 OF THE AREA WAS SHEEN. IT WAS SUSPECTED THAT THE GAS PIPELINE WAS LEAKING DUE TO THE COLOR, SO NOTIFICATION WAS MADE TO THE VARIOUS REGULATORY AGENCIES, INCLUDING THE NRC (REPORT #555851). THE GAS LINE WAS SHUT IN, FILLED WITH FILTERED WATER AND HYDROTESTED TO 600+PSIG, WHICH PROVED THE GAS LINE TO BE INTACT. THE SHEEN DISAPPEARED DUE TO TIDES. THE OIL PIPELINE WAS NEXT SHUT IN TO HYDROTEST TO PROVE OR DISPROVE IF IT HAD A LEAK. A POLY PIG WAS SHIPPED AHEAD OF THE FILTERED WATER, DISPLACING THE OIL, BUT A GOOD HYDROTEST COULD NOT BE ACCOMPLISHED. IT WAS SUSPECTED THAT THE PRESSURE FLUCTUATION COULD HAVE BEEN DUE TO RESIDUAL OIL/GAS REMAINING IN THE PIPELINE AND COMPRESSING OR DUE TO TEMPERATURE VARIATION. A CUP PIG WAS NEXT SHIPPED TO ENSURE THAT NO OIL REMAINED IN THE PIPELINE. THE SECOND HYDROTEST ATTEMPT INDICATED THAT THE OIL LINE HAD A LEAK. DUE TO THE BLACKWATER NATURE OF THE COOK INLET WATERS, GAS WAS THEN USED TO DISPLACE THE WATER TO ALLOW DIVERS TO FIND THE LEAK LOCATION BY FOLLOWING THE BUBBLES. AFTER SERVERAL DIVES, THE DIVERS FOUND A 1/4 INCH HOLE AT THE BOTTOM OF THE PIPELINE. OTHER THAN THE INITIAL SHEEN OBSERVED BY THE PILOT, NO OTHER SPILL INDICATIONS WERE OBSERVED. DIVING CEASED DUE TO DANGER FROM PAN ICE IN THE INLET TO THE DIVE BOAT AND DIVERS. AT THE PRESENT, GAS PRESSURE IS BEING MAINTAINED ON THE LINE TO MINIMIZE WATER INTRUSION INTO THE PIPELINE AND TO PREVENT FREEZE-UP AT THE ONSHORE CROSSING. DIVING INVESTIGATION TO DETERMINE MODE OF FAILURE WILL RESUME WHEN THE ICE IS OUT OF THE INLET.
2017-09-29 08:50 | YES | NO | 20010028 | 2001-02-28 | 30909 | TRANSMONTAIGNE PIPELINE INC | YES | 2001-02-06 | 1305 | IN | LAKE |  | NO |  | NO | SW/4 S20 T37N R9W- LAKE COUNTY, IN- NORTH TOWNSHIP IN CITY OF EAST CHICAGO, IN @ 3823 INDIANALIS BLVD. TRANSMONTAIGNE E. CHICAGO FACILITY TANK # 140 DIKE ON EAS |  | TANK FARM | VALVE |  | 1980 | OTHER | DAMAGE BY NATURAL FORCES | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 5288.5906 | 10669.2234 | DIESEL FUEL | 3 | 75 | 75 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY NATURAL FORCES |  | Null |  |  | Null | Null | RICK HOOD | 5015716903 | THE CAUSE OF THE RELEASE WAS ICE IN A 4" WATER DRAW VALVE ON TANK 140. WATER TRAPPED IN THE VALVE FROZE CAUSING THE GASKET TO BREAK AND FAIL.
2017-09-29 08:50 | YES | NO | 20010029 | 2001-02-27 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2001-01-29 | 1430 | LA | ST CHARLES |  | NO |  | NO | IMTT METER STATION, ST ROSE, LOUISIANA. | 555132 | OTHER | PUMP |  | 1999 | OTHER | MECHANICAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 850000 | 561912.7517 | 1133604.9856 | CRUDE OIL | 1 | 475 | 415 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | THE RELEASE OCCURRED WHEN A SMALL VIKING MAGNETIC DRIVE PUMP USED TO CIRCULATE OIL FAILED. THE RELEASE WAS FROM THE PUMP CASING. THE HOLE IS BELIEVED TO HAVE BEEN CAUSED BY ABNORMAL SHAFT MOVEMENT AND INNER ROTATING MAGNET ASSEMBLY CONTACT WITH THE PUMP CASING. THE PUMP HAD BEEN IN SERVICE JUST UNDER TWO YEARS.
2017-09-29 08:50 | NO | NO | 20010030 | 2001-03-05 | 31479 | BORGER CO2 PIPELINE, LLC | NO | 2001-02-25 | 1250 | TX |  | HUTCHINSON | NO |  | NO | BETWEEN PL STATIONS 20 + 25 & 32 + 37 APPROXIMATELY 200-300-FT. SOUTHEAST OF INTERSECTION OF HWY 136 & FM 1559 SOUTH | 557814 | LINE PIPE | PIPE |  | 1979 | OTHER | CORROSION, EXTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 11052 | 7306.1879 | 14739.5321 | CARBON DIOXIDE |  | 18 | 0 | NO | NO | 8 | 0.188 | 42000 |  |  | 1480 | 680 | YES | 24 | 2070 | 10 | 2000 | EXTERNAL | Null | Null | OTHER | UNKNOWN AT THIS TIME |  |  | Null |  |  | Null | Null | WAYNE K TAYLOR | 9185877782 | PIPELINE IN PROCESS OF BEING RESTORED TO SERVICE. TESTED WITH WATER 10/18/2000. PRESSURED WITH CO2 TO 680 PSI, LEAK OBSERVED BY PERSONS ON HIGHWAY AND REPORTED 2/25/2001. ACCIDENT RESPONSE PROCEDURE WAS FOLLOWED. SUBSEQUENT CALCULATION OF CO2 LOST IN LEAK AMOUNTED TO 17.5 BBL, LESS THAN 50 BBL THRESHOLD FOR REQUIRED REPORTING. THERE NO INJURIES, FIRE, NOR EVACUATION REQUIRED. THERE WAS NO POLLUTION TO SURFACE WATER. ESTIMATED COST OF ACCIDENT WAS LESS THAN $50,000
2017-09-29 08:50 | YES | NO | 20010031 | 2001-03-07 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2001-02-03 | 1230 | TX | HARRIS |  | NO |  | NO | 4227 DECKER DRIVE BAYTOWN, TEXAS. |  | TANK FARM | TANK |  | 1963 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6610.7383 | 13336.5292 | GASOLINE | 2 | 195 | 190 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LEONARD W. MALLETT | 7137593615 | AT APPROXIMATELY HRS. OPERATIONS PERSONNEL BEGAN FILLING TANK 630 AT TEPPCOS BAYTOWN TERMINAL. SHORTLY THEREAFTER PRODUCT WAS FOUND LEAKING FROM THE FILL LINE THROUGH A PIPE PLUG WHICH HAD BEEN REMOVED TO STRIP THE TANK ON THE PREVIOUS DAY. THE TEPPCO EMERGENCY RESPONSE PLAN WAS INITIATED IMMEDIATELY. FLOW TO THE TANK WAS CEASED. ALL SPILLED PRODUCT WAS CONTAINED WITHIN THE TANKS SECONDARY CONTAINMENT AREA. CLEAN-UP ACTIVITIES STARTED WITH VACUUM TRUCKS BEING USED TO RECOVER THE PRODUCT. APPROXIMATELY 190 BARRELS OF PREMIUM UNLEADED GASOLINE WAS RECOVERED.
2017-09-29 08:50 | YES | NO | 20010033 | 2001-03-08 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2000-11-15 | 1530 | TX | HARRIS | KEMAH | NO |  | NO | INTERSECTION OF STATE HIGHWAY 146 AND STATE HIGHWAY 97. |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1200000 | 812470.8482 | 1639081.8706 | GASOLINE | 2 | 15 | 0 | NO | NO | 10.75 | 0.375 | 35000 | WELDED |  | 725 | 375 | YES | 24 | 1000 | 0 | 1970 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | LEONARD W. MALLETT | 7137593615 | ON NOVEMBER 15, 2000 AT APPROXIMATELY 1530 HRS. TEPPCO DISCOVERED A 10" PIPELINE HAD BEEN DAMAGED BY A THIRD PARTY CONTRACTOR WORKING ON A HIGHWAY CONSTRUCTION PROJECT. AT THAT TIME THERE WAS NO FREE PRODUCT BUT THERE WAS A STRONG PRODUCT SMELL. OUR ENVIRONMENTAL CONTRACTOR WAS CALLED TO THE SITE WHEN A SLIGHT SHEEN WAS DISCOVERED IN THE DRAINAGE DITCH ALONG THE NEW ROAD CONSTRUCTION. REMEDIAL ACTION WAS TAKEN BY PLACING BOOM IN VARIOUS LOCATIONS IN THE DITCH AND CLEANING THE SHEEN OFF THE STANDING WATER. THE TNRCC VISITED THE SITE ON THE DATE OF THE INCIDENT AND CLEARED OUR ACTIVITIES. WORK NECESSARY TO REPLACE THE DAMAGED SECTION OF PIPELINE WAS COMPLETED SHORTLY AFTER THE INCIDENT DATE. SINCE THAT TIME, SOIL SAMPLES INDICATED ADDITIONAL REMEDIATION WAS NEEDED. TO DATE, SEVERAL HUNDRED CUBIC YARDS OF SOIL HAVE BEEN REMOVED AND REPLACE IN AN EFFORT TO CLEAN THE SITE.
2017-09-29 08:50 | YES | NO | 20010034 | 2001-03-08 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2001-02-19 | 1100 | LA | NATACHITOCHES |  | NO |  | NO | 31 DEG 52' 05", -93DEG 16' 24". | 557194 | LINE PIPE | PIPE |  | 1944 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 297483.2215 | 600143.8159 | GASOLINE | 2 | 100 | 30 | YES | NO | 20 | 0.312 | 35000 |  |  | 690 | 500 | YES | 24 | 900 | 0 | 1957 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | LEONARD W. MALLETT | 7137593615 | AT APPROXIMATELY 1100 HOURS CST, TEPPCOS PIPELINE CONTROL CENTER RECEIVED A CALL FROM THE NATCHITOCHES PARRISH SHERIFF DEPARTMENT NOTIFYING THEM A FIRE OF UNDETERMINED NATURE WAS LOCATED NEAR OUR 20" MAINLINE RIGHT-OF-WAY. THE SYSTEM WAS IMMEDIATELY SHUT DOWN AND THE TEPPCO EMERGENCY RESPONSE PLAN WAS INITIATED. PERSONNEL BEGAN CLOSING MAINLINE BLOCK VALVES SOUTH OF THE SITE AND PUMPS NORTH WERE UTILIZED TO PULL PRESSURE OFF THE PIPELINE. LOCAL AND STATE EMERGENCY PERSONNEL RESPONDED TO THE SITE. STOPPLES WERE UTILIZED TO MAKE THE FINAL ISOLATION OF THE SITE. IT HAS BEEN DETERMINED THE LEAK WAS CAUSED BY A PIN HOLE RESULTING FROM EXTERNAL CORROSION AT A GIRTH WELD. 120 IF OF THE MAINLINE PIPE WAS REMOVED AND REPLACED. THE SYSTEM WAS RETURNED TO SERVICE AT 0100 HRS. ON 02-23-01.
2017-09-29 08:50 | YES | NO | 20010035 | 2001-03-08 | 2190 | CENTRAL FLORIDA PIPELINE CORP | NO | 2001-02-13 | 1125 | FL |  | TAMPA | NO |  | NO | LOCATION OF INCIDENT IS WITHIN THE CSX RAILWAY CORRIDOR APPROXIMATELY 200 FEET EAST OF THE INTERSECTION OF 22ND STREET AND THE LEE ROY. SELMON CROSSTOWN EXPRESS | 556582 | LINE PIPE | PIPE |  | 1972 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 297483.2215 | 600143.8159 | DIESEL FUEL | 2 | 49 | 49 | NO | NO | 10.75 | 0.279 | 3114 | WELDED |  | 1420 | 1257 | YES | 1790 | 1790 | 2 | 1972 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RICHARD M. LIEN | 8132411128 | CFPL LOCATED DIESEL FUEL IN THE DITCHES ALONG THE CSX RAILROAD CORRIDOR WHERE THE RAILROAD INTERSECTS WITH 22ND STREET IN TAMPA, FLORIDA. THE LEAK LOCATION WAS JUST SOUTH OF THE LEE ROY SELMON EXPRESSWAY. CFPL IMMEDIATELY INITIATED EMERGENCY ACTIONS WHICH INCLUDED SHUT DOWN OF THE 10-3/4" PIPELINE, NOTIFICATION OF ALL REQUIRED EMERGENCY AND ENVIRONMENTAL AGENCIES INCLUDING THE NATIONAL RESPONSE CENTER. THE SECTION OF PIPE LEAKING WAS EXCAVATED AND FOUND TO BE DAMAGED BY MECHANICAL EQUIPMENT. THE PIPELINE WAS REPAIRED BY INSTALLING A NEW SECTION OF PIPE TO REPLACE THE DAMAGED SECTION. ALL FREE PRODUCT WAS PICKED UP BY VACUUM TRUCK AND REMOVAL OF CONTAMINATED SOIL IS NOW UNDERWAY.
2017-09-29 08:50 | NO | NO | 20010036 | 2001-03-16 | 26136 | PARAMOUNT PETROLEUM CORP | NO | 2000-11-16 | 930 | CA |  | LONG BEACH | NO |  | NO | 1000 WEST CARSON, LONG BEACH BEACH, CA. |  | LINE PIPE | OTHER | FLANGE GASKET FAILURE. | 1920 | OTHER | FAILURE OF GASKET IN BURIED FLANGE. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 69844 | 47288.5116 | 95400.0285 | OIL AND GASOLINE | 3 | 2 | 2 | NO | NO | 8 | 0.322 | 0 | FLANGED |  | 725 | 250 | YES | 4 | 955 | 7 | 2000 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | DOUGLAS THOMPSON | 5625312060 | ON NOVEMBER 16, 2000, A LEAK OCCURRED IN PARAMOUNTS LINE 160. THE LEAK OCCURRED DUE TO THE FAILURE OF THE GASKET ON A BURIED FLANGE. AT THE TIME OF THE LEAK, GASOIL WAS BEING PUMPED THROUGH THE PIPELINE. THE LEAK OCCURED AT 1000 WEST CARSON IN LONG BEACH, CA., ON PROPERTY OWNED BY EDISON, AND WAS INITIALLY REPORTED TO PARAMOUNT BY A LEASEHOLDER ON THE PROPERTY. A PARAMOUNT PIPELINE MARKER WITH PARAMOUNTS EMERGENCY PHONE NUMBER WAS LOCATED WITHIN 10 FEET OF THE LEAK. IMMEDIATELY UPON NOTIFICATION OF THE LEAK, THE PIPELINE WAS SHUT DOWN AND CORRECTIVE ACTIONS WERE TAKEN. THE LEAK WAS REPORTED TO THE NATIONAL RESPONSE CENTER AND THE CALIFORNIA OFFICE OF EMERGENCY SERVICES, REPORT NUMBERS 548410 AND 00-5375, RESPECTIVELY. THE CALIFORNIA STATE FIRE MARSHAL, CALIFORNIA DEPARTMENT OF FISH & GAME AND LONG BEACH FIRE DEPARTMENT RESPONDED TO THE INCIDENT. A DOT 7000-1 WAS NOT INITIALLY SUBMITTED FOR THIS INCIDENT BECAUSE NONE OF THE TRIGGERS WERE MET. UPON A RECENT REVIEW OF THIS INCIDENT, IT WAS DISCOVERED THAT THE CLEAN-UP COSTS EXCEEDED $50,000 AND A 7000-1 REPORT IS THEREFORE REQUIRED. A BACKHOE WAS USED TO LOCATE THE LEAK AND REMOVE ALL CONTAMINATED SOIL. THE CONTAMINATED SOIL WAS SENT TO TPS TECHNOLOGIES FOR RECYCLING. THE FLANGE WAS CUT OUT AND REPLACED WITH PRE-HYDROTESTED SECTION OF PIPE. THE EXCAVATION WAS FILLED WITH TWO-BAG SLURRY TO ASSURE PROPER COMPACTION.
2017-09-29 08:50 | YES | NO | 20010037 | 2001-03-19 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 2001-02-05 | 1325 | OK | OSAGE |  | NO |  | NO | SEC.19-T23N-R8E, OSAGE COUNTY, OKLAHOMA. |  | LINE PIPE | PIPE |  | 0 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 2 | 20 | 20 | NO | NO | 2 | 0.219 | 80 | WELDED |  | 300 | 0 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null |  |  | Null | Null | LARRY (RICK) LOVELESS | 8063422048 | GILLAIND & PENNJELLY DISCHARGE LINE RUN OVER BY A PICK-UP, LEAK TRAVELED DOWN HILL TO A UN-NAMED CREEK. THE MATERIAL WAS BOOMED AND ABSORDED.
2017-09-29 08:50 | YES | NO | 20010038 | 2001-03-21 | 31415 | PREMCOR PORT ARTHUR COKER LP | NO | 2001-02-20 | 1320 | TX | JEFFERSON |  | NO |  | NO | LUCAS STATION TANKFARM (SEE ATTACHED MAP) | 557315 | NO DATA | PIPE |  | 1950 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 9916.1074 | 20004.7939 | CRUDE OIL | 3 | 350 | 350 | NO | NO | 10 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JOHN JENKINS | 4099851239 | 1:20PM- OPERATOR SPOTTED OIL IN DITCH NEAR THE WEST TEXAS GULF TAKE OFF. 1:35PM - MAINTENANCE CREW RESPONDS TO SPILL (S. GUNTER, R. HALL, JOE LYONS, WINNIE WELDING CREW, VACCUM TRUCK, TRACK HOE). 1:45PM - VACUUM TRUCK BEGINS REMOVING OIL FROM DITCH. 1:50PM - R. HATTON PASSED IC ROLE TO S. GUNTER 2:00PM - JOHN JENKINS (ENVIRONMENTAL SPECIALIST) IS NOTIFIED 2:05PM - FIRST LOAD IN VACUUM TRUCK IN UNLOADED 2:25 PM - SECOND LOAD IN VACUUM TRUCK IS UNLOADED, J. JENKINS ARRIVES 2:35PM - J. JENKINS MAKES AGENCY NOTIFICATIONS, ESTIMATE OF SPILL 300 TO 500 BBLS 3:00PM- START EXCAVATING LEAK 3:24 PM- THIRD LOAD IN VACUUM TRUCK IS UNLOADED 3:51 PM- S. GUNTER PAGED BY DANNY NICHOLS OF THE PIPELINE SAFETY SECTION OF THE TEXAS RAILROAD COMMISSION (713)869-8425 3:55 PM- FOURTH LOAD IN VACUUM TRUCK UNLOADED 3:38PM - CALLED PLANT TO ORDER TRENCH BOX SO LEAK REPAIR CAN BE MADE 4:20 PM- NOTIFIED BY MLT THAT THE USCG IS ON THEIR WAY TO LEAK SITE 4:42 PM - PLANK ARRIVES WITH TRENCH BOX 4:51PM - FIFTH LOAD IN VACUUM TRUCK UNLOADED 4:57 PM - USGC ARRIVES - DERRICK TRAPP, JASON IHLENFIELD 5:05PM - OIL AND GAS DIVISION OF THE RAILROAD COMMISSION ARRIVES - DAVID LANDRY 5:15PM -USCG LEAVES SITE 6:45PM - LEAK CLAMP INSTALLED 7:00PM - MAINTENANCE CREW AND MR. LANDRY LEAVE SITE
2017-09-29 08:50 | YES | NO | 20010039 | 2001-03-26 | 31443 | ALON USA, LP | NO | 2001-02-11 | 1137 | TX | GRIMES |  | NO |  | NO | LAT N 30 41' 28.3"; LONGITUDE W. 95 57' 28.2"; TRACT 4-5 WITHIN THE WILLIAM FISHER SURVEY, A -211; APPROX 5.5 MI S OF BEDIS, TX 0.73 MI SE OF STATE HWY 90 | 556396 | LINE PIPE | PIPE |  | 1928 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 165268.4564 | 333413.2311 | CRUDE OIL | 1 | 245 | 240 | NO | NO | 10 | 0.307 | 35000 | WELDED |  | 1050 | 747 | YES | 8 | 1346 | 3 | 1989 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | BOB REED | 9152639256 | THE PIPELINE HAD BEEN SHUT-IN, FROM 1/24/01 UNTIL THE START-UP AT 10:33 A.M. ON 2/11/01. SHIRO STATION, NEAREST THE LEAKSITE, HAD BEEN STARTED AT 10:54 A.M. WITH THE ENTIRE PROCESS BEING SMOOTH AND UNEVENTFUL. AT 11:37 A.M. WHILE PATROLLING THE PIPELINE DURING THE STARTUP, ALONS ONTRACT PATROLLING SERVICE PATROL SAW THE LEAK AND NOTIFIED THE BIG SPRING (TEXAS) CONTROL CENTER> THE PREVIOUS PATROL OF THIS LINE HAD BEEN MADE ON FEBRUARY 7TH, WITH NO PROBLEMS FOUND. IMMEDIATELY UPON NOTIFICATION, THE CONTROL CENTER OPERATOR BEGAN THE PROCESS OF SHUTTING-DOWN THE PIPELINE, BEGINNING WITH NOTIFICATION OF SUN AT SMITHS BLUFF. THE "UPSTREAM" STATIONS, GRAYBURG AND SHIRO, WERE SHUTDOWN AT 11:40 A.M. "DOWNSTREAM" STATIONS WERE ALLOWED TO SHUTDOWN ON LOW SUCTION, IN ORDER TO PULL AS MUCH OIL AWAY FROM THE LEAKSITE AS POSSIBLE. TEMPLE, EVANT AND BRONTE STATIONS (THE "DOWNSTREAM" STATIONS) WERE SHUTDOWN AT 11:48, 11:53 AND 12:01 PM., RESPECTIVELY. AT 12:53 PM THE LEAK WAS CONFIRMED BY COMPANY PERSONNEL. COMPANY AND CONTRACT PERSONNEL FROM VARIOUS LOCATIONS TRAVELED TO THE SITE DURING THE AFTERNOON AND EVENING OF FEB 11TH. NOTIFICATIONS WERE MADE TO AGENCIES BETWEEN 4:30 AND 5:00PM., 2/11/01. AT 5:05 PM ON THAT DATE, THE LEAK SOURCE HAD BEEN EXCAVATED AND THE CAUSE OF THE LEAK (EXTERNAL CORROSION) DETERMINED. AT 5:31PM THE CREW WAS COMPLETING THE INSTALLATION OF A CLAMP ON THE PIPELINE, AND HAD MADE A WELDED REPAIR OF THE SITE BY 10:30PM. THE PIPELINE WAS RESTARTED AT APPROX 11PM. CLEANUP WAS BEGUN ON 2/11/01 AND CONTINUED UNTIL 2/21, WITH ADDITIONAL SPOT CLEANING AFTER THAT DATE.
2017-09-29 08:50 | YES | NO | 20010040 | 2001-03-16 | 11169 | LAKEHEAD PIPE LINE COMPANY, LP | YES | 2001-03-04 | 1105 | MN | CASS |  | NO |  | NO | 145N SEC 15 QUARTER NE 1/4 | 558546 | LINE PIPE | WELDING FITTING |  | 1990 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 132214.7651 | 266730.5849 | CRUDE OIL | 1 | 25 | 15 | NO | NO | 34 | 0.281 | 52000 | WELDED |  | 619 | 484 | YES | 8 | 840 | 7 | 1991 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | L H DEBRYAN | 2187250102 | AT 11:00 MST A MEMBER OF THE PUBLIC CALLED THE ECC AFTER NOTICING OIL POOLED ON THE GROUND. THE LINES WERE IMMEDIATELY SHUT DOWN, AND FIELD VERFICATION FOLLOWED. EMERGENCY RESPONSE CREWS WERE DISPATCHED AND CONTAINED THE OIL USING SNOW AND EARTH BERMS. A FULL INCIDENT COMMAND SYSTEM WAS ESTABLISHED. THE ESTIMATED RELEASE IN 25 BARRELS, WITH NO SIGNIFICANT ADVERSE ENVIRONMENTAL IMPACTS PREDICTED.
2017-09-29 08:50 | YES | NO | 20010041 | 2001-03-26 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 2001-02-28 | 1730 | OK | OSAGE |  | NO |  | NO | 19.75 MILES NE OF PAWHUSKA, OKLAHOMA | 558171 | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | CRUDE OIL | 1 | 165 | 165 | NO | NO | 6 | 0.188 | 200 | WELDED |  | 400 | 200 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | LARRY LOVELESS | 8063422048 | SIX INCH PIPELINE LEAKED TO SOIL, TRAVELED APPROX 200 YARDS TO SMALL UN-NAMED DRAW. SPILL TRAVELED APPROX 3/4 MILE TO TRIBUTARY TO POND CREEK. UNDERFLOW DAM WAS CONSTRUCTED ON TRIBUTARY WITH NINE SETS OF BOOM TO PREVENT ANY SHEEN FROM REACHING POND CREEK. ALL OIL HAS BEEN REMOVED FROM THE DRAW AND FROM THE TRIBUTARY.
2017-09-29 08:50 | YES | NO | 20010042 | 2001-03-29 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 2000-01-19 | 820 | PA | LUZERNE | JACKSON | NO |  | NO | NEAR INTERSECTION OF HUNTSVILLE AND CHASE ROADS AT SUN PIPE LINE'S PLYMOUTH PUMP STATION - DRAWING ATTACHE |  | PUMPING STATION | VALVE |  | 1999 | OTHER | BALL VALVE BODY USED AS A DRAIN VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 677059.0401 | 1365901.5589 | GASOLINE | 1 | 120 | 100 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | DAVID B MEADOWS | 6106703203 | PLYMOUTH PUMP STATION, THE THIRD PUMP STATION IN A SERIES OF FOUR ON THE MONTELLO TO SYRACUSE LINE, WAS SHUT DOWN AT 0806 HOURS ON JANUARY 19, 2000 FOR OPERATIONAL CHANGES AT THE PIPELINES ORIGINATING PUMP STATION. AT 0817 HOURS, PLYMOUTH PUMP STATION WAS RESTARTED. THE PRODUCT IN THE PIPELINE AND PUMP STATION WAS 94 OCTANE GASOLINE. AT 0829, LUZERNE COUNTY 911 CENTER RECEIVED A CALL OF STRONG GASOLINE ODORS IN THE VICINITY OF THE PUMP STATION. AT 0838 HOURS, THE FIRE COMPANY ARRIVE ON-SCENE AT PLYMOUTH STATION TO FIND A SPRAY OF GASOLINE FROM ABOVE GROUND PIPE. THE FIRE COMPANY NOTIFIED SUN PIPE LINE OF THE SITUATION. SUN PIPE LINE COMPANY IMMEDIATELY SHUT DOWN ALL PUMP STATIONS ON THIS LINE, WITH THE EXCEPTION OF THE DOWN STREAM PUMP STATION, WHICH WAS LEFT RUNNING TO PULL PRODUCT FROM THE LEAK LOCATION. MANUAL MAIN LINE VALVES WERE CLOSED SOUTH OF PLYMOUTH PUMP STATION AT 0917 HOURS, REDUCING PRESSURE AT THE LEAK. ADDITIONAL PUMP STATION ISOLATION VALVES WERE CLOSED AT 1035 HOURS AFTER THE AREA WAS SAFED UP WITH FIRE DEPARTMENT HOSE AND FOAM. SUN PIPE LINE MAINTENANCE PERSONNEL FOUND THE LEAK SOURCE TO BE A FRACTURE IN A ONE INCH DIAMETER BALL VALVE BODY. THIS VALVE WAS ATTACHED TO THE BOTTOM OF ABOVE GROUP PUMP STATION SUCTION PIPING AND WAS USED AS A DRAIN VALVE. OUT PRELIMINARY INVESTIGATION REVEALS WATER OR MOISTURE MAY HAVE ACCUMULATED IN THE BALL VALVE BODY, FROZE AND SUBSEQUENTLY FRACTURED THE VALVE BODY.
2017-09-29 08:50 | YES | NO | 20010043 | 2001-03-28 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2001-02-27 | 1615 | CA | ALAMEDA |  | NO |  | NO | R-3E, T-2, S-24. |  | LINE PIPE | VALVE |  | 1989 | OTHER | FAILURE OF 12-INCH GATE VALVE. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 761533 | 503429.5336 | 1015620.7124 | CRUDE OIL | 1 | 889 | 818 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. CHEAFF | 7132414381 | THE DIRECT CAUSE WAS THE FAILURE OF A 12 INCH M&J M303 GATE VALVE. THE VALVE FAILED AT A POINT WHERE THE BODY OF THE VALVE IS FILLET WELDED TO THE PUP OF PIPE THAT PROTRUDES FROM THE BODY. A ROOT CAUSE ANALYSIS IS UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE FILED.
2017-09-29 08:50 | YES | NO | 20010044 | 2001-03-29 | 15674 | PLANTATION PIPE LINE CO | YES | 2001-03-02 | 2145 | GA | WINSTON | DOUGLAS | NO |  | NO | PPL STA. 1051+08 (2950 WARD DRIVE, WINSTON, GEORGIA 30187). |  | LINE PIPE | PIPE |  | 1968 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 700000 | 462751.6779 | 933557.047 | GASOLINE | 3 | 87 | 87 | YES | NO | 26 | 0.281 | 52000 | WELDED |  | 720 | 320 | YES | 24 | 1204 | 8 | 1968 |  | Null | YES |  |  | OTHER | LARGE ROCK AGAINST PIPE. | Null |  |  | Null | Null | JACQUE WILLIAMS | 7707514095 | AT APPROXIMATELY 9:45 P.M., EST, ON MARCH 2, 2001, A LEAK WAS DISCOVERED ON PLANTATIONS 26-INCH, .281 WALL THICKNESS, GRADE X-52, PETROLEUM PRODUCTS PIPELINE WHICH OPERATES BETWEEN COLLINS, MISSISSIPPI, AND GREENSBORO, NORTH CAROLINA. THE LEAK OCCURRED 490 FEET EAST OF WARD DRIVE IN DOUGLAS COUNTY, GEORGIA. A LARGE ROCK WAS FOUND AGAINST THE PIPE WHICH HAD CAUSED A DENT ABOUT TWELVE INCHES LONG AT THE NINE OCLOCK POSTION. AN EIGHT INCH LONG HAIRLINE CRACK WAS FOUND WITHIN THE DENT. THE PIPE WAS REPAIRED WITH A 3 LONG FULL ENCIRCLEMENT SLEEVE. REFERENCE PART G (3): ESTIMATED QUANTITIES OF PRODUCT SPILLED AND RECOVERED IS UNDETERMINED AT THIS TIME DUE TO ONGOING REMEDIATION. THE SITE WILL BE REMEDIATED IN ACCORDANCE WITH ALL APPLICABLE REGULATIONS. REFERENCE PART G (5): TWO SMALL LOCALIZED FLASH FIRES OCCURRED DURING EXCAVATION AS A RESULT OF THE BACKHOE STRIKING ROCK.
2017-09-29 08:50 | NO | NO | 20010045 | 2001-03-29 | 18092 | SANTA FE PACIFIC PIPELINE PARTNERS LP | NO | 2001-02-27 | 1145 | CA | CONTRA COSTA | CROCKETT | NO |  | NO | UNDER SOUTHBOUND CARQUINEZ BRIDGE SPAN OVERPASS (I 80) AT L.S. 37 MP 7.35 |  | LINE PIPE | PIPE |  | 1969 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 26442.953 | 53346.117 | GASOLINE | 3 | 0 | 0 | NO | NO | 12 | 0.219 | 52000 | WELDED |  | 1286 | 210 | YES | 24 | 1618 | 6 | 1969 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | EDWARD A FANT | 7133699454 | ON FEBRUARY 27, 2001 AT 1145 HOURS, EMPLOYEES OF CALTRANS REPORTED PRODUCT BUBBLING UP IN A DRAINAGE DITCH IN CROCKETT, CALIFORNIA, WHICH SUBSEQUENTLY PROVED TO BE A RELEASE FROM LS-37. THIS ACCIDENT WAS REPORTED TELEPHONICALLY TO THE OFFICE OF EMERGENCY SERVICES (OES) AT 1446 HOURS PST ON FEBRUARY 27, 2001 (CASE #01-1200). WHEN KINDER MORGAN WAS NOTIFIED OF THIS OCCURRENCE, EMERGENCY PROCEDURES WERE PUT INTO PLACE AND THE PIPELINE WAS SHUT-IN. UPON EXCAVATION, MECHANICAL DAMAGE WAS OBSERVED IN THE TWELVE OCLOCK POSITION. THE PROBABLE CAUSE OF THIS RELEASE WAS DUE TO MECHANICAL DAMAGE CAUSED BY A THIRD PARTY. KINDER MORGAN WAS NOT PREVIOUSLY NOTIFIED OF EXCAVATION RELATED ACTIVITY IN THIS AREA.
2017-09-29 08:50 | YES | NO | 20010046 | 2001-04-04 | 31270 | WFS - NGL PIPELINE COMPANY, L.L.C. | YES | 2001-03-04 | 1700 | MS | HANCOCK |  | NO |  | NO | HANCOCK COUNTY IN KILN MISSISSIPPI, 1/2 MILE NORTHEAST OF THE BOBINGER ROAD AND KILN-PICAYUNE ROAD INTERSECTION. | 558559 | LINE PIPE | LONGITUDINAL WELD |  | 1946 | OTHER | CORROSION, INTERNAL | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 198322.1477 | 400095.8773 | L. P. G. | 2 | 15 | 5 | NO | NO | 16 | 0.25 | 35000 | WELDED |  | 729 | 500 | YES | 8 | 900 | 0 | 0 | INTERNAL | Null | YES | OTHER | COMPLETED |  |  | Null |  |  | Null | Null | CHRIS MASON | 9185748016 | A TENANT FARMER CALLED THE 24 HR PIPELINE CONTROL NUMBER TO REPORY DEAD VEGETATION OVER THE RIGHT OF WAY. UPON VERIFICATION OF A LEAK, THE LINE WAS SHUT DOWN FOR REPAIRS. A 3FT. SECTION OF PIPING CONTAINING A PIN-HOLE LEAK WAS REMOVED AND SENT TO A METALLURGICAL LABORATORY FOR FAILURE ANALYSIS. THE LINE WAS REPAIRED WITH A NEW JOINT OF PIPE. THE LINE WAS PUT BACK IN SERVICE WITH THE UPSTREAM CONTROL VALVE PRESSURE SIGNIFICANTLY REDUCED UNTIL METALLURGICAL ANALYSIS AND OTHER INSPECTIONS ARE PERFORMED. SUPPLEMENTAL INFORMATION - METALLURGICAL ANALYSIS OF THE FAILED SECTION OF PIPE BY KIEFNER AND ASSOCIATES, INC, HAS CONCLUDED THAT A MANUFACTURING DEFECT WAS THE CAUSE OF THE PIPELINE FAILURE. THE LEAK OCCURRED AS A RESULT OF A COLD WELD DEFECT AND OD SURFACE REPAIR WELD THAT WAS USED APPARENTLY BY THE MANAFACTURER IN AN ATTEMPT TO REPAIR THE ORIGINAL MANUFACTURING DEFECT. THE DEFECTIVE AREA DID NOT EXPERIENCE A LEAK DURING THE 1998 HYDROSTATIC TEST. NO EVIDENCE OF FATIGUE, CORROSION, OR ENVIRONMENTAL CRACKING WAS FOUND IN OR AROUND THE DEFECT. BASED ON THIS INFORMATION AND THE REMAING CONTENT OF THE REPORT, THE LINE OPERATING PRESSURE WILL BE RESTORED TO NORMAL OPERATING STATUS.
2017-09-29 08:50 | YES | NO | 20010047 | 2001-04-04 | 18194 | SEMINOLE PIPELINE CO | YES | 2001-01-25 | 1512 | TX | HOWARD |  | NO |  | NO | FORSAN PUMP STATION. |  | NO DATA | PUMP |  | 1981 | OTHER | PUMP SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 1983.2215 | 4000.9588 | L. P. G. | 2 | 15 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | CHRIS MASON | 9185748016 | ON JANUARY 25, 2001 FOUR EMPLOYEES WERE REPLACING THE #2 TURBINE OF FORSAN STATION. AFTER INSTALLING THE TURBINE AND INITIATING A START TO TEST THE UNIT, THE INBOARD SEAL HAD A CASTASTROPHIC FAILURE AND THE SUCTION MOV FAILED TO CLOSE COMPLETELY. THREE TECHNICIANS WERE OUT BY THE TURBINE. THE WIND WAS BLOWING OUT OF THE SOUTH AT APPROXIMATELY 25 MILES PER HOUR. 15:12 TECHNICIAN #1 SHUTDOWN THE TURBINE IMMEDIATELY FROM THE CONTROL BUILDING. 15:12 TECHNICIAN #2 PUSHED THE STATION ESD BUTTON AT THE CONTROL BUILDING. 15:12 THE PLC RECEIVED A PUMP SEAL FAILURE BY PRESSURE SWITCH THEN BY RTD. 15:12 TECHNICIAN #1 NOTIFIED PIPELINE CONTROL. 15:14 THE TECHNICIANS NOTICED THE RELEASE FROM THE SEAL WAS NOT DIMINISHING. 15:14 THE TECHNICIANS ASSESSED THE SITUATION AND APPROACHED THE #2 PUMP SUCTION MOV UPWIND AND ATTEMPTED TO HAND CRANK THE VALVE CLOSED. A 1" PIPE WAS INSTALLED IN THE TOP OF THE PUMP TO REDIRECT SOME OF THE VAPORS. THE DISCHARGE VALVE OF THE #2 PUMP WAS ALSO CLOSED TO ENSURE COMPLETE ISOLATION. 15:15 UPDATED PIPELINE CONTROL ON THE STATUS. 15:16 TURBINE #2 HAZARDOUS GAS ALARM WAS RECEIVED IN THE CONTROL ROOM. 15:17 A BLOWDOWN HOSE WAS INSTALLED ON THE SEMINOLE BLUE MAINLINE TO SAFELY BLOWDOWN THE LINE AS QUICKLY AS POSSIBLE. 15:19 TWO TECHINICANS WENT DOWN WIND TO PREVENT OIL FIELD TRAFFIC FROM DRIVING THROUGH THE VAPOR CLOUD. 15:25 TECHINICAN #1 NOTIFIED PIPELINE CONTROL TO SHUTDOWN THE SEMINOLE BLUE LINE. 15:30 TECHNICIAN #3 NOTIFIED THE AREA MANAGER OF THE SITUATION. 15:42 THE SEMINOLE BLUE MAINLINE VALVE WENT CLOSED. 15:42 THE STATION PLC RECEIVED A BLUE LOW SUCTION PRESSURE FAULT (325PSIG) 15:45 TECHNICIAN #3 NOTFIED THE SUPERVISOR OF THE SITUATION. THE TECHNICIANS PERFORMED LOCKOUT/TAGOUT TO THE APPROPRIATE VALVES AND CONTROL DEVICES ON THE BLUE LINE.
2017-09-29 08:50 | YES | NO | 20010048 | 2001-04-04 | 15485 | PHILLIPS 66 CO | NO | 2001-03-01 | 45 | TX | BRAZORIA |  | NO |  | NO | FM 2611, 1.6 MILES SOUTHWEST OF STATE HWY 36 ON WEST SIDE OF THE ROAD. AT ETHYLENE METER STATION. | 558193 | NO DATA | OTHER | CLOSURE ON STRAINER AT PIPELINE METER STATION | 1992 | OTHER | FAILURE OF O-RING SEAL ON CLOSURE. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1900 | 1256.0403 | 2533.9406 | GASOLINE | 2 | 41 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | DENNIS TOEPPERWEIN | 9797983954 | AT 12:45 AM A CITIZEN REPORTED A PIPELINE LEAK NEAR FM 2611 SOUTH OF HWY 36. AT THIS LOCATION CHEVRON PHILLIPS CHEMICAL CO. MEASURES ETHYLENE DELIVERED TO EQUISTAR PIPELINE COMPANY. THE REMOTE VALVE AT THE METER WAS CLOSED AND PIPELINE PERSONNEL WERE DISPATCHED TO THE SCENE. UPON ARRIVAL AT THE LOCATION AT APPROXIMATELY 12:55 THE PIPELINE PERSONNEL NOTED THAT THE LEAK WAS COMING FROM A PIPELINE STRAINER AND THAT THE WIND WAS BLOWING TOWARDS FM 2611. SHERIFFS DEPARTMENT PERSONNEL ON THE SCENE BLOCKED THE TRAFFIC ON FM 2611 AT APPROXIMATELY 1:00 AM. PHILLIPS EMERGENCY PERSONNEL ON THE SCENE WERE ABLE TO GET TO THE SITE AND BLOCK MANUAL INLET AND OUTLET VALVES AT THE METER STATION AT 1:30AM. THESE MANUAL BLOCK VALVES FURTHER ISOLATED THE AMOUNT OF PIPING THAT WOULD NEED TO DEPRESSURE. AT 1:55 AM THE METER SECTION IN BETWEEN THE TWO BLOCK VALVES WAS DEPRESSURED AND THE VAPORS WERE DISSIPATED. THE ROADBLOCK WAS DISCONTINUED AND TRAFFIC WAS ALLOWED TO PASS AT 2:00AM. AT 2:30AM- NATIONAL RESPONSE CENTER WAS NOTIFIED: CASE NO. 558193. AT 2:45AM RAILROAD COMMISSION OF TEXAS, PIPELINE SAFETY SECTION WAS NOTIFIED. ROOT CAUSE OF THE INCIDENT WAS DETERMINED TO BE THE RESULT OF IMPROPER SEATING OF THE O-RING. THE OPERATION OF O-RING CLOSURES HAS BEEN THOROUGHLY DISCUSSED AS A SAFETY TOPIC IN PIPELINE SAFETY MEETINGS TO HELP PREVENT OR REDUCE FUTURE OCCURRENCES.
2017-09-29 08:50 | YES | NO | 20010049 | 2001-04-17 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | NO | 2001-03-19 | 1050 | OK | OSAGE |  | NO |  | NO | SE OF WYNONA, OKLAHOMA. | 559986 | LINE PIPE | PIPE |  | 1950 | OTHER | THERMAL EXPANSION AND ROCK WEAR. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 2 | 15 | 14 | NO | NO | 4.5 | 0.337 | 0 | WELDED |  | 450 | 100 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LARRY (RICK) LOVELESS | 8053422048 | AS A RESULT OF THERMAL EXPANSION AND ROC WEAR, RELEASE OCCURED TO SOIL. RELEASE TRAVELED 60 YARDS TO A WET UN-NAMED DRAW. LEAK WAS CLAMPED SPILL CONTAINED AND OIL WAS SKIMMED FROM THE WATER. MINIMAL SOIL AND WATER IMPACT.
2017-09-29 08:50 | YES | NO | 20010050 | 2001-04-17 | 30855 | EOTT ENERGY PIPELINE LIMITED PARTNERSHIP | YES | 2001-03-13 | 1205 | OK | OSAGE |  | NO |  | NO | 2.5 MILES SW OF WYNONA, OK. PINNEY HILL. |  | NO DATA | PIPE |  | 1950 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRUDE OIL | 2 | 7 | 6 | NO | NO | 4.5 | 0.237 | 0 | FLANGED |  | 400 | 25 | Null | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | LARRY (RICK) LOVELESS | 8063422048 | 7 BBLS OF CRUDE OIL WAS RELEASED TO THE SURFACE. THERE HAD BEEN A RECENT RAIN IN THE AREA. ORIGINALLY THE SPILL WAS REPORTED TO WATER. EPA WAS CALLED TO REPORT THAT THE SPILL WAS NOT TO WATER. JUST A LITTLE SURFACE RAIN WATER IN THE IMMEDIATE AREA.
2017-09-29 08:50 | YES | NO | 20010051 | 2001-04-18 | 3466 | DOME PIPELINE CORP | YES | 2001-04-01 | 1814 | ND | BOTTINEAU |  | NO |  | NO | NE 1/4 SEC. 21 T161N R81W 200 YARDS SOUTH HIGHWAY 83 ALONG SECTION 21/22 LINE. | 561447 | LINE PIPE | PIPE |  | 1977 | OUTSIDE FORCE DAMAGE |  | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 885000 | 585050.3356 | 1180282.838 | ETHYLENE | 2 | 27660 | 0 | YES | YES | 12.75 | 0.213 | 60000 | WELDED |  | 1440 | 1296 | YES | 24 | 1961 | 12 | 1977 |  | Null | YES |  |  |  |  | Null | ONE CALL |  | Null | Null | DAVID MILLAGE | 3193547722 | ON SUNDAY EVENING, APRIL 1, COCHIN PIPELINE EXPERIENCED A CATASTROPHIC LINE FAILURE WITH RESULTANT FIRE AND EXPLOSION NEAR MILEPOST 647 THREE MILES NORTHWEST OF MAXBASS, ND,, A VERY LOW POPULATION DENSITY RURAL AREA. APPROXIMATELY 43 FEET OF PIPE WERE BLOWN FREE, AND 27,660 BBL OF ETHYLENE WAS LOST IN THE RESULTANT FIRE. PROPERTY DAMAGE WAS MINIMAL, AND THERE WERE NO FATALITIES OR INJURIES. ENVIRONMENTAL DAMAGE WAS LIMITED TO THE FIRE EMISSIONS AND APPROXIMATELY ONE ACRE OF SCORCHED EARTH. REPAIRS WERE COMPLETED AND THE PIPELINE RETURNED TO SERVICE WITH AN 86-HOUR INTERRUPTION.
2017-09-29 08:50 | YES | NO | 20010052 | 2001-04-20 | 31045 | GENESIS CRUDE OIL LP | NO | 2001-03-23 | 230 | TX | ROSHARON |  | NO |  | NO | THE NEAREST INTERSECTION IS HIGHWAY 288 AND HWY 1462 IN ROSHARON, TEXAS, LAT: 29 20' 61"N 95 21'70"W. | 560553 | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 115687.9195 | 233389.2617 | CRUDE OIL | 1 | 220 | 200 | NO | NO | 8 | 165 | 0 | WELDED |  | 635 | 400 | YES | 8 | 86 | 0 | 1996 | EXTERNAL | Null | YES | OTHER | DEEPWELL ANDODES | OTHER | EXTERNAL CORROSION | Null |  |  | Null | Null | PATRICK D. HODGINS | 7138602500 | THE GENESIS ROW PILOT WAS FLYING THE 8" WEST COLUMBIA TO WEBSTER LINE WHEN HE SPOTTED CRUDE OIL IN DITCH. THE GENESIS SPILL MANAGEMENT TEAM (SMT) RESPONDED TO THE INCIDENT SITE, WHERE THEY FOUND THE PIPELINE LEAKING OIL. UPON FURTHER INVESTIGATION A HOLE WAS FOUND IN THE 8" LINE. THE OIL ENTERED AN IRRIGATION DITCH AND TRAVERSED ALONG THE DITCH FOR APPROXIMATELY 1.7 MILES. THE GENESIS SMT INSTALLED CONTAINMENT AND SORBANT BOOM ALONG THE DITCH AND STOPPED THE LEADING EDGE OF THE OIL SPILL IN THE DITCH APPROXIMATELY 50 YARDS SOUTH OF HIGHWAY 1462. THE GENESIS SMT OPERATED UNDER THE NATIONAL INTERAGENCY INCIDENT MANAGEMENT SYSTEM (NIMS) ICS IN A UNIFIED COMMAND STRUCTURE WITH THE RAILROAD COMMISSION OF TEXAS DISTRICT THREE (3). A INCIDENT ACTION PLAN (IAP) WAS DEVELOPED BY THE SMT AND DOCUMENTED ACTIONS TAKEN TO SAFELY MITIGATE THE INCIDENT AND MINIMIZING ANY IMPACT TO THE ENVIRONMENT.
2017-09-29 08:50 | YES | YES | 20010053 | 2001-04-17 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2001-03-20 | 1400 | IL | MARION |  | NO |  | NO | WEST TANK FARM (OWNED BY THIRD PARTY PIPELINE COMPANY) LOCATED AT US HIGHWAY 51 & DICKEY POND ROAD, VERNON, IL (3/4 MILE SOUTH OF VERNON, IL ON US HIGHWAY 51. | 560183 | TANK FARM | PIPE |  | 1949 | OTHER | BENTONITE ISOLATION PLUG FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 5 | 0 | 5 |  | 0 | 0 | CRUDE OIL | 1 | 0 | 0 | YES | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A. SCHELL | 4194213201 | A CONTRACT WELDING CREW WAS PERFORMING PIPELINE TIE-IN WORK ON 24 INCH PIPING CONNECTING A MARATHON ASHLAND PIPE LINE LLC SYSTEM TO ANOTHER PIPELINE OPERATORS TANK FARM PIPING ON MARCH 20, 2001. AT APPROXIMATELY 2:00 PM A FLASH FIRE OCCURRED DURING THE STARTUP OF WELDING OPERATIONS. FIVE CONTRACTOR EMPLOYEES WERE TRANSPORTED FOR TREATMENT. TWO INDIVIDUALS WERE TREATED AND RELEASED, TWO WERE HELD OVERNIGHT FOR OBSERVATION AT A LOCAL HOSPITAL, AND ONE WAS AIR LIFTED TO THE BARNES HOSPITAL BURN UNIT IN ST. LOUIS. ALL INJURED PERSONS HAVE BEEN RELEASED FROM THE HOSPITAL AND, AS OF APRIL 18, 2001, ARE EXPECTED TO RECOVER FULLY. CONTRACT EMPLOYEES WERE WEARING FIRE RETARDANT CLOTHING DURING PIPELINE TIE-IN WORK. THIS EVENT WAS REPORTED TO THE NRC (REPORT NUMBER 560183) ON MARCH 20,2001. AN INVESTIGATION OF THE INCIDENT DETERMINED THE CAUSE OF THE VAPOR RELEASE WAS THE FAILURE OF A BENTONITE ISOLATION PLUG INTENDED TO ISOLATE THE SOUTH SECTION (MANIFOLD SECTION) OF THE 24 INCH PIPING.
2017-09-29 08:50 | YES | NO | 20010054 | 2001-04-24 | 1845 | BUCKEYE PIPELINE CO LP | YES | 2001-03-25 | 2055 | OH | LUCAS |  | NO | NOT APPLICABLE | NO | SEE ATTACHED DRAWING NUMBER 11887-A |  | LINE PIPE | PIPE |  | 1967 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 135000 | 89244.9664 | 180043.1448 | GASOLINE | 3 | 20 | 20 | NO | NO | 10 | 0.219 | 2120 | WELDED |  | 1200 | 135 | YES | 24 | 1518 | 8 | 1979 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | CARL A. OSTACH | 4842324495 | ON FRIDAY, MARCH 23, 2001 AT 1640 HOURS, BUCKEYE PIPE LINE COMPANYS TOLEDO STATION WAS NOTIFIED OF A SHEEN IN A DITCH AT THE CORNER OF COY & BROWN ROADS. BUCKEYES EMPLOYEES RESPONDED IMMEDIATELY AND STARTED TO INVESTIGATE. ON SUNDAY, MARCH 25, 2001 AT 2055 HOURS, BUCKEYE DISCOERED ITS 10" PIPELINE HAD BEEN DAMAGED BY AN UNKNOWN THIRD PARTY AND WAS SPRAYING PRODUCT. A TEMPORARY REPAIR WAS MADE AND THE PIPELINE WAS PURGED. A PERMANENT REPAIR WAS MADE BY REPLACING THE DAMAGED SECTION OF PIPE WITH NEW PIPE. ON THURSDAY, MARCH 29, 2001, THE PIPELINE WAS PLACED BACK IN OPERATION. ALL APPLICABLE REGULATORY AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE PERFORMED UNDER THE SUPERVISION OF THE UNITED STATES COAST GUARD, OHIO ENVIRONMENTAL PROTECTION AGENCY, AND THE OREGON FIRE DEPARTMENT.
2017-09-29 08:50 | YES | NO | 20010055 | 2001-04-24 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 1999-04-07 | 1050 | IN | WARRICK |  | NO |  | NO | THE LEAK OCCURRED NEAR OUR DAYLIGHT STATION, BOONEVILLE-NEW HARMONY RD 1/2 MILE EAST OF I-64 |  | LINE PIPE | WELDING FITTING |  | 1978 | OTHER | FATIGUE CRACK | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 215000 | 148576.7978 | 299739.4137 | CRUDE OIL | 1 | 250 | 235 | NO | NO | 20 | 0.23 | 52000 | WELDED |  | 860 | 780 | YES | 24 | 1076 | 0 | 1968 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A SCHELL | 4194213201 | A MARATHON ASHLAND PIPELINE LLC (MAPL) EMPLOYEE DISCOVERED THE LEAK JUST DOWNSTREAM OF DAYLIGHT STATION AND HE IMMEDIATELY REPORTED THE LEAK TO HIS SUPERVISOR. THE SUPERVISOR CALLED THE CONTROL CENTER IN FINDLAY, OHIO AND HAD THE PIPELINE SHUT DOWN. THE LINE WAS SHUT DOWN AT 1058 CST. THE BLOCK VALVE UPSTREAM OF THE STATION WAS CLOSED. THE DOWNSTREAM VALVE WAS LEFT OPEN TO ALLOW DRAINAGE INTO OWENSBORO STATION. AN AERIAL PATROL WAS DISPATCHED TO FIND THE LEADING EDGE OF CRUDE OIL. THE OIL HAD PROGRESSED APPROXIMATELY 1.5 MILES FROM THE LEAK SITE ON BLUE GRASS CREEK. KOESTER ENVIRONMENTAL WAS CALLED OUT TO DEPLOY BOOMS ON THE CREEK AND STARTED CLEANUP. TWO MAPL CONSTRUCTION AND MAINTENANCE CREWS WERE DISPATCHED TO THE LEAK SITE. THE PIPELINE WAS EXCAVATED STARTING AT 1645 CST. A WELD FITTING WAS DISCOVERED WITH A CRACK IN IT. THE PIPELINE WAS PURGED WITH NITROGEN, FAILED SECTION OF PIPE REMOVED AND REPLACED WITH NEW PIPE. THE PIPELINE WAS PLACED BACK INTO SERVICE ON APRIL 9, 1999 AT 0511 CST. AT THE PRESENT TIME, MINOR RECOVERY OF CRUDE OIL TRACES IN THE AFFECTED PORTIONS OF BLUE GRASS CREEK IS CONTINUING.
2017-09-29 08:50 | NO | NO | 20010056 | 2001-04-30 | 26301 | BP NORTH AMERICA INC | NO | 2001-04-04 | 400 | TX | HARRIS | DEER PARK | NO |  | NO | THE LEAK OCCURED AIRSTECH PLANT. |  | PUMPING STATION | OTHER | 1/4" TUBING PARTED. | 1992 | OTHER | 1/4" TUBING PARTED. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 13 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | BP PIPELINES N.A. | 2814574030 | 1/4" TUBING ON THE METER STATION PARTED RESULTING IN APPROXIMATELY 13.4 BBLS OF CHEMICAL GRADE PROPYLENE BEING RELEASED TO THE ATMOSPHERE.
2017-09-29 08:50 | YES | NO | 20010057 | 2001-05-04 | 22175 | DYNEGY MIDSTREAM SERVICES, L.P. | NO | 2001-04-14 | 1850 | LA |  | PLAQUEMINES | NO |  | NO | APPROXIMATELY 1/2 MILE WEST OF THE VENICE TERMINAL AND RED PASS AT THE STORAGE WELL AREA-WELL #3. | 562954 | LINE PIPE | PIPE |  | 1964 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 3635.906 | 7335.0911 | L. P. G. | 2 | 42 | 0 | NO | NO | 6 | 0.329 | 42000 | WELDED |  | 2160 | 1300 | YES | 8 | 2800 | 4 | 1996 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | ALAN BORNE | 5046762223 | ON SATURDAY,04/14/01 AT 6:50 A.M. MR.EDWARD PERCHES, FACILITY TECHNICIAN AT THE VESCO COMPLEX, 1565 TIDEWATER ROAD, VENICE, LOUISIANA, REPORTED A PIPELINE LEAK AND ASSOCIATED HYDROCARBON RELEASE NEAR THE #3 LPG STORAGE WELL.. AT WHICH TIME, FACILITY PERSONNEL TOOK THE NECESSARY STEPS TO ISOLATE THE PIPELINE. WITHIN TEN MINUTES, THE PIPELINE WAS ISOLATED. THERE WERE NO INJURIES AND DAMAGE WAS LIMITED TO THE PIPING WHERE THE LEAK OCCURED. THE LINE WAS DEPRESSURED TO ZERO PSIG USING THE FLARE SYSTEM. THE AMOUNT OF VAPOR RELEASED WAS ESTIMATED AT 42 BBLS. THERE WERE NO INJURIES. E. HANNA NOTIFIED THE OFFICE OF THE STATE POLICE BY PHONE AT 6:56 AM ON THE MORNING OF THE INCIDENT AND WAS ISSUED AN INCIDENT # 01-021-52. HE THEN NOTIFIED THE NATIONAL RESPONSE CENTER, THE LOUISIANA DEPARTMENT OF NATURAL RESOURCES, LEPC AND THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY AS REQUIRED FOR RELEASE OF A REPORTABLE QUANTITY. HE RECEIVED A FOLLOW-UP PHONE CALL FROM THE USGC. WE WERE ASSIGNED A RESPONSE NUMBER OF 562-954 BY THE NATIONAL RESPONSE CENTER. THE FAILURE OCCURRED ON AN ABOVE GRADE 6" LPG PIPELINE NEAR THE WATER LINE THAT TRANSPORTS LPG FROM THE VENICE PLANT TO A STORAGE WELL. THE CAUSE OF THE FAILURE APPEARS TO BE EXTERNAL CORROSION WHERE THE COATING ON THE PIPE HAD DETERIORATED THIS SECTION OF PIPE WILL BE REPLACED AND INSTALLED ACCORDING TO DEPARTMENT OF TRANSPORTATION GUIDELINES AS REQUIRED UNDER THEIR REGULATORY JURISDICTION. ADDITIONAL INSPECTIONS OF ABOVE GRADE PIPING NEAR THE WATER LINE WILL BE MADE TO INSURE THE INTEGRITY OF OUR OTHER LPG PIPELINES THAT TRANSFER PRODUCTS TO OTHER STORAGE WELLS IN THIS AREA.
2017-09-29 08:50 | YES | NO | 20010058 | 2001-05-07 | 22855 | KOCH PIPELINE COMPANY, L.P. | YES | 2001-04-07 | 758 | IA | HANCOCK | CONCORD | NO |  | NO | 2415 VAIL AVENUE, GARNER, IOWA. | 562158 | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 6650 | 4396.1409 | 8868.7919 | ANHYDROUS AMMONIA | 2 | 176 | 0 | NO | NO | 0 | 0 | 0 |  |  | 1440 | 968 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY NATURAL FORCES |  | Null |  |  | Null | Null | ROYCE HOEMANN | 5734865488 | AT 07:57 ON 4/7/01, A SEVERE THUNDERSTROM CONTAINING WINDS OF BETWEEN 50-80 MPH BLEW A 2"X8" BOARD FROM A NEARBY BUILDING INTO THE INJECTION PIPING SKID SHEARING OFF A 1/2" PIPE NIPPLE ON THE 3" AMMONIA LINE. THE NIPPLE WAS THREADED INTO A TOL WELDED ONTO THE PIPE. ATTACHED TO THIS NIPPLE WAS A VALVE, A PRESSURE GAUGE AND TRANSMITTER TO KOCHS PIPELINE CONTROL CENTER. FARMLAND FACILITY PERSONNEL RESPONDED AFTER BEING NOTIFIED. THE ESD WAS ACTIVATED AND THE INJECTION SHUTDOWN AT 08:14, THE RELEASE WAS ISOLATED AND STOPPED AT 8:25. THE RELEASE WAS VAPORIZED IN THE OPEN AIR. REPAIRED BY REPLACING THE 1/2" NIPPLE.
2017-09-29 08:50 | YES | NO | 20010059 | 2001-05-14 | 12555 | MINNESOTA PIPELINE CO | YES | 2001-04-24 | 1010 | MN | ANOKA |  | NO |  | NO | SOUTHEAST OF ZIMMERMAN, MINNESOTA, ZIMMERMAN PUMP STATION ON MINNESOTA PIPELINE. FROM HWY 169 & COUNTY 12, GO EAST ON COUNTY 12 ONE BLOCK TO COUNTY 13, NORTH ON |  | PUMPING STATION | VALVE |  | 1989 | OTHER | MALFUNCTION OF A FLANGE GASKET AND 1/2 INCH VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 151059 | 99861.151 | 201460.2771 | CRUDE OIL | 1 | 2 | 2 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | MICK HEMENWAY | 6514803826 | IT WAS DISCOVERED THAT THE RELEASE RESULTED FROM SMALL LEAKS AROUND THE FLANGE GASKET ON THE LINE THREE TIE-IN VALVE FLANGE AND FROM A 1/2 INCH BLEED VALVE CONNECTED TO THE LINE THREE BLOCK VALVE, BOTH LOCATED ON THE DOWNSTREAM END OF THE ZIMMERMAN PUMP STATION.
2017-09-29 08:50 | YES | NO | 20010060 | 2001-05-16 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 2001-04-10 | 1305 | KS | MCPHERSON |  | NO |  | NO | 8 MILES WEST OF THE CITY OF MCPHERSON, KS ON HYW 56, T19S, R5W, NE/4 SECTION 23. |  | LINE PIPE | OTHER | 1/2" NIPPLE. | 1970 | OUTSIDE FORCE DAMAGE | DAMAGE BY NATURAL FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 9200 | 6081.8792 | 12269.6069 | NATURAL GAS LIQUID | 2 | 404 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY NATURAL FORCES |  | Null |  |  | Null | Null | JOHNNY L. CAVITT | 9185748412 | LOCALIZED INTENSE WINDS BLOW THE LID OFF A VALVE CAN WHISTLE STRIKING A 1/2" PIPE NIPPLE AND SHEARING IT OFF. EMERGENCY RESPONSE PLAN WAS INITIATED. LEAK WAS BLOCKED IN AND RELEASE STOPPED. NIPPLE REPLACED.
2017-09-29 08:50 | YES | NO | 20010061 | 2001-05-18 | 2335 | CHICAP PIPELINE CO | YES | 2001-05-02 | 2345 | IL | MARION |  | NO |  | NO | 1505 DICKEY POND ROAD, VERNON, IL 62892 (PATOKA PUMP STATION) | 564805 | PUMPING STATION | OTHER | DRAIN LINE ON STRAINER | 1968 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33053.6913 | 66682.6462 | CRUDE OIL | 1 | 200 | 120 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | PATRICK ARMSTRONG | 7084799260 | AT APPROXIMATELY 11:45 PM ON MAY 2,2001, RICK MAXEY, AN UNOCAL EMPLOYEE, VISUALLY FOUND CRUDE OIL IN THE DRAINAGE DITCH NEXT TO THE PATOKA CONTROL CENTER. RICK AND ANOTHER UNOCAL EMPLOYEE, RAY HALBROOK, IMMEDIATELY SHUTDOWN THE CAPLINE DELIVERY AND CHICAP PIPELINE, CLOSED THE ISOLATION VALVES, AND BEGAN TAKING ACTIONS TO CONTAIN THE OIL TO THE CHICAP PROPERTY. THESE ACTIONS INCLUDED INSTALLING DITCH PLUGS AND ABSORBENT MATERIAL IN THE DRAINAGE DITCH. ALTHOUGH MOST OF THE OIL WAS CONTAINED TO CHICAP PROPERTY, A SMALL AMOUNT OF OIL (LESS THAN 1 BBL) WAS ABLE TO UNDERFLOW THE DITCH PLUG AND GET INTO A CULVERT THAT LEADS OFF THE PROPERTY. THIS OIL ENTERED A DRY DRAINAGE CHANNEL AND FLOWED FOR APPROXIMATELY 120 FEET. AT 11:47 PM, THE CONTROL CENTER EMPLOYEE BEGAN MAKING INTERNAL NOTIFICATIONS, INCLUDING TO THE SUPERVISOR JIM EAGLETON. AT 12:05 AM, JIM EAGLETON ARRIVED AT PATOKA AND ASSUMED COMMAND OF THE INCIDENT AND BEGAN MAKING NOTIFICATIONS, INCLUDING TO THE PATOKA FIRE DEPARTMENT, TO FOLTZ CONSTRUCTION (A LOCAL RESPONSE CONTRACTOR), TO 911, TO THE AFFECTED LANDOWNER, AND TO PATRICK ARMSTRONG, THE DISTRICT MANAGER. AT 12:40, PATRICK ARMSTRONG ARRIVES AT THE MOKENA OFFICE AND BEGINS MAKING ADDITIONAL NOTIFICATIONS, INCLUDING TO THE NATIONAL RESPONSE CENTER, TO THE ILLINOIS EMERGENCY MANAGEMENT AGENCY, TO THE UNOCAL PIPELINE GENERAL MANAGER, AND TO TWO RESPONSE CONTRACTORS, ERST-OBRIENS AND HERITAGE ENVIRONMENTAL. AT APPROXIMATELY 1:00AM (MAY 3), FOLTZ CONSTRUCTION CREWS ARRIVED AT PATOKA AND BEGAN RECOVERING THE CRUDE OIL WITH A VACUUM TRUCK. RECOVERY CONTINUED UNTIL 5:00 AM, WHEN ALL OF THE RECOVERABLE OIL HAD BEEN PICKED UP. AT 5:00 AM, EXCAVATION BEGAN IN THE MANIFOLD AREA NEAR THE SITE OF THE LEAK. AT 7:00 AM, PATRICK ARMSTRONG AND BRIAN BURNS ARRIVED ON SITE AND ASSUMED THE ROLES OF INCIDENT COMMANDER AND SAFETY OFFICER, RESPECTIVELY. THE SITUATION WAS SIZED UP AND A DECISION WAS MADE TO MOBILIZE ADDITIONAL RESOURCES TO WORK ON THE CLEANUP. A CREW FROM HERTAGE ENVIRONMENTAL WAS MOBILIZED FROM LOUISVILLE, KENTUCKY. AT 1:00 PM, ADDITIONAL OVERFLOW DAMS WERE INSTALLED IN THE DRAINAGE DITCH ALONG DICKEY POND ROAD, DOWNSTREAM OF THE AFFECTED AREA, TO PREVENT ANY FURTHER MIGRATION OF OIL IN THE EVENT OF RAIN. BY 5:15 PM ( MAY 3), AFTER 12 HOURS OF EXCAVATION IN THE MANIFOLD AREA, THE STRAINER WAS LIFTED OUT OF THE MANIFOLD BY CRANE, AND WAS EXAMINED TO DETERMINE THE LOCATION OF THE FAILURE. AT THAT TIME, IT WAS OBSERVED THAT THERE IS A 1/4" BY 1" HOLE IN THE 2" DRAIN LINE AT A POINT JUST BELOW THE WELD THAT FASTENS THE DRAIN LINE TO THE BOTTOM OF THE STRAINER. A DECISION WAS MADE TO TEMPORARILY REPLACE THE STRAINER WITH A 26" FLANGED SPOOL PIECE. RECOVERY CONTINUED IN THE MANIFOLD DURING THE DAY AND ANOTHER 30 BARRELS OF OIL AND WATER IS COVERED. AT 5:30 PM (MAY 3), THE HERITAGE ENVIRONMENTAL CREW ARRIVED AND BEGAN CLEANUP OF THE OFFSITE AREA AND EXCAVATION OF THE DRAINAGE DITCH. CONTAMINATED SOIL WAS STOCKPILED ON VISQUEEN IN THE TANK 1 BASIN. CLEANUP OF THE DRAINAGE DITCH CONTINUED ALL OF THE NEXT DAY (MAY 4). AT 9:00 AM (MAY 4), TOM POWELL WITH ILLINOIS EPA EMERGENCY RESPONSE GROUP, TOURED THE SITE AND DISCUSSED CLEANUP OBJECTIVES. AT 8:00 PM (MAY 4), THE TEMPORARY FLANGED SPOOL WAS INSTALLED IN PLACE OF THE STRAINER AND THE CHICAP PIPELINE WAS RE-STARTED. CLEANUP CONTINUED ALL DAY ON MAY 5; BY THE END OF THE DAY, ALL OF THE DRAINAGE DITCH AREAS HAD BEEN EXCAVATED AND STOCKPILED, AND ALL CULVERTS HAD BEEN PRESSURE WASHED CLEAN. SOIL SAMPLES WERE TAKEN IN THE DRAINAGE DITCHES ON MAY 8TH, AND ARE BEING TESTED TO DETERMINE IF IEPA CLEANUP OBJECTIVES HAVE BEEN MET. CLEANUP IN THE MANIFOLD AREA IS PROCEEDING WITH A SUPER SUCKER. PLANS ARE BEING DEVELOPED FOR LONG TERM IN-SITU REMEDIATION IN THIS AREA. INVESTIGATION OF THE CAUSE OF THE LEAK, AND RECOMMENDATIONS TO PREVENT RE-OCCURRENCE ARE ON-GOING.
2017-09-29 08:50 | YES | NO | 20010062 | 2001-06-05 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | NO | 2001-05-01 | 1059 | MO | PLATTE |  | NO |  | NO | SEC 21, TOWNSHIP 53N, RANGE 35 W PLATTE COUNTY, IN A FIELD ALONG MISSOURI 273 BETWEEN PLATTE CITY AND WESTON. |  | LINE PIPE | PIPE |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 230000 | 152046.9799 | 306740.1726 | PROPANE | 2 | 13500 | 0 | YES | YES | 10.75 | 0.188 | 52000 | WELDED |  | 1310 | 1181 | YES | 8 | 1688 | 0 | 1970 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JOHNNY CAVITT | 9185748412 | ON MAY 1,2001 A RATE OF CHANGE PARAMETER ALARM WAS RECEIVED IN OPERATIONS CONTROL FROM THE KEARNEY STATION (MP 183) ON THE 10" EAST RED PIPELINE. THE CONTROLLER BEGAN EVALUATING THE SITUATION AND ALONG WITH OTHER ALARMS BEGAN TO SUSPECT A POSSIBLE RELEASE. THE CONTROLLER INITIATED THE EMERGENCY RESPONSE PLAN, BEGAN TO SHUT DOWN THE LINE, AND CALLED OUT FIELD PERSONNEL TO INVESTIGATE. OPERATIONS CONTROL RECEIVED A CALL FROM THE PLATTE COUNTY SHERIFFS OFFICE CONFIRMING A LEAK ALONG HIGHWAY 273. A UNIFIED COMMAND SYSTEM WAS SET UP WITH LOCAL EMERGENCY RESPONDERS TO MITIGATE THE INCIDENT. THE LINE WAS PUT BACK INTO SERVICE MAY 2ND AT A VOLUNTARY REDUCED PRESSURE SINCE THE CAUSE OF THE FAILURE AT THAT TIME WAS UNKNOWN. SINCE THE CAUSE OF THE FAILURE COULD NOT BE READILY DETERMINED THE REMOVED SECTION OF PIPE WAS SENT FOR METALLURGICAL ANALYSIS.
2017-09-29 08:50 | NO | NO | 20010063 | 2001-06-07 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2001-05-07 | 1500 | MT | PONDERA |  | NO |  | NO | N1/2, N1/2 OF SECTION 5, T28N, R3W, PONDERA COUNTY 3.5 MILES NORTH OF CONRAD, MT. | 565289 | LINE PIPE | PIPE |  | 1967 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 49580.5369 | 100023.9693 | CRUDE OIL |  | 30 | 15 | NO | NO | 12.75 | 0.281 | 60000 | WELDED |  | 1904 | 1800 | YES | 8 | 2380 | 0 | 1990 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | RANDY W. BEGGS | 3036494090 | AT APPROXIMATELY 3:00 P.M, MAY 7, 2001, A LANDOWNER 4 MILES NORTH OF THE GLAICER CONRAD PUMP STATION, NOTIFIED CONOCO OF A STRONG PETROLEUM ODOR. AT 3:08 P.M., THE 12" LINE WAS SHUT DOWN AND THE AREA SPILL MANAGEMENT TEAM WAS DISPATCHED TO THE CLOSE BLOCK VALES AND TO THE INCIDENT SITE. CRUDE OIL WAS FOUND IN SPRING CREEK WHICH CONTAINED WATER AND AN OIL SHEEN HAD MIGRATED DOWNSTREAM APPROXIMATELY 1 MILE. THE PIPE WAS EXCAVATED AND A SMALL ERW SEAM DEFECT OF APPROXIMATELY 1/8" IN DIAMETER WAS FOUND ON THE 12" LINE. A HIGH PRESSURE LEAK SLEEVE WAS APPLIED TO THE DEFECT TO MINIMIZE FURTHER DISCHARGE OF CRUDE. CUT OUT AND REPLACEMENT OF THE JOINT OF PIPE WAS COMPLETED ON MAY 19, 2001. THE JOINT OF PIPE HAS BEEN SENT IN TO A LAB FOR FURTHER METALLURGICAL ANALYSIS.
2017-09-29 08:50 | NO | NO | 20010064 | 2001-06-12 | 30755 | CITGO PRODUCTS PIPELINE CO | YES | 2001-05-14 | 833 | OK | LINCOLN |  | NO |  | NO | SE/4 SECTION 10-TOWNSHIP 14 NORTH-RANGE 5 EAST, LINCOLN COUNTY, OKLAHOMA-FROM THE TOWN OF DAVENPORT, OK 1 MILE EAST THEN 1/2 MILE SOUTH ON THE WEST SIDE OF THE | 566019 | LINE PIPE | PIPE |  | 1919 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33053.6913 | 66682.6462 | GASOLINE | 3 | 10 | 1 | NO | NO | 8 | 0.322 | 36000 | COUPLED |  | 696 | 15 | YES | 8 | 900 | 4 | 1991 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | DALE STOGSDILL | 8173554054 | AT 0833 HOURS ON MAY 14, 2001 THE LANDOWNER NOTIFIED CPPL EMPLOYEE JOE ROLLINS THAT HE HAD NOTICED SOME STAINED GRASS AT THE EDGE OF HIS HAY FIELD AND UPON FURTHER INVESTIGATION HE SMELLED A GASOLINE ORDOR. JOE ARRIVED AT THE SITE AND CONFIRMED THE LANDOWNER REPORT. THE SITE WAS EXCAVATED AND THE LEAK WAS TEMPORARILY REPAIRED WITH A SADDLE CLAMP AT 1515 HOURS.
2017-09-29 08:50 | YES | NO | 20010065 | 2001-06-18 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2001-05-22 | 1630 | IL | LAWRENCE |  | NO |  | NO | 1000 FT SOUTH OF THE INTERSECTION OF COUNTY RD 1800 N AND COUNTY RD 1100E. 60 FT WEST OF CR1100E. | 566967 | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 9916.1074 | 20004.7939 | GASOLINE | 2 | 344 | 0 | NO | NO | 4 | 0.125 | 1680 | WELDED |  | 1440 | 709 | YES | 4 | 1970 | 4 | 1990 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | TAD A. SCHELL | 4194213201 | ON MAY 22, LINE BALANCE EVALUATIONS INDICATED THAT THE ROBINSON TO PRINCETON PIPELINE SYSTEM WAS RUNNING SHORT. LOCAL PERSONNEL AND CONTRACT PATROL AIRCRAFT WERE DISPATCHED TO SURVEY THE SYSTEM FOR VISIBLE LEAKAGE. PATROL AIRCRAFT LOCATED AN AREA OF VISIBLE FROST ON THE GROUND NEAR BIRDS, ILLINOIS. THE LINE WAS SHUTDOWN, AND APPROPRIATE STATE AND LOCAL NOTIFICATIONS WERE MADE, AND COMPANY AND CONTRACT RESPONSE PERSONNEL WERE DISPATCHED TO THE RELEASE SITE. THE PIPELINE WAS PURGED WITH NITROGEN AND REPAIRED. THE CAUSE OF THE RELEASE WAS A PIN HOLE CAUSED BY EXTERNAL CORROSION. THE RELEASE WAS IN A RURAL BEAN FIELD. NO EXPOSURE TO HUMANS, LIVESTOCK OR WILDLIFE OCCURRED.
2017-09-29 08:50 | YES | NO | 20010066 | 2001-06-15 | 1845 | BUCKEYE PIPELINE CO LP | YES | 2001-04-17 | 1435 | MI | MONROE |  | NO |  | NO | SEE ATTACHED DRAWING | 563213 | LINE PIPE | VALVE |  | 1977 | OUTSIDE FORCE DAMAGE | FROSTHEAVE | NATURAL FORCE DAMAGE | TEMPERATURE | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 72718.1208 | 146701.8217 | GASOLINE | 3 | 5 | 5 | NO | NO | 12 | 0.375 | 2060 | WELDED |  | 1300 | 368 | YES | 24 | 1638 | 9 | 1993 |  | Null | Null |  |  | FROSTHEAVE |  | Null |  |  | Null | Null | CARL A. OSTACH | 4842324495 | ON TUESDAY, APRIL 17, 2001 A BUCKEYE PIPE LINE EMPLOYEE WAS WITH A RIGHT-OF-WAY CLEARING CONTRACTOR AND NOTICED A SMALL AMOUNT OF PRODUCT ON THE GROUND INSIDE A FENCED-IN MAINLINE BLOCK VALVE SITE. BUCKEYE PIPE LINE COMPANYS WAYNE STATION (MICHIGAN) WAS NOTIFIED AND THE PIPELINE WAS SHUTDOWN. THE WAYNE STATION MAINTENANCE CREW WAS DISPATCHED IMMEDIATELY. AFTER FURTHER INVESTIGATION, A GREASE FITTING ON THE MAINLINE VALVE WAS FOUND TO BE CRACKED. THE GREASE FITTING WAS PLUGGED AND THE PIPELINE RE-STARTED. ALL APPLICABLE REGULATORY AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE PERFORMED UNDER THE SUPERVISION OF THE MICHIGAN DEPARTMENT OF ENVIRONMENTAL QUALITY.
2017-09-29 08:50 | YES | NO | 20010067 | 2001-05-21 | 13162 | NAVAJO REFINING CO | NO | 2001-05-14 | 1452 | TX | GAINES | DENVER | NO |  | NO | FM 2055 SOUTH 5 MILES SW. | 566032 | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6610.7383 | 13336.5292 | CRUDE OIL | 3 | 65 | 60 | NO | NO | 12.75 | 0.375 | 42000 | WELDED |  | 35 | 7 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | JIM G. TOWNSEND | 5057465218 | THE LEAK WAS DISCOVERED BY AN EMPLOYEE DURING ROUTINE DAILY STATION CHECKS. THE PIPING WAS IMMEDIATELY ISOLATED AND A MAINTENANCE CREW WAS DISPATCHED TO REPAIR. THE LEAK OCCURRED WITHIN THE MAINFOLD PIPING AREA. THE ARE IMPACTED BY THIS LEAK SITE WAS ALL WITHIN THE BERMED AREA OF THE STATION. THE PIPE AND TANKS ARE CATHODICALLY PROTECTED.
2017-09-29 08:50 | NO | NO | 20010068 | 2001-06-15 | 1845 | BUCKEYE PIPELINE CO LP | YES | 2001-04-26 | 1330 | MI | MONROE |  | NO | NOT APPLICABLE | NO | SEE ATTACHED DRAWING | 564171 | LINE PIPE | PIPE |  | 1963 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 39664.4295 | 80019.1755 | GASOLINE | 3 | 2 | 2 | NO | NO | 12 | 0.219 | 1790 | WELDED |  | 1300 | 456 | YES | 24 | 1638 | 9 | 1993 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null |  |  | Null | Null | CARL A. OSTACH | 4842324495 | ON THRUSDAY, APRIL 26, 2001 BUCKEYE PIPE LINE COMPANYS WAYNE STATION WAS NOTIFIED TO A SMELL OF GASOLINE IN THE AREA OF ITS PIPELINE. BUCKEYES WAYNE STATION SHUTDOWN THE PIPELINE AND THE MAINTENANCE CREW WAS DISPATCHED IMMEDIATELY. AFTER FURTHER INVESTIGATION, BUCKEYE DISCOVERED A PINHOLE LEAK IN ITS 12" PIPELINE. A TEMPORARY REPAIR WAS MADE AND THE PIPELINE WAS INSPECTED IN BOTH DIRECTIONS FROM THE INCIDENT LOCATION. THE PIPELINE WAS PLACED BACK IN OPERATION AT A REDUCED MAXIMUM OPERATING PRESSURE. A PERMANENT REPAIR WAS MADE BY REPLACING THE DAMAGED SECTION OF PIPE WITH CERTIFIED REPLACEMENT PIPE. BUCKEYE BELIEVES THAT THE DAMAGE MAY HAVE BEEN DONE DURING ORIGINAL CONTRUCTION OR WHEN A PARALLEL 16" PIPELINE WAS INSTALLED IN 1967. ALL APPLICABLE REGULATORY AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE PERFORMED UNDER THE SUPERVISION OF THE U.S. DEPARTMENT OF ENVIRONMENTAL PROTECTION, MICHIGAN DEPARTMENT OF ENVIRONMENTAL QUALITY, AND THE IDA TOWNSHIP FIRE DEPARTMENT.
2017-09-29 08:50 | NO | NO | 20010069 | 2001-06-26 | 22855 | KOCH PIPELINE COMPANY, L.P. | YES | 2001-05-24 | 2400 | IA |  |  | NO |  | NO | CLAY COUNTY, 3425 180TH AVE. SPENCER, IA 51301. |  | NO DATA | OTHER | PIPING AND COMPONENTS ASSOCIATED WITH THE DELIVERY | 1970 | OTHER | FAILURE OF SEALS, O'RINGS, GASKETS ASSOCIATED ON I | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ANHYDROUS AMMONIA | 2 | 3 | 0 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ROYCE HOEMANN, OPERATIONS MANAGER | 5734865488 | ON 5/23/01, THE PIPELINE CONTROL CENTER IN WICHITA NOTICED THE METER PRESSURE TRANSMITTER WAS SLOWLY DECREASING AT SPENCER CFI AND CONTACTED A KOCH EMPLOYEE TO INVESTIGATE. ON 5/24/01 THE EMPLOYEE INVESTIGATED THE PROBLEM AND FOUND THAT THE DELIVERY SKID HAD ONLY 5 POUNDS OF PRESSURE. THE SKID HAD BEEN IDLE FOR SEVERAL MONTHS. NO SIGN OF VANDALISM. NO NOTICE OF AMMONIA VAPOR OR ODOR BY CFI PERSONNEL NOR THE NIGHT WATCHMAN AT THE FACILITY ON HIS ROUNDS AFTER HOURS WHICH INCLUDED WALKING BY THE DELIVERY SKID. REPLACED SEALS, O-RINGS, AND GASKETS ASSOCIATED WITH THE SKID AND FILED THE SKID WITH NITROGEN. THE SKID WILL NOT BE PUT BACK INTO SERVICE UNTIL FURTHER INVESTIGATION HAS BEEN COMPLETED. THE SKID PRESSURE WILL BE MONITORED BY THE PIPELINE CONTROL CENTER IN WICHITA AND ALSO VISUALLY MONITORED BY FIELD EMPLOYEES ON A PERIODIC BASIS.
2017-09-29 08:50 | YES | NO | 20010070 | 2001-06-25 | 4458 | ENRON PRODUCTS PIPELINE INC | NO | 2001-05-20 | 630 | OK | CARTER | RATLIFF | NO |  | NO | SEC 7, 1S, 3W. 2M WEST OF RATLIFF CITY, 2M NORTH. |  | TANK FARM | NO DATA |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 79328.8591 | 160038.3509 | CRUDE OIL | 1 | 12 | 0 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | Null |  |  |  |  | Null |  |  | Null | Null | RONNY DAVENPORT, PIPELINE SAFETY SPECIALIST | 7136466389 | A SMALL LEAK WAS DISCOVERED IN THE TANK NO. 4. SUBSEQUENT INVESTIGATION EXAMINATION REVEALED A SMALL HOLE IN TANK BOTTOM FROM INTERNAL CORROSION. API 653 INSPECTION WAS PERFORMED, TANK BOTTOM IS BEING REPAIRED, COATED AND PLACED BACK IN SERVICE.
2017-09-29 08:50 | YES | NO | 20010071 | 2001-06-25 | 4458 | ENRON PRODUCTS PIPELINE INC | NO | 2001-06-09 | 1500 | OK | WASHITA | CLINTON | NO |  | NO | SEC. 26, 11N,18W |  | LINE PIPE | NO DATA |  | 1949 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 82634.2282 | 166706.6155 | CRUDE OIL | 1 | 100 | 50 | NO | NO | 10.75 | 0.365 | 24000 | WELDED |  | 640 | 100 | YES | 24 | 800 | 0 | 1949 | INTERNAL | Null | Null |  |  |  |  | Null |  |  | Null | Null | RONNY DAVENPORT, PIPELINE SAFETY SPECIALIST | 7136466389 | INTERNAL CORROSION CAUSED LEAK WHICH GOT INTO SMALL DRY CREEK TO IMPOUNDMENT THEN TO BOGGY CREEK. OIL WAS CONTAINED AND PREVENTED FROM REACHING WASHITA RIVER. LINE WAS SMART PIGGED IN 1996 AND NUMEROUS CHANEOUTS MADE. LINE WILL BE BUDGETED FOR HYDROTESTING IN 2002.
2017-09-29 08:50 | YES | NO | 20010072 | 2001-06-25 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2001-05-24 | 2000 | MO |  | ST LOUIS | NO |  | NO | LAMBERT- ST. LOUIS INTERNATIONAL AIRPORT. |  | LINE PIPE | PIPE |  | 1989 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 198322.1477 | 400095.8773 | TURBINE FUEL | 2 | 35 | 5 | NO | NO | 10 | 0.25 | 0 |  |  | 275 | 50 | YES | 9 | 500 | 0 | 1989 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF, COMPLIANCE ASSURANCE MANAGER | 7132414381 | A THIRD PARTY OBSERVER, NOTING AN ODOR IN A NEARBY MANWAY, INITIALLY DETECTED RELEASE. EXCAVATION OF THE PIPELINE BY EQUILON IDENTIFIED THE LOCATION OF THE RELEASE AND CORRODED PIPE.
2017-09-29 08:50 | YES | NO | 20010073 | 2001-06-25 | 21315 | VINTAGE PIPELINE INC | NO | 2001-05-11 | 530 | TX | HARRIS |  | NO |  | NO | SHORE ACRES, HARRIS COUNTY, TEXAS; EXXON PIPELINE CORRIDOR #550 ALONG SIDE BOOGIE BAYOU. | 565688 | LINE PIPE | PIPE |  | 1948 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 101000 | 66768.4564 | 134698.9453 | CRUDE OIL | 1 | 85 | 85 | NO | NO | 12 | 0.375 | 1440 | WELDED |  | 900 | 340 | YES | 24 | 1400 | 0 | 1994 | INTERNAL | Null | YES | OTHER | DIRECT CURRENT |  |  | Null |  |  | Null | Null | ENVIRONMENTAL COORDINATOR | 3612347487 | THE FOLLWING STEPS WERE TAKEN TO CONTROL, RECOVER, AND CLEAN UP THE AFFECTED AREA. A. SHUT IN PIPELINE AND ISOLATED LEAKING SECTION. B. CONTACTED RESPONSE PERSONNEL AND INITIATED ODPR/SPCC PLAN. C. NOTIFIED ALL REQUIRED GOVERNMENTAL AGENCIES. AGENCIES RESPONDING WITH NO SITE PERSONNEL; U.S. COAST GUARD (LEAD AGENCY), TEXAS RAILROAD COMMISSION, TEXAS GENERAL LAND OFFICE, HARRIS COUNTY PUBLIC HEALTH AND ENVIRONMENTAL SERVICES, LA PORTE POLICE, LA PORTE FIRE DEPARTMENT. D. GARNER ENVIRONMENTAL ARRIVED AND PLACED NECESSARY WATER CONTAINMENT BOOMS, OIL SKIMMERS, RECOVERY EQUIPMENT, CLEANUP EQUIPMENT, AND PERSONNEL INTO ACTION. THIS ACTION PROVED SUCCESSFUL IN ISOLATING OIL CONCENTRATION AREAS, OIL RECOVERY, AND PREVENTING THE SPREAD OF OIL RESIDUES TO OTHER AREAS. E. BROUGHT IN EQUIPMENT TO RECOVER AND TRANSPORT RECOVERED LIQUIDS TO STORAGE TANKS. RECOVERED 85-BBL OIL. F. GARNER PERSONNEL AND EQUIPMENT WASHED SHORELINE WITH WATER RECOVERING OIL RESIDUES WITH ABSORBENT MATERIALS. SHORELINE FREE OF OIL WITH NO SHORELINE SOIL CONTAMINATION. PLACED ABSORBENT MATERIAL ALONG AFFECTED AREAS TO ABSORB REMAINING RESIDUE. ALL ABSORBENT MATERIALS PICKED UP LATER AND PLACED INTO STORAGE BIN FOR DISPOSAL. G. BROUGHT IN EQUIPMENT TO UNCOVER PIPELINE AND DELINEATED AREA, BOTH HORIZONTALLY AND VERTICALLY. PLACED REMOVED CONTAMINATED SOILS INTO TRANSPORTATION STORAGE BINS. H. SOIL SAMPLES SENT TO LAB FOR ANALYTICAL TESTING. TEST RESULTS DETERMINED THAT TPH AND BTEX WERE WELL BELOW THRESHOLDS AND DELINEATION WAS ACHIEVED. I. REMOVED 5 SECTION OF LEAKING 12" PIPE. REPLACED WITH NEW 5 X 12" HYDRO-TESTED PIPE, AND X-RAYED ALL REPAIR WELDS. J. REPLACED REMOVED SOILS WITH FRESH SOIL. BACK-FILLED HOLES AND DITCHES AND DRESSED AREA. K. TRANSPORTED CONTAMINATED SOILS TO RECYCLING FACILITY. L. MADE ADDITIONAL INSPECTIONS, BY BOAT, OF WATERWAYS TO VERIFY ALL OIL RESIDUE REMOVED FROM AREA. PHYSICAL INSPECTIONS DETERMINED THE SHORELINES ARE CLEAN.
2017-09-29 08:50 | YES | NO | 20010074 | 2001-07-02 | 4906 | EXXONMOBILE PIPELINE CO | YES | 2001-06-10 | 1640 | TX | HARRIS | ALDINE | NO |  | NO | WEST GULF BANK ROAD, ALDINE, TX. | 569027 | TANK FARM | TANK |  | 0 | OTHER |  | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 3966.443 | 8001.9175 | JET FUEL |  | 69 | 45 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ENVIR. BOARD | 7136562190 | STATION WAS SHUT DOWN 6/8/01 DUE TO SEVERE WEATHER, FLOODING AND COMMUNICATION OUTAGE. UNABLE TO CHECK STATION UNTIL 6/10 DUE TO FLOODING. FOUND SLOP TANK HAD RUN OVER BUT PRODUCT WAS CONTAINED IN THE FIREWALL OF THE TANK. NO PRODUCT LEFT STATION PROPERTY. SUMP FILLED DUE TO FLOODING AND OVERFILLED THE SLOP TANK. CLEANUP WAS ACCOMPLISHED BY SKIMMERS AND VACUUM TRUCKS. PICKED UP PRODUCT AND PUT IT BACK IN THE PIPELINE SYSTEM AT EMPCOS BAYTOWN PRODUCTS #1 STATION.
2017-09-29 08:50 | YES | NO | 20010075 | 2001-07-03 | 2552 | COLONIAL PIPELINE CO | YES | 2001-05-30 | 1130 | NC | ENOCHVILLE | ROWAN | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1963 | OTHER | DENT IN LINE PIPE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1318072 | 871342.8993 | 1757850.5772 | FUEL OIL | 2 | 400 | 264 | NO | NO | 36 | 0.281 | 52 | WELDED |  | 509 | 198 | YES | 24 | 637 | 7 | 1963 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | STEPHEN E. GILLIAM | 4048412314 | ON MAY 23, 2001 A LANDOWNER REPORTED TO COLONIALS CONTROL CENTER A FAINT ODOR IN THEIR DRINKING WATER WELL. COLONIALS LINE NO. 1 AND LINE NO. 2 PASS THROUGH THE VICINITY OF THIS AREA. COLONIAL SENT PERSONNEL TO THE SITE SAMPLE THE WELL. AFTER LABORATORY RESULTS INDICATED TRACE LEVELS OF MTBE AND BENZENE CONTAMINATION, A SUBSURFACE INVESTIGATION OF THE AREA WAS SCHEDULED TO DETERMINE WHETHER THE PIPELINES WERE THE SOURCE. ON MAY 30, 2001, THE SUBSURFACE INVESTIGATION REVEALED FREE PETROLEUM LIQUIDS (DIESEL FUEL) IN THE SUBSURFACE. THE LINES WERE SHUT DOWN AND APPROPRIATE NOTIFICATIONS WERE MADE TO FEDERAL, STATE AND LOCAL AGENCIES. LINE NO. 2 WAS EXCAVATED IN THE AREA OF A 1991 PIG DIG. THE EXAMINATION OF THE PIPE REVEALED A CRACK IN A DENT AREA OF THE PIPE. ON MAY 30, 2001 REPAIRS TO THE PIPE WERE INITIATED AND A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED AS A TEMPORARY REPAIR UNTIL THE SECTION OF PIPE IS REMOVED FOR PERMANENT REPAIR. COLONIAL ALSO CONTINUED EMERGENCY RESPONSE ACTIVITY COORDINATION WITH EPA AND STATE ON SCENE COORDINATORS TO ADDRESS ENIRONMENTAL CONCERNS. COLONIAL RESTARTED THE LINE ON MAY 31, 2001. ASSESSMENT AND REMEDIATION ACTIVITIES ARE CONTINUING.
2017-09-29 08:50 | YES | NO | 20010076 | 2001-07-03 | 4461 | ENRON OIL & GAS CO | Null | 2001-05-19 | 1445 | TX | SCURRY | COLORADO CITY | NO |  | NO |  |  | PUMPING STATION | PUMP |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 99161.0738 | 200047.9386 | CRUDE OIL | 1 | 10 | 0 | YES | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null |  |  | Null | Null | RONNY DAVENPORT | 7136466389 | A CENTRIFUGAL PUMP WAS RUNNING IN ORDER TO MAKE A DELIVERY TO BASIN. THE PUMPS MECHANICAL FAILED ALLOWING OIL TO ESCAPE. THIS OIL CAUGHT FIRE FROM AND UNKNOWN IGNITION SOURCE. THE FIRE WAS SPOTTED BY EQUILON PERSONNEL IN THE AREA AND LOCAL VOLUNTEER FIRE DEPARTMENT WAS CALLED. FIRE DEPARTMENT ARRIVED AND EXTINGUISHED THE FIRE WITHOUT FURTHER INCIDENT.
2017-09-29 08:50 | YES | NO | 20010077 | 2001-07-03 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 2001-03-09 | 2135 | TX |  |  | NO |  | NO | 2 MILES SOUTH OF REFUGIO, REFUGIO COUNTY, TEXAS. | 559102 | PUMPING STATION | PUMP |  | 1971 | OTHER | PUMP SEAL FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 676 | 446.8859 | 901.5494 | CRUDE OIL | 3 | 60 | 34 | NO | NO | 12 | 0.219 | 52000 | WELDED |  | 981 | 435 | YES | 8 | 1226 | 5 | 1991 |  | Null | YES |  |  |  |  | Null | ONE CALL |  | Null | Null | JAMES TREVINO | 3162425504 | AS A RESULT OF SMART PIG VERIFICATION ACTIVITIES ASSOCIATED WITH GENERAL PIPELINE INSPECTION/MAINTENANCE, A RELEASE OF PETROLEUM FUEL WAS OBSERVED AT THE ABOVE REFERENCED LOCATION AT 15:41 ON FEBRUARY 22, 2001. AT THE TIME RELEASE DISCOVERY, REFINED GASOLINE WAS BEING TRANSPORTED THROUGH THE 16-INCH PRODUCTS PIPELINE. OTHER REFINED PRODUCTS THAT ARE ALSO TRANSPORTED THROUGH THE PIPELINE INCLUDE JET FUEL AND DIESEL. EMERGENCY RESPONSE ACTIONS INCLUDED DEPLOYING BOOMS ACROSS THE ADJACENT INTERMITTENT STREAM, EXCAVATING SOIL TO EXPOSE THE PIPELINE AND IDENTIFYING AND STOPPING THE SOURCE OF THE RELEASE. RESIDUAL PRODUCT (AND SURFACE WATER) THAT ACCUMULATED ON THE WATER SURFACE AT THE INTERMITTENT STREAM ADJACENT TO THE RELEASE POINT WAS VACUUMED AND CONTAINERIZED ON-SITE IN FIVE 55-GALLON DRUMS PENDING PROPER DISPOSAL. UPON INSPECTION OF THE PIPELINE, THE CAUSE OF THE RELEASE WAS ASSOCIATED WITH GASKET/FLANGE COMPOSITION OF A "STOPPLE" VALVE. THE RELEASE RATE WAS CONSIDERED SLOW (I.E. IT WAS OBSERVED TO BE RELEASING IN DRIPS/SLOW TRICKLE). THE GASKET/FLANGE OF THE STOPPLE VALVE WAS REPAIRED AND WAS OBSERVED FOR APPROXIMATELY TWO WEEKS PRIOR TO BACKFILLING THE EXCAVATION ON MARCH 7, 2001.
2017-09-29 08:50 | YES | NO | 20010078 | 2001-07-03 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2001-06-07 | 1120 | TX | GLASSCOCK |  | NO |  | NO | 4" WEST TEXAS LTD PARTNERSHIP LPG PIPELINE, INTERSECTION OF PERKINS LATERAL @ MP 8.585 US HIGHWAY 87 CROSSING, 18 MILES SOUTH OF BIG SPRING, TEXAS SEC.193, BLK. | 568650 | LINE PIPE | PIPE |  | 1960 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 31000 | 20493.2886 | 41343.2407 | L. P. G. | 2 | 1361 | 0 | NO | NO | 4 | 0.142 | 42000 | WELDED |  | 1349 | 800 | YES | 8 | 2039 | 0 | 1982 |  | Null | YES |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | J. RANDY BURKE | 2815963569 | A RELEASE OF 1,361 BARRELS LPG TO AIR (2,016,400 SCF) OCCURRED WHEN THE CONTRACT BACKHOE OPERATOR (E.D. WALTON CONST CO) WAS IN THE PROCESS OF DIGGING OUT THE PERKINS 4" LPG LATERAL TO PERFORM A HIGHWAY ADJUSTMENT FOR THE STATE OF TEXAS, 18 MILES SOUTH OF BIG SPRING, TX. WHILE DIGGING OUT THE LINE, THE BACKHOE OPERATOR STRUCK THE LINE WITH BACKHOE CAUSING A PUNCTURE AND PRODUCT TO BE RELEASED TO THE ATMOSPHERE AND CROSS HWY 87. THE CONTRACTORS, TEXAS HIGHWAY DEPARTMENT OFFICIALS AND A CHEVRON PIPELINE EMPLOYEE IMMEDIATELY VACATED THE AREA AND STOPPED ALL TRAFFIC ON HIGHWAY 87. THE INCIDENT COMMAND SYSTEM WAS ACTIVATED IMMEDIATELY & RESPONSE TEAMS FROM BIG SPRING, HOWARD, STERLING AND GLASSCOCK COUNTIES ASSISTED IN SECURING AREA UNTIL ADDITIONAL CPL REPRESENATIVES ARRIVED. CPL EMPLOYEES PERFORMED 2 PRECAUTIONARY EVACUATIONS OF NEARBY RESIDENTS. AGENCY NOTIFICATIONS: NATIONAL RESPONSE CENTER- 06/07/01 @ 12:02 (MS. PICKNEY, REPORT # 5686500); SERC-06/07/01 @ 12:02 (DOUG KELLY, RPT #20011470), TRC- 06/07/01 @ 12:09 (MAURICE CURD, RPT #01-HC-099), TNRCC, MIDLAND OFFICE- 06/07/01 @ 12:11 (ALREADY WERE INFORMED BY SERC), EPA- 06/07/01 @ 12:50 (LON CALLED US).
2017-09-29 08:50 | YES | NO | 20010079 | 2001-07-06 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2001-06-24 | 1147 | LA | SULPHUR | CALCASIEU | NO |  | NO | 1/2 MILE SOUTH OF THE INTERSECTION OF LA HWY #108, OFF LA HWY #1133 ADJACENT TO THE EAST SIDE OF THE RD. SW 1/4 OF NW 1/4 SEC 24 T | 570662 | LINE PIPE | PIPE |  | 1959 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 165268.4564 | 333413.2311 | CRUDE OIL | 1 | 885 | 885 | NO | NO | 20 | 0.25 | 42000 | WELDED |  | 608 | 392 | YES | 8 | 765 | 4 | 1990 | INTERNAL | Null | YES | OTHER | MICRO BIOLOGICAL |  |  | Null |  |  | Null | Null | JAMES J JONES | 3374914466 | AT APPROXIMATELY 11:38 ON JUNE 24, 2001 THE OPERATOR ON DUTY WAS INVESTIGATING A DEVIATION ALARM ON THE LOCAL SCADA SYSTEM WHEN HE RECEIVED NOTIFICATION BY TELEPHONE, THAT OIL WAS OBSERVED ON THE GROUND AT THE LOCATION OF THIS SPILL. THE OPERATOR IMMEDIATELY SHUT IN THE PIPELINE AND CALLED OUT EMERGENCY RESPONSE PERSONNEL. RESPONSE PERSONNEL WERE ON-SCENE WITHIN AN HOUR AND MINIMIZED THE IMPACT AREA BY BUILDING AN EARTHEN BERM IN THE FLOW PATH FOR CONTAINMENT. RECOVERY OPERATIONS BEGAN IMMEDIATELY WITH VACUUM TRUCKS. 600 BBLS OF FREE OIL WAS REMOVED BY VACUUM TRUCK, 75 BBLS. WERE REMOVED IN CONTAMINATED SOIL AND THE REMAINING 100 BBLS WERE LOST TO EVAPORATION.
2017-09-29 08:50 | YES | NO | 20010080 | 2001-07-11 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2001-06-15 | 1500 | OH | RICHLAND | MADISON | NO |  | NO | APPROX.2 MILES EAST OF MANSFIELD LAHM MUNICIPAL AIRPORT, 1821 BEAL RD, RICHLAND COUNTY, MADISON TOWNSHIP, SECTION 1, TOWNSHIP 21N, RANGE 18W, R/W 38 S/N 2265+85 | 569682 | LINE PIPE | PIPE |  | 1947 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 85939.5973 | 173374.8802 | GASOLINE | 3 | 165 | 0 | NO | NO | 6 | 0.28 | 35000 | WELDED |  | 1420 | 600 | YES | 8 | 1958 | 0 | 1990 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | TAD A. SCHELL | 4194213201 | ON JUNE 15, 2001, THE MARATHON ASHLAND PIPE LINE LLC TOLEDO-STEUBENVILLE 6" PRODUCTS PIPELINE SYSTEM WAS STRUCK BY EARTH MOVING EQUIPMENT OPERATED BY A THIRD-PARTY CONTRACTOR IN THE COURSE OF CONSTRUCTING A POND. THE CONTRACTOR DID NOT UTILIZE THE AVAILABLE STATE ONE-CALL SYSTEM. THE RELEASED PRODUCT WAS CONTAINED IN THE POND AREA WHICH WAS DRY. FREE PRODUCT WAS RECOVERED AND IMPACTED SOIL WAS COLLECTED FOR PROPER DISPOSAL. ON JUNE 15, TWELVE RESIDENCES WERE EVACUATED BY THE LOCAL FIRE DEPARTMENT AS A PRECAUTION. ON JUNE 16, OCCUPANTS WERE PERMITTED TO RETURN TO THEIR RESIDENCES. THE RELEASE WAS REPORTED TO THE NRC (REPORT ID 569682) AND OTHER AGENCIES AS REQUIRED. NO SURFACE OR GROUND WATERS WERE AFFECTED. NO WILDLIFE WAS IMPACTED.
2017-09-29 08:50 | YES | NO | 20010081 | 2001-07-10 | 4461 | ENRON OIL & GAS CO | NO | 2001-06-09 | 1500 | OK | WASHITA | CLINTON | NO |  | NO | SEC.26, 11N,18W. |  | LINE PIPE | NO DATA |  | 1949 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 82634.2282 | 166706.6155 | CRUDE OIL | 1 | 100 | 50 | NO | NO | 10.75 | 0.365 | 24000 | WELDED |  | 640 | 200 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | Null |  |  |  |  | Null |  |  | Null | Null | RONNY DAVENPORT | 7136466389 | INTERNAL CORROSION CAUSED LEAK WHICH GOT INTO SMALL DRY CREEK TO IMPOUNDMENT THEN TO BOGGY CREEK. OIL WAS CONTAINED AND PREVENTED FROM REACHING WASHITA RIVER. PIPELINE WAS REPAIRED BY REPLACING AFFECTED PIPE. LINE WAS SMART PIGGED IN 1996 AND NUMEROUS CHANGEOUTS MADE. LINE WILL BE BUDGETED FOR HYDROTESTING IN 2002.
2017-09-29 08:50 | YES | NO | 20010082 | 2001-07-09 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2001-06-09 | 1600 | TX | HARRIS |  | NO |  | YES | EAST HOUSTON TANK FARM-TANK #1222. | 568951 | NO DATA | TANK |  | 1948 | OTHER | EXCESSIVE RAIN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 49580.5369 | 100023.9693 | DIESEL FUEL |  | 2500 | 2500 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | EXCESSIVE RAIN CAUSED THE ROOF ON TANK #1222 TO SINK, CAUSING DIESEL TO ESCAPE THROUGH THE ROOF DRAIN INTO THE TANK DIKE AREA. THE PRODUCT WAS CONTAINED AND VACUUMED UP.
2017-09-29 08:50 | YES | NO | 20010083 | 2001-07-16 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2001-06-09 | 1600 | TX | HARRIS |  | NO |  | NO | EAST HOUSTON TANK FARM- TANK #1388. |  | NO DATA | TANK |  | 1954 | OTHER | EXCESSIVE RAIN | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 210000 | 138825.5034 | 280067.1141 | DIESEL FUEL |  | 250 | 250 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | EXCESSIVE RAIN CAUSED THE ROOF ON TANK #1388 TO SINK AND BUCKLE. APPROXIMATELY 250 BARRELS OF DIESEL FUEL WAS RELEASED THROUGH THE ROOF DRAIN LINE INTO THE TANK DIKE AREA. THE PRODUCT WAS CONTAINED AND VACUUMED UP.
2017-09-29 08:50 | YES | NO | 20010084 | 2001-07-19 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 2001-06-16 | 1800 | PA |  | ASTON | NO |  | NO | APPROXIMATELY 50 YARDS NORTH OF THE INTERSECTION OF OLD PENNELL ROAD AND MANOR LANE. | 569803 | LINE PIPE | PIPE |  | 1956 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 330536.9128 | 666826.4621 | GASOLINE |  | 50 | 40 | NO | NO | 14 | 0.25 | 52000 | WELDED |  | 1200 | 1150 | YES | 49 | 1500 | 9 | 1956 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | CHARLES E. MASER | 2159376240 | LOCAL AUTHORITIES WERE CALLED TO THE SCENE AS A STRONG ODOR OF FUEL OIL WAS PRESENT. THE LOCAL FIRE MARSHAL DISCOVERED FREE PRODUCT IN THE STORM CULVERT FLOWING DOWNHILL TO RT452, PENNELL ROAD FROM OLD PENNEL ROAD. RESPONDERS FROM ASTON TOWNSHIP, DELAWARE COUNTY, SUNOCO REFINERY IN MARCUS HOOK AND SUN PIPE LINE SECURED THE ROADWAYS AND CONSTRUCTED AN UNDERFLOW DAM TO COLLECT PRODUCT AND PREVENT IT FROM FLOWING INTO CHESTER CREEK APPROXIMATELY 1/4 MILE FROM THE SITE. SUN PIPE LINE TOOK RESPONSIBILITY FOR THE CLEAN UP OPERATIONS. TWO OSROS WITH VAC TRUCKS AND EXCAVATING EQUIPMENT AND PERSONNEL WERE BROUGHT IN TO PERFORM THE CLEAN UP. A FRAC TANK WAS LOCATED ON SITE TO STORE RECOVERED PRODUCT. THE PIPELINE WAS EXCAVATED AND A SMALL HOLE WAS DISCOVERED. REPAIRS WERE MADE AND THE LINE WAS PUT BACK IN SERVICE. PERMANENT REPAIRS WERE PERFORMED BY THE END OF THE MONTH.
2017-09-29 08:50 | YES | NO | 20010085 | 2001-07-23 | 18718 | SUN PIPE LINE CO | NO | 2001-06-23 | 1030 | TX |  | LIBERTY | NO |  | NO | NEAR TRINITY RIVER - SEE ATTACHED MAP FOR SPECIFIC LOCATION |  | LINE PIPE | PIPE |  | 1951 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 85939.5973 | 173374.8802 | CRUDE OIL | 1 | 165 | 165 | NO | NO | 8.625 | 0.28 | 1247 | WELDED |  | 522 | 150 | YES | 8 | 659 | 0 | 1996 | INTERNAL | Null | YES | OTHER | MICROBIOLOGICALLY INDUCED CORROSION |  |  | Null |  |  | Null | Null | EDITH F COEN | 9185866942 | BARNEY GAMBY, A REPRESENTATIVE OF THE TEXAS RAILROAD COMMISSION CONTACTED OUR TULSA CONTROL CENTER AT APPROXIMATELY 10:30 AM ON JUNE 23, 2001 TO REPORT A CRUDE OIL SPILL NEAR THE TRINITY RIVER. SUN PIPE LINE FIELD PERSONNEL WERE IMMEDIATELY DEPLOYED TO THE SITE. OIL SPILL RESPONSE CONTRACTORS WERE CONTACTED AND SPILL CONTAINMENT BOOM WAS IN PLACE BY 1:15 PM. THE LEAK WAS DUE TO INTERNAL CORROSION IN A LOW SPOT UNDER A SMALL BAYOU IN THE TRINITY RIVER BOTTOM.
2017-09-29 08:50 | YES | NO | 20010086 | 2001-07-30 | 15490 | PHILLIPS PIPE LINE CO | YES | 2001-06-28 | 859 | TX |  | YOAKUM | NO |  | NO | GAINES-BORGER LINE "80" -SRW-37=34-MP 95-40+00 SEC 392, BLOCK D YOAKUM CO, TX NORTHWEST OF PLAINS, TX APPROX 1 1/2 MILES ON HWY 380 |  | LINE PIPE | PIPE |  | 1942 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6610.7383 | 13336.5292 | CRUDE OIL | 1 | 430 | 330 | NO | NO | 8.625 | 0.188 | 40000 | WELDED |  | 1150 | 245 | YES | 22 | 1486 | 3 | 1976 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | LINUS J SCHMITZ | 9186614814 | A CONTRACT EXCAVATOR WORKING FOR AN ENGINEERING FIRM STRUCK AND DAMAGED THE LINE 80 WHILE LAYING ANOTHER LINE. PPL PERSONNEL HAD RESPONDED TO THE ONE-CALL MADE BY THE ENGINEERING FIRM ON JUNE 26. THE CONTRACT EXCAVATOR HAD ALREADY HAND SPOTTED AND UNCOVERED THE PPL LINE WHERE THE PROPOSED EXCAVATION WOULD CROSS. THE PPL LINE WAS CLEARLY VISIBLE AND WAS EXCAVATED SUFFICIENTLY TO DETERMINE THE LINE DIRECTION. NO CALL WAS MADE TO PPL PERSONNEL BY THE CONTRACTOR EXCAVATOR WHEN WORK BEGAN ON JUNE 28 AS AGREED TO DURING THE LOCATE. THE CONTRACT EXCAVATOR DID NOT STOP THE EXCAVATION EQUIPMENT PRIOR TO REACHING THE LINE CROSSING AND PUNCTURED THE LINE. THE PPL CONTROL CENTER SAW A DROP IN LINE PRESSURE AND IMMEDIATELY SHUT THE LINE DOWN. THE RELEASED OIL WAS TOTALLY CONTAINED IN THE CONTRACTORS DITCH AND WAS PICKED UP BY VACUUM TRUCKS.
2017-09-29 08:50 | YES | NO | 20010087 | 2001-07-31 | 31161 | AEC EXPRESS HOLDINGS, INC. | YES | 2001-07-03 | 600 | MO | LINCOLN | SALISBURY | NO |  | NO | THE RELEASE OCCURRED WITHIN AND WAS CONTAINED WITHIN THE BOUNDARY OF THE FACILITY. |  | LINE PIPE | PIPE |  | 1953 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 66107.3826 | 133365.2924 | CRUDE OIL | 1 | 300 | 300 | NO | NO | 26 | 0.281 | 757 | WELDED |  | 100 | 60 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | INTERNAL |  |  | Null |  |  | Null | Null | CHRISTOPHER B MURRAY | 3072336181 | AT APPROXIMATELY 0600 ON 7/3/01, AEC PIPELINE (USA) INC OPERATING PERSONNEL DISCOVERED CRUDE OIL IN THE AREA BETWEEN THE MANIFOLD AND THE TANK FARM. INTERNAL NOTIFICATION WERE MADE AND THE PIPELINE WAS SHUTDOWN WHILE THE SITUATION WAS INVESTIGATED. ADDITIONALLY, THE TANK LINES WERE ISOLATED AND LOCKED OUT. EXCAVATION REVEALED THAT THE LEAK WAS IN TANK LINE #803, WHICH SERVICED MONTANA MIX CRUDE OIL. THE TANK LINE WAS COLD CUT AND DRAINED DOWN. APPROXIMATELY 120 FEET OF TANK LINE WAS REPLACED. ALL WELDS AND PIPE REPAIR WERE INSPECTED AND THE LINE WAS TIED BACK IN. EXTERNAL NOTIFICATIONS WERE MADE TO NRC, MISSOURI DEPARTMENT OF NATURAL RESOURCES, LINCOLN COUNTY LEPC.
2017-09-29 08:50 | YES | NO | 20010088 | 2001-08-03 | 31371 | BUCKEYE GULF COAST PIPELINE LLC | NO | 2001-07-18 | 1325 | TX | LAPORTE | HARRIS | NO |  | NO | 11,400 BLOCK OF "L" STREET IN LAPORTE, TEXAS. |  | LINE PIPE | GIRTH |  | 1980 | OTHER | PINHOLE IN WELD | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 118993.2886 | 240057.5264 | DATA NOT SPECIFIED | 2 | 0 | 0 | NO | NO | 10 | 0.188 | 46000 | WELDED |  | 880 | 670 | YES | 8 | 1104 | 10 | 1987 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | J.J. HLAVINKA | 7136547150 | COMMODITY LOST - PROPYLENE A HYDROCARBON ODOR WAS DETECTED AT A CASING VENT PIPE AT THE PIPELINE CROSSING AT "L" STREET IN LAPORTE, TEXAS. TESTS CONFIRMED THE PRESENCE OF HYDROCARBON. PRESSURE ON THE PIPE WAS REDUCED TO 240 PSI. THE AFFECTED PIPELINE SECTION WAS ISOLATED BY CLOSING MAINLINE BLOCK VALVES. EXCAVATION EQUIPMENT EXPOSED THE CASING ENDS AND CONFIRMED THAT PROPYLENE WAS NOT ENTERING THE CASING FROM ANOTHER SOURCE BUT MUST BE ESCAPING INSIDE THE CASING. THE PIPELINE IS LOCATED IN A PIPELINE CORRIDOR WITH SEVERAL OTHER PIPELINES, SOME TRANSPORTING PROPYLENE. A PORTABLE FLARE WAS MOVED IN TO FLARE THE PROPYLENE INVENTORY TRAPPED BETWEEN THE BLOCK VALVES. APPROXIMATELY 650,000 POUNDS. APPROXIMATELY 200 FEET OF PIPE WAS REMOVED FROM THE CASED ROAD CROSSING. CLOSE INSPECTION OF THE REMOVED PIPE INDICATED THAT THE PIPE WAS IN VERY GOOD CONDITION BOTH INTERNALLY AND EXTERNALLY. HYDROSTATIC TEST OF THE REMOVED SECTION IDENTIFIED THE CAUSE OF THE LEAK AS A DEFECT IN A WELD. SUBSEQUENT X-RAY CONFIRMED THE PRESENCE OF A PINHOLE IN A WELD.
2017-09-29 08:50 | YES | NO | 20010089 | 2001-08-02 | 13131 | CONOCO INC (AKA CONOCO PIPE LINE) | YES | 2001-06-20 | 545 | IL | MADISON |  | NO |  | NO | WOOD RIVER PRODUCTS TERMINAL TK421 SECTION 9, TOWNSHIP 4 NORTH, RANGE 9 WEST MADISON COUNTY, ILLINOIS. |  | TANK FARM | NO DATA |  | 1954 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 19832.2148 | 40009.5877 | OIL AND GASOLINE | 1 | 150 | 122 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | VANCE WEBB | 5807674845 | SUMMARY: ON 20 JUNE, 2001 A SPILL OCCURRED AT THE CONOCO PRODUCTS TERMINAL IN HARTFORD, IL. THE SPILL WAS A RESULT OF OVERFILLING AN 80,000 BBL. TRANSMIX TANK, T-421. BACKGROUND: THE OPERATOR ON SHIFT WAS RECEIVING TMIX FROM MARATHON PIPELINE INTO TANK 421. THAT RECEIPT WAS FOLLOWED BY A RECEIPT OF TMIX FROM EXPLORER PIPELINE THAT ALSO WENT INTO TANK 421. ADDITIONALLY, THAT RECEIPT WAS FOLLOWED BY A DELIVERY FROM EXPLORER PIPELINE OF RFG GASOLINE INTO TANK 411. DUE TO A VALVE BEING TEMPORARILY OUT OF SERVICE FOR MAINTENANCE IN THE EXPLORER MAINIFOLD, AN ALTERNATE VALVE LINE UP WAS REQUIRED TO RECEIVE RFG INTO TANK 411. THE ALTERNATE VALVE LINE UP REQUIRED THE UTILIZATION OF THE OIL SIDE OF THE EXPLORER MANIFOLD VIA THE TANK 410 RECEIPT LINE. THIS PARTICULAR VALVE LINE UP PROVIDES A CONNECTION TO THE TANK 421 RECEIPT LINE VIA THE CPL MAINFOLD. (SIMILAR LINE UPS HAVE BEEN USED ON PAST RECEIPTS WITH NO PROBLEMS) WHEN THIS OUT OF ORDINARY LINE UP WAS EXECUTED, VALVE TM 407 WAS IN THE OPEN POSITION. THIS VALVE SHOULD HAVE BEEN CLOSED TO PREVENT RFG FROM CROSSING OVER FROM THE TANK 410 RECEIPT LINE TO THE TANK 421 RECEIPT LINE, WHICH IS NORMALLY LINED UP FOR PUMPING THE CPL SUMP. VALVE TM 407 WAS NOT LISTED ON THE VALVE LINE-UP SHEETS. BECAUSE THIS VALVE (NOT LISTED ON THE VALVE LINE UP SHEET) WAS OPEN, RFG GASOLINE WAS ALLOWED TO STRIP INTO TANK 421. CONSEQUENTLY, THE HIGH LEVEL ALARM FOR TANK 421 ACTIVATED AT APPROXIMATELY 04:24 HRS. AS A RESULT OF THIS ALARM, THE OPERATOR ON DUTY CLIMBED AND GAUGED TANK 421 TO DETERMINE THE CAUSE OF THE ALARM. THE OPERATOR ASSUMED THAT THE ALARM WAS THE RESULT OF THE ORIGINAL DELIVERY INTO TANK 421, AS THE RECEIPT VALVE FOR THIS TANK HAD BEEN CLOSED AT THE MANIFOLD. THE OPERATOR TOOK NO FURTHER ACTION UNTIL OBSERVING THE TANK IN AN OVERFILL CONDITION. UPON FINDING THE TANK IN AN OVERFILL CONDITION, THE OPERATOR NOW ASSISTED BY THE FACILITY MANAGER, LOCATED AND CLOSED VALVE TM 407 ISOLATING TANK 421 FROM THE INCOMING STREAM INTENDED TO FILL TANK 411. FORTUNATELY, THE RELEASED PRODUCT WAS CONTAINED INSIDE SECONDARY CONTAINMENT, AND WAS RECOVERED QUICKLY WITH THE USE OF A VACUUM TRUCK FROM THE LOCAL OSRO. THE TOTAL AMOUNT OF RFG INADVERTENTLY DELIVERED INTO TANK 421 WAS 2905 BBLS. THE TOTAL AMOUNT OF TRANSMIX THAT SPILLED INTO THE DIKE WAS APPROXIMATELY 150 BBLS. THE TOTAL AMOUNT OF TRANSMIX RECOVERED WAS 122 BBLS.CONCLUSION: THE OPERATOR ON DUTY DID NOT FOLLOW PROPER PROCEDURE WHEN PREPARING FOR OR EXECUTING A VALVE LINE UP. THIS VIOLATION OF PROCEDURE RESULTED IN THE UNINTENTIONAL CONTINUED MOVEMENT OF PRODUCT INTO TANK 421, RESULTING IN THE OVERFILL CONDITION.
2017-09-29 08:50 | YES | NO | 20010090 | 2001-08-01 | 15490 | PHILLIPS PIPE LINE CO | YES | 2001-05-16 | 1210 | OK | PAYNE |  | NO |  | NO | BUXTON-BORGER LINE-BUXTON METER HEADER (16")-SRW-401-67-MP 272-00+00 SEC. 15, T17N, R5E, PAYNE CO., OK. |  | PUMPING STATION | NO DATA |  | 1987 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 10577.1812 | 21338.4468 | CRUDE OIL | 1 | 75 | 10 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | OTHER | MICROBIOLOGICALLY INFLUENCED CORROSION (MIC) |  |  | Null |  |  | Null | Null | LINUS J. SCHMITZ | 9186614814 | CRUDE OIL RELEASED FROM LOW STRESS ORIGIN STATION PIPING. APPEARED TO BE MICROBIOLOGICALLY INFLUENCED CORROSION (MIC).
2017-09-29 08:50 | YES | NO | 20010091 | 2001-08-10 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 2001-07-12 | 1610 | OK | CARTER |  | NO |  | NO | SECTION 40, RANGE 3W, TOWNSHIP 2S |  | LINE PIPE | PIPE |  | 1989 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 15700 | 10378.8591 | 20938.3509 | DATA NOT SPECIFIED | 2 | 14 | 0 | NO | NO | 4.5 | 0.125 | 1680 | WELDED |  | 1288 | 700 | YES | 8 | 1629 | 11 | 1989 | EXTERNAL | Null | YES | GALVANIC |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | BOB AEBI | 5803956294 | IMPROPER COATING PROTECTION DURING BACKFILLING WHEN THE LINE WAS BUILT CAUSING COATING DAMAGE WHICH RESULTED IN CORROSION.
2017-09-29 08:50 | YES | NO | 20010092 | 2001-08-07 | 31045 | GENESIS CRUDE OIL LP | NO | 2001-07-11 | 1630 | TX | LIMESTONE | THORNTON | NO |  | NO | THE NEAREST INTERSECTION IS COUNTY ROAD 720 AND FM 2749 THORNTON, TEXAS. LAT:31-20'94" N BY LONG: 96-31'47" W. | 572651 | LINE PIPE | PIPE |  | 1931 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 29748.3221 | 60014.3816 | CRUDE OIL | 1 | 700 | 676 | NO | NO | 8 | 0.322 | 25000 | WELDED |  | 0 | 52 | YES | 8 | 896 | 0 | 1991 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | Null | Null | PATRICK D. HODGINS | 7138602543 | THE LANDOWNER HIRED A HEAVY EQUIPMENT OPERATOR TO CLEAR TREES ON HIS LAND. ACCORDING TO THE LANDOWNER, (MR.WILKERSON) THE DOZER OPERATOR WAS PERFORMING EXCAVATING WORK IN A DRY CREEK BED AND HAD BEEN BUILDING A ROAD WAY THROUGH THE CREEK BED WHEN HE HIT OUR PIPELINE WITH THE DOZER BLADE. THE DOZER OPERATOR THEN PROCEEDED TO DAM UP THE CREEK WITH DIRT TO KEEP THE OIL IN THE DR CREEK BED FROM SPREADING DOWN GRADIENT FROM THE INCIDENT SITE. UPON FURTHER INVESTIGATION A HOLE APPROXIMATELY 5-INCHS IN DIAMETER WAS FOUND IN THE 8" LINE. THE TEAM TOOK PICTURES OF THE INCIDENT SITE FOR DOCUMENTATION. A "ONE CALL" WAS NOT PLACED PRIOR TO THE RECENT EXCAVATING ACTIVITIES. THERE WAS A ONE CALL PLACED SEVERAL YEARS AGO BY THE LANDOWNER FOR LAND CLEARING WORK AT THAT TIME AND THE LINE WAS MARKED FOR THE LANDOWNER. GENESIS PIPELINE ROW MARKER SIGN(S) WERE IDENTIFIED AT THE ENTRANCE TO THE PROPERTY SEVERAL HUNDRED FEET FROM THE INCIDENT SITE AND A COUPLE HUNDRED YARDS DOWN GRADIENT OF THE INCIDENT SITE. THE CRUDE OIL IMPACTED SOILS IN THE VICINITY OF THE PIPE BREAK AND TRAVERSED ALONG THE DRY CREEK BED FOR APPROXIMATELY 650 FEET. THE GENESIS SMT PLACED (5) FIVE 200 BBL. VACUUM TRUCKS ALONG THE CREEK AND RECOVERED 684 BARRELS OF OIL. THE IMPACTED SOILS WERE REMOVED FROM THE DRY CREEK BED AND ARE BEING LANDFARMED ON SITE (PER LANDOWNER AND RRC APPROVAL). THE LANDFARMING AREA IS BEING TILLED WEEKLY AND WILL CONTINUE UNTIL TEST RESULTS SHOW IT TO BE CLEAN. THE GENESIS SMT OPERATED UNDER THE NATIONAL INTERAGENCY INCIDENT MANAGEMENT SYSTEM (NIIMS) ICS. A SITE SAFETY PLAN WAS DEVELOPED BY THE SMT AND DOCMENTED ACTIONS TAKEN TO SAFELY MITIGATE THE INCIDENT AND MINIMIZING ANY IMPACT TO THE ENVIRONMENT. A COPY OF THE SITE SAFETY PLAN AND THE REMEDIATION PLAN WILL BE FORTH COMING TO THE TX RRC ONCE ACTIVITIES AT THE LANDFARM ARE COMPLETED.
2017-09-29 08:50 | NO | NO | 20010093 | 2001-08-17 | 31546 | CENTRAL LOUISIANA ENERGY PIPELINE CO (CLEPCO) | NO | 2001-07-16 | 1415 | LA |  | LASALLE | NO |  | NO | SECTION 2, T9N, R2E; APPROXIMATELY 4 MILES NORTH OF SEVEY, LA | 573158 | LINE PIPE | PIPE |  | 0 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 1983.2215 | 4000.9588 | CRUDE OIL | 1 | 30 | 28 | NO | NO | 4 |  | 200 | WELDED |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | YES | D D EDWARDS | 3189924111 | A LOGGING CONTRACTOR RUPTURED THE PIPELINE WITH A BULLDOZER. APPROXIMATELY 30 BARRELS OF CRUDE OIL WAS DISCHARGED TO THE GROUND. AN AREA APPROXIMATELY 40X100 WAS CONTAMINATED. THE SPILL DID NOT REACH A NAVIGABLE WATERWAY OR A TRIBUTARY OF A NAVIGABLE WATERWAY. UNDER THE DIRECT SUPERVISION OF CLEPCO EMPLOYEE, DUB STAPLETON, THE SPILL WAS CONTAINED BY THE LOGGING CONTRACTORS DOZER BY EXCAVATING AN AREA APPROXIMATELY 25; WIDTH X 30 LENGTH X 3 DEPTH. THE DIVERSION METHOD EMPLOYED HALTED THE MIGRATION OF SPILL AND ALLOWED TIME FOR THE PIPELINE TO BE SHUTDOWN AND THE AREA TO BE SECURED. WITHIN 45 MINUTES OF INITIAL REPORT TO CLEPCO THE SPILL HAD BEEN CONTAINED, THE PIPELINE WAS SHUTDOWN, AND THE MAINLINE VALVES WERE CLOSED ON THE AFFECTED SECTION OF PIPELINE. FOUR CLEPCO PERSONNEL, RUSH RIG BACKHOE SERVICE, PIONEER VACUUM TRUCK SERVICE, ND JUSTISS OIL COMPANIES SIX (6) MAN CONTRACT CREW RESPONDED TO THE SPILL INCIDENT. THE PIPELINE WAS REPAIRED WITHIN 6 HOURS OF THE INCIDENT. THE INITIAL CLEANUP INVOLVED REMOVING THE LIQUID CRUDE BY VACUUM TRUCK, ESTABLISHING A PERIMETER ALONG THE OUTERMOST MIGRATION ROUTES, AND CLEARING AND REMOVING DEBRIS-LEAVES, LIMBS, AND UNDERBRUSH. LADEQ AND LSP BOTH DISPATCHED REPRESENTATIVES TO THE INCIDENT SITE. AFTER A BRIEFING AND SITE TOUR, A CONFERENCE WAS HELD TO EVALUATE PREVIOUS ACTIONS AND TO DETERMINE THE APPROPRIATE COURSES OF ACTION TO MITIGATE THE INCIDENT. APPROXIMATELY 30 BARRELS OF LIQUID CRUDE THAT WAS RECOVERED BY VACUUM TRUCK WAS REINJECTED INTO CLEPCOS PIPELINE SYSTEM @ SEARCY STATION. THE REMAINING CONTAMINATION WAS REMOVED USING BACKHOE AND SHOVELS. THE WASTE IS PRESENTLY BEING STORED IN A BFU LEASED WASTE CONTAINER @ CLEPCOS SEARCY STATION. TESTS ARE PRESENTLY BEING PLANNED ON THE WASTE BEFORE IT MAY BE SUBMITTED FOR DISPOSAL. LADEQ WILL BE MAILED A COPY OF THE WASTE DISPOSAL MANIFEST. AT PRESENT, WE PLAN TO MONITOR THE SITE ON A DAILY BASIS FOR SEVERAL DAYS. NO FURTHER CLEANUP IS PLANNED.
2017-09-29 08:50 | YES | NO | 20010094 | 2001-08-28 | 12628 | MOBIL PIPELINE CO | YES | 2001-07-24 | 1715 | PA | LANCASTER | MANHEIM | NO |  | NO | MOBIL PIPE LINE COMPANY LANCASTER JUNCTION LOCATED AT 2410 WEAVER RD. | 574152 | LINE PIPE | VALVE |  | 0 | OTHER | INCORRECT OPERATION BY OPERATOR'S CONTRACTOR. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 396644.2953 | 800191.7546 | GASOLINE | 3 | 702 | 3 | YES | NO | 4 |  | 0 | FLANGED |  | 1440 | 580 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KAREN R. BAILOR | 7136560227 | A HYDROTEST ON THE LANCASTER TERMINAL LATERAL 4" PIPELINE (THE SPUR LINE) WAS NEARING COMPLETION. THE SPUR LINE HAD BEEN ISOLATED FROM THE MALVERN TO HARRISBURG 8/10" MAINLINE ("THE MAINLINE") BY REMOVING A SPOOL PIECE BETWEEN THE 4" CHECK VALVE LOCATED ON A TEE ON THE MAINLINE AND A BLOCK VALVE ON THE SPUR LINE. A BLIND FLANGE WAS PLACED ON THE 4" CHECK VALVE IN PREPARATION FOR BRINGING THE SPUR LINE BACK INTO SERVICE FOLLOWING COMPLETION OF THE HYDROTEST, AN EMPLOYEE OF TERRA ENVIRONMENTAL, MPLCOS CONTRACTOR BEGAN LOOSENING EVERY OTHER BOLT FROM THE BLIND FLANGE ON THE 4" CHECK VALVE. THE MAINLINE (ON WHICH THE 4" CHECK VALVE WAS ATTACHED) WAS STILL UNDER PRESSURE, AND THE VALVES ON BOTH SIDES OF THE TEE WERE OPEN. AFTER THE FACT THAT THE LINE WAS STILL PRESSURED WAS BROUGHT TO THE CONTRACTOR EMPLOYEES ATTENTION, HE RE-TIGHTENED ONE OF THE TWO LOOSENED BOLTS ON THE FLANGE. A FEW MOMENTS LATER THE FLANGE GASKET FAILED. UNLEADED GASOLINE AND ITS VAPOR WAS RELEASED FROM THE FLANGE AND WAS IGNITED BY THE RUNNING DIESEL ENGINE OF A VEHICLE PARKED ON THE OPPOSITE SIDE OF THE ROAD. LOCAL RESPONDERS WERE NOTIFIED AND RESPONDED WITH EMERGENCY EQUIPMENT. THE VOLUME OF GASOLINE INVOLVED WAS AN APPROXIMATE TOTAL OF 702 BBLS. OF THAT TOTAL, 3 BBLS WERE RECOVERED, AND THE REMAINING BARRELS WERE CONSUMED IN THE FIRE.
2017-09-29 08:50 | YES | YES | 20010095 | 2001-08-27 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 2001-07-30 | 1811 | TX | COLLIN |  | NO |  | NO | FROM THE TOWN OF PRINCETON, TEXAS-NORTH ON FM 75 TO 1827, RIGHT ON 1827 TO 995, FOLLOW TO RELEASE SITE. | 574852 | LINE PIPE | PIPE |  | 1981 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 | 88000 | 58174.4966 | 117361.4573 | PROPANE | 2 | 3932 | 0 | NO | NO | 6.625 | 0.188 | 1716 | WELDED |  | 1372 | 730 | YES | 22 | 2182 | 12 | 1981 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | BOB AEBI | 5803956294 | JOHN D. STEVENS COMPANY INSTALLING CONTRACTOR FOR THE CITY OF IRVING, TEXAS WATER PROJECT WAS MAKING ROW PREPARATIONS FOR THE INSTALLATION OF A NEW 72" WATER LINE PARALLEL TO A KOCH PIPELINE CO. L.P. (KPL) 6" HIGH PRESSURE LPG PIPELINE. A TRACKHOE PREPARING THE ROW BY MAKING A 2-3 BENCH CUT IN THE GROUND SURFACE FOR THE DITCHING MACHINE TO FOLLOW LATER. KPL PIPELINE ENTERED THIS PROPERTY FROM THE WEST MADE A 6 DEGREE TURN TO THE SOUTH FOR 502 TOWARDS THE NEW WATER LINE ROW. THE PIPELINE THEN MADE A 13-DEGREE TURN BACK TO THE NORTH FOR 285 THEN A 5 DEGREE TURN EXITING THE PROPERTY IN AN EASTERLY DIRECTION. THE PIPELINE WAS STRUCK AT APPROXIMATELY MID POINT OF THE PROPERTY NEAR THE POINT OF THE 13 DEGREE TURN.
2017-09-29 08:50 | YES | NO | 20010096 | 2001-08-27 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 2001-07-23 | 1059 | KS | BUTLER |  | NO |  | NO | SEC 12, TOWNSHIP 27S, RANGE 5E BUTLER COUNTY, IN A PASTURE HALF MILE EAST OF US HIGHWAY 77, 7 MILES SOUTH OF EL DORADO. |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 9916.1074 | 20004.7939 | PROPANE | 2 | 111 | 0 | NO | NO | 6.625 | 0.125 | 60000 | WELDED |  | 1630 | 620 | YES | 24 | 2195 | 0 | 1968 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | JOHNNY CAVITT | 9185748412 | ON JULY 23, 2001 AT APPROXIMATELY 12:43, A LANDOWNER CALLED THE MID-AMERICA PIPELINE OPERATIONS CONTROL CENTER IN TULSA, OK TO REPORT A POSSIBLE LEAK. THE CONTROLLER INITIATED THE EMERGENCY RESPONSE PLAN, BEGAN TO SHUT DOWN THE LINE, AND CALLED OUT FIELD PERSONNEL TO INVESTIGATE. AT 13:05 OPERATIONS CONTROL RECEIVED A CALL FROM FIELD PERSONNELL CONFIRMING THE REPORT OF A SMALL LEAK. THE PIPELINE WAS ISOLATED, LEAK SITE EXCAVATED AND A CLAMP INSTALLED AND AREA MONITORED OVERNIGHT. THE LINE WAS REPAIRED WITH NEW PRE-TEST X-RAYED PIPE AND PUT BACK IN SERVICE ON JULY 25. THE REMOVED SECTION OF PIPE APPEARED TO HAVE BEEN DAMAGED BY A THIRD PARTY WHEN A CULVERT HAD BEEN INSTALLED OVER THE LINE AT SOME POINT IN TIME. THE REMOVED SECTION OF PIPE WAS SENT FOR METALLURGICAL ANALYSIS TO CONFIRM THIS CONCLUSION.
2017-09-29 08:50 | YES | NO | 20010097 | 2001-09-09 | 30735 | TESORO ALASKA PIPELINE COMPANY | NO | 2001-07-31 | 930 | AK | CAPTAIN COOK STATE PARK |  | NO |  | NO | SEE ATTACHED LOCATION MAP. | 574991 | LINE PIPE | PIPE |  | 1976 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 330536.9128 | 666826.4621 | TRANSMIX (PART.REFINED PETRO) | 3 | 0 | 26 | NO | NO | 10 | 0.219 | 52000 | WELDED |  | 1440 | 1080 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | SHAWN T. BROWN | 9077763520 | AT APPROXIMATELY 9:30 P.M. ON JULY 31, 2001, EMPLOYEES OF TESORO INVESTIGATED AND CONFIRMED A LEAK AT MILEPOST 13.75 OF THE TERSORO ALASKA PIPELINE COMPANY, 10" PRODUCTS PIPELINE. AN EMPLOYEE OF PHILLIPS PETROLEUM CO., WHO WAS PERFORMING A LINE LOCATION IN THE VICINITY OF THE LEAK, REPORTED THE INITIAL REPORT OF A POTENTIAL PIPELINE LEAK TO TESORO. BASED ON THE TESORO EMPLOYEES CONFIRMATION OF A LEAK AT THE LOCATION, THE PIPELINE WAS SHUTDOWN AND THE PRESSURE REDUCED TO HEAD PRESSURE FROM TERRAIN ELEVATION ONLY. BLOCK VALVES ON EITHER SIDE OF THE AREA OF FAILURE WERE ALSO CLOSED AT THIS TIME. IMMEDIATELY FOLLOWING THE DISCOVERY, NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER, U.S.C.G., ADEC AND STATE PARKS. BOTH TESORO AND CISPRI RESPONDERS WERE ON SITE BY 11:00 P.M., PERFORMING INITIAL SITE ASSESSMENT, AND DEPLOYING SORBENT BOOM AND SORBENT PADS TO COLLECT FREE PRODUCT AND PREVENT SPREAD OF CONTAMINATION. EXCAVATION EQUIPMENT WAS ON SITE BY 12:30 A.M. ON AUGUST 1, 2001, WITH THE DECISION MADE AT THIS TIME TO WAIT UNTIL DAYLIGHT TO START EXCAVATING DUE TO SAFETY CONCERNS. EXCAVATION WAS STARTED ON WEDNESDAY, AUGUST 1, 2001 WITH THE INTENT OF LOCATING THE AREA OF FAILURE. AREA OF FAILURE WAS IDENTIFIED AT 2:35 P.M. WITH TEMPORARY SLEEVE INSTALLED AT 5:15 P.M. TO STOP LEAK. PERMANENT REPAIR INVOLVED THE INSTALLATION OF A PLIDCO MECHANICAL SPLIT SLEEVE, WHICH WAS BACK-WELDED FOLLOWING INSTALLATION. THIS REPAIR WAS APPROVED BY THE U.S. DOT WITH INSTALLATION AND BACK-WELDING BEING MONITORED BY U.S. DOT REPRESENTATIVE MR. JERRY DAVIS. ALL RECORDS PERTAINING TO THIS REPAIR ARE AVAILABLE AT OUR OFFICE FOR YOUR REVIEW.TESORO HAD RECENTLY COMPLETED A CORROSION PIGGING SURVEY OF THE PIPELINE AND WAS IN THE PROCESS OF PERFORMING A FIELD INSPECTION OF ANOMALIES IN THIS AREA. PRIOR TO THE FAILURE, THIS AREA WAS FIELD IDENTIFIED ON WEDNESDAY, JULY 25, 2001, FOR INSPECTION, WITH EXCAVATION SCHEDULED FOR THE WEEK OF AUGUST 6, 2001. FOLLOWING COMPLETION OF THE REPAIR, THE PIPELINE WAS PLACED BACK IN SERVICE AT A REDUCED PRESSURE UNTIL ADDITIONAL INSPECTIONS OF THE PIPELINE HAVE BEEN PERFORMED. FOUR (4) AREAS OF CONCERN WERE IDENTIFIED, BASED ON A REVIEW BY THE U.S. DOT OF CORROSION PIG DATA PROVIDED BY TESORO. THESE AREAS HAD BEEN IDENTIFIED BY TESORO FOR INSPECTION BASED ON THEIR REVIEW AND WILL NOW BE EXPEDITED. SPILL RESPONSE AND SITE REMEDIATION ACTIVITES CONTINUE AT THIS TIME AND ARE BEING COORDINATED WITH THE ADEC.
2017-09-29 08:50 | YES | NO | 20010098 | 2001-09-03 | 31291 | DIAMOND KOCH | YES | 2001-08-04 | 1407 | TX | MONTGOMERY | CONROE | NO |  | NO | LOOP 336 AROUND CONROE TEXAS. | 575391 | LINE PIPE | PIPE |  | 1971 | OTHER | DAMAGE BY OPERATOR OR ITS CONTRACTOR | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 34346 | 22705.2416 | 45805.6433 | NATURAL GAS LIQUID | 2 | 10 | 0 | NO | NO | 12.75 | 0.25 | 1468 | WELDED |  | 1440 | 765 | YES | 24 | 2039 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | Null | Null | BOB AEBI | 5803956294 | T.D. WILLIAMS WAS IN THE PROCESS OF FINISHING A STOPPLE PROCEDURE ON THE PIPELINE WHEN A GASKET FAILED WHICH RELEASED NATURAL GAS LIQUIDS INTO THE ATMOSPHERE.
2017-09-29 08:50 | YES | YES | 20010099 | 2001-09-18 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2001-08-12 | 1710 | TX | PARKER |  | NO |  | NO | 14" WEST TEXAS LTD PARTNERSHIP LPG PIPELINE AT MP 102.25 (PIPELINE STATIONING 5,399+13) WESTERN LAKES ESTATES, (VICINITY OF TIN TOP COMMUNITY) 8 MILES SOUTH OF | 576276 | LINE PIPE | PIPE |  | 1966 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 650000 | 429697.9866 | 866874.4008 | L. P. G. | 2 | 10740 | 0 | YES | NO | 14 | 0.219 | 52000 | WELDED |  | 1140 | 1008 | YES | 24 | 1487 | 10 | 1981 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.RANDY BURKE | 2815963569 | A THIRD PARTY LAND TENANT USING A SMALL BOBCAT TO SCRAPE A DRIVEWAY, HIT THE 14" LPG LINE OWNED BY WEST TEXAS LPG LTD PARTNERSHIP, OPERATED BY CHEVRON PIPE LINE COMPANY (CPL). THE PIPELINE WAS CLEARLY MARKED, BUT NO "ONE-CALL" WAS MADE. CPLS CONTROL CENTER WAS CALLED AT 7:30PM CDT BY A NEARBY RESIDENT, FOLLOWED BY ANOTHER CALL BY THE LOCAL SHERIFFS DEPARTMENT. THE PIPELINE SYSTEM WAS SHUT DOWN AT 7:43 PM CDT. THE INITIAL RELEASE VOLUME ESTIMATED AT 13,500 BARRELS (LINE FILL VOLUME). THIS AMOUNT WAS REVISED TO 10,740 BARRELS AFTER CONFIRMING THE LOST VOLUME WITH THE MONTH-END LOSS-GAIN TICKETS. RESIDENTS WITHIN A 1/2 MILE RADIUS WERE EVACUATED TO LOCAL RED CROSS SHELTER & HOTELS AS A PRECAUTIONARY MEASURE. THE LAND TENANTS MOBILE HOME & OUT BUILDING WERE BURNED IN THE FIRE. NO OTHER PUBLIC DAMAGES AS OF THE DATE OF THIS REPORT. WE EXPECT TOTAL PIPELINE DAMAGES OF APPROX $650,000. AGENCY NOTIFICATIONS: AGENCIES NOTIFIED WERE THE NATIONAL RESPONSE CENTER (RPT#576276), TEXAS NATURAL RESOURCE CONSERVATION COMMISSION (RPT#657), DEPT OF TRANSPORTATION, TEXAS RAILROAD COMMISSION, PARKER COUNTY LEPC & SERC. ON-SCENE AGENCIES ARE THE PARKER COUNTY SHERIFF DEPT, DEPT OF PUBLIC SAFETY-TX, PARKER COUNTY EMERGENCY OPERATIONS, AND VARIOUS LOCAL FIRE DEPTS.
2017-09-29 08:50 | YES | NO | 20010100 | 2001-09-19 | 31546 | CENTRAL LOUISIANA ENERGY PIPELINE CO (CLEPCO) | NO | 2001-08-16 | 1145 | LA | CATAHOULA |  | NO |  | NO | SECTION 30 T G N R 5 E (RURAL) | 576775 | LINE PIPE | PIPE |  | 1957 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33053.6913 | 66682.6462 | CRUDE OIL | 1 | 100 | 90 | NO | NO | 4 |  | 0 | WELDED |  | 0 | 150 | NO | 0 | 0 | 0 | 0 | EXTERNAL | Null | YES |  |  |  |  | Null |  |  | Null | Null | DWIGHT D EDWARDS | 3189924111 | A PINHOLE FORMED ON THE BOTTOM OF AN EXPOSED SECTION OF 4" STEEL PIPELINE THAT CROSSED CYPRESS BAYOU. THE CAUSE OF THE PINHOLE WAS EXTERNAL CORROSION. APPROXIMATELY 100 BARRELS OF CRUDE OIL DISCHARGED ONTO THE GROUND WATER LOCATED IN CYPRESS BAYOU. AN AREA OF APPROXIMATELY 1 1/2 MILE WAS CONTAMINATED. THE CONTAMINATION RANGED IN COLOR FROM BLACK TO BROWN TO RAINBOW SHEENING. CLOSING THE FLAP GATES LOCATED ON THE DRAINING PIPES CONTAINED THE SPILL. IN THE 1 1/2 AREA OF CONTAMINATION THERE WERE TWO SUCH FLAP GATE AREAS. TO ASSIST IN CONTROLLING THE PIPELINE SEEPAGE FROM THE PINHOLE, CLEPCO PERSONNEL CLOSED THE SCRAPER TRAP PLUG VALVES; THUS, ISOLATING THE AFFECTED LINE SEGMENT FROM THE MAINLINE. IN ADDITION, INSTALLING A LEAK CLAMP OVER THE PINHOLE LEAK PERFORMED A TEMPORARY REPAIR. AFTER THE SPILL AREA WAS EVALUATED AND SURVEYED BY CLEPCO, LADEQ, AND THE LOUISIANA STATE POLICE THE INCIDENT COMMAND SYSTEM WAS UTILIZED BY ALL RESPONDERS TO DEVISE AND DEVELOP A RESPONSE PLAN. THE INITIAL CLEANUP INVOLVED REMOVING THE THICK BLACK COLORED LIQUID CRUDE THAT HAD GATHERED AT THE 1ST DUMP FLAP GATE SITE BY USING VACUUM TRUCKS. TO ASSIST IN THE CLEANUP OF THE BAYOU CONTAMINATION, AMERICAN ENVIRONMENTAL SERVICES, A PROFESSIONAL CLEANUP CREW ARRIVED ON SITE @ 4:30 PM ON 8-16-01. UPON THEIR ARRIVAL, EACH DUMP GATE LOCATION WAS SECURED BY ADDING FLOATATION BOOMS IN FRONT OF THE DUMPS TO HELP CONTAIN, HOLD, AND DIRECT THE MIGRATING CRUDE TO THE VACUUM TRUCKS FROM REMOVAL. WASH DOWN PUMPS WAS DEPLOYED AT THE UPPERMOST POINT OF CONTAMINATION AND BEGAN MOVING THE SPILL TO THE 1ST DUMP FOR RETRIEVAL. BY THE END OF THE FIRST DAY, APPROXIMATELY 10% OF THE CONTAMINATION WAS REMOVED USING THE ABOVE PERSONNEL AND EQUIPMENT. IN DAY TWO (8-17-01) OF THE INCIDENT, RESPONDERS USED THE SAME TECHNIQUES AS DAY ONE. THE ONLY SIGNIFICANT CHANGE WAS THAT THE SCOPE OF THE CLEANUP SHIFTED FROM DUMP #1 TO STAGING AREA #1 WHICH WAS ABOUT HALF THE DISTANCE BETWEEN DUMP #1 AND DUMP #2. STAGING AREA #1 WAS A MINI-BOOM LOCATION SUPPLEMENTED BY A VACUUM TRUCK AND RETRIEVAL PERSONNEL. AT THE END OF DAY TWO, APPROXIMATELY 25% THE SPILL WAS RETRIEVED. DAY THREE (8-18-01) AN ADDITIONAL CLEANUP CONTRACTOR, PETRON, WAS ADDED TO THE EXISTING CLEANUP CREWS TO ASSIST IN THE CLEANUP EFFORT. PETRON AND AMERICAN ENVIRONMENTAL CONTINUED TO UTILIZE THE SAME STRATEGIES AND TECHNIQUES AS DAY ONE AND DAY TWO. THE DRAGGING OF MINI-BOOMS AND ABSORBENT BOOMS ON DAY THREE WAS EFFECTIVE WHEN THE CRUDE BECAME FRACTURED AND HEAVY DUE TO RAINFALL. AT THE END OF DAY THREE, 90% OF THE CRUDE OIL SPILLED WAS RETRIEVED. AMERICAN ENVIRONMENTAL SERVICES WAS RELEASED. 8-19-01 PETRON AND CLEPCO PERSONNEL CONTINUED THE CLEANUP USING ABSORBENTS AND THE WASH DOWN OF RESIDUALS. PETRON SPRAYED THE AREA WITH HAZCLEAN E-R TO ASSIST IN THE CLEANING OF AFFECTED VEGETATION. THE ESTIMATED 90 BARRELS OF LIQUID CRUDE THAT WAS RECOVERED BY VACUUM TRUCK WAS REINJECTED INTO CLEPCOS PIPELINE SYSTEM @ CLEPCOS SEARCY STATION. TESTS ARE PRESENTLY BEING PLANNED ON THE WASTE BEFORE IT MAY BE SUBMITTED FOR DISPOSAL. LADEQ WILL BE MAILED A COPY OF THE WASTE DISPOSAL MANIFEST. AT PRESENT, WE PLAN TO MONITOR THE SITE ON A DAILY BASIS FOR SEVERAL DAYS. ANY RESIDUE THAT APPEARS AT THE TWO BOOM SITES WILL BE PROMPTLY REMOVED. JASON DEWITT, LADEQ, IS PRESENTLY ASSISTING IN THE DAILY MONITORING AND RESIDUAL CLEANUP. A FINAL INSPECTION BY LADEQ IS PLANNED LATER IN THE WEEK.
2017-09-29 08:50 | YES | NO | 20010101 | 2001-09-20 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 2001-08-23 | 627 | IA | JOHNSON |  | NO |  | NO | 207 PIPELINE ROAD, CORALVILLE, IA, 52241, JOHNSON COUNTY, IOWA. |  | TANK FARM | VALVE |  | 2001 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 231.3758 | 466.7785 | PROPANE | 2 | 16 | 0 | NO | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A. FANT | 7133699454 | A BODY BLEED VALVE HAD BEEN INADVERTENTLY LEFT OPEN AFTER ROUTINE MAINTENANCE. DURING THE INITIAL START UP SEQUENCE AFTER THE MAINTENANCE ACTIVITY, PROPANE- A HIGHLY VOLATILE LIQUID- ESCAPED TO THE ATMOSPHERE THROUGH THE BODY BLEED VALVE.
2017-09-29 08:50 | YES | NO | 20010102 | 2001-09-20 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | NO | 2001-08-28 | 1630 | FL | TAMPA | HILLSBOROUGH | NO |  | NO | NE CORNER OF ADAMO DRIVE (HIGHWAY 60) AND 45TH STREET, TAMPA, FLORIDA. |  | NO DATA | WELDING FITTING |  | 1972 | OTHER | CRACK IN 45 DEGREE FITTING. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 99161.0738 | 200047.9386 | TURBINE FUEL | 2 | 0 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A. FANT | 7133699454 | AT 4:30P.M. ON AUGUST 28, 2001 THE CENTRAL FLORIDA PIPELINE (CFPL) RIGHT-OF-WAY DEPARTMENT NOTICED A SMALL AREA OF DEAD VEGETATION WHICH APPEARED TO BE A SURFACE SPILL AT ADAMO DRIVE AND 45TH STREET IN TAMPA, FLORIDA. CFPL SHUT DOWN THE 10" PIPELINE TO PERFORM A PRESSURE TEST. DUE TO A SMALL CONTINUOUS LOSS OF PRESSURE, CFPL EXCAVATED THE LOCATION AND FOUND A SMALL CRACK IN A 1075" 45 DEGREE ELBOW BEND AT THE BOTTOM OF THE FITTING RUNNING PERPENDICULAR TO THE PIPE DIRECTION. THE CAUSE OF THE CRACK IS UNKNOWN AT THIS TIME. VARIOUS AGENCIES WERE NOTIFIED. THE FITTING WAS REMOVED AND A NEW 10.75" 45 DEGREE ELBOW WAS WELDED IN. THE NEW PIPELINE WELDS WERE NON-DESTRUCTIVELY TESTED AND THEN THE 10" PIPELINE SYSTEM WAS BROUGHT BACK INTO OPERATION ON AUGUST 31, 2001. REFERENCE PART G (3): ESTIMATED QUANTITIES OF PRODUCT SPILLED AND RECOVERED IS UNDERTERMINED AT THIS TIME DUE TO ONGOING REMEDIATION. THE SITE WILL BE REMEDIATED IN ACCORDANCE WITH ALL APPLICABLE REGULATIONS.
2017-09-29 08:50 | YES | NO | 20010103 | 2001-09-24 | 26301 | BP NORTH AMERICA INC | YES | 2001-08-17 | 750 | OK | JACKSON |  | NO |  | NO | FROM BLAIR OKLAHOMA, GO SOUTH ON HIGHWAY 283 TO COUNTY ROAD E-1550. GO WEST ON E-1550 1 MILE THEN SOUTH N-2030 1/4 MILE TO THE LEAK SITE ON THE EAST SIDE OF THE | 576822 | LINE PIPE | PIPE |  | 0 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 66107.3826 | 133365.2924 | CRUDE OIL | 1 | 3000 | 2500 | NO | NO | 16 | 0.25 | 35000 |  |  | 788 | 80 | Null | 48 | 984 | 3 | 1974 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | TOM BROZOVICH | 8068977022 | #2 SYSTEM #2 LINE SLAUGHTER TO DRUMRIGHT 16" PIPELINE WAS HIT BY A COUNTY ROAD GRADER WHILE CLEANING OUT THE DITCH AT THE SIDE OF THE ROAD.
2017-09-29 08:50 | YES | NO | 20010104 | 2001-09-25 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | Null | 2001-08-22 | 2000 | LA | GRANT |  | NO |  | NO | SOUTH SIDE OF HIGHWAY 8, APPROXIMATELY 7.5 MILES EAST OF THE CITY OF POLLOCK, LA. | 577453 | LINE PIPE | PIPE |  | 1998 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 132214.7651 | 266730.5849 | ANHYDROUS AMMONIA | 2 | 258 | 0 | NO | NO | 6.625 | 0.28 | 42000 | WELDED |  | 1340 | 500 | YES | 4 | 2118 | 1 | 1998 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null |  |  | Null | Null | ROYCE HOEMANN | 5734865488 | AT APPROXIMATELY 20:00 ON 8/22/01, KOCHS PIPELINE CONTROL CENTER RECEIVED NOTIFICATION FROM A LANDOWNER OF A VAPOR CLOUD AROUND A VALVE SITE LOCATED ON ITS 6" AMMONIA PIPELINE IN GRANT PARISH, LA. UPON INVESTIGATION, KOCH DETERMINED THE CAUSE OF THE RELEASE TO BE VANDALISM. VANDALS HAD DRILLED A 11/64" HOLE IN THE SIDE WALL OF THE PIPELINE. KOCH PERSONNEL DONNED ON LEVEL "A" PPE AND STOPPED THE RELEASE BY AFFIXING A CLAMP WITH A RUBBER NIPPLE OVER THE DRILL HOLE. FURTHER REPAIRS WERE MADE BY STOPPLING THE PIPELINE AND REPLACING THE DAMAGED PIPE. FIVE LOCAL RESIDENTS WERE TREATED AND RELEASED FROM THE HOSPITAL AS A RESULT OF THE RELEASE. NO FATALITIES RESULTED FROM THE RELEASE. APPROXIMATELY 70 RESIDENTS WERE EVACUATED AND LOUISIANA HIGHWAY 8 AND SURROUNDING ROADS WERE CLOSED UNTIL REPAIRS COULD BE MADE.
2017-09-29 08:50 | NO | NO | 20010105 | 2001-09-25 | 30735 | TESORO ALASKA PIPELINE COMPANY | NO | 2001-09-07 | 825 | AK |  |  | NO |  | YES | BETWEEN NORTH/SOUTH RUNWAY AND TAXIWAY AT GPS LOCATION-61 11.11N, 150 00.26 W. | 579116 | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 26442.953 | 53346.117 | GASOLINE | 3 | 5 | 0 | NO | NO | 10 | 0.219 | 52000 | WELDED |  | 1440 | 175 | NO | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | NO | SHAWN T. BROWN | 9077763520 | ON FRIDAY, SEPTEMBER 7TH, AT APPROXIMATELY 0800 A LEAK OCCURRED ON THE TESORO ALASKA PIPELINE COMPANYS 10-INCH PRODUCTS PIPELINE, AT WHICH TIME THE PIPELINE WAS TRANSPORTING GASOLINE. AN EQUIPMENT OPERATOR EMPLOYED BY DIMOND ELECTRIC WHO WAS DIGGING A TRENCH FOR A PROJECT AT THE TED STEVENS ANCHORAGE INTERNATIONAL AIRPORT CAUSED THE LEAK BY HITTING THE PIPELINE. THE PIPELINE WAS SHUTDOWN, ISOLATED, AND REPAIRED. DETAILS OF EVENTS LEADING UP TO THE INCIDENT ARE AS FOLLOWS. TESORO ALASKA PIPELINE SUPERVISOR, MR. SPIKE BURGER, RECEIVED A CALL FROM AIRPORT POLICE AT APPROXIMATELY 0825 THAT THE TESORO PIPELINE MAY HAVE BEEN STRUCK BY EQUIPMENT OPERATING IN THE AREA, AND WAS LEAKING. MR. BURGER IMMEDIATELY INSTRUCTED OPERATING PERSONNEL TO SHUTDOWN THE PIPELINE. MR. BURGER THEN PROCEEDED TO THE ACCIDENT SITE LOCATED ON THE EAST SIDE OF THE NORTH/SOUTH RUNWAY AT THE TED STEVENS ANCHORAGE INTERNATIONAL AIRPORT. AT THIS TIME, NOTIFICATION WAS MADE TO THE NRC, USDOT, ADEC AND THE USCG. IN ADDITION, RESPONSE ACTIONS WERE COORDINATED WITH THE AIRPORT POLICE, SAFETY AND ENVIRONMENTAL DEPARTMENTS. INITIAL SAFETY ASSESSMENT WAS PERFORMED AT THE SITE TO ALLOW FOR THE SAFE INSTALLATION OF A TEMPORARY MECHANICAL REPAIR SLEEVE TO STOP THE FLOW OF PRODUCT TO THE SURROUNDING SOILS. AT 11:04 A.M., INSTALLATION OF THE SLEEVE WAS STARTED WITH LEAK CONTAINMENT COMPLETED AT 11:36 A.M. VOLUME OF PRODUCT SPILLED IS ESTIMATED AT BETWEEN 100 AND 200 GALLONS. FOLLOWING INSTALLATION OF THE MECHANICAL SLEEVE, TESORO RECEIVED APPROVAL FROM THE USDOT TO RESUME OPERATION OF THE PIPELINE AT A REDUCED MAXIMUM OPERATING PRESSURE OF 1000 PSI. AT 12:35 P.M., REMOVAL OF CONTAMINATED SOIL AT THE AREA OF THE SPILL WAS STARTED WITH THE OPERATION CONTINUING UNTIL 4:30 P.M.
2017-09-29 08:50 | YES | NO | 20010106 | 2001-09-28 | 19522 | TOSCO CORP | NO | 2001-08-08 | 1515 | CA | SANTA BARBARA |  | NO |  | NO | 3042 INDUSTRAIL PARKWAY, SANTA MARIA, CA. |  | LINE PIPE | VALVE |  | 1954 | OTHER | UNDER INVESTIGATION AT THIS TIME. LAB ANALYSIS BEI | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 16526.8456 | 33341.3231 | CRUDE OIL | 3 | 182 | 150 | Null | Null | 8 |  | 0 | FLANGED |  | 0 | 650 | YES | 8 | 1016 | 11 | 1989 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KENT PENNINGROTH | 8053497639 | AT 15:15 HOURS ON AUGUST 8, 2001 TOSCO WAS INFORMED THAT A RELEASE OF CRUDE OIL HAD OCCURRED AT 3042 INDUSTRAIL PARKWAY IN THE CITY OF SANTA MARIA, CALIFORNIA. CRUDE OIL HAD BEEN REPORTED FLOWING FROM A VALVE VAULT AT THAT LOCATION. TOSCO IMMEDIATELY SHUT DOWN THE 8" ORCUTT TO SUEY JUNCTION SEGMENT OF UNOCAP LINE 300 WHICH RUNS THROUGH THE AREA. EMERGENCY RESPONSE PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE SITE AND BEGAN ARRIVING AT 15:30. THE SANTA MARIA FIRE DEPARTMENT WAS ALREADY ON SITE AND HAD CONSTRUCTED A SMALL EARTHEN BERM TO HELP CONTAIN THE RELEASE. APPROXIMATELY 10 BBLS OF CRUDE OIL WERE RELEASED TO THE SURROUNDING LANDSCAPED AND PAVED AREA, APPROXIMATELY 172 BBLS WAS CONTAINED IN THE VAULT ITSELF. AFTER RESPONSE PERSONNEL SECURED THE AREA AND WERE ABLE TO DRAIN THE VAULT PERSONNEL WERE THEN ABLE TO DETERMINE THAT THE RELEASE HAD OCCURRED THROUGH A HOLE IN THE BODY OF THE VALVE. AFTER CLEAN-UP OF THE AREA WAS COMPLETE THE VALVE WAS REPLACED AND THE PIPELINE WAS RETURNED TO SERVICE ON 08/10/01. THE VALVE WAS SENT TO A LABORATORY FOR ANALYSIS TO DETERMINE THE EXACT CAUSE OF THE RELEASE. THE RESULTS OF THE LABORATORY ANALYSIS ARE NOT COMPLETE AT THIS TIME.
2017-09-29 08:50 | NO | NO | 20010107 | 2001-09-28 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2000-04-24 | 2400 | OH | LIMA |  | NO |  | NO | SEC 14 T4S R6E SHAWNEE TOWNSHIP, ALLEN COUNTY, OHIO. RIO 8" PRODUCTS PIPELINE SYSTEM ROW | 580499 | NO DATA | BOLTED FITTING |  | 1947 | OTHER | GASKET FAILURE IN UNDERGROUND FLANGED CONNECTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 65247 | 44176.0712 | 89120.979 | FUEL OIL | 3 | 2 | 2 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A. SCHELL | 4194213201 | ON APRIL 24, 2000, STAINED VEGETATIOIN WAS OBSERVED ON THE PIPELINE ROW, MEASURING APPROXIMATELY 300 X 60. THE SITE WAS EXCAVATED TO IDENTIFY THE SOURCE OF THE STANDING, AND A LEAKING FLANGE GASKET WAS DISCOVERED. THE OHIO EPA AND ALLEN COUNTY LEPC WERE NOTIFIED ON APRIL 24, 2000. THE SOURCE OF THE LEAK WAS AN INSULATING FLANGE GASKET LOCATED UNDERGROUND. THE FLANGE FITTING WAS REPLACED WITH PRE-TESTED PIPE. IMPACTED SOIL WAS REMOVED AND DISPOSED OF PURSUANT TO OHIO SOLID WASTE REGULATIONS. ON AUGUST 30, 2001, IN THE COURSE OF JOB CLOSING REVIEWS, IT WAS DETERMINED THAT ACCUMULATED COSTS FOR THIS EVENT EXCEEDED $50,000, AND A FORM 7000-1 REPORT WAS INITIATED. ON SEPTEMBER 21, 2001, IT WAS DETERMINED THAT AN NRC NOTIFICATION HAD NOT BEEN MADE, AND NRC NOTIFICATION WAS MADE (REPORT NUMBER 580499).
2017-09-29 08:50 | YES | NO | 20010108 | 2001-09-26 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2001-08-13 | 1205 | LA |  |  | NO | 29.21.61" N LATITUDE;88.3 | NO | MAIN PASS PIPELINE SYSTEM BETWEEN PLATFORMS IN MAIN PASS BLOCKS 133-A AND 144-A 6" CRUDE OIL PIPELINE, FEDERAL OCS WATERS OFF LOUISIANA. |  | LINE PIPE | PIPE |  | 1972 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 79328.8591 | 160038.3509 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 6 | 0.344 | 42000 | WELDED |  | 1440 | 0 | YES | 8 | 1800 | 9 | 1972 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | J. RANDY BURKE | 2815963569 | 6" CRUDE OIL PIPELINE (UJI), MAIN PASS PIPELINE SYSTEM, FEDERAL OCS WATERS OFF LOUISIANA-CRUDE; AN OIL SHEEN WAS REPORTED BY A CHEVRON PRODUCTION COMPANY EMPLOYEE, AS COMING FROM A 6" CRUDE PIPELINE BETWEEN MAIN PASS BLOCKS 133-A AND 144-A. CHEVRON PIPE LINE (CPL) RESPONDED & FOUND BUBBLES SURFACING ON THE WATER. THE SILVERY SHEEN SIZE WAS APPROX 50 TO 200 WIDE BY APPROX 2 MILES LONG. VOLUME WAS ESTIMATED BASED ON API CHART TO BE 4.224 GALLONS, OR 0.1 BARRELS. THE ROOT CAUSE FOR THE LEAK WAS DETERMINED TO BE PIPELINE COATING DAMAGE, SUSPECTED AS CAUSED BY A TRAWLING VESSEL, WHICH ALLOWED EXTERNAL CORROSION TO OCCUR ON THE PIPE, DESPITE CATHODIC PROTECTION. AGENCIES NOTIFIED: NRC (P.O. JONES) WAS NOTIFIED 12:37 CDT (RPT.#576350). AT 13:20 CDT, P.O. JASON PETTIT, USCG MSO-NEW ORLEANS, CALLED FOR DETAILS. AT 15:30 CDT, CALL RETURNED TO P.O. PETTIT TO INFORM HIM THAT WE WERE PRESSURING UP ON OUR PIPELINE TO DETERMINE IF THERE WAS A LEAK, AND WHERE IT WAS LOCATED. AT 16:25 CDT, P.O. PETTIT WAS UPDATED ON THE SITUATION TO LET HIM KNOW THAT IT WAS A LEAK ON OUR 6" PIPELINE, AND THAT WE WERE DEVELOPING PIPELINE REPAIR PROCEDURES TO CORRECT THE PROBLEM. ON 8/15/01 AT 13:45 CDT, THE USCG MSO-NEW ORLEANS OFFICE WAS FAXED A COPY OF THE PROJECT ENGINEERS REPAIR PROCEDURES FOR THEIR RECORDS.
2017-09-29 08:50 | YES | NO | 20010109 | 2001-10-02 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2001-09-03 | 1130 | LA | LAFOURCHE |  | NO |  | NO | LAT: 29 DEGREE 22' 55.840N/ LONG: 90 DEGREE 19' 68.307W. | 578684 | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 330536.9128 | 666826.4621 | CRUDE OIL | 1 | 80 | 0 | NO | NO | 12 | 0.25 | 42000 | OTHER |  | 800 | 115 | YES | 24 | 1740 | 0 | 1953 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null |  |  | Null | Null | G.L. ZIMMERMAN | 7132414381 | THE RELEASE OCCURRED ON THE WESTERN EDGE OF CATFISH LAKE. IT IS SUSPECTED THAT A SMALL COMMERCIAL FISHING VESSEL (TRAWLER) IMPACTED THE LINE WITH ITS PROPELLER. SKIMMING EQUIPMENT WAS DEPLOYED TO MAINTAIN THE CONTAINMENT. AN ABSORBENT BOOM REMAINS IN PLACE TO PREVENT SPREAD OF THE RELEASE TO THE REMAINDER OF THE CATFISH LAKE AREA.
2017-09-29 08:50 | YES | NO | 20010110 | 2001-10-12 | 12452 | MID - AMERICA PIPELINE CO (MAPCO) | YES | 2001-09-07 | 1545 | OK | NOBLE |  | NO |  | NO | SW 1/4 SECTION 24-T 22N- R 1W, NOBLE CO. | 579165 | LINE PIPE | PIPE |  | 1976 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 220000 | 145436.2416 | 293403.6433 | ANHYDROUS AMMONIA | 2 | 77 | 0 | NO | NO | 6 | 0.141 | 46000 | WELDED |  | 1350 | 200 | YES | 24 | 1927 | 3 | 1977 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KENNETH L. LYBARGER | 9185748029 | FARMER PUNCTURED LINE WITH A DOZER. HE DID NOT CALL THE STATE ONE-CALL AGENCY. COMPANY PERSONNEL RESPONDED IMMEDIATELY. STOPPLES WERE SET TO ISOLATE THE LINE, NEW PRETESTED PIPE WAS INSTALLED, AND SERVICE RESTORED.
2017-09-29 08:50 | YES | NO | 20010111 | 2001-10-12 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2001-09-12 | 730 | TX | EL PASO |  | NO |  | NO | EQUILON PROPERTY, EL PASO TANK FARM. | 579526 | TANK FARM | TANK |  | 1958 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 66107.3826 | 133365.2924 | DIESEL FUEL | 2 | 450 | 376 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | TANK NO. 9, CONTAINING LOW SULFUR DIESEL, OVERFILLED DUE TO MECHANICAL FAILURE OF THE FLOAT SWITCH AND THE VAREC TANK GAUGE.
2017-09-29 08:50 | YES | NO | 20010112 | 2001-10-12 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2001-07-31 | 1630 | TX | JOHNSON |  | NO |  | NO | 46 MILES MILES NORTH OF CORICANA, TEXAS. | 574959 | LINE PIPE | PIPE |  | 1949 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 66107.3826 | 133365.2924 | DIESEL FUEL | 3 | 60 | 50 | NO | NO | 12 | 0.281 | 1850 | WELDED |  | 1102 | 65 | YES | 8 | 1378 | 0 | 1989 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | D.F. SHEAFF | 7132414381 | POWER COMPANYS CONTRACT POLE DRILLER PUNCTURED NORTH LEG OF ORIONS 12" PIPELINE. THE CONTRACTOR (J.W. BUCK, DOING WORK FOR BRAZOS ELECTRIC COOPERATIVE) IMMEDIATELY BUILT A BERM AND CONTAINED THE RELEASE IN A SMALL AREA. THE PIPELINE WAS IDLED AND IMMEDIATELY ISOLATED. THE PIPELINE WAS TEMPORARILY MARKED ON JUNE 29, 2001 INSTALLATION OF A POWER POLE. DURING THE POLE INSTALLATION, MANY OF THE TEMPORARY FLAGS WERE KNOCKED DOWN AND RUN OVER BY THE CONTRACTOR. THE LINE WAS HIT AT THE SAME TIME THE CONTRACTOR WAS EXCAVATING FOR A SECOND POLE, WHICH WAS NOT IN THE SCOPE OF THE 6/29 MARKING. NO SECOND ONE CALL WAS MADE.
2017-09-29 08:50 | NO | NO | 20010113 | 2001-10-19 | 31553 | ENBRIDGE ENERGY COMPANY INC | YES | 2001-05-02 | 800 | MN |  | DEER RIVER | NO |  | NO | STATION:DEER RIVER AT MILEPOST 0995.83 TOWNSHIP:56N, SECTION:22, QUARTER:NW 1/4 OF NW 1/4 RANGE: 27W, MERIDIAN: 4TH. |  | PUMPING STATION | BOLTED FITTING |  | 1980 | OTHER | LOOSE BLIND FLANGE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 57500 | 38011.745 | 76685.0431 | CRUDE OIL | 1 | 5 | 4 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | L.H. DEBRIYN | 2187250102 | AT APPROXIMATELY 0800 CST ON MAY 2, 2001, A COMPANY EMPLOYEE DISCOVERED OIL ON THE GROUND SURFACE OUTSIDE OF THE LINE 4 STATION 3 PUMPHOUSE. THE STATION WAS IMMEDIATELY SHUT DOWN AND THE OIL WAS CONTAINED IN THE IMMEDIATE AREA. THE PIPE LINE MAINTENANCE CREW WAS DISPATCHED TO THE STATION AND EXCAVATED THE PIPING IN THE AREA OF THE LEAK. IT WAS DISCOVERED THAT OIL WAS LEAKING FROM A BLIND FLANGE CONNECTION. THE FLANGE WAS TIGHTENED AND ALL CONTAMINATED SOIL WAS EXCAVATED AND HAULED TO AN APPROVED LAND FARM. THE STATION WAS THEN RESTARTED AND RETURNED TO NORMAL OPERATION. AFTER CONFIRMING THAT THE FLANGE WAS NO LONGER LEAKING, IT WAS RECOATED AND THE AREA WAS BACKFILLED WITH CLEAN SAND AND RESTORED TO PRE-EXCAVATION CONDITIONS. THE ORIGINAL ESTIMATE OF TOTAL PROPERTY DAMAGE WAS UNDER THE REPORTING THRESHOLD OF $50,000. AS NONE OF THE OTHER REPORTING CRITERIA WAS MET, SUBMISSION OF AN ACCIDENT REPORT AT THE TIME OF THE INCIDENT WAS NOT REQUIRED. WITH THE NEWLY REVISED ESTIMATED TOTAL PROPERTY DAMAGE NOW EXCEEDING THIS LIMIT, THE FILING OF AN ACCIDENT REPORT IS REQUIRED AT THIS TIME.
2017-09-29 08:50 | YES | NO | 20010114 | 2001-10-23 | 2552 | COLONIAL PIPELINE CO | YES | 1986-01-09 | 348 | MD | BALTIMORE | BALTIMORE | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1982 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 47315.1484 | 95453.7657 | FUEL OIL | 3 | 153 | 149 | Null | NO | 12.75 | 0.25 | 60000 | WELDED |  | 80 | 15 | YES | 24 | 100 | 10 | 1982 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J.S. SORROW, SR. | 4042611470 | A DELIVERY TO A SHIPPER WAS MADE ON 12/10/85 AND THE DELIVERY LINE WAS SECURED UPON COMPLETION OF THE TRANSACTION. SHORTLY AFTER INITIATING THE NEXT DELIVERY ON 01/09/86 A SHIPPER REPRESENTATIVE TELEPHONED TO ADVISE THAT FUEL OIL WAS BUBBLING OUT OF THE GROUND INSIDE HIS TERMINAL IN THE VICINITY OF THE DELIVERY LINE. UPON EXCAVATION IT WAS FOUND THAT THE SOURCE OF THE PRODUCT WAS THREE HOLES IN THE PIPE CAUSED BY A BACKHOE BUCKET. THE SHIPPER HAD INSTALLED A NEW DRIVEWAY TO HIS LOADING RACK AROUND DECEMBER 15, 1985, AND IN THE PROCESS OF EXCAVATING FOR THE FOUNDATION APPARENTLY DAMAGED THE PIPE AND BACKFILLED THE EXCAVATION WITHOUT NOTICE TO COLONIAL. MOST OF THE 153 BBLS. OF FUEL OIL LOST FROM THE DELIVERY LINE FLOWED INTO A STORM SEWER WHERE 149 BBLS. WERE RECOVERED AND RETURNED TO THE SYSTEM LEAVING A NET LOSS OF 4 BBLS. IMMEDIATE TELEPHONE NOTICE WAS MADE TO THE BALTIMORE FIRE DEPARTMENT, MARYLAND DEPARTMENT OF NATURAL RESOURCES, AND THE NATIONAL RESPONSE CENTER. THE FIRE DEPARTMENT, STATE OF MARYLAND, AND U.S. COAST GUARD RESPONDED TO THE SITE. REPAIR OF THE DAMAGED DELIVERY LINE REQUIRED REMOVAL OF 14 6" OF 12-3/4" DIA., 0.250" WT, X-60 PIPE AND REPLACEMENT WITH A LIKE AMOUNT OF PRE HYDROSTATICALLY TESTED PIPE. TIE-IN WELDS WERE X-RAYED.
2017-09-29 08:50 | YES | NO | 20010115 | 2001-10-23 | 26149 | ALYESKA PIPELINE SERVICE CO | YES | 2001-09-22 | 2221 | AK |  |  | NO |  | NO | PUMP STATION THREE MILEPOST 104.2 OF THE TRANS-ALASKA PIPELINE SYSTEM. LAT. 68 50 34 LONG. 148 49 47 |  | PUMPING STATION | PUMP |  | 1976 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 198322.1477 | 400095.8773 | CRUDE OIL | 1 | 5 | 5 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | WILLIAM D. HOWITT | 9074505417 | THE PUMP SEAL ON MAIN LINE UNIT #2 AT PUMP STATION 3 FAILED DURING STARTUP OF THE PIPELINE ON 22 SEPTEMBER 2001 AFTER A PLANNED MAINTENANCE SHUTDOWN. AS A RESULT OF THE SEAL FAILURE 25 EACH 200 POUND BOTTLES OF HALON WERE DUMPED IN THE PUMP ROOM. COST ESTIMATE OF $300,000.00 IS BASED ON 5,000 POUNDS OF HALON AT $25.00 PER POUND PLUS LABOR AND MATERIALS FOR CLEANUP.
2017-09-29 08:50 | YES | NO | 20010116 | 2001-10-23 | 26149 | ALYESKA PIPELINE SERVICE CO | YES | 2001-09-22 | 1733 | AK |  |  | NO |  | YES | PUMP STATION FIVE MILEPOST 274.5 OF THE TRANS-ALASKA PIPELINE SYSTEM. LAT.66 48 51 LONG. 150 38 31. |  | PUMPING STATION | OTHER | RELIEF HEADER | 1976 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 66107.3826 | 133365.2924 | CRUDE OIL | 1 | 49 | 44 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | WILLIAM D. HOWITT | 9074505417 | OIL SPILLED FROM A 12 INCH OPEN PIPE APPENDAGE OF THE 24 INCH RELIEF INLET HEADER DURING REFILL OF THE PS05 MAINLINE PIPING FOLLOWING A SCHEDULED SHUTDOWN AND ASSOCIATED MAINTENANCE WORK. WHEN THE STATION WAS REPRESSURIZED, THE PICV504A RELIEF VALVE OPENED ON RATE-OF-PRESSURE-RISE ALLOWING CRUDE OIL TO BACKFLOW FROM BREAKOUT TANK TK150 THROUGH THE RELIEF INLET HEADER AND OUT OF THE 12 INCH OPEN PIPE APPENDAGE, ONTO THE FLOOR OF THE RELIEF BAY.
2017-09-29 08:50 | YES | NO | 20010117 | 2001-11-08 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2001-10-20 | 1000 |  |  |  | NO | LAT.28^15'34.34", LONG.91 | NO | APPROX. 1 MILE NORTH-NORTHWEST OF AVIARA'S PLATFROM A IN SOUTH MARSH ISLAND BLOCK 142. |  | LINE PIPE | BOLTED FITTING |  | 1977 | OTHER | FAILED FLANGE GASKET | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 132214.7651 | 266730.5849 | CRUDE OIL | 1 | 0 | 0 | NO | NO | 8 | 0.5 | 35000 | FLANGED |  | 1440 | 1000 | YES | 8 | 3650 | 0 | 1977 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | TAD A. SCHELL | 4194213201 | THE PRODUCTION PLATFORM OPERATOR, AVIRA, OBSERVED INTERMITTENT SMALL SHEENS APPEARING AT THE SURFACE OF THE WATER. AVIARA SUSPECTED IT MIGHT BE THEIR LINE SINCE SHEEN SEEMED TO COINCIDE WITH STARTING UP/SHUTTING DOWN LINE. AVIARA MOBILIZED A DIVE BOAT TO INVESTIGATE AND ULTIMATELY FOUND THAT THE SEEP WAS FROM A SET OF FLANGES ON THE SUBSEA VALVE ASSEMBLY ON THE MAPL VERMILION 8" LINE (SUB-SEA TIE-IN WITH AVIARA). CAUSE WAS FOUND TO BE A FAULTY GASKET WHICH HAS BEEN REPLACED.
2017-09-29 08:50 | NO | NO | 20010118 | 2001-11-21 | 15674 | PLANTATION PIPE LINE CO | YES | 2001-11-02 | 1111 | LA | ZACHARY | EAST BATON ROUGE | NO |  | NO | SEE ATTACHED MAP |  | LINE PIPE | PIPE |  | 1951 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 49580.5369 | 100023.9693 | GASOLINE | 2 | 0 | 0 | NO | NO | 18 | 0.375 | 35000 | WELDED |  | 1050 | 670 | NO | 0 | 0 | 0 | 1995 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A. FANT | 7133699454 | ON 11/2/01, A PROPERTY OWNER CALLED OPERATIONS CONTROL CENTER (OCC) TO REPORT A STAIN AND A PETROLEUM ODOR ON THE RIGHT OF WAY. PIPELINES WERE IMMEDIATELY SHUT DOWN BY OCC AT 11:11 CST. WHEN PLANTATION PERSONNEL ARRIVED ON SITE, APPROXIMATELY 11:50 CST, THEY CONFIRMED THAT THEIR WAS AN INDICATION OF A RELEASE AND CALLED A HAZWOPER TRAINED CONTRACTOR, DON MILLER AND ASSOCIATES (DMA) TO INVESTIGATE FURTHER. DMA RESPONDED WITH PERSONNEL AND EQUIPMENT TO EXPOSE THE PIPELINE. AFTER EXCAVATING THE AREA OF THE STAIN, THE SOURCE OF THE RELEASE WAS FOUND TO BE A MILL DEFECT IN THE MDG PIPELINE. LOOKING DOWNSTREAM, THE DEFECT WAS LOCATED BETWEEN THE 8:00 AND 9:00 OCLOCK POSITION. THE DEFECT APPEARED TO BE APPROXIMATELY 3" IN LENGTH ON THE PIPELINE. THE DEFECT WAS COVERED AND CLAMPED WITH A THREE FOOT LONG FULL ENCIRCLEMENT SPLIT SLEEVE. THE SLEEVE WAS WELDED LONGITUDINALLY AND ON BOTH ENDS TO CREATE A PRESSURE VESSEL TYPE "B" SLEEVE. REFERENCE PART G (3): ESTIMATED QUANTITIES OF PRODUCT SPILLED AND RECOVERED IS UNDETERMINED AT THIS TIME DUE TO ONGOING REMEDIATION. THE SITE WILL BE REMEDIATED IN ACCORDANCE WITH ALL APPLICABLE REGULATIONS. AN UPDATED DOT 7000-1 WILL BE SUBMITTED UPON DETERMINATION OF ESTIMATED AMOUNT OF COMMODITY SPILLED AND RECOVERED.
2017-09-29 08:50 | YES | NO | 20010119 | 2001-12-05 | 30871 | MID - VALLEY PIPELINE COMPANY | YES | 2001-11-16 | 1305 | OH | ALLEN | LIMA | NO |  | NO | 985 WEST BUCKEYE ROAD LIMA, OHIO. | 586443 | TANK FARM | OTHER | TANK MIXER | 1985 | OTHER | FAILURE OF A TANK MIXER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25000 | 16526.8456 | 33341.3231 | CRUDE OIL | 3 | 118 | 115 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDITH F. COEN | 9185866942 | ON NOVEMBER 16TH, 2001 AT 1:05 PM THE STATION TERMINAL OPERATOR DISCOVERED OIL IN THE FIREWALL OF TANK #82. UPON FURTHER INVESTIGATION, THE TERMINAL OPERATOR DETERMINED THAT THE OIL WAS COMING FROM THE JENSEN TANK MIXER ON THE EAST SIDE OF THE TANK. COMPANY AND RESPONSE PERSONNEL WERE CALLED AND THE CLEAN-UP WAS INITIATED. THE OIL WAS ESCAPING FROM THE GEAR BOX ASSEMBLY. THE TANK WAS PUMPED DOWN BELOW THE MIXER AND ISOLATED. THE MIXER WAS REMOVED AND A BLIND FLANGE WAS INSTALLED IN ITS PLACE. A REPRESENTATIVE FOR THE MANUFACTURER OF THE MIXER (JENSEN) WILL BE ONSITE TO INSPECT THE MIXER TO HELP DETERMINE THE CAUSE OF THE FAILURE.
2017-09-29 08:50 | YES | NO | 20010120 | 2001-12-03 | 26149 | ALYESKA PIPELINE SERVICE CO | YES | 2001-10-04 | 1430 | AK |  |  | NO |  | NO | MILEPOST 400.975 OF THE TRANS-ALASKA PIPELINE SYSTEM. LAT. 65 26 30 LONG. 148 35 22. | 582013 | LINE PIPE | PIPE |  | 1975 | OTHER | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 3000000 | 1983221.4765 | 4000958.7728 | CRUDE OIL | 1 | 6800 | 3909 | NO | NO | 48 | 0.462 | 65000 | WELDED |  | 901 | 500 | YES | 24 | 1188 | 0 | 1977 |  | Null | Null |  |  | OTHER | VANDALISM | Null | OTHER |  | Null | Null | BILL HOWITT | 9074505417 | SECURITY PERSONNEL IN A SURVEILLANCE HELICOPTER NOTIFIED OPERATIONS AT PUMP STATION 7 ABOUT 1455 HR ON THRUSDAY 4 OCTOBER 2001 THAT A BULLET HAD PIERCED THE TRANS-ALASKA PIPELINE (TAPS) NEAR MILEPOST 400, NORTH OF PUMP STATION 7, AND OIL WAS SPURTING OUT. THE PIPELINE NORTH OF PUMP STATION 6 WAS QUICKLY SHUT DOWN BY THE OPERATIONS CONTROL CENTER (OCC) IN VALDEZ. THE SOUTH END OF THE PIPELINE REMAINED FOR A TIME IN OPERATION SO THE PIPE IN THE REGION OF THE SPILL COULD BE PUMPED DOWN TO THE EXTENT POSSIBLE TO MINIMIZE THE POTENTIAL SPILL VOLUME. RESPONSE CREWS WERE IMMEDIATELY MOBILIZED BUT WERE KEPT AWAY FROM THE SPILL AREA BY LAW ENFORCEMENT UNTIL THE SUSPECT WAS CAPTURED AND THE ALASKA STATE TROOPERS DEEMED THE AREA SAFE FOR ENTRY. CREWS FROM PUMP STATION 7 AND FAIRBANKS THEN TOOK AGGRESSIVE ACTION TO LOCATE AND BLOCK THE LEADING EDGE OF THE SPILL. BY 0130 HR 5 OCTOBER, FRIDAY THEY HAD STOPPED THE ADVANCE OF THE OIL FRONT. A NUMBER OF DEVELOPMENTS HAD TO COME TOGETHER BEFORE A CLAMP COULD BE PLACED ON THE PUNCTURE, INCLUDING LOWERING THE PIPELINE PRESSURE AT THE LEAK, ASSEMBLY THE RIGHT PEOPLE AND ENSURING A SAFE WORKING ENVIRONMENT FOR PEOPLE DOING THE WORK. ONCE THIS WAS ACHIEVED, A HYDRAULICALLY ACTIVATED PIPE CLAMP, SPECIALLY CONSTRUCTED IN 1997 FOR TAPS INCIDENTS SUCH AS THIS, WAS PLACED ON THE PIPE AND AT ABOUT 0300 HR SATURDAY AND THE LEAK WAS STOPPED. A PERMANENT REPAIR WAS COMPLETED EARLY SUNDAY MORNING 7 OCTOBER 2001, WITH THE INSTALLATION OF A T.D. WILLIAMSON INC. THREAD-O-RING (TOR) FITTING (THE SAME KIND OF FITTING USED FOR A NUMBER OF APPLICATIONS ON TAPS). THE PIPELINE WAS RESTARTED AT 0324 HR SUNDAY MORNING.
2017-09-29 08:50 | YES | NO | 20010121 | 2001-12-06 | 26301 | BP NORTH AMERICA INC | YES | 2001-11-05 | 1630 | TX | WOOD |  | NO |  | NO | FROM THE CITY OF HAINSVILLE IN WOOD COUNTY, WEST ON FM 49 FOR 2 MILES, THEN NORTH ON COUNTY ROAD 2590 APPROXIMATELY 2 MILES, THEN WEST ON THE PROPERTY ACCESS RO |  | LINE PIPE | PIPE |  | 1946 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33053.6913 | 66682.6462 | CRUDE OIL | 1 | 250 | 225 | NO | NO | 6.625 | 0.333 | 25000 | WELDED |  | 740 | 45 | YES | 8 | 925 | 0 | 1990 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | RANDY A WILSON | 9156879914 | SPILL OCCURRED AT A TIME WHEN THE PIPELINE WAS NOT BEING PUMPED. THE COATING AT THIS LOCATION HAD BECOME DISBONDED ALLOWING WATER UNDER THE COATING AND REDUCING THE EFFECTIVENESS OF THE CP. A SMALL CORROSION PIT ALLOWED OIL TO ESCAPE FROM THE PIPELINE IMPACTING A SHORT STRETCH OF DRY CREEKBED AND A STOCK POND.
2017-09-29 08:50 | NO | NO | 20010122 | 2001-12-14 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 2001-11-18 | 2135 | NJ |  | NEWARK | NO |  | NO | AT SUNOCO TERMINAL ON DOREMUS AVENUE (SEE ATTACHED MAP |  | TANK FARM | BOLTED FITTING |  | 1973 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33053.6913 | 66682.6462 | GASOLINE | 1 | 48 | 40 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | DAVID B MEADOWS | 6109421924 | ON NOVEMBER 18, 2001, THE 14-INCH TWIN OAKS TO NEWARK LINE WAS DELIVERING 87 RF INTO NEWARK MOTIVA, APPROXIMATELY 1/2 MILE FROM THE END-OF-LINE DELIVERY FACILITY AT NEWARK SUNOCO. AT THE END OF THIS DELIVERY, THE FLOW WAS TO BE SWITCHED TO NEWARK SUNOCO. AT 2107 HOURS, PIPELINE CONTROL CENTER SETUP NEWARK SUNOCO FOR DELIVERY FROM THE 14-INCH LINE. AT 2134 HOURS A COMMAND WAS SENT TO SHUTDOWN THE DELIVERY AT NEWARK MOTIVA. FLOW INTO NEWARK SUNOCO ESTABLISHED. AT 2136 HOURS, A HIGH-PRESSURE METER MANIFOLD ALARM FOR NEWARK SUNOCO WAS RECEIVED IN THE PIPELINE CONTROL CENTER. THE SURGE RELIEF VALVE ACTIVATED AND BLED PRODUCT INTO THE TANK NUMBER 26, THE DESIGNATED SURGE RELIEF TANK. THERE WAS AN AUTOMATIC FACILITY LOCKOUT AND THE PIPELINE SHUT DOWN. A PIPELINE MECHANCIAL TECHINCIAN WAS DISPATCHED TO RESPOND TO INVESTIGATE THE CAUSE OF THE HIGH-PRESSURE METER MANIFOLD ALARM. UPON ARRIVAL AT THE TERMINAL, THE PIPELINE TECHNICIAN FOUND GASOLINE SPRAYING FROM THE FLANGE ON THE DOWNSTREAM SIDE OF THE SURGE RELIEF VALVE. THE SURGE RELIEF LINE HAD MOVED OFF THE SUPPORTS AND WAS SAGGING, APPARENTLY DUE TO HYDRAULIC HAMMER. THE WEIGHT OF THE SAGGING LINE APPARENTLY CAUSED THE FLANGE TO SPREAD SLIGHTLY ALLOWING PRODUCT TO LEAK OUT. THE PIPELINE TECHNICIAN ISOLATED THE LEAKING FLANGE AND NOTIFIED THE AREA MAINTENANCE SUPERVISOR PIPELINE MAINTENANCE CREWS AND CLEAN VENTURES (OSRO) WERE DISPATCHED TO THE SITE TO BEGIN CLEANUP. TERMINAL PERSONNEL NOTIFIED THE NEWARK FIRE DEPARTMENT, THE NEW JERSEY DEP, AND NRC. THE NEXT MORNING, USDOT/OPS-TRENTON OFFICE WAS NOTIFIED BY TELEPHONE. AN ESTIMATED 2,000 GALLONS OF 87RF GASOLINE WAS RELEASED FROM THE FLANGE SPILLLING ONTO THE GROUND AROUND THE MANIFOLD WITH A SMALL QUANTITY ENTERING THE PASSAIC RIVER. INVESTIGATION INTO THE INCIDENT SHOWS THAT THE DELIVERY CONTROL VALVE AT NEWARK SUNOCO HAD LOST ITS SET-POINT CONTROL LOOP DURING A POWER FAILURE THE NIGHT BEFORE DURING AN AREA-WIDE POWER OUTAGE. AT THE TIME THE TERMINAL SWITCH WAS TO ME MADE, INFORMATION RECEIVED AT THE CONTROL CENTER INDICATED THAT THERE WAS AN OPEN PATH INTO THE NORMAL DELIVERY TANK. WHEN DELIVERY WAS STARTED, INSTEAD OF RAMPING OPEN, THE CONTROL VALVE RAMPED CLOSED, BLOCKING IN THE LINE. WITHOUT A VALUE FOR THE PLC SET-POINT CONTROL LOOP IN THE PROGRAM, THE SET-POINT CONTROL LOOP WENT TO A DEFAULT VALUE WHEN POWER WAS RESTORED TO THE FACILITY. THIS PROGRAM HAS BEEN CORRECTED TO INSURE CORRECT OPERATION OF THE CONTROL VALVE AT ALL TIMES, EVEN AFTER A POWER FAILURE. AN ENGINEERING REVIEW OF THE RELIEF VALVE-PIPING CONFIGURATION IS UNDERWAY TO DETERMINE IF ANY MODIFICATIONS ARE NEEDED.
2017-09-29 08:50 | YES | NO | 20010123 | 2001-12-13 | 31058 | MARATHON ASHLAND PIPE LINE LLC | YES | 2001-11-19 | 1520 |  |  |  | YES | LAT 28 DEG 11'55.09" LONG | NO | EAST CAMERON 322 A PLATFORM - ON THE OIL EXPORT RISER |  | LINE PIPE | PIPE |  | 1974 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 417000 | 275667.7852 | 556133.2694 | CRUDE OIL | 1 | 1 | 0 | NO | NO | 8.625 | 0.594 | 35000 | WELDED |  | 2100 | 1206 | YES | 24 | 3657 | 8 | 1974 | EXTERNAL | Null | YES | OTHER | ATMOSPHERIC |  |  | Null |  |  | Null | Null | TAD A SCHELL | 4194213201 | A PIONEER PLATFORM OPERATOR OBSERVED A SHEEN ON THE WATER AT THE EAST CAMERON 3221 PLATFORM. PIONEER NOTIFIED MARATHON ASHLAND PIPE LINE LLC THAT THERE WAS A LEAK AT THE RISER AREA AT THE J-TUBE ENTRY POINT OF THE MARATHON PIPE LINE EAST CAMERON 8" CRUDE OIL EXPORT PIPELINE. THE CAUSE WAS FOUND TO BE EXTERNAL CORROSION ON THE PIPE WHICH HAS BEEN REPAIRED. NOTE THAT ENVIRONMENTAL DAMAGE WAS NEGLIGBLE. THE PROPERTY DAMAGE ESTIMATE OF $417,000 INCLUDES THE COST OF MOBILIZING A WORK BOAT TO THE OFFSHORE LOCATION.
2017-09-29 08:50 | YES | NO | 20010124 | 2001-12-17 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2001-10-23 | 1545 | CA | CONTRA COSTA |  | NO |  | NO | 600 FEET SOUTH OF AVON PUMP STATION, CONCORD CALIFORNIA | 584119 | LINE PIPE | WELDING FITTING |  | 1981 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 66107.3826 | 133365.2924 | CRUDE OIL | 1 | 420 | 420 | NO | NO | 20 | 0.25 | 52000 | THREADED |  | 936 | 300 | Null | 4 | 1176 | 11 | 1989 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D F SHEAFF | 7132414381 | DURING EXCAVATION OF THE LINE WITH A BACKHOE, CONTRACTOR HIT A BURIED HALF-INCH VALVE AND NIPPLE.
2017-09-29 08:50 | NO | NO | 20010125 | 2001-12-19 | 4805 | EXPLORER PIPELINE CO | YES | 2001-08-20 | 400 | TX | JEFFERSON | PORT ARTHUR | NO |  | NO | EXPLORER PIPELINE COMPANY PORT ARTHUR STATION 6300 WEST PORT ARTHUR ROAD, PORT ARTHUR, TEXAS |  | TANK FARM | PIPE |  | 1971 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 66000 | 43630.8725 | 88021.093 | JET FUEL | 1 | 35 | 32 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | ROGER W FLEMING | 9184935112 | ON AUGUST 20, 2001, AT 0400 THE PORT ARTHUR OPERATIONS TECHNICIAN WAS MAKING A WALK-AROUND CHECK OF THE FACILITIES WHEN HE DISCOVERED JET FUEL SEEPING FROM THE GROUND NEAR #3 MAINLINE PUMP UNIT. THE UNIT WAS SHUT DOWN AND ISOLATED. VACUUM TRUCKS AND MAINTENANCE CONTRACTORS WERE DISPATCHED TO THE SITE. THE AREA WAS EXCAVATED AND SOURCE OF THE RELEASE WAS DETERMINED TO BE AN INTERNAL CORROSION PIN-HOLE IN THE 2" DIAMETER UNDERGROUND PIPE USED TO REFILL THE PUMP UNIT FOLLOWING MAINTENANCE WORK. THIS IS AN INFREQUENTLY USED FILL LINE THAT INTERNALLY CORRODED AS A RESULT OF STATIC WATER ACCUMULATION IN THE LINE. A TEMPORARY LEAK CLAMP WAS INSTALLED WITH REPLACEMENT TO FOLLOW. CONTAMINATED SOIL WAS REMOVED, TEMPORARILY PLACED IN ROLL-OFF CONTAINMENT BOXES, AND SOIL SAMPLES COLLECTED FOR ANALYSIS TO DETERMINE THE APPROPRIATE REMEDIATION METHOD. AT THE TIME OF THE INCIDENT IT WAS DETERMINED THAT NONE OF THE REQUIREMENTS OUTLINED IN CFR 49 PART 195.50 OR 195.52 REQUIRING WRITING OR TELEPHONIC REPORTING WERE MET, SO A REPORT WAS NOT SUBMITTED. ANALYSIS OF THE CONTAMINATED SOIL INDICATES THE APPROPRIATE METHOD OF TREATMENT IS INCINERATION AT AN ESTIMATED COST OF $49,000. AS A RESULT OF THIS REMEDIATION EXPENSE, THE TOTAL COST OF THE INCIDENT IS NOW ESTIMATED TO BE $66,000. THEREFORE, A 7000-1 ACCIDENT REPORT IS BEING SUBMITTED AT THIS TIME DUE TO PROPERTY DAMAGE EXCEEDING $50,000.
2017-09-29 08:50 | YES | NO | 20010126 | 2003-12-03 | 22610 | WILLIAMS PIPE LINE COMPANY | Null | 2001-02-20 | 1533 | KS | ALLEN COUNTY |  | NO |  | NO | SW | 557343 | LINE PIPE | PIPE |  | 0 | FAILED PIPE |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 33053.6913 | 66682.6462 | FUEL OIL | 3 | 170 | 0 | NO | NO | 12.75 | 0.312 | 42000 | WELDED |  | 1172 | 1087 | YES | 8 | 1902 | 6 | 1994 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JOHNNY CAVITT | 9185748412
2017-09-29 08:50 | YES | NO | 20020001 | 2002-01-04 | 1845 | BUCKEYE PIPELINE CO LP | YES | 2001-11-08 | 805 | MA | HAMPDEN |  | NO |  | NO | SEE ATTACHED DRAWING NUMBER 11901-A | 585446 | LINE PIPE | PIPE |  | 1961 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 215000 | 142130.8725 | 286735.3787 | FUEL OIL | 3 | 47 | 29 | NO | NO | 12 | 0.219 | 1790 | WELDED |  | 720 | 55 | YES | 24 | 1101 | 10 | 1993 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | CARL A OSTACH | 4842324495 | ON THURSDAY, NOVEMBER 8, 2001, A THIRD PARTY CONTRACTOR PUNCTURED BUCKEYE PIPE LINE COMPANYS PIPELINE WHILE PERFORMING EXCAVATION ACTIVITY. AFTER RECEIVING A ONE-CALL NOTIFICATION A BUCKEYE PIPELINE COMPANY EMPLOYEE LOCATED THE PIPELINE AND PLACED TEMPORARY MARKINGS AT THE EXCAVATION SITE. SUBSEQUENTLY, THE THIRD-PARTY CONTRACTOR SUPERVISOR AND BUCKEYE PIPE LINE COMPANY ESTABLISHED A MEETING TIME OF 0900 ON NOVEMBER 8, 2001, AND THE THIRD-PARTY CONTRACTOR WAS ADVISED NOT TO PERFORM ANY EXCAVATION WORK IN THE VICINITY OF THE PIPELINE UNTIL A BUCKEYE PIPE LINE COMPANY EMPLOYEE WAS ON SITE. HOWEVER, THE THIRD-PARTY CONTRACTORS TRACK HOE OPERATOR STARTED EXCAVATION ACTIVITIES PRIOR TO THE 0900 MEETING AND WITHOUT A BUCKEYE PIPELINE COMPANY EMPLOYEE ON-SITE. TEMPORARY MARKERS AND A PERMANENT CASING VENT WITH MARKER WERE CLEARLY VISIBLE AT THE EXCAVATION SITE. THE THIRD-PARTY CONTRACTOR HAS ACCEPTED FULL RESPONSIBILTY FOR THIS INCIDENT. ALL APPLICABLE REGULATORY AGENCIES WERE NOTIFIED. RECOVERY AND CLEANUP ACTIVITIES WERE PERFORMED UNDER THE SUPERVISION OF THE MASSACHUSETTS DEPARTMENT OF ENVIRONMENTAL PROTECTION.
2017-09-29 08:50 | YES | NO | 20020002 | 2002-01-04 | 31170 | CHEVRON PIPE LINE NORTHWEST REGION | YES | 2001-11-12 | 1115 | TX | SCURRY |  | NO |  | NO | 10" SYNDER TO WINK PIPELINE AT MP 150.9 (EL PASO CRUDE SYSTEM) APPROX 8 MILES WEST OF SYNDER, TX NEAR HWY 208 BLK 97, SEC. 393 H&TCRR |  | LINE PIPE | PIPE |  | 0 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 13221.4765 | 26673.0585 | CRUDE OIL | 1 | 1262 | 986 | NO | NO | 10 | 0.25 | 42000 | WELDED |  | 1200 | 460 | YES | 8 | 1606 | 0 | 1980 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | J RANDY BURKE | 2815963569 | GRIMMETT BROS CONSTRUCTION, A THIRD PARTY CONTRACTOR, WAS CONTRACTED BY KINDER-MORGAN TO CLEAN OUT A CREEK ON MR. ELDON BECKS PROPERTY, WHERE APPROXIMATELY ONE YEAR EARLIER A SALTWATER LEAK HAD OCCURRED. MR. BECK, LANDOWNER, TOLD RAY M GRIMMETT THAT THE PIPELINE WAS 20 SOUTH OF ITS ACTUAL LOCATION, ALSO STATING HE WAS PRESENT WHEN LINE WAS LAID & DEFINITELY KNEW WHERE IT WAS. HE GAVE MR. GRIMMETT THE OKAY TO DIG WHERE THE SPRING WAS LOCATED. AS IT TURNED OUT, CHEVRONS 10" SYNDER TO WINK TRUNK LINE WAS ADJACENT TO THE ROAD, AND NOT DIRECTLY UNDER IT AS IT WAS ASSUMED. THE TRACKHOE RUPTURED THE LINE. CHEVRON PIPE LINES CONTROL CENTER IN HOUSTON, TX REGISTERED A PRESSURE DROP ON THIS LINE FROM 460 TO 60 PSI. CHEVRON PIPE LINES ROSCOE FIELD TEAM & OTHER PERSONNEL HANDLED THE AGENCY NOTIFICATIONS & INITIAL RESPONSE. APPROXIMATELY 1,262 BARRELS OF CRUDE OIL WAS RELEASED TO LAND, BUT MOST OF THE OIL SETTLED NEARBY IN A SPRING-FED CREEK BED USED AS A STOCK TANK TO WATER CATTLE. KINDER-MORGAN ASSUMED RESPONSIBILITY FOR THE CLEANUP AND REIMBURSEMENT OF ANY CHEVRON COSTS. AGENCY NOTIFICATIONS: NATIONAL RESPONSE CENTER - 11/12/01 @ 11:40 (REPORT #001-968-653) OTHER TIMELY AGENCY NOTIFICATIONS WERE MADE TO THE DEPT OF TRANSPORTATION ENVIRONMENTAL PROTECTION AGENCY, AND THE TEXAS RAILROAD COMMISSION.
2017-09-29 08:50 | YES | NO | 20020003 | 2002-01-04 | 26301 | BP NORTH AMERICA INC | YES | 2001-06-16 | 630 | IL | WILL | UNIVERSITY PARK | NO |  | NO | ILLINOIS, WILL COUNTY, UNIVERSITY PARK, NEAR WILTON CENTER ROAD | 569761 | LINE PIPE | PIPE |  | 2001 | FAILED PIPE | OTHER | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 23137.5839 | 46677.8523 | CRUDE OIL | 1 | 75 | 75 | NO | NO | 26 | 0.375 | 42000 | OTHER |  | 1025 | 403 | YES | 4 | 1800 | 0 | 1986 |  | Null | Null |  |  | OTHER | INTERNAL INSPECTION TOOL GEAR | Null | ONE CALL |  | Null | Null | JEFF AYERSMAN | 8154786101 | LEAK OCCURRED AT A PIPELINE IN-LINE SCRAPER TRAP LAUNCHER/RECEIVER SPOOL PIECE. A PIPELINE INSPECTION TOOL (GEOMETRY TOOL) WAS IN THE RECEIVER SPOOL AT THE TIME THE LEAK WAS DETECTED. IT APPEARS THAT THE GAUGING WHEELS ON THE INSPECTION TOOL WHERE ROTATING IN PLACE DUE TO THE FLOW IN THE LINE. THESE ROTATING WHEELS MAY HAVE ACTED SIMILAR TO A "GRINDER WHEEL", WHICH ACTIVELY REMOVED METAL FROM THE INSIDE OF THE PIPELINE TO THE POINT OF FULL WALL LOSS.
2017-09-29 08:50 | YES | NO | 20020004 | 2002-01-07 | 19223 | SUN PIPELINE CORP - GENERAL WASH BLDG | YES | 2001-12-14 | 1000 | MI | MACOMB | WASHINGTON | NO |  | NO | 26 MILE ROAD, EAST OF JEWELL ROAD | 588682 | LINE PIPE | PIPE |  | 1950 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 165268.4564 | 333413.2311 | BUTANE | 2 | 174 | 25 | NO | NO | 8.625 | 0.25 | 30000 | WELDED |  | 1200 | 330 | YES | 24 | 1500 | 10 | 1958 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | YES | YES | DAVID B MEADOWS | 6109421924 | KALTZ EXCAVATING COMPANY, INC WAS PERFORMING A TEST DIG ON THE SPL 8-INCH INKSTER- SARNIA PIPELINE ALONG 26 MILE ROAD. THIS WAS BEING DONE TO DETERMINE THE DEPTH OF THE PIPELINE PRIOR TO INSTALLING AND UNDERGROUND ELECTRIC LINE ACROSS THE ROAD BY HORIZONTAL DRILLING. A SUN PIPE LINE COMPANY EMPLOYEE WAS ON-SITE WORKING WITH THE CONTRACTOR. AFTER REMOVING THE HIGHWAY ASPHALT AND SUB-BASE MATERIAL TO EXCAVATE A TEST HOLE, ANOTHER LAYER OF CONCRETE WAS ENCOUNTERED. IN THE PROCESS OF REMOVING THIS ADDITIONAL CONCRETE LAYER, MECHNICAL EQUIPMENT BEING USED BY THE CONTRACTOR TO REMOVE THE CONCRETE STRUCK THE PIPELINE DAMAGING IT AND RESULTING IN A LEAK OF PRODUCT FROM THE LINE. AT THE TIME OF THE ACCIDENT, THE LINE WAS NOT OPERATING AND HAD APPROXIMATELY 330 PSIG RESIDUAL PRESSURE. OPERATIONALLY, PRESSURE AND PRODUCT WERE PULLED AWAY FROM THE LEAK LOCATION BY PUMPING THE LINE FROM BOTH UPSTREAM AND DOWNSTREAM DIRECTIONS. ALL VEHICLES AND EQUIPMENT WERE SHUT DOWN, THE ROAD WAS BLOCKED OFF, LOCAL FIRE AND SHERIFFS DEPARTMENTS WERE CALLED TO THE SCENE. SUN PIPE LINE PERSONNEL AND A SPILL RESPONSE CONTRACTOR RESPONDED TO THE SCENE. APPROXIMATELY 20 RESIDENTS WERE EVACUATED. A TELEPHONE REPORT WAS MADE TO NATIONAL RESPONSE CENTER AT 10:40 HOURS. THE USDOT OFFICE OF PIPELINE SAFETY WERE ON-SCENE TO INVESTIGATE.
2017-09-29 08:50 | YES | NO | 20020005 | 2002-01-08 | 15156 | SINCLAIR PIPELINE CO | YES | 2001-11-03 | 1253 | MO | CHARITON | MENDON | NO |  | NO | SOUTH OF MENDON, MO ON HWY 11 TO BLACKTOP "BB". GO WEST ON BB 2.5 MILES TO END OF PAVEMENT. LEAK SITE STRAIGHT WEST APPROXIMATELY 1,000 FEET IN FIELD ALONG BNS | 585052 | LINE PIPE | PIPE |  | 1929 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 132214.7651 | 266730.5849 | GASOLINE | 3 | 1050 | 597 | NO | NO | 8.625 | 0.322 | 0 | WELDED |  | 490 | 150 | YES | 8 | 739 | 10 | 1999 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | RANDALL D DANIELSON | 6605420206 | AT APPROXIMATELY 12:53 PM ON 11/3/01 A FARMER WAS CLEARING THE ENDS OF DRAINAGE DITCHES THROUGH HIS FIELD WITH A DOZER AND PENETRATED OUR PIPELINE WITH THE BLADE ATTACHED TO HIS DOZER. THE PIPELINE IMMEDIATELY RUPTURED CAUSING UNLEADED GASOLINE TO ESCAPE FROM THE PIPELINE AND RUN INTO A NEARBY DRAINAGE DITCH THAT PARALLELS THE BURLINGTON NORTHERN SANTA FE RAILROAD TRACKS. PRODUCT FROM THE PIPELINE ALSO RAN TO THE SOUTH AWAY FROM THE RR TRACKS INTO THE FIELD DRAINAGE DITCH THE FARMER HAD BEEN EXCAVATING. THE FARMER PLACED AN EARTHEN DAM APPROXIMATELY A QUARTER MILE NORTHEAST OF THE SPILL SITE TO PREVENT THE GASOLINE FROM FLOWING ANY FURTHER IN THAT DIRECTION. HE THEN CALLED OUR CONTROL CENTER USING THE PHONE NUMBER FROM SINCLAIRS PIPELINE WARNING SIGN INSTALLED AT A ROAD CROSSING NEAR THE LEAK SITE. OUR CONTROL CENTER RECORDED ALL INFORMATION OBTAINED FROM THE FARMER AND DISPATCHED PERSONNEL TO THE SPILL SITE AND TO NEARBY BLOCK VALVES TO ISOLATE THE LOCATION OF THE SPILL. A SECOND EARTHEN DAM WAS INSTALLED SOUTHWEST OF THE SPILL SITE IN THE RR DRAINAGE DITCH. THE PIPELINE WAS ALLOWED TO DRAIN UP AND A NEW PIPE WAS INSTALLED. CLEANUP OPERATONS BEGAN SOON AFTER SINCLAIR AND CONTRACT PERSONNEL WERE ON SITE. ALL OF THE FREE LIQUIDS IN THE RR DRAINAGE DITCH WERE REMOVED WITH VACUUM AND TRANSPORT TRUCKS AND HAULED TO SINCLAIR PIPELINE COMPANY TANKAGE NEAR CARROLLTON, MO. THE SOIL IN THE BOTTOM OF THE DRAINAGE DITCH WAS EXCAVATED AND PLACED ON A PLASTIC LINER AND COVERED WITH PLASTIC. AFTER DIGGING EXPLORATORY PITS IN THE VICINITY OF THE FIELD DRAINAGE DITCH A PLASTIC PERFORATED PIPE WAS INSTALLED TO GATHER ANY GASOLINE THAT REACHED THE WATER TABLE. THIS RECOVERY OPERATION IS CONTINUING AT THE TIME OF THIS REPORT. THE FARMER HAD NOT CONTACTED THE PIPELINE OPERATOR OR THE ONE CALL SERVICE PRIOR TO THIS EXCAVATION NEAR OUR PIPELINE AND NO TEMPORARY PIPELINE MARKINGS WERE INSTALLED IN THE AREA OF THE EXCAVATION. THIS INCIDENT COULD HAVE BEEN AVOIDED IF THE EXCAVATOR HAD FOLLOWED PROPER NOTIFICATION PROCEDURES PRIOR TO THE EXCAVATION. THE FARMER INVOLVED WITH THIS INCIDENT ALSO SERVES AS THE MAYOR OF MENDON, MISSOURI AND HAD BEEN CONTACTED BY OUR OFFICE AS PART OF OUR PUBLIC EDUCATION PROGRAM.
2017-09-29 08:50 | YES | NO | 20020006 | 2002-01-10 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2001-11-02 | 1740 | CA | KERN |  | NO |  | NO | MC KITTRICK, CA |  | OTHER | OTHER | HIGH PRESSURE LINE TO TRUCK | 0 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 39664.4295 | 80019.1755 | CRUDE OIL | 1 | 100 | 70 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | DAVID F SHEAFF | 7132414381 | THE OPERATOR WAS PURGING AIR FROM A PARTIALLY FILLED CRUDE LINE. A VACUUM TRUCK WITH PRESSURE HOSE WAS CONNECTED TO THE PIPE TO RECEIVE AIR AND 11 GRAVITY CRUDE OIL FROM THE LINE. THE HOSE APPARENTLY BECAME PLUGGED AND FAILED NEAR THE CONNECTION FITTING DURING THE PROCESS. PERSONNEL WERE UNABLE TO CLOSE THE NEARBY VALVE BECAUSE OF THE SPRAYING OIL FROM THE HOSE. THE RUPTURED HOSE RELEASE 75-100 BBLS CRUDE WHICH WAS PRIMARILY CONTAINED ON OPERATORS PROPERTY.
2017-09-29 08:50 | YES | NO | 20020007 | 2002-01-15 | 15485 | PHILLIPS 66 CO | NO | 2001-10-15 | 1336 | TX | BRAZORIA |  | NO |  | NO | SEE ATTACHED SKETCH LOCATION: 1/3 MILE SOUTH SOUTH WEST OF INTERSECTION, FM 1459 AND COUNTY ROAD 332 |  | LINE PIPE | PIPE |  | 1961 | FAILED PIPE | DAMAGE BY OTHERS | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED PIPE BODY OR SEAM | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 165268.4564 | 333413.2311 | NATURAL GAS LIQUID | 2 | 4659 | 0 | NO | NO | 6 | 0.188 | 35000 |  |  | 1430 | 1409 | YES | 8 | 1804 | 10 | 1987 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | R G BRADFORD | 9794912240 | AT APPROXIMATELY 13:36 ON OCTOBER 15, 2001, A LEAK INITATED ON A PIPELINE NEAR THE TOWN OF SWEENY TEXAS. SHERIFF AND LOCAL EMERGENCY RESPONSE PERSONNEL ARRIVED AT THE SITE AND BEGAN EVACUATION OF THE HOUSES SURROUNDING THE LEAK SITE DUE TO THE PRESENCE OF HYDROCARBON VAPOR IN THE AREA. SWEENY COMPLEX EMERGENCY RESPONSE PERSONNEL ARRIVED AT THE SITE AND BEGAN ASSISTING WITH THE EVACUATION OF THE PUBLIC AROUND THE SITE AND ESTABLISHING A SAFE PERIMETER AROUND THE AREA. TWO ROADS AROUND THE AREA WERE BLOCKED BY LOCAL LAW ENFORCEMENT PERSONNEL. AN EMERGENCY COMMAND CENTER WAS ACTIVATED AT THE SWEENY COMPLEX AND ADDITIONAL PERSONNEL WERE DISPATCHED TO THE SCENE. A LOCAL COMMUNITY CENTER WAS OPENED FOR DISPLACED RESIDENTS IN THE AREA AND HOTEL ROOMS WERE PROVIDED FOR THOSE AFFECTED. SINCE THERE WERE MULTIPLE LINES IN THIS RIGHT OF WAY INITIAL EFFORTS WERE FOCUSED ON IDENTIFYING THE CORRECT LINE AND SHUTTING DOWN ANY POTENTIAL SUSPECTS. A TOTAL OF 10 LINES WERE SHUTDOWN DURING THIS PROCESS INCLUDING THE #9 PROPYLENE PIPELINE. ALL OF THESE PIPELINES TAKE PRODUCT FROM THE SWEENY COMPLEX TO UNDERGROUND STORAGE AT THE CLEMENS TERMINAL STORAGE FACILITY. DUE TO THE AMOUNT OF VAPOR COMING FROM THE LEAK PERSONNEL WERE NOT ABLE TO SAFELY GET INTO THE IMMEDIATE AREA SURROUNDING THE LEAK TO TAKE A SAMPLE OR STOP THE LEAK AT THE SOURCE OF THE VAPOR. THE PROPYLENE LINE WAS SUSPECTED TO BE THE LEAKING LINE DUE TO THE PRESSURE DROP SEEN ON THE LINE. ACTIONS WERE TAKEN TO ROUTE THE PROPYLENE TO EXISTING FLARES ON BOTH ENDS OF THE SYSTEM. THE LINE DEPRESSURED TO THE ATMOSPHERE AT THE LEAK SITE AND TO THE FLARES AT BOTH UNTIL APPROXIMATELY 11:50PM ON OCTOBER 15, 2001 WHEN THE LINE EMPTIED OF VAPORS. MONITORING OF THE AREA SURROUNDING THE LEAK CONTINUED THROUGHOUT THE NIGHT. THE ROADBLOCKS WERE RELEASED THE NEXT DAY. AT THE TIME OF THE INCIDENT THE SKY WAS CLEAR AND THERE WAS LIGHT WINDS. THE WIND SHIFTED DURING THE NIGHT WHEN A FRONT CAME INTO THE AREA. MONITORING OF VAPORS WAS ADJUSTED ACCORDINGLY DURING THE NIGHT. THE CAUSE OF THE LEAK WAS PREVIOUS EXTERNAL DAMAGE TO THE PIPELINE. THE LEAK AT THE SITE CONSISTED OF APPROXIMATELY A 12" SPLIT WHICH STARTED AT A WELD AT CLOCK LOCATION OF 2:00. EVIDENCE OF THE EXTERNAL DAMAGE WAS EVIDENT ON THE PIPE. A DENT WAS PRESENT AT THE APPARENT START OF THE SPLIT AND SCRAP MARKS WERE FOUND ALONG THE TOP OF THE PIPE AND IN THE DIRECTION OF THE SPLIT. A 4 FEET SECTION OF PIPE ALONG THE TOP OF THE PIPE WAS FLATTENED. THE COATING ON THE PIPE WAS SCRAPED OFF WITH NO EVIDENCE OF HAVING BEEN REPAIRED. THE PIPE UNDER THE COATING SHOWED LITTLE TO NO EVIDENCE OF CORROSION. CATHODIC PROTECTION READINGS AT THE LEAK SITE WERE -1323 M V WHICH IS ABOVE THE -850MV CRITERIA USED ON THIS PIPELINE. DIRECTLY UNDER THIS LINE WAS A CROSSING LINE WHICH HAD BEEN LAID IN 1997. FURTHER INVESTIGATION WAS CONDUCTED TO DETERMINE OTHER CAUSES CONTRIBUTING TO THE RELEASE. PRIOR TO THE START OF THE LEAK A LINE UP HAD OCCURRED WHICH PUT A HIGHER THAN NORMAL PRESSURE ON THE LINE. ALTHOUGH THE PRESSURE WAS BELOW THE MOP OF THE LINE IT WAS ABOVE THE PRESSURE NORMALLY SEEN ON THE LINE. AS A PRECAUTION THE LINES WHICH HAD BEEN CROSSED BY THE LINE LAID IN 1997 WERE EXCAVATED TO CHECK FOR DAMAGE. THREE LINES IN THE CORRIDOR SHOWED COATING DAMAGE AT THE CROSSING LOCATION. ONE UNREGULATED NITROGEN LINE SHOWED A SMALL GOUGE ON THE LINE WHICH WAS EVALUATED NOT TO COMPROMISE THE INTEGRITY OF THE LINE. METALLURGICAL ANALYSIS OF THE FAILED PIPE IS BEING PERFORMED. A 20 FEET SECTION OF THE LINE WAS INSTALLED AT THE LEAK LOCATION TO REPLACE TO FAILED PIPE. PIPELINE WAS PUT BACK IN SERVICE ON OCTOBER 19, 2001. UPDATE 3-28-02 BASED ON HIS FINDINGS WE BELIEVE THAT THE OVERHELMING PHYSICAL EVIDENCE PRESENT ON THE PIPE SECTION WOULD MAKE FURTHER METALLURICAL ANALYSIS OF LIMITED VALUE. THE PIPE SECTION HAD AND INWARD DENT PRESENT AT THE START OF THE SPLIT, SCRAP MARKS ALONG AND PAST THE SPLIT, AND APPROXIMATELY 4 FEET OF FLATTENED
2017-09-29 08:50 | YES | YES | 20020008 | 2002-01-14 | 6856 | KOCH PIPELINE COMPANY, L.P. AMMONIA | YES | 2001-12-14 | 1513 | IA | KOSSUTH |  | NO |  | NO | 8 MILES WEST OF ALGONA, IA ON HWY 18, THEN 1 1/2 MILES NORTH ON 40TH AVE T96N, R30W, SEC 28 | 588708 | LINE PIPE | WELDING FITTING |  | 1991 | OUTSIDE FORCE DAMAGE | DAMAGE BY OPERATOR OR ITS CONTRACTOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | 0 | 0 | 0 | 1 | 0 | 1 | 2000000 | 1322147.651 | 2667305.8485 | ANHYDROUS AMMONIA | 2 | 1442 | 0 | NO | NO | 8.625 | 0.203 | 42000 | WELDED |  | 1420 | 500 | YES | 82 | 1994 | 0 | 1970 |  | Null | Null |  |  | DAMAGE BY OPERATOR OR ITS CONTRACTOR |  | Null | ONE CALL |  | YES | YES | ROYCE HOEMANN | 5734865488 | AT APPROXIMATELY 15:13 HOURS ON 12/14/01, WHILE EXCAVATING A SEGMENT OF KOCH PIPELINE COMPANY, L.PS ANHYDROUS AMMONIA PIPELINE TO PERFORM PREVENTIVE MAINTENANCE, AN EMPLOYEE OF A CONTRACTOR (PIPELINE SERVICES OF IOWA, INC) FOR KOCH ACCIDENTALLY STRUCK AN EXISTING THREADED O-RING ("TOR") FITTING WITH A BACKHOE BUCKET CAUSING THE FITTING TO SEPARATE FROM THE PIPELINE. THIS RESULTED IN ANHYDROUS AMMONIA ESCAPING INTO THE EXCAVATION DITCH AND INTO THE ATMOSPHERE. A ON SITE KOCH EMPLOYEE TELEPHONED KOCHS PIPELINE CONTROL CENTER IN WICHITIA, KS TO ORDER AN IMMEDIATE SHUT DOWN OF THE PIPELINE SEGMENT. BY 15:25 HOURS ON 12/14/01, THE PIPELINE FLOW WAS SHUT DOWN AND THE CLOSET VALVES ON EITHER SIDE OF THE RELEASE POINT WERE CONFIRMED CLOSED TO ISOLATE THE DAMAGED SECTION OF PIPE. KOCH INFORMED THE LOCAL LEPC AND LAW ENFORCEMENT AGENCIES OF THE INCIDENT. THESE AGENCIES STATED THEY WOULD ASSIST IN THE EVENT EVACUATIONS OR ROAD CLOSURES BECAME NECESSARY. ALTHOUGH NO OFFICIAL EVACUATION WAS ORDERED, SOME AREA FAMILIES VOLUNTARILY LEFT FOR THE NIGHT AND A NEARBY ROAD CLOSED IN BOTH DIRECTIONS FOR APPROXIMATELY 1 MILE. THERE WERE NO REPORTED INJURIES TO THE PUBLIC, BUT ONE EMPLOYEE OF PIPELINE SERVICES OF IOWA WAS TAKEN TO A LOCAL HOSPITAL FOR OVERNIGHT OBSERVATION AND RELEASED THE MORNING OF 12/15/2001. ONCE THE DAMAGED PIPELINE SEGMENT WAS ISOLATED AND SHUT DOWN, KOCH HAD ITS CONTRACTOR REPLACE EXCAVATION DIRT ON TOP OF THE RELEASE POINT TO MINIMIZE THE EFFECT OF THE VAPORS FROM THE IMPACTED AREA. KOCH ALSO SET UP BURNERS TO COMBUST VAPORS FROM THE IMPACTED SOIL ON TOP OF THE RELEASE POINT. BY APPROXIMATELY 23:00 ON 12/14/2001, THE PIPELINE RELEASE WAS CONTROLLED AND PRESENTED NO FURTHER DANGER TO AREA RESIDENTS. THIS SECTION OF PIPE WAS CUT OUT AND REPLACED ON 12/15. KOCH EMPLOYEE DETERMINED THAT AT SOME POINT DURING OR AFTER THE RELEASE EVENT, AMMONIA HAD ENTERED A FARM FIELD DRAIN TILE SYSTEM, WHICH ALLOWED AMMONIA TO ENTER A NEARBY CREEK, CAUSING IMPACT THERE. UPON THIS DISCOVERY, KOCH BEGAN WORKING TO CLOSE OFF FIELD DRAIN TILE IN THE VICINITY AND BEGAN WORKING WITH THE IOWA-DNR TO MITIGATE THE EFFECTS OF THE AMMONIA INCURSION INTO THE CREEK. MADE CONVERSION OF COMMODITY FROM 155 TONS TO 930 BARRELS.
2017-09-29 08:50 | YES | NO | 20020009 | 2002-01-15 | 15490 | PHILLIPS PIPE LINE CO | YES | 2001-10-16 | 1915 | CO | ADAMS |  | NO |  | NO | DENVER TERMINAL - 1" PROVER DRAIN VALVE, ADAMS CO, COLORADO | 583397 | NO DATA | VALVE |  | 1990 | INCORRECT OPERATION BY OPERATOR PERSONNEL |  | INCORRECT OPERATION | INCORRECT OPERATION | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 991.6107 | 2000.4794 | BUTANE | 2 | 5 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LINUS J SCHMITZ | 9186614814 | THE ENGINEER ON DUTY NOTICED VAPOR COMING OUT OF THE UNDERGROUND SUMP TANKS VENT. THE SOURCE OF THE RELEASE WAS FOUND ON THE PROVER DRAIN AND WAS ISOLATED. MAINTENANCE WORK ON THE PROVER INVOLVING THE USE OF THE 1" DRAIN VALVE WAS COMPLETED EARLIER IN THE DAY, AND THE VALVE HAD NOT BEEN TOTALLY CLOSED WHEN THE WORK WAS COMPLETED.
2017-09-29 08:50 | YES | NO | 20020010 | 2002-01-15 | 4906 | EXXONMOBILE PIPELINE CO | YES | 2001-11-19 | 1130 | TX | MIDLAND |  | NO |  | NO | SUCTION/FILL TO TANK 2174, MIDLAND STATION TANK FARM, 3.5 MILES ESE OF MIDLAND, TEXAS, THE STATION IS APPROX. 1500' S OF COUNTY ROAD 90 |  | TANK FARM | PIPE |  | 1950 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3305.3691 | 6668.2646 | CRUDE OIL | 1 | 160 | 150 | NO | NO | 16 | 0.25 | 0 | WELDED |  | 270 | 30 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES |  |  |  |  | Null |  |  | Null | Null | KAREN R BAILOR | 7136560227 | STATION OPERATOR NOTED LEAK AT 11:30AM 11/19/01. LEAK OCCURRED ON SUCTION/FILL LINE FOR TANK 2714 EAST OF TANK AND EXPOSED AN AREA SSE OF TANK 2714 APPROX. 100X100X1. PIPING WAS ISOLATED AND EQUIPMENT SHUTDOWN AS NEEDED. CREWS AND EQUIPMENT ARRIVED ON SITE TO PICK UP FREE CRUDE AND LIMIT EXPOSURE TO ENVIRONMENT. THE DETERMINATION WAS MADE 160 BBLS WERE RELEASED AND 150 BBLS WERE RECOVERED WITH 10 BBLS LOST. A TEMPORARY CLAMP WAS PLACED ON THE PIPING WHICH WAS THEN RETURNED TO SERVICE. PIPE TEST/REPAIR OR REPLACEMENT WILL OCCUR AT A LATER DATE.
2017-09-29 08:50 | NO | NO | 20020011 | 2002-01-14 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 2001-11-16 | 1830 | OK | TULSA |  | NO |  | NO | WPL GLENPOOL STATION 126 STREET SOUTH & HIGHWAY 75 GLENPOOL, OK 74131 (SECTION 2-TOWNSHIP 17N RANGE 12 E TULSA COUNTY | 586268 | PUMPING STATION | VALVE |  | 1998 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 39664.4295 | 80019.1755 | JET FUEL | 3 | 15 | 13 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KENNETH L LYBARGER | 9185733050 | FOUR THERMAL RELIEF DEVICES - (ONE ON THE BOOSTER PUMP DISCHARGE, ONE ON THE 30 INCH MANIFOLD, AND TWO ON BLOCK VALVE BODIES IN THE LOW PRESSURE PIPING) RELIEVED AND FAILED TO RESEAT, RELEASING PRODUCT TO THE SUMP. THIS LEVEL SWITCH IN THE SUMP WAS DEFECTIVE ALLOWING PRODUCT TO BE RELEASED FROM THE SUMP. REMEDIATION BEGAN IMMEDIATELY UNDER APPROVAL OF STATE CORPORATION COMMISSION, ENVIRONMENTAL SECTION. THIRTEEN BBLS WERE RECOVERED. SOIL CONTAINING REMAINING PRODUCT WILL BE REMEDIATED ACCORDING TO ACCEPTED PRACTICES.
2017-09-29 08:50 | NO | NO | 20020012 | 2002-01-11 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2001-11-05 | 945 | TX | BRAZORIA | FREEPORT | NO |  | NO | 2 MILES NORTH OF FREEPORT ON BRAZOS RIVER. |  | OTHER | OTHER |  | 0 | OTHER | LEAKING FITTING FROM HYDRAULIC HOSE ON LOADING ARM | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRANSMIX (PART.REFINED PETRO) | 3 | 0 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | LEONARD MALLETT | 7137593615 | EMPLOYEES WITNESSED 2-3 DROPS OF HYDRAULIC FLUID FROM HYDRAULIC HOSE ON THE MARINE DOCK LOADING ARM FALL INTO THE BRAZOS RIVER. FITTING WAS IMMEDIATELY REPAIRED AND THE HYDRAULIC FLUID IMMEDIATELY DISSIPATED ON THE RIVER, NO CLEAN UP REQUIRED.
2017-09-29 08:50 | YES | NO | 20020013 | 2002-01-22 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | YES | 2001-11-17 | 1537 | IL | BUREAU |  | NO |  | NO | WALNUT PUMP STATION, 28710 1500 E. STREET, P.O. BOX 430, WALNUT, IL 61376. |  | PUMPING STATION | PUMP |  | 2000 | OTHER | INBOARD AND OUTBOARD PUMP SEALS FAILED. | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 7624 | 5040.0268 | 10167.7699 | BUTANE | 2 | 21 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | EDWARD A. FANT | 7133699454 | ON 11/17/2001, AT 1537 HOURS, CST, KMEPS CONTROL CENTER RECEIVED AN ESD ALARM FROM OUR WALNUT PUMP STATION AND INITIATED OUR EMERGENCY RESPONSE PLAN. PERSONNEL ARRIVED AT 1550 HOURS, CST, AND CONFIRMED THE PRESENCE OF A VAPOR CLOUD. IT WAS DETERMINED THAT THE # 2 PUMPS INBOARD AND OUTBOARD SEALS FAILED.
2017-09-29 08:50 | YES | NO | 20020014 | 2002-01-18 | 31291 | DIAMOND KOCH | NO | 2001-12-11 | 1130 | TX | SCHLEICHER |  | NO |  | NO | NE 1/4 OF SECTION 33, BLOCK M, GH & SA RR. | 588362 | LINE PIPE | NO DATA |  | 1976 | OTHER | DAMAGE BY OTHERS | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 8500 | 5619.1275 | 11336.0499 | DATA NOT SPECIFIED | 2 | 300 | 0 | NO | NO | 4.5 | 0.188 | 52000 | WELDED |  | 0 | 200 | YES | 12 | 1800 | 11 | 1976 |  | Null | YES |  |  | DAMAGE BY OTHERS |  | Null |  |  | Null | Null | BOB AEBI | 5803956294 | CONOCO HAD A CONTRACTOR DISMANTLING THE ELDORADO PLANT AND SELLING IT FOR SCRAP METAL. IN THE PROCESS OF REMOVING THEIR PIPING, THE CONTRACTOR CUT DIAMOND-KOCHS 4 INCH LATERAL LINE.
2017-09-29 08:50 | YES | NO | 20020015 | 2002-01-24 | 10012 | KANEB PIPE LINE CO | YES | 2001-11-19 | 1315 | IA | POTTAWATTAMIE |  | NO |  | NO | SEE ATTACHED DRAWING |  | LINE PIPE | PIPE |  | 1941 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6610.7383 | 13336.5292 | GASOLINE | 3 | 150 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | L. LEROY ANDERSON | 3167739000 | THE OWNER OF THE PROPERTY WHERE THE RELEASE OCCURRED WAS PULLING A DEEP CHISEL IMPLEMENT BEHIND A TRACTOR IN ORDER TO BREAKUP THE SUBSURFACE SOIL OF THE CROPLAND. DURING THE CHISELING ACTIVITY, THE IMPLEMENT STRUCK AND BREACHED THE PIPELINE THUS ALLOWING THE GASOLINE INSIDE TO ESCAPE. ALTHOUGH, THE PIPELINE WAS IDLE AT THE TIME OF THE INCIDENT, IT WAS PRESSURIZED AT APPROXIMATELY 450 POUNDS PER SQUARE INCH GAUGE. THE VOLUME OF THE RELEASE WAS DUE, PRIMARILY, TO DRAIN DOWN ASSOCIATED WITH ELEVATION DIFFERENTIALS.
2017-09-29 08:50 | NO | NO | 20020016 | 2002-01-23 | 31566 | DENBURY OFFSHORE INC | NO | 2001-10-20 | 800 |  |  |  | NO | LAT 29 11 9.1 LONG. 89 31 | NO | WEST DELTA BLOCK24, STATE WATERS LOUISIANA. | 583761 | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 62000 | 40986.5772 | 82686.4813 | CRUDE OIL | 1 | 9 | 0 | Null | Null | 12 | 0.0375 | 0 | WELDED |  | 1440 | 185 | NO | 0 | 0 | 0 | 0 | INTERNAL | Null | YES |  |  |  |  | Null |  |  | Null | Null | STEPHEN J. WALTON | 9858931530 | ON MONDAY MORNING, OCTOBER 22, 2001, THE FIELD SUPERVISOR REPORTED THAT A SLIGHT SHEEN HAD APPEARED. WITHIN 45 MINUTES, HE REPORTED IT HAD BECOME WORSE AND WAS MOVING TO THE WEST. THE DENBURY SPILL RESPONSE TEAM WAS ASSEMBLED AND WE ESTABLISHED AN INCIDENT COMMAND. TWO CGA VESSELS WERE DISPATCHED TO THE SITE AND A HELICOPTER. WITHIN 1/2 HOUR OF THE SECOND REPORT FROM THE FIELD SUPERVISOR, WE DISCOVERED THE VENICE SEPARATION PLANT (WHERE THE PIPELINE TERMINATES) HAD INADVERTENTLY BACK PRESSURED OUR PIPELINE. WE INSTRUCTED THEM TO IMMEDIATELY RELIEVE ALL PRESSURE TO THE ATMOSPHERIC VENT. BY 1430 HOURS MONDAY AFTERNOON, BOTH CGA BOATS WERE AT THE SPILL SITE. THE HELICOPTER WAS PROVIDING UPDATES ON THE LEADING EDGE. THE SPILL SOURCE WAS RAPIDLY DIMINISHING, AND THE SPILL SHEEN WAS BREAKING UP. BY 1700 THE HELICOPTER REPORTED THE SPILL HAD BROKEN UP SUBSTANTIALLY. THE DIVERS HAD THE PIPELINE CLAMP IN PLACE AND THE SPILLAGE WAS STOPPED. PRODUCTION REMAINED SHUT-IN, AND THE FAST RESPONSE BOAT "TIMBALIER BAY" STAYED ON LOCATION AT THE SOURCE. TUESDAY MORNING, OCTOBER 23, 2001, THE HELICOPTER MADE ANOTHER ARIEL SURVEILLANCE AND REPORTED THAT THERE WERE NO SIGHTINGS OF A SPILL. THE PIPELINE WAS REPRESSURED WHILE DIVERS WATCHED THE CLAMP REPAIR AND THE CGA BOAT, TIMBALIER BAY, STOOD BY. THE PIPELINE HELD PRESSURE WITHOUT LEAKING. THE EQUIPMENT WAS DEMOBILIZED.
2017-09-29 08:50 | NO | NO | 20020017 | 2002-01-23 | 31554 | TEXACO PETROCHEMICAL PIPELINE LLC | YES | 2001-10-29 | 650 | LA |  | JEFFERSON DAVIS | NO |  | NO | 23425 PLACIDE ROAD, JENNINGS, LOUISIANA (RURAL AREA) GPS COORDINATES-NORTH 30 DEGREES 22.700'/WEST 92 DEGREES 39.250' EVANGELINE ETHYLENE PIPELINE SYSTEM. | 584548 | LINE PIPE | OTHER | EXISTING STOPPLE FITTING | 0 | OTHER | O-RING FAILURE SEAL FAILURE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 25058 | 16565.1879 | 33418.675 | L. P. G. | 2 | 0 | 0 | NO | NO | 16 | 0.312 | 52000 | WELDED |  | 1336 | 867 | YES | 25 | 1754 | 6 | 2001 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | HENRY L. LEGER | 3376548915 | TEXACO PETROCHEMCIAL PIPELINE LLCS EVANGELINE ETHYLENE PIPELINE SYSTEM HAS RECENTLY GONE THROUGH A CONVERSION OF SERVICE FROM NATURAL GAS SERVICE (49 CFR PART 192) TO HAZARDOUS LIQUIDS (HVL) SERVICE (49 CFR PART 195) AS PER 49 CFR PART 195.5. DURING THE INITIAL ETHYLENE PIPELINE FILL AND PACK OPERATIONS, A SMALL UNDERGROUND LEAK WAS NOTED BY COMPANY PERSONNEL. THE IMPACTED LINE SEGMENT WAS ISOLATED AND THE ETHYLENE WAS DISPLACED WITH NITROGEN, THEN BLED DOWN TO ZERO PSIG. THE PIPELINE WAS THEN EXCAVATED, THE LEAKING STOPPLE WAS CUT OUT OF THE PIPELINE AND A NEW SECTION OF PRE-TESTED PIPE WAS WELDED INTO PLACE. IT MUST BE NOTED THAT ETHYLENE IS A "HIGHLY VOLATILE LIQUID" (HVL) AND TOGETHER WITH THE LINE PRESSURE AND AMBIENT TEMPERATURE AS THEY WERE, THE ETHYLENE ENTERED THE ATMOSPHERE THROUGH THE LEAK AS A VAPOR. AS A VAPOR THERE WAS NO PRODUCT "SPILLED" OR PRODUCT "RECOVERED".THERE WAS NO ENVIRONMENTAL IMPACT OR CLEAN-UP REQUIRED.THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATURAL RESPONSE CENTER IN ACCORDANCE WITH 49 CFR PART 195.50(C) AND 195.52(A)(5). PLEASE NOTE THAT THE NATIONAL RESPONSE CENTER INCIDENT NUMBER IS NRC 584548.
2017-09-29 08:50 | NO | NO | 20020018 | 2002-01-28 | 2552 | COLONIAL PIPELINE CO | YES | 2001-11-12 | 1045 | VA | BEDFORD | ROANOKE | NO |  | NO | ROANOKE DELIVERY FACILITY, HIGHWAYS 460 AND 607 MONTVAL, VA 24122. | 585792 | TANK FARM | TANK |  | 1986 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 73000 | 48258.3893 | 97356.6635 | KEROSENE | 1 | 22 | 18 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | STEPHEN E. GILLIAM | 6787622314 | AT APPROXMATELY 10:43 ON 11-12-01, THE OPERATOR AT THE ROANOKE DELIVERY DISCOVERED THAT TANK 5226 WAS RELEASING KEROSENE NEAR THE BASE OF THE TANK. THIS WAS OCCURRING WHILE FILLING A TANK TRUCK FROM THAT TANK. THE OPERATOR NOTIFIED MITCHELL JUNCTION AND THE OPERATIONS MANAGER. THE OPERATIONS MANAGER NOTIFIED THE ATLANTA CONTROL CENTER AND THE PIPELINE SERVING ROANOKE DELIVERY WAS SHUTDOWN BECAUSE TANK 5226 IS PART OF THE RELIEF SYSTEM. THE OPERATOR INITIATED EFFORTS TO MITIGATE THE AMOUNT OF PRODUCT BEING RELEASED. RECONNAISSANCE DISCOVERED PRODUCT IN THE TANK DIKE AND IN A DRY DRAINAGE DITCH SOUTHEAST OF THE FACILITY. MEASURES TO PREVENT PRODUCT FROM REACHING THE NEARBY CREEK WERE SUCCESSFULLY IMPLEMENTED. NOTIFICATIONS WERE MADE TO FEDERAL, STATE AND LOCAL AGENCIES. THE NATIONAL RESPONSE CENTER WAS NOTIFIED AT 1440 HOURS (REPORT NUMBER 585792). INITIALLY THIS RELEASE WAS BELIEVED TO HAVE LESS THAN $50,000 IN ESTIMATED PROPERTY DAMAGES AND HAS LESS THAN 50 BARRELS RELEASED. THESE INITIAL ESTIMATES RENDERED THIS RELEASE A NON-REPORTABLE RELEASE UNDER THE GUIDELINES OF 49 CFR 195.50 AND .52. HOWEVER, ON JANUARY 2, 2002, A REVISED ESTIMATED PROPERTY DAMAGE INDICATED THE $50,000 THRESHOLD MIGHT BE EXCEEDED, THEREFORE RESULTING IN THIS INCIDENT BEING A REPORTABLE ACCIDENT UNDER 49 CFR 195.50. THE METHOD OF REPAIR IS BEING EVALUATED BASED ON AN OUT OF SERVICE API 653 INSPECTION OF THE TANK. CLEANUP AND REMEDIATION ACTIVITIES ARE CONTINUING. COLONIAL CONTINUES PROVIDING ASSISTANCE TO THE VIRGINIA STATE CORPORATION COMMISSION DIVISION, PIPELINE SAFETY DIVISION RELATING TO THEIR REVIEW OF THIS ACCIDENT.
2017-09-29 08:50 | YES | NO | 20020019 | 2002-01-29 | 6911 | GULF STATE PIPELINE CO INC | NO | 2001-10-07 | 1320 | TX | ORANGE |  | NO |  | NO | ATTACHED MAPS |  | LINE PIPE | PIPE |  | 1975 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 165268.4564 | 333413.2311 | GASOLINE | 1 | 2685 | 218 | NO | NO | 8.625 | 0.203 | 1186 | WELDED |  | 800 | 466 | YES | 24 | 1878 | 10 | 1975 | INTERNAL | Null | YES | OTHER | PIPE BEING METALLURGIGALLY ANALIZED |  |  | Null |  |  | Null | Null | HANK BOWMAN | 4093851400 | THE PIPELINE BEGAN OPERATING ON OCTOBER 6TH AT 07:30 AND CONTINUED UNTIL 15:45 WHEN A POWER FAILURE BROUGHT THE LINE DOWN UNTIL 17:10 WHEN PUMPING WAS RESUMED. THE PUMPING CONTINUED UNINTERRUPTED UNTIL 13:20 OCTOBER 7TH, WHEN A HUNTER REPORTED THE LEAK TO THE CONTROL ROOM. PUMPING WAS IMMEDIATELY STOPPED. THE SPILL RESPONSE PLAN WAS INITIATED. I WAS NOTIFIED AT 13:30. THE CONTRACT PILOT THAT HAS FLOWN THE PIPELINE FOR IN EXCESS OF FIFTEEN YEARS FLEW THE PIPELINE TO SURVEY THE EXTENT OF THE SPILL, HE CONFIRMED THE SPILL LOCATION, ESTIMATING A SMALL SPILL IN THE R.O.W. APPLICABLE BLOCK VALVES WERE CLOSED TO ISOLATE THE DAMAGED LINE SECTION. RAIL ROAD COMMISSION WAS NOTIFIED. THE PIPE IN THIS SEGMENT OF PIPELINE HAS BEEN INSPECTED AND INTERNAL CORROSION IS EVIDENT AT THE 6:00 O-CLOCK POSITION. THE SUBJECT PIECE OF PIPE HAS BEEN SENT OUT FOR METALLURGICAL ANALYSIS INTO THE REASON FOR THE CORROSION AT THIS POSITION. THE EXTERNAL COATING WAS FOUND TO BE IN EXCELLENT CONDITION, AT THE SAME TIME CATHODIC PROTECTION WAS READ AT A NEGATIVE 0.951 VOLTS.
2017-09-29 08:50 | YES | NO | 20020020 | 2002-02-06 | 31566 | DENBURY OFFSHORE INC | NO | 2002-01-24 | 830 |  |  |  | NO | LAT 29 11 9.1 LONG. 89 31 | NO | WEST DELTA BLOCK 24, SL2869, GULF OF MEXICO | 592171 | LINE PIPE | PIPE |  | 1963 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 52050.0118 | 105005.8976 | CRUDE OIL | 2 | 14 | 0 | NO | NO | 12 | 0.0375 | 0 | WELDED |  | 1440 | 120 | YES | 4 | 150 | 10 | 2001 | INTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | STEPHEN J. WALTON | 9858931530 | ON JANUARY 25, 2002 WE RECEIVED A CALL THAT THE OIL/CONDENSATE TRANSPORTATION PIPELINE IN WEST DELTA BLOCK 24 APPEARED TO HAVE A LEAK. THE FIELD WAS SHUT-IN AND THE PRESSURE ON BOTH ENDS OF THE PIPELINE WAS DROPPED TO ZERO POUNDS. TOTAL ESTIMATED RELEASE TO THE GULF OF MEXICO FROM THE TIME THE PIPELINE BEGAN TO LEAK UNTIL THE REPAIR WAS COMPLETED IS 13.8 GALLONS. DENBURY MOBILIZED A DIVE TEAM, OBRIENS OIL SPILL SPECIALISTS, SORBENT BOOM, PIPELINE REPAIR CLAMP AND A PROJECT MANAGER. A JACKUP BOAT WITH A CRANE THAT WAS IN THE FIELD DOING OTHER WORK WAS DIVERTED TO THIS PROJECT. THE CREWS ARRIVED IN THE FIELD AT APPROXIMATELY 1800 HOURS 01/25/02 AND TRANSFERRED TO THE JACKUP BOAT. THE JACKUP BOAT. THE JACKUP WAS REPOSITIONED TO WHERE THE LEAK APPEARED TO BE EMANATING. ONCE THE SORBENT BOOM WAS IN PLACE, THE DIVERS BEGAN LOOKING FOR THE LEAK AND CHIPPING CONCRETE FROM THE 12 INCH DIAMETER PIPELINE. THE DIVERS FOUND THE LEAK AND THE PRESSURE CLAMP WAS INSTALLED. THE PIPELINE WAS REPRESSURED AND HELD FOR 4 HOURS. ONCE IT WAS DETERMINED THE PRESSURE WAS HOLDING AND THE CLAMP WAS SEALED, THE REPAIR AND SPILL TEAM WERE DEMOBILIZED AT APPROXIMATELY 1400 HOURS ON JANUARY 27, 2002.
2017-09-29 08:50 | YES | NO | 20020021 | 2002-02-19 | 30950 | EL PASO FIELD SERVICES | NO | 2001-12-22 | 115 | TX | DAMON | BRAZORIA | NO |  | NO | APPROXIMATELY 1 MILE NORTH OF HWY. 36 IN DAMON, TX IN A PASTURE OF LAND OWNER. |  | LINE PIPE | PIPE |  | 1966 | OTHER | UNDER INVESTIGATION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 99161.0738 | 200047.9386 | PROPANE | 2 | 5 | 0 | NO | NO | 8.625 | 0.188 | 0 | WELDED |  | 1175 | 0 | YES | 8 | 0 | 0 | 1966 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | E.R. WEST VP | 8326765410 | LANDOWNER REPORTED AN ICE-BALL ON PIPELINE RIGHT-OF-WAY IN HIS PASTURE. UPON INVESTIGATION, EL PASO FIELD SERVICES 8" HOUSTON LPG LINE CONTAINING A PROPYLENE PROPANE MIX WAS LEAKING. THE LINE WAS IMMEDIATELY SHUT IN TEMPORARY FLARES INSTALLED FOR VENTING/BLOWING DOWN THE LINE; STOPPLES INSERTED AND 7 JOINTS OF PIPE REPLACED. THE REPAIRS AND REINSTATEMENT OF SERVICE TO THIS LINE OCCURRED ON 12-24-01.
2017-09-29 08:50 | YES | NO | 20020022 | 2002-02-07 | 19237 | TE PRODUCTS PIPELINE CO., LP | YES | 2001-11-27 | 1330 | TX | ORANGE | VIDOR | NO |  | Null | APPROXIMATELY 220 YARDS NORTH OF STATE HIGHWAY 105, 4.5 MILES SOUTH OF VIDOR, TEXAS. |  | LINE PIPE | PIPE |  | 1975 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 620000 | 409865.7718 | 826864.813 | KEROSENE | 1 | 2575 | 1048 | NO | NO | 14 | 0.234 | 42000 | WELDED |  | 1440 | 1362 | YES | 24 | 2005 | 0 | 1975 |  | Null | YES | OTHER | BIOLOGICAL |  |  | Null |  |  | Null | Null | JAMES E. MIKA | 7137593755 | AT APPROXIMATELY 0238 HOURS CST ON NOVEMBER 27, 2001, TEPPCO EXPERIENCED A LOSS OF PRESSURE ON OUR 14" MAINLINE SYSTEM AT THE BEAUMONT TERMINAL. THIS SYSTEM ORIGINS AT BEAUMONT, TEXAS AND TERMINATES IN EL DORADO, ARKANSAS. PERSONNEL WERE IMMEDIATELY DISPATCHED TO SHUT THE SYSTEM IN AND BEGIN SEARCHING FOR ANY INDICATION THE INTEGRITY OF THE PIPELINE HAD BEEN COMPROMISED. A LEAK-SITE WAS IDENTIFIED AT APPROXIMATELY 1330 HOURS CST. THE TEPPCO EMERGENCY PLAN WAS INITIATED AND CONTRACT PERSONNEL WERE STAGED TO ASSIST IN THE CONTAINMENT AND CLEAN-UP OF THE SITE. THE SECTION OF PIPELINE EXPERIENCING THE FAILURE WAS REMOVED, A NEW SECTION OF PIPE WAS INSTALLED. AFTER LABORATORY ANALYSIS, IT WAS DETERMINED THE FAILURE RESULTED FROM A 15" SECTION OF FAILED COATING WHICH ALLOWED BIOLOGIC CORROSION TO REDUCE THE WALL THICKNESS OF THE PIPELINE.
2017-09-29 08:50 | YES | NO | 20020023 | 2002-02-12 | 31174 | EQUILON PIPELINE COMPANY LLC | NO | 2001-10-12 | 1210 | CA | KERN |  | NO |  | NO | CARNERAS PUMP STATION, KERN COUNTY, CALIFORNIA, SEC. 34, T-27S, R-20E |  | PUMPING STATION | PUMP |  | 1989 | OTHER | PUMP SEAL FAILED | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 26442.953 | 53346.117 | CRUDE OIL | 1 | 100 | 60 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | THE SEAL ON PUMP #3 FAILED, CAUSING OIL TO RELEASE TO THE GROUND.
2017-09-29 08:50 | NO | NO | 20020024 | 2002-02-11 | 31045 | GENESIS CRUDE OIL LP | NO | 2002-01-11 | 1030 | TX | MATAGORDA | BAY CITY | NO |  | NO | THE NEAREST INTERSECTION IS COUNTY ROAD 404 AND COUNTY ROAD 402 IN BAY CITY, TEXAS. LAT: 28 DEGREES 59' 516" N LONG: 95 DEGREES 59' 431" W. |  | LINE PIPE | PIPE |  | 1940 | OTHER | SEEPING FROM CONNECTION | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 650.6251 | 1312.5737 | CRUDE OIL | 1 | 3 | 3 | NO | NO | 8 | 0.165 | 25000 | COUPLED |  | 191 | 100 | NO | 0 | 0 | 0 | 2001 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | MR. PATRICK D. HODGINS | 7138602543 | THE LINE HAD A SEEP AT THE JOINT CONNECTION. THE SEEP SURFACED IN THE DITCH. WE ESTIMATE THE OIL RELEASED TO BE 2-3 BARRELS OR LESS. THE GENESIS IN-HOUSE CREW ARRIVED AND WELDED A PATCH ON THE LINE. GENESIS CLEANUP CREW CLEANED UP THE SPILL AND ARE MONITORING THE SITE DAILY. SAMPLES FROM THE EXCAVATION OF THE PIPELINE WAS COMPLETED AND BNC HAS SENT THE SAMPLES TO A THIRD PARTY LAB FOR TPH AND BTEX SAMPLING AS REQUIRED.
2017-09-29 08:50 | YES | NO | 20020025 | 2002-02-11 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 2001-11-26 | 1311 | KS | CHEROKEE |  | NO |  | NO | SW QUARTER, SECTION 10-TOWNSHIP 33S-RANGE 23E, CHEROKEE COUNTY, KANSAS. |  | LINE PIPE | NO DATA |  | 1929 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 23137.5839 | 46677.8523 | GASOLINE | 1 | 87 | 0 | NO | NO | 12 | 0.303 | 24000 | OTHER |  | 730 | 249 | YES | 8 | 925 | 0 | 1983 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KENNETH L. LYBARGER | 9185730350 | EMPLOYEE OF FARMER HIT LINE WHILE DEEP PLOWING. LINE WAS IDENTIFIED BY PIPELINE MARKERS, BUT FARMER DID NOT CALL ONE-CALL CENTER. THE LINE WAS PROMPTLY REPAIRED AND RETURNED TO SERVICE. CONTAMINATED SOIL WAS REMOVED AND REPLACED WITH CLEAN SOIL. CONTAMINATED SOIL WILL BE DISPOSED OF IN ACCORDANCE WITH STATE ENVIRONMNETAL REQUIREMENTS.
2017-09-29 08:50 | YES | NO | 20020026 | 2002-02-19 | 22610 | WILLIAMS PIPE LINE COMPANY | YES | 2002-01-02 | 1300 | IA |  | DES MOINES | NO |  | NO | WILLIAMS PIPELINE COMPANY, DES MOINES STATION 2503 S. E. 43RD STREET DES MOINES, IA 50317. |  | PUMPING STATION | OTHER | PROVER | 1985 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3253.1257 | 6562.8686 | BUTANE | 2 | 0 | 0 | YES | NO | 0 | 0 | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | KEN LYBARGER | 9185730350 | ICE FORMED INSIDE THE HOUSING OF THE RELIEF DEVICE ON A PROPANE PROVER CAUSING IT TO STICK OPEN PERMIT THE DROP TANK CONNECTED TO IT TO FILL WITH ISO-BUTANE. CONTENTS OF THE DROP TANK FLOWED TO THE FLARE FASTER THAN THE FLARE COULD BURN IT, RESULTING IN PARTIALLY BURNED ISO-BUTANE FALLING TO THE GROUND AROUND THE FLARE, IGNITING VEGETATION. THE FIRE WAS QUICKLY EXTINGUISHED. A SMALL PIECE OF ICE WAS REMOVED FROM THE RELIEF DEVICE ON THE PROVER, RESTORING ITS FUNCTIONALITY. SUPPLEMENTAL SENT IN 10-14-03 AMOUNT SPILLED IS 7.14 GALLONS
2017-09-29 08:50 | NO | NO | 20020027 | 2002-02-22 | 4906 | EXXONMOBILE PIPELINE CO | YES | 2002-01-08 | 1100 | TX | WISE |  | NO |  | NO | 1848 COUNTY ROAD 2360, DECATUR, TEXAS 76234. THE LEAK SITE IS APPROXIMATELY 6 MILES NORTH OF DECATUR, TEXAS. |  | LINE PIPE | PIPE |  | 1953 | OUTSIDE FORCE DAMAGE | DAMAGE BY OTHERS | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 650.6251 | 1312.5737 | CRUDE OIL | 1 | 2 | 1 | NO | NO | 16 | 0.25 | 42000 | WELDED |  | 860 | 40 | YES | 8 | 1077 | 1 | 1994 |  | Null | Null |  |  | DAMAGE BY OTHERS |  | Null | ONE CALL |  | NO | NO | KAREN R. BAILOR | 7136560227 | LANDOWNER WAS DRILLING POST HOLES FOR FENCING ON HIS PROPERTY USING A HYDRAULIC TRACTOR AUGER. PIPELINE MARKER SIGNS WERE IN PLACE AND VISIBLE AT THE SITE. THE LANDOWNER DID NOT MAKE A ONE-CALL NOTIFICATION TO EMPCO. HE HIT THE LINE WITH THE POWER AUGER, THEN CALLED EMPCO WITH HIS CELL PHONE AT THE SITE. EMPCO IMMEDIATELY SHUT DOWN THE SYSTEM AND DISPATCHED PIPELINE REPAIR AND CLEANUP PEOPLE TO THE SITE. PERMANENT REPAIRS WERE COMPLETED BY WELDING A FULL WRAP ON THE LINE SEGMENT. CLEANUP WAS COMPLETED BY RECOVERING FREE OIL, REMOVING SOIL FOR REMEDIATION, AND REPLACING SOIL AT THE LEAK SITE.
2017-09-29 08:50 | YES | NO | 20020028 | 2002-02-22 | 31555 | KINDER MORGAN CO2 CO. LP | YES | 2002-01-09 | 1240 | TX | YOAKUM |  | NO |  | NO | ALLRED STATION LOCATED APPROX 8 MILES NW OF DENVER CITY, TEXAS |  | NO DATA | OTHER | SAFETY RELIEF VALVE | 0 | OTHER | MAL-FUNCTION OF SAFETY RELIEF VALVE | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 0 | 0 | 0 | 6600 | 4294.126 | 8662.9866 | CARBON DIOXIDE | 3 | 3600 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | PAULA D. WILLIAMS | 9155747043 | SAFETY RELIEF VALVE MAL-FUNCTIONED FOR APPROXIMATELY 11 MINUTES RELEASING AN ESTIMATED 3,600 BBLS OF CARBON DIOXIDE. THE VALVE WAS TAKEN OUT OF SERVICE AND ANOTHER VALVE IN LINE WAS PUT INTO SERVICE PENDING REPAIRS TO THE FAULTY VALVE.
2017-09-29 08:50 | YES | YES | 20020029 | 2002-02-22 | 22855 | KOCH PIPELINE COMPANY, L.P. | NO | 2001-12-12 | 815 | TX | TARRANT | EULESS | NO |  | NO | TANK 451 AT EULESS TERMINAL12550 TRINITY BOULEVARD-EULESS, TEXAS 76040. |  | TANK FARM | TANK |  | 1990 | OTHER | ON-GOING INVESTIGATION AS OF 12-12-2001 | ALL OTHER CAUSES | MISCELLANEOUS | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | DATA NOT SPECIFIED |  | 0 | 0 | YES | YES | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | JAMES TREVINO | 3612425504 | TANK #451 WAS BEING PREPARED FOR CONFINED SPACE ENTRY AND CLEANUP BY CONTRACTOR. UPON OPENING MANWAYS EXPLOSION AND FIRE ENSUED. CAUSE OF INCIDENT UNDER INVESTIGATION. OSHA HAS BEEN ON-SITE.
2017-09-29 08:50 | YES | NO | 20020030 | 2002-02-27 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2001-12-29 | 1530 |  |  |  | NO | LAT:28 26.1 N/LONG:91 18. | NO |  | 589759 | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 396644.2953 | 800191.7546 | CRUDE OIL | 1 | 5 | 0 | NO | NO | 16 | 0.375 | 52000 | OTHER |  | 1440 | 300 | YES | 24 | 1740 | 0 | 1967 | EXTERNAL | Null | YES | GALVANIC |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132414381 | A DIVER WAS USING A WATERBLASTER TO REMOVE CONCRETE COATING FROM THE LINE AS PART OF AN ANODE RETROFIT PROJECT. A RELEASE OCCURRED WHEN CORROSION PITS WERE ENCOUNTERED.
2017-09-29 08:50 | YES | NO | 20020031 | 2002-03-01 | 31574 | GIANT PIPELINE CO | YES | 2002-01-12 | 1050 | UT | SAN JUAN |  | NO |  | NO | GIANT PIPELINE COMPANY'S ANETH STATION IN MONTEZUMA CREEK, UTAH. |  | TANK FARM | NO DATA |  | 1986 | MALFUNCTION OF CONTROL OR RELIEF EQUIPMENT |  | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | 0 | 0 | 0 | 0 | 0 | 0 | 5062 | 3293.4645 | 6644.2482 | CRUDE OIL | 1 | 100 | 80 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | ROY ARMENTA | 5056324009 | A PRESSURE RELIEF VALVE ON THE SCRAPER RECEIVER WAS NOT SEATING PROPERLY, WHICH ALLOWED INCOMING CRUDE OIL FROM THE GATHERING LINE TO OVERFILL AN ISOLATED STORAGE TANK.
2017-09-29 08:50 | YES | NO | 20020032 | 2002-03-01 | 4458 | ENRON PRODUCTS PIPELINE INC | NO | 2002-01-21 | 1815 | OK | WASHITA | CLINTON | NO |  | NO | S13 (SE/4 OF NE/4), T11N, R17W- SEE ATTACHED USGS QUAD MAP. |  | LINE PIPE | PIPE |  | 1949 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 130125.0295 | 262514.744 | CRUDE OIL | 1 | 600 | 200 | NO | NO | 10.75 | 0.365 | 24000 | WELDED |  | 640 | 100 | YES | 8 | 800 | 0 | 1949 | INTERNAL | Null | YES |  |  |  |  | Null |  |  | Null | Null | MICHAEL CRUMP | 7133451623 | LANDOWNER REPORTED A SMELL OF CRUDE OIL AT APPROXIMATELY 1815 HOURS ON 1/21/2002. INVESTIGATION REVEALED CRUDE OIL SPILLED ONTO ROW AND FLOWED INTO DRIED UP POND BED. NO TELEPHONIC REPORTS WERE MADE BECAUSE NO WATER WAS INVOLVED AND THE ESTIMATED COST WAS LESS THAN $50,000, OKLAHOMA CORPORATION COMMISSION, PIPELINE SAFETY, WAS NOTIFIED 0830 HOURS ON 1/22/2002 OF THE LEAK AND THE ESTIMATED COST WAS LESS THAN $50,000. SUBSEQUENT CLEANUP HAS REVEALED MORE EXTENSIVE DAMAGE THAN ORIGINALLY ESTIMATED AND THE REQUIREMENT TO SUBMIT DOT FORM 7000-1 PER 49 CFR 195.50.
2017-09-29 08:50 | NO | NO | 20020033 | 2002-03-04 | 31174 | EQUILON PIPELINE COMPANY LLC | YES | 2002-01-26 | 1420 | LA | PLACQUEMINES |  | NO |  | NO | GARDEN ISLAND 6IN. AT STATION 5 | 592311 | NO DATA | VALVE |  | 1936 | CORROSION |  | CORROSION | UNSPECIFIED CORROSION | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 32531.2574 | 65628.686 | CRUDE OIL |  | 3 | 0 | NO | NO | 0 |  | 0 |  |  | 0 | 0 | Null | 0 | 0 | 0 | 0 |  | Null | Null |  |  |  |  | Null |  |  | Null | Null | D.F. SHEAFF | 7132410783 | VALVE ON IDLED PIECE OF PIPE WAS FOUND WEEPING CRUDE.
2017-09-29 08:50 | NO | NO | 20020034 | 2002-03-04 | 3527 | DOW PIPELINE CO | YES | 2002-02-01 | 1900 | TX | CHAMBERS |  | NO |  | NO | MT. BELVIEW DOW PIPELINE OFFICE. 10142 FM 1942 MT BELVIEU TEXAS 77520. |  | PUMPING STATION | PIPE |  | 0 | FAILED WELD |  | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED WELD | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 162.6563 | 328.1434 | GASOLINE | 1 | 1 | 0 | NO | NO | 1 | 0.187 | 0 | WELDED |  | 2000 | 675 | YES | 8 | 4000 | 11 | 1995 |  | Null | YES |  |  |  |  | Null | ONE CALL |  | NO | NO |  |  | A LEAK OCCURRED IN THE PIPING AT THE P-1 PUMPS AT THE MT. BELVIEU PUMP STATION. THE EQUPIMENT WAS SHUT DOWN, INSPECTIONS REVEALED THAT THERE WAS A CRACK AT A WELD ON A PIECE OF PIPE NEAR THE PUMP.
2017-09-29 08:50 | NO | NO | 20020035 | 2002-03-18 | 4458 | ENRON PRODUCTS PIPELINE INC | NO | 2001-10-11 | 1345 | OK | WASHITA | CLINTON | NO |  | NO | S9 (S W/4), T11N R16W LAT LON 35 26.331 N - 098 54.264 W |  | LINE PIPE | PIPE |  | 0 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 61100 | 40391.6107 | 81486.1937 | CRUDE OIL | 1 | 25 | 2 | NO | NO | 10.75 | 0.365 | 24000 | WELDED |  | 640 | 100 | YES | 8 | 800 | 0 | 1949 | INTERNAL | Null | YES |  |  |  |  | Null |  |  | Null | Null | RONNY DAVENPORT | 7136466389 | AERIAL PATROL REPORTED OIL STAIN WHICH WAS INVESTIGATED FURTHER, REVEALIING CRUDE OIL RELEASE.
2017-09-29 08:50 | YES | NO | 20020036 | 2002-03-13 | 879 | CHEMOIL REFINING | NO | 2002-02-06 | 340 | CA | LONG BEACH | LOS ANGELES | NO |  | NO |  |  | LINE PIPE | PIPE |  | 1965 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 58556.2633 | 118131.6348 | FUEL OIL | 3 | 0 | 0 | NO | NO | 8 | 0.287 | 25000 | WELDED |  | 700 | 35 | YES | 4 | 1000 | 7 | 2000 | EXTERNAL | Null | YES | OTHER | DAMAGED COATING FROM UNKNOWN DIG | DAMAGE BY OTHERS |  | Null |  |  | Null | Null | RANDY TUREK | 5629011961 | PIPELINE LEAKED INTO STORM DRAIN.